## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 06-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-04-2025 | during | 06-04-2025 | during | 06-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 150 | 110 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 110 | 110 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 307 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 314 | 327 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 0 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16.5 | 0 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 12 | 13 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 0 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 0 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 500 | 584 | 584 | 584 | 584 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 450 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2881.5 | 2841 | 5236.9 | 5298.9 | 4690.3 | 4752.3
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 145 | 150 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 82 | 82 | 82 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 82 | 98 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 0 | 0 | 0 | 0 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 3.94 | 0 | 3.94 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 845 | 1000 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 5 | 0 | 6 | 1 | 6 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 421 | 422 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1566 | 1801 | 3425.66 | 3398.72 | 3425.66 | 3398.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 193 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 345 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 33 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 48 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 168 | 172 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 20 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 57 | 120 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 35 | 36 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 97 | 97 | 114 | 114 | 97 | 97 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 44 | 91 | 115 | 115 | 44 | 90 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1212 | 1374.2 | 2125.99 | 2060.99 | 1793.05 | 1793.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 05-04-2025 | during | 06-04-2025 | during | 06-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 189 | 196 | 210 | 210 | 210 | 210 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 134 | 95 | 200 | 200 | 125 | 125 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 55 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.69 | 0 | 43 | 0 | 43 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 443.69 | 358 | 646.4 | 601.5 | 561.4 | 516.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 37 | 35 | 35 | 35 | 33 | 33 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 39 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 143 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 82 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 390 | 380 | 380 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 120 | 220 | 130 | 130 | 130 | 130 | Due to GBC Problem
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 865 | 979 | 903 | 903 | 866 | 866
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 915 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Under Maintenance
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 92.82 | 0 | 93.5 | 0 | 93.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 383 | 512 | 1234.2 | 1234.2 | 618 | 618 | U#1 Under Reserve shut down
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1388.82 | 1427 | 3613.7 | 3520.2 | 2377.52 | 2284.02
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 10 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 116 | 124 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 871 | 1015 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 236 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1524.6 | 1495 | 2062.12 | 2061.12 | 2010.12 | 2009.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 209 | 190 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 178 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 176 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 398 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.15 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1086.46 | 1210.72 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 49.62 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2226.23 | 2168.72 | 3108.73 | 2942.53 | 2990.54 | 2824.34
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 57 | 55 | 60 | 60 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 162 | 167 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.2 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 160 | 0 | 167.52 | 0 | 167.52 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 499.2 | 450 | 675.92 | 472 | 675.92 | 472
System Total |  |  |  |  | 27566.2 | 28535.742 | 12607.04 | 12893.92 | 21798.42 | 21258.96 | 19390.51 | 18916.05
Forecast Scenario (06-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12900 |  | 0 |  | 12900
|  |  |  | 1:00 | 12700 |  | 0 |  | 12700
|  |  |  | 2:00 | 12350 |  | 0 |  | 12350
|  |  |  | 3:00 | 11980 |  | 0 |  | 11980
|  |  |  | 4:00 | 11680 |  | 0 |  | 11680
|  |  |  | 5:00 | 11320 |  | 0 |  | 11320
|  |  |  | 6:00 | 11020 |  | 0 |  | 11020
|  |  |  | 7:00 | 11150 |  | 0 |  | 11150
|  |  |  | 8:00 | 11400 |  | 0 |  | 11400
|  |  |  | 9:00 | 11800 |  | 0 |  | 11800
|  |  |  | 10:00 | 11900 |  | 0 |  | 11900
|  |  |  | 11:00 | 12300 |  | 0 |  | 12300
|  |  |  | 12:00 | 12900 |  | 0 |  | 12900
|  |  |  | 13:00 | 13400 |  | 0 |  | 13400
|  |  |  | 14:00 | 13500 |  | 0 |  | 13500
|  |  |  | 15:00 | 13600 |  | 0 |  | 13600
|  |  |  | 16:00 | 13300 |  | 0 |  | 13300
|  |  |  | 17:00 | 12900 |  | 0 |  | 12900
|  |  |  | 18:00 | 12000 |  | 0 |  | 12000
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13200 |  | 0 |  | 13200
|  |  |  | 19:30 | 13300 |  | 0 |  | 13300
|  |  |  | 20:00 | 13400 |  | 0 |  | 13400
|  |  |  | 21:00 | 13600 |  | 0 |  | 13600
|  |  |  | 22:00 | 13550 |  | 0 |  | 13550
|  |  |  | 23:00 | 13500 |  | 0 |  | 13500
Probable Maximum Temperature: |  |  | 33.00°C
Probable Maximum Demand at Day Peak: |  |  | 12900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 301.35 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:15 hrs on 06-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [8 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [8 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 05-04-2025 | [28 empty] | Date: | 05-04-2025 | [28 empty] | Date: | 05-04-2025 | [28 empty] | Date: | 05-04-2025 | [28 empty] | Date: | 05-04-2025 | [17 empty] | Date: | 05-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [17 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Keraniganj 100 MW PP (Powerpac) | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 75.240 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 400 | 278 | 520 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 90 | 9.5 | 12 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 96 | 0 | 0 | 46 | 7 | 36 | 418 | 0 | 0 | 0 | 0 | 18 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 185 | 0 | 355 | 0 | 48 | 140 | 32 | 29 | 45 | 165 | 14 | 20 | 98 | 30 | 26 | 0 | 0 | 0 | 0 | 205 | 36 | 38 | 0 | 152 | 21 | 0 | 85 | 28 | 0 | 17 | 0 | 0 | 75 | 95 | 201 | 0 | 0 | 12 | 7064.5 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1358 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 208 | 0 | 389 | 0 | 0 | 0 | 165 | 58 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1244 | 0 | 5888 | 12952.5 | 83.93
01:00 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 400 | 270 | 470 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 90 | 9.5 | 12 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 98 | 0 | 0 | 46 | 34 | 32 | 420 | 0 | 0 | 0 | 14 | 51 | 149 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 185 | 0 | 355 | 0 | 46 | 70 | 33 | 17 | 45 | 181 | 10 | 20 | 98 | 28 | 45 | 0 | 0 | 0 | 120 | 275 | 36 | 39 | 0 | 137 | 21 | 0 | 85 | 30 | 0 | 17 | 0 | 0 | 55 | 75 | 201 | 0 | 0 | 12 | 7052.5 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 0 | 1369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 209 | 0 | 339 | 0 | 0 | 0 | 164 | 58 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 108 | 220 | 0 | 0 | 1180 | 0 | 5646 | 12698.5 | 83.92
02:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 298 | 470 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 90 | 9.5 | 12 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 98 | 0 | 0 | 46 | 0 | 34 | 420 | 0 | 0 | 0 | 17 | 0 | 149 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 185 | 0 | 355 | 0 | 50 | 37 | 34 | 16 | 45 | 181 | 9 | 20 | 88 | 28 | 52 | 0 | 0 | 0 | 120 | 286 | 36 | 39 | 0 | 134 | 21 | 0 | 85 | 30 | 0 | 17 | 0 | 0 | 45 | 55 | 201 | 0 | 0 | 0 | 6884.5 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 207 | 0 | 352 | 0 | 0 | 0 | 161 | 58 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 220 | 0 | 0 | 1100 | 0 | 5417 | 12301.5 | 83.91
03:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 301 | 470 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 90 | 9.5 | 12 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 46 | 0 | 42 | 420 | 0 | 0 | 0 | 17 | 0 | 149 | 0 | 0 | 0 | 1040 | 0 | 51 | 0 | 185 | 0 | 355 | 0 | 51 | 52 | 34 | 17 | 50 | 181 | 0 | 20 | 70 | 26 | 52 | 0 | 0 | 0 | 120 | 287 | 36 | 39 | 0 | 137 | 21 | 0 | 85 | 30 | 0 | 17 | 0 | 0 | 45 | 55 | 201 | 0 | 0 | 0 | 6773.5 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 0 | 1103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 12 | 0 | 200 | 0 | 336 | 0 | 0 | 0 | 162 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 220 | 0 | 0 | 1089 | 0 | 5193 | 11966.5 | 83.9
04:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 295 | 470 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 70 | 9.5 | 12 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 46 | 0 | 42 | 420 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 960 | 0 | 51 | 0 | 177 | 0 | 355 | 0 | 52 | 103 | 31 | 17 | 50 | 182 | 0 | 20 | 52 | 26 | 40 | 0 | 0 | 0 | 120 | 288 | 36 | 39 | 0 | 135 | 21 | 0 | 85 | 30 | 0 | 17 | 0 | 0 | 24 | 45 | 199 | 0 | 0 | 0 | 6596.5 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 1102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 40 | 0 | 199 | 0 | 339 | 0 | 0 | 0 | 166 | 59 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 10 | 120 | 220 | 0 | 0 | 1087 | 0 | 5081 | 11677.5 | 83.89
05:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 298 | 470 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 9.5 | 12 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 42 | 420 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 910 | 0 | 51 | 0 | 147 | 0 | 320 | 0 | 52 | 194 | 31 | 17 | 50 | 181 | 0 | 20 | 52 | 26 | 0 | 0 | 0 | 0 | 120 | 288 | 36 | 39 | 0 | 135 | 21 | 0 | 85 | 30 | 0 | 17 | 0 | 0 | 24 | 45 | 195 | 0 | 0 | 0 | 6363.5 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 140 | 0 | 195 | 0 | 334 | 0 | 0 | 0 | 165 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 120 | 220 | 0 | 0 | 1014 | 0 | 5026 | 11389.5 | 83.88
06:00 | 0 | 0 | 0 | 110 | 0 | 150 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 296 | 400 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 9.5 | 12 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 42 | 420 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 147 | 0 | 320 | 0 | 51 | 193 | 31 | 17 | 50 | 181 | 0 | 20 | 52 | 24 | 0 | 1 | 0 | 0 | 120 | 288 | 36 | 39 | 0 | 133 | 21 | 0 | 85 | 30 | 0 | 17 | 0 | 0 | 28 | 45 | 188 | 0 | 0.21 | 0 | 6188.71 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 380 | 0 | 1007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 170 | 0 | 160 | 0 | 175 | 0 | 340 | 0 | 0.03 | 0 | 163 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 120 | 220 | 0 | 0 | 910 | 0 | 4823.6 | 11012.31 | 83.87
07:00 | 0 | 5 | 0 | 110 | 0 | 150 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 278 | 400 | 0 | 0 | 0 | 280 | 0 | 0 | 4 | 17 | 9.5 | 12 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 46 | 0 | 26 | 420 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 900 | 2 | 51 | 0 | 147 | 0 | 320 | 0 | 51 | 186 | 31 | 17 | 50 | 136 | 0 | 20 | 52 | 28 | 0 | 11 | 0 | 0 | 120 | 288 | 36 | 39 | 0 | 135 | 21 | 0 | 85 | 30 | 0 | 17 | 0 | 0 | 65 | 122 | 188 | 0 | 5.86 | 1 | 6258.36 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.23 | 385 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 6.98 | 170 | 0 | 160 | 0 | 172 | 0 | 327 | 0 | 0.57 | 0 | 165 | 58 | 0 | 4 | 0 | 0 | 0 | 0.7 | 19 | 0.08 | 0 | 200 | 10 | 108 | 220 | 0 | 0 | 890 | 0 | 4841.56 | 11099.92 | 83.86
08:00 | 0 | 17 | 0 | 110 | 0 | 150 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 290 | 400 | 0 | 0 | 0 | 280 | 0 | 0 | 12 | 26 | 9.5 | 12 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 2 | 46 | 0 | 2 | 422 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 905 | 6 | 51 | 0 | 143 | 0 | 320 | 0 | 50 | 182 | 28 | 17 | 50 | 136 | 5 | 20 | 52 | 28 | 0 | 30 | 0 | 0 | 120 | 298 | 36 | 39 | 0 | 132 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 75 | 124 | 186 | 1 | 16.02 | 12 | 6379.52 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.02 | 386 | 0 | 1011.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 17.87 | 170 | 0 | 160 | 0 | 170 | 0 | 321 | 0 | 1.44 | 0 | 164 | 58 | 0 | 10 | 10 | 0 | 0 | 2.2 | 54 | 0.22 | 0 | 200 | 9 | 108 | 220 | 0 | 0 | 891 | 0 | 4928.15 | 11307.67 | 83.85
09:00 | 0 | 35 | 8 | 110 | 0 | 150 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 21 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 271 | 300 | 0 | 0 | 0 | 323 | 0 | 0 | 19 | 52 | 16 | 12 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 3 | 46 | 0 | 2 | 421 | 0 | 0 | 0 | 8 | 0 | 148 | 0 | 0 | 0 | 840 | 13 | 51 | 0 | 143 | 0 | 355 | 0 | 49 | 220 | 27 | 32 | 50 | 136 | 9 | 17 | 40 | 28 | 0 | 48 | 0 | 0 | 120 | 356 | 36 | 39 | 0 | 132 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 75 | 135 | 198 | 1 | 26.16 | 12 | 6619.16 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.39 | 384 | 0 | 1010.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 29.33 | 170 | 0 | 160 | 0 | 184 | 0 | 320 | 0 | 2.49 | 0 | 158 | 58 | 35 | 17 | 70 | 0 | 0 | 3.6 | 96 | 0.31 | 0 | 163 | 9 | 108 | 220 | 0 | 0 | 800 | 0 | 4979.96 | 11599.12 | 83.84
10:00 | 0 | 35 | 16 | 110 | 0 | 150 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 299 | 400 | 0 | 0 | 0 | 318 | 0 | 0 | 26 | 70 | 17.5 | 12 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 3 | 46 | 0 | 2 | 420 | 0 | 0 | 0 | 8 | 0 | 145 | 0 | 0 | 0 | 805 | 14 | 43 | 0 | 143 | 0 | 347 | 0 | 48 | 209 | 30 | 38 | 50 | 68 | 9 | 19 | 17 | 26 | 0 | 44 | 0 | 0 | 120 | 390 | 36 | 38 | 0 | 134 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 68 | 136 | 194 | 1 | 24.03 | 12 | 6682.53 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.86 | 383 | 0 | 944.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 39.94 | 193 | 0 | 204 | 0 | 206 | 0 | 377 | 0 | 3.39 | 0 | 157 | 58 | 35 | 25 | 49 | 0 | 0 | 5 | 131 | 0.55 | 0 | 150 | 9 | 108 | 220 | 0 | 0 | 700 | 0 | 5058.29 | 11740.82 | 83.83
11:00 | 0 | 35 | 24 | 110 | 0 | 150 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 298 | 450 | 0 | 0 | 0 | 314 | 0 | 0 | 28 | 70 | 17.5 | 12 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 3 | 40 | 0 | 5 | 420 | 0 | 0 | 0 | 8 | 0 | 145 | 0 | 0 | 0 | 805 | 18 | 43 | 0 | 168 | 0 | 347 | 0 | 45 | 204 | 30 | 34 | 50 | 72 | 9 | 20 | 55 | 28 | 0 | 62 | 0 | 0 | 120 | 388 | 35 | 39 | 0 | 134 | 21 | 0 | 81 | 30 | 0 | 17 | 0 | 0 | 67 | 135 | 191 | 2 | 40.84 | 12 | 6843.34 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.89 | 382 | 0 | 917.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 49.01 | 212 | 0 | 206 | 0 | 205 | 0 | 414 | 0 | 4.13 | 0 | 162 | 58 | 35 | 29 | 49 | 0 | 0 | 5.8 | 160 | 0.59 | 0 | 200 | 9 | 116 | 220 | 0 | 0 | 705 | 0 | 5232.17 | 12075.51 | 83.82
12:00 | 0 | 35 | 24 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 297 | 450 | 0 | 0 | 0 | 314 | 0 | 0 | 30 | 108 | 16.5 | 12 | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 82 | 0 | 0 | 40 | 0 | 2 | 421 | 0 | 0 | 0 | 8 | 0 | 145 | 0 | 0 | 0 | 845 | 18 | 51 | 0 | 168 | 0 | 345 | 0 | 47 | 193 | 30 | 44 | 50 | 57 | 9 | 20 | 97 | 35 | 0 | 66 | 0 | 0 | 120 | 366 | 37 | 39 | 0 | 155 | 21 | 0 | 80 | 30 | 0 | 17 | 0 | 0 | 67 | 134 | 189 | 2 | 39.69 | 12 | 6968.19 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.82 | 383 | 0 | 1086.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 49.62 | 209 | 0 | 194 | 0 | 190 | 0 | 398 | 0 | 4.15 | 0 | 162 | 57 | 35 | 30 | 49 | 0 | 0 | 6.2 | 160 | 0.6 | 0 | 307 | 10 | 116 | 220 | 0 | 0 | 871 | 0 | 5638.85 | 12607.04 | 83.81
13:00 | 0 | 35 | 24 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 17 | 40 | 0 | 23 | 450 | 299 | 450 | 0 | 0 | 0 | 314 | 0 | 0 | 30 | 108 | 16.5 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 82 | 0 | 2 | 40 | 0 | 2 | 421 | 0 | 0 | 0 | 8 | 0 | 147 | 0 | 0 | 0 | 920 | 18 | 51 | 0 | 170 | 0 | 346 | 0 | 46 | 193 | 29 | 34 | 50 | 21 | 18 | 19 | 97 | 36 | 52.2 | 59 | 0 | 0 | 120 | 387 | 37 | 39 | 0 | 152 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 67 | 125 | 188 | 2 | 41.98 | 12 | 7142.68 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.71 | 425 | 0 | 1183.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 51.85 | 208 | 0 | 180 | 0 | 181 | 0 | 382 | 0 | 4.37 | 0 | 160 | 57 | 35 | 30 | 110 | 0 | 0 | 6 | 160 | 0.64 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1033 | 0 | 5958.06 | 13100.74 | 83.8
14:00 | 0 | 35 | 24 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 35 | 135 | 0 | 30 | 450 | 289 | 300 | 0 | 0 | 0 | 314 | 0 | 0 | 24 | 108 | 18.5 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 87 | 15 | 3 | 40 | 0 | 2 | 421 | 0 | 0 | 0 | 8 | 0 | 147 | 0 | 0 | 0 | 855 | 12 | 51 | 0 | 180 | 0 | 340 | 0 | 44 | 193 | 30 | 34 | 50 | 20 | 22 | 19 | 97 | 36 | 52.2 | 49 | 8 | 0 | 120 | 361 | 37 | 38 | 0 | 151 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 67 | 123 | 188 | 2 | 35.22 | 12 | 6918.92 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.53 | 512 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 45.12 | 206 | 0 | 189 | 0 | 190 | 0 | 382 | 0 | 3.83 | 0 | 161 | 57 | 70 | 27 | 110 | 0 | 0 | 5.3 | 140 | 0.54 | 0 | 307 | 10 | 110 | 220 | 0 | 0 | 1170 | 0 | 6361.32 | 13280.24 | 83.79
15:00 | 0 | 17 | 8 | 110 | 0 | 150 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 55 | 144 | 0 | 50 | 450 | 286 | 300 | 0 | 40 | 0 | 313 | 0 | 0 | 19 | 125 | 13 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 11 | 34 | 0 | 0 | 48 | 38 | 2 | 40 | 0 | 2 | 421 | 0 | 0 | 0 | 8 | 0 | 146 | 0 | 0 | 0 | 833 | 9 | 51 | 0 | 180 | 0 | 340 | 0 | 44 | 195 | 31 | 34 | 50 | 27 | 27 | 18 | 97 | 32 | 52.2 | 46 | 21 | 0 | 120 | 379 | 35 | 38 | 0 | 150 | 22 | 0 | 78 | 30 | 0 | 17 | 0 | 0 | 67 | 123 | 185 | 1 | 26.22 | 12 | 6991.42 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.51 | 555 | 0 | 1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 35.47 | 206 | 0 | 139 | 0 | 188 | 0 | 394 | 0 | 3.17 | 0 | 165 | 55 | 115 | 21 | 112 | 0 | 0 | 4 | 108 | 0.17 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1225 | 0 | 6364.32 | 13355.74 | 83.78
16:00 | 0 | 17 | 8 | 110 | 0 | 120 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 55 | 144 | 0 | 61 | 450 | 281 | 300 | 0 | 55 | 0 | 313 | 0 | 0 | 4 | 125 | 13.5 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 48 | 12 | 1 | 40 | 0 | 2 | 421 | 0 | 0 | 0 | 8 | 0 | 147 | 0 | 0 | 0 | 900 | 5 | 51 | 0 | 180 | 0 | 350 | 0 | 43 | 183 | 31 | 34 | 67 | 46 | 27 | 18 | 97 | 38 | 52.2 | 26 | 21 | 0 | 120 | 351 | 35 | 38 | 0 | 151 | 22 | 0 | 77 | 30 | 0 | 17 | 0 | 0 | 67 | 123 | 186 | 1 | 18.45 | 12 | 6986.15 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.31 | 557 | 0 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 23.33 | 206 | 0 | 140 | 0 | 180 | 0 | 371 | 0 | 2.11 | 0 | 167 | 55 | 35 | 13 | 34 | 0 | 0 | 2.5 | 61 | 0.27 | 0 | 307 | 10 | 108 | 220 | 0 | 0 | 1227 | 0 | 6051.52 | 13037.67 | 83.77
17:00 | 0 | 17 | 8 | 110 | 0 | 110 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 35 | 144 | 0 | 67 | 450 | 282 | 300 | 0 | 0 | 0 | 315 | 0 | 0 | 1 | 108 | 13.5 | 7 | 0 | 350 | 0 | 0 | 0 | 0 | 4 | 34 | 0 | 0 | 48 | 12 | 1 | 40 | 0 | 8 | 420 | 0 | 0 | 0 | 8 | 0 | 148 | 0 | 0 | 0 | 905 | 1 | 51 | 0 | 180 | 0 | 354 | 0 | 43 | 184 | 31 | 34 | 64 | 35 | 28 | 20 | 97 | 38 | 34 | 10 | 23 | 0 | 170 | 350 | 35 | 38 | 0 | 141 | 22 | 0 | 78 | 30 | 0 | 17 | 0 | 0 | 76 | 123 | 186 | 0 | 6.42 | 12 | 6891.92 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.3 | 506 | 0 | 1370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8.49 | 206 | 0 | 155 | 0 | 178 | 0 | 372 | 0 | 0.72 | 0 | 167 | 55 | 35 | 6 | 34 | 0 | 0 | 1 | 28 | 0.1 | 0 | 250 | 10 | 100 | 220 | 0 | 0 | 1120 | 0 | 5772.61 | 12664.53 | 83.76
18:00 | 0 | 17 | 8 | 110 | 0 | 110 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 35 | 144 | 0 | 83 | 300 | 289 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 108 | 11.5 | 7 | 0 | 300 | 0 | 0 | 0 | 0 | 1 | 34 | 2 | 0 | 48 | 12 | 0 | 40 | 0 | 9 | 420 | 0 | 0 | 0 | 8 | 0 | 101 | 0 | 0 | 0 | 900 | 0 | 51 | 6 | 153 | 0 | 280 | 0 | 48 | 187 | 31 | 76 | 50 | 61 | 31 | 20 | 97 | 28 | 34 | 0 | 19 | 0 | 220 | 301 | 35 | 38 | 0 | 131 | 22 | 0 | 81 | 20 | 0 | 17 | 0 | 0 | 75 | 95 | 188 | 0 | 0.67 | 12 | 6403.17 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 475 | 0 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 150 | 0 | 156 | 0 | 154 | 0 | 321 | 0 | 0.07 | 0 | 166 | 55 | 35 | 1 | 34 | 0 | 0 | 0.1 | 2 | 0.01 | 0 | 150 | 9 | 92 | 180 | 0 | 0 | 1000 | 0 | 5100.63 | 11503.8 | 83.75
19:00 | 0 | 17 | 0 | 110 | 0 | 110 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 54 | 0 | 79 | 450 | 246 | 400 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 108 | 0 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 98 | 12 | 0 | 40 | 0 | 16 | 420 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 1010 | 0 | 51 | 12 | 180 | 0 | 355 | 0 | 51 | 181 | 33 | 89 | 50 | 91 | 33 | 20 | 97 | 36 | 52.2 | 0 | 19 | 0 | 220 | 350 | 35 | 37 | 0 | 145 | 23 | 0 | 81 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 192 | 0 | 0 | 12 | 7152.2 | 869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 1312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 150 | 0 | 170 | 0 | 159 | 0 | 309 | 0 | 0 | 0 | 168 | 55 | 110 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 10 | 108 | 220 | 0 | 0 | 1042 | 0 | 5623 | 12775.2 | 83.74
19:30 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 50 | 350 | 295 | 400 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 97 | 12 | 0 | 40 | 0 | 22 | 420 | 0 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 980 | 0 | 51 | 0 | 180 | 0 | 300 | 0 | 51 | 203 | 34 | 90 | 50 | 120 | 28 | 20 | 97 | 34 | 52.2 | 0 | 19 | 0 | 220 | 387 | 35 | 37 | 0 | 132 | 23 | 0 | 81 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 191 | 0 | 0 | 12 | 6808.2 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 1208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 171 | 0 | 168 | 0 | 353 | 0 | 0 | 0 | 167 | 55 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 100 | 180 | 0 | 0 | 1000 | 0 | 5376 | 12184.2
20:00 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 305 | 400 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 97 | 12 | 0 | 40 | 0 | 22 | 421 | 0 | 0 | 0 | 8 | 0 | 148 | 0 | 0 | 0 | 980 | 0 | 51 | 0 | 180 | 0 | 300 | 0 | 50 | 207 | 34 | 90 | 50 | 120 | 28 | 20 | 97 | 36 | 52.2 | 0 | 19 | 0 | 220 | 391 | 35 | 37 | 0 | 143 | 20 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 191 | 0 | 0 | 12 | 6864.2 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 0 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 174 | 0 | 172 | 0 | 372 | 0 | 0 | 0 | 168 | 55 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 124 | 130 | 0 | 0 | 998 | 0 | 5376 | 12240.2 | 83.73
21:00 | 0 | 0 | 0 | 110 | 0 | 110 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 307 | 583 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 70 | 0 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 98 | 12 | 0 | 40 | 0 | 20 | 422 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 172 | 0 | 355 | 0 | 48 | 201 | 33 | 91 | 50 | 120 | 28 | 20 | 97 | 36 | 52.2 | 0 | 20 | 0 | 220 | 390 | 35 | 39 | 0 | 143 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 196 | 0 | 0 | 12 | 7353.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 0 | 1210.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 178 | 0 | 176 | 0 | 414 | 0 | 0 | 0 | 167 | 55 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 10 | 124 | 110 | 0 | 0 | 1015 | 0 | 5540.72 | 12893.92 | 83.72
22:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 302 | 583 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 90 | 0 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 98 | 12 | 0 | 40 | 0 | 30 | 361 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1103 | 0 | 51 | 0 | 173 | 0 | 355 | 0 | 49 | 189 | 34 | 71 | 50 | 135 | 28 | 20 | 97 | 36 | 52.2 | 0 | 20 | 0 | 220 | 358 | 35 | 38 | 0 | 153 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 178 | 0 | 0 | 12 | 7260.2 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 0 | 1319.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 183 | 0 | 178 | 0 | 395 | 0 | 0 | 0 | 168 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 114 | 110 | 0 | 0 | 1132 | 0 | 5886.29 | 13146.49 | 83.71
23:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 304 | 583 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 90 | 15 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 98 | 12 | 0 | 40 | 0 | 32 | 215 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 1165 | 0 | 51 | 0 | 173 | 0 | 355 | 0 | 50 | 212 | 34 | 45 | 51 | 146 | 28 | 20 | 80 | 36 | 52.2 | 0 | 20 | 0 | 220 | 300 | 35 | 38 | 0 | 154 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 182 | 0 | 0 | 12 | 7130.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1312.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 192 | 0 | 187 | 0 | 414 | 0 | 0 | 0 | 168 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 129 | 110 | 0 | 0 | 1244 | 0 | 6104.16 | 13234.36 | 83.7
Total KWH | 0 | 316800 | 162720 | 2602600 | 0 | 2917219 | 0 | 0 | 9338400 | 0 | 0 | 2880 | 0 | 0 | 596304 | 216000 | 0 | 0 | 239880 | 912960 | 0 | 410880 | 9547000 | 7018095 | 10429091 | 0 | 110392 | 0 | 7496121 | 0 | 0 | 196522 | 1952400 | 252600 | 254520 | 0 | 10335909 | 0 | 0 | 0 | 0 | 43680 | 478049 | 26016 | 0 | 1795200 | 181440 | 20379 | 995640 | 56873 | 434400 | 9614545.45 | 0 | 0 | 0 | 234909 | 105382 | 3506211 | 0 | 0 | 0 | 22985452 | 113940 | 1078332 | 23418 | 4014545 | 0 | 8507700 | 0 | 1152960 | 4182000 | 751320 | 959040 | 1211990 | 2757120 | 376320 | 463310 | 1881000 | 742080 | 743938 | 454773 | 202916 | 0 | 3550300 | 8324000 | 850000 | 899760 | 0 | 3411736 | 518808 | 0 | 1968960 | 700896 | 0 | 408000 | 0 | 0 | 1449600 | 2400000 | 4490880 | 12050 | 283250 | 233280 | 164905691.45 | 21879264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 676080 | 11549090 | 0 | 28505455 | 0 | 0 | 0 | 38016 | 0 | 19872 | 0 | 10158 | 0 | 590260 | 23846 | 357752 | 4784000 | 0 | 3611282 | 0 | 4663609 | 0 | 8766763 | 0 | 29940 | 0 | 4039000 | 1284654 | 1137962 | 214916 | 1531440 | 0 | 0 | 42609.24 | 1131840 | 3982.5 | 2112 | 5891000 | 237087 | 2718000 | 4813820 | 0 | 0 | 25476363.64 | 0 | 134030173.38 | 298935864.83

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 05-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12607.04 | MW | 12:00 Hr. | Energy Generated |  |  | 298.9359 |  | MKWHr.
| Day Peak Demand |  |  | 12607.04 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 12893.92 | MW | 21:00 Hr. | Energy Demand |  |  | 298.9359 |  | MKWHr.
| Evening Peak Demand |  |  | 12893.92 | MW | 21:00 Hr. | Maximum Temperature |  |  | 37.2 |  | °C
| Minimum Generation of the Day |  |  | 11012.31 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1068.49 |  | MMCFD
| Maximum Generation of the Day |  |  | 13355.74 | MW | 15:00 Hr. | Production Cost per KWHr |  |  | 5.809 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 60.1916 | 0 | 4.9212 | 0 | 0 | 0.19652 | 0 | 0 | 65.3093 | Gas | 140.2122 | Gas | 458712776.79
| Chattogram Zone |  |  | 3.9406 | 32.6 | 2.8779 | 0 | 0.99564 | 0.13432 | 0 | 0.04368 | 40.5921 | Coal | 80.8401 | Coal | 575859585.5342
| Cumilla Zone |  |  | 21.3622 | 0 | 6.9438 | 0 | 0 | 0.45477 | 0.74208 | 0 | 29.5028 | HFO | 21.5891 | HFO | 365715337.19
| Mymensingh Zone |  |  | 4.4909 | 0 | 4.0829 | 0 | 0 | 0.2953 | 0 | 0 | 8.8691 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 20.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.6325 | Hydro | 0.99564 | Hydro | 99564
| Khulna Zone |  |  | 0 | 11.5491 | 0 | 0 | 0 | 0.67608 | 21.8793 | 0 | 34.1044 | Solar | 4.1283 | Solar | 67102697.1814
| Barishal Zone |  |  | 7.7689 | 31.3674 | 0.002112 | 0 | 0 | 0.0039825 | 0 | 0 | 39.1424 | Import | 51.1268 | Import | 268378092.36
| Rajshahi Zone |  |  | 21.8257 | 0 | 0.091892 | 0 | 0 | 0.97795 | 28.5055 | 0 | 51.401 | Wind | 0.04368 | Wind | 639475.2
| Rangpur Zone |  |  | 0 | 5.3237 | 2.6694 | 0 | 0 | 1.3894 | 0 | 0 | 9.3824
| Total |  |  | 140.2122 | 80.8401 | 21.5891 | 0 | 0.99564 | 4.1283 | 51.1268 | 0.04368 | 298.9359
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 458712776.79 |  | Hydro | 99564
|  |  |  | Coal | 575859585.5342 |  | Solar | 67102697.1814
|  |  |  | HFO | 365715337.19 |  | Import | 268378092.36
|  |  |  | HSD | 0 |  | Wind | 639475.2
[5 empty] | Total: | 173,65,07,528 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 107054.54 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8793 | Peak Hr Flow | 915.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7172581.85 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.5055 | Peak Hr Flow | 1210.72 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 290 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.74208 | Peak Hr Flow | 36.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 782 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.1268 | Peak Hr Flow | 2161.72 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3079
|  |  |  | Chattogram |  | 0 |  | 1356
|  |  |  | Cumilla |  | 0 |  | 1323
|  |  |  | Mymensingh |  | 0 |  | 1232
|  |  |  | Sylhet |  | 0 |  | 567
|  |  |  | Khulna |  | 0 |  | 1767
|  |  |  | Barishal |  | 0 |  | 490
|  |  |  | Rajshahi |  | 0 |  | 1617
|  |  |  | Rangpur |  | 0 |  | 922
|  |  |  | Total |  | 0 |  | 12353
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:17 | 09:13 | Satkhira 132/33kV S/S Transformer-2 (T-2) LT Forced S/D | [7 empty] | 50.0MW load
interrup.
| 08:19 | 09:13 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Forced S/D
| 09:03 | 11:41 | Hasnabad 230/132kV S/S AUTO TR-1 LT Scheduled S/D Due to Over temperature .
| 09:03 | 11:41 | Hasnabad 230/132kV S/S AUTO TR-1 HT Scheduled S/D Due to Over temperature.
| 09:55 |  | Bibiyana-III 400 MW CCPP, FGMO is OFF with remarks:-
|  | 10:03 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT is restored.
| 10:09 | 12:11 | Gopalganj(N)-Madaripur 132kV Ckt-1 Forced S/D from Gopalganj 400/132kV end.
| 11:14 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:-
| 11:17 | 12:25 | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to Kumarkhali Feeder Red Hot Maintenance by | [7 empty] | 46.0MW load
|  |  | PBS | [7 empty] | interrup.
| 11:18 | 12:24 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Kumarkhali Feeder Red Hot Maintenance by | [7 empty] | 46.0MW load
|  |  | PBS | [7 empty] | interrup.
|  | 11:41 | Dhamrai 132/33kV S/S Transformer-1 LT is restored.
|  | 11:41 | Dhamrai 132/33kV S/S Transformer-1 HT is restored.
| 12:00 |  | Day peak Generation is 12603 MW
|  | 12:59 | Bashundhara-Rampura 132 kV Ckt-2 is restored.
| 17:32 | 21:26 | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing Directional over current relay trip.
relays.
| 17:42 | 17:59 | Kabirpur - Manikganj 132kV Ckt-1 Tripped from Kabirpur 132/33kV end showing Distance
relay operated, Zone-1, Y&B phase. relays.
| 18:02 | 18:48 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing Distance relay
operated, Zone-1, C-phase. relays. and from Tongi 230/132/33kV end showing Distance
relay, Zone 1, B-Phase relays Due to Bad whether
|  | 18:36 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 HT is restored.
|  | 18:44 | Cantonment 132/33kV S/S Transformer-1 (T-1) HT is restored.
|  | 18:50 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 LT is restored.
| 18:51 | 18:55 | Kamrangirchar-Keraniganj 132kV Ckt Tripped from Keranigonj 230/132/33kV end showing | [7 empty] | 75.0MW load
|  |  | distance relay . zone -02 relays Due to heavy wind blowing weather. | [7 empty] | interrup.
Keranigonj
230/132/33kV end
| 18:54 | 19:05 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Lock out relay 1, Lock out relay -2 relays
Due to For 33 kv agla feeder.
| 18:54 | 20:09 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing Distance relay
operated, Zone-1, C-phase. relays. and from Tongi 230/132/33kV end showing Distance
relay relays Due to Bad weather
|  | 19:05 | Nawabganj 132/33kV S/S TR-2 LT is restored.
| 19:58 | 20:07 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance relay
relays Due to Bad weather
| 20:04 |  | Bhola Natun Biddut BD LTD GT-11 was shut down due to an offline water wash.
| 20:08 | 23:00 | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing SOTF,Z1,AR
Block,VT fail relays. and from Ghorashal 230kV end showing Distance Protection Relay
relays.
| 20:12 | 22:38 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance relay
relays Due to Bad weather and from Kabirpur 132/33kV end showing Distance relay operated,
Zone-1. relays.
| 21:00 |  | Evening Peak Gen. 12893 MW
| 21:24 |  | Ghorashal GT-4 was shutdown.
| 21:24 |  | Ghorasal Repowered CCPP Unit-4 Shutdown
| 05:00 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is OFF with remarks:-
| 06:00 |  | Minimum generation 11418 MW
| 07:10 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 LT Scheduled S/D Due to Painting
work.
| 07:16 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 HT Scheduled S/D Due to Painting
work.
| 07:22 |  | Cantonment 132/33kV S/S Transformer-1 (T-1) HT Scheduled S/D Due to Painting work.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 05-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 110 | 2917219 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 110 | 2602600 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9338400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9547000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 307 | 7018095 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 327 | 7496121 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 2880 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 216000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 239880 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 110392 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 252600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 13 | 254520 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 162720 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 596304 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 316800 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 410880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 912960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 196522 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 0 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 10335909 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 10429091 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1952400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2841 | 65309293
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 234909 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 113940 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 995640 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3506211 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 105382 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 26016 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 478049 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 98 | 1795200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 434400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 20379 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 56873 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 181440 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 22985452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 43680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 422 | 9614545.45 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1801 | 40592116.45
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 201 | 4182000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8507700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 751320 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1152960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 172 | 4014545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1078332 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 23418 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 20 | 202916 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1211990 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2757120 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 36 | 742080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 743938 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 463310 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 97 | 1881000 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 376320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 959040 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 454773 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1374.2 | 29502762
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 196 | 4490880 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 2400000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 55 | 1449600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 283250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 233280 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 358 | 8869060
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 35 | 850000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 899760 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 143 | 3411736 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 700896 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1968960 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 408000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 518808 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | shutdown due to maintenance work on gas field
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 8324000 | FGMO Active
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 220 | 3550300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 979 | 20632460
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 21879264 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 676080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 512 | 11549090 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1427 | 34104434
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 2112 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 237087 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 124 | 2718000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1015 | 25476363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 4813820 | GT-11 Shutdown under Offline water wash
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 236 | 5891000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3982.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1495 | 39142365.14
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 10158 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 190 | 4784000 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 178 | 3611282 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 176 | 4663609 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8766763 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 23846 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 19872 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 38016 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1210.72 | 28505455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 357752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 590260 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2168.72 | 51400953
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1284654 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 167 | 4039000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1531440 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42609.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1137962 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 214916 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1131840 | -
Rangpur Area Total |  |  |  |  | 950 | 450 | 9382421.24
Eastern Grid Total |  |  |  |  | 16921.242 | 7353.2 | 164905691.45
Western Grid Total |  |  |  |  | 11614.5 | 5540.72 | 134030173.38
National Grid Total |  |  |  |  | 28535.742 | 12893.92 | 298935864.83
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 05-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7557.47 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4796.7 | MW
i) Dhaka area |  |  | 3079.47 |  | MW | i) Khulna area |  |  |  | 1767 | MW
ii) Chattogram area |  |  | 1356 |  | MW | ii) Barishal area |  |  |  | 490.5 | MW
iii) Cumilla area |  |  | 1323 |  | MW | iii) Rajshahi area |  |  |  | 1617.2 | MW
iv) Mymensingh area |  |  | 1232 |  | MW | iv) Rangpur area |  |  |  | 922 | MW
v) Sylhet area |  |  | 567 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12354.17 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 14 | 11:00 | 67 | Jaldhaka | 84 | 19:00 | 133 | Payra | 34 | 00:00
2 | AKSML | 118.2 | 02:00 | 68 | Jamalpur | 139 | 19:30 | 134 | Postogola | 41 | 18:30
3 | Aftabnagar | 30 | 13:00 | 69 | Jashore | 154 | 19:00 | 135 | Purbachal | 28 | 13:00
4 | Agargaon | 102 | 18:30 | 70 | Jhenaidah | 150 | 19:00 | 136 | Purbasadipur | 128 | 13:00
5 | Agrabad | 78 | 19:00 | 71 | Joydebpur | 96 | 14:00 | 137 | Rahanpur | 32 | 21:00
6 | Amnura | 57 | 19:00 | 72 | Joypurhat | 74 | 21:00 | 138 | Rahim | 20 | 17:00
7 | Ashuganj | 81 | 00:00 | 73 | Juldah | 16 | 00:00 | 139 | Rajbari | 82 | 19:00
8 | BSRM | 169 | 04:00 | 74 | KSRM | 20 | 09:00 | 140 | Rajendrapur | 107 | 16:00
9 | Bagerhat | 89 | 22:00 | 75 | Kabirpur | 163 | 16:00 | 141 | Rajshahi | 104 | 21:00
10 | Bajitpur | 49 | 00:00 | 76 | Kachua | 91 | 19:00 | 142 | Rajshahi-230 | 93 | 21:00
11 | Bakulia | 79 | 23:00 | 77 | Kallyanpur | 93 | 23:00 | 143 | Ramganj | 120 | 20:00
12 | Banani | 41.2 | 12:00 | 78 | Kalurghat | 32 | 15:00 | 144 | Rampur | 39 | 23:00
13 | Bangabhaban | 6 | 10:00 | 79 | Kamrangirchar | 38.77 | 18:30 | 145 | Rangamati | 17 | 18:30
14 | Barapukuria | 73 | 19:30 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 147 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kasba | 42 | 20:00 | 147 | Ruppur | 5.4 | 11:00
16 | Barishal | 108 | 21:00 | 82 | Kazla | 73 | 23:00 | 148 | SSM | 0 | 00:00
17 | Barishal-230 | 112 | 00:00 | 83 | Keranigonj | 61 | 00:00 | 149 | Saidpur | 115 | 14:00
18 | Baroaulia | 62 | 15:00 | 84 | Khagrachori | 34 | 19:00 | 150 | Satkhira | 138 | 20:00
19 | Baroirhat | 61 | 18:30 | 85 | Khulna | 81 | 13:00 | 151 | Satmasjid | 86 | 18:30
20 | Bashundhara | 150 | 16:00 | 86 | Khulshi | 158 | 22:00 | 152 | Savar | 143 | 15:00
21 | BashundharaCement | 6 | 15:00 | 87 | Kishoreganj | 140 | 00:00 | 153 | SevenRings | 15.42 | 15:00
22 | Beanibazar | 74 | 19:00 | 88 | Kodda | 198 | 16:00 | 154 | ShahCement | 10 | 07:00
23 | Benapole | 76 | 22:00 | 89 | Kulaura | 46 | 20:00 | 155 | Shahjadpur | 83 | 19:00
24 | Bhaluka | 147 | 15:00 | 90 | Kurigram | 72 | 18:30 | 156 | Shahjibazar | 126 | 22:00
25 | Bhandaria | 58 | 00:00 | 91 | Kushtia | 138 | 19:00 | 157 | Shahmirpur | 59 | 00:00
26 | Bhangura | 45 | 19:30 | 92 | Lalbag | 20 | 13:00 | 158 | Shariatpur | 91 | 00:00
27 | Bheramara(GK) | 61 | 19:00 | 93 | Lalmonirhat | 69 | 19:00 | 159 | Sherpur | 168 | 18:30
28 | Bhulta | 133 | 23:00 | 94 | MI_Cement | 1.9 | 18:00 | 160 | Shikalbaha | 22 | 00:00
29 | Bog-Sherpur | 64 | 19:00 | 95 | Madanganj | 43 | 22:00 | 161 | Shitalakhya | 61.7 | 13:00
30 | Bogura | 166 | 19:30 | 96 | Madaripur | 123 | 23:00 | 162 | Sholosohor | 36 | 22:00
31 | Borhanuddin | 93 | 00:00 | 97 | Madartek | 75.63 | 18:30 | 163 | Shyampur | 78 | 11:00
32 | Brahmanbaria | 141 | 00:00 | 98 | Madunaghat | 51 | 18:00 | 164 | Siddhirganj | 82 | 14:00
33 | Cantonment | 82 | 18:30 | 99 | Magura | 76 | 19:00 | 165 | Sirajganj | 108 | 19:00
34 | Chandpur | 75 | 00:00 | 100 | Mahasthangarh | 82 | 20:00 | 166 | Sonargaon | 65 | 13:00
35 | Chandraghona | 37 | 19:00 | 101 | Manikganj | 118 | 00:00 | 167 | Sreemongol | 84 | 20:00
36 | Chapai | 70 | 23:00 | 102 | Maniknagar | 55 | 18:30 | 168 | Sreepur | 88 | 14:00
37 | Charsaidpur | 18 | 17:00 | 103 | Matarbari | 51 | 19:00 | 169 | Srinagar | 47.24 | 00:00
38 | Chauddagram | 80 | 18:30 | 104 | Matuail | 38 | 00:00 | 170 | Sunamganj | 50 | 00:00
39 | Chhatak | 34 | 18:30 | 105 | Millgate | 54 | 15:00 | 171 | Sylhet | 43 | 19:00
40 | Chowmuhani | 234 | 20:00 | 106 | Mirpur | 111 | 18:00 | 172 | Sylhet-132 | 114 | 18:30
41 | Chuadanga | 114 | 19:00 | 107 | Mirsorai | 8 | 19:00 | 173 | TK | 23 | 19:00
42 | Coxsbazar | 138 | 19:00 | 108 | Mirzapur | 45 | 21:00 | 174 | Tangail | 182 | 18:30
43 | Cumilla(N) | 185 | 19:00 | 109 | Mithapukur | 70 | 19:00 | 175 | Thakurgaon | 108 | 19:00
44 | Cumilla(S) | 154 | 18:30 | 110 | Modern | N/A | N/A | 176 | Tongi | 90 | 12:00
45 | Daudkandi | 152 | 18:30 | 111 | Mogbazar | 105.7 | 15:00 | 177 | Ullahpara | 44 | 19:00
46 | Dhaka | 30 | 12:00 | 112 | Mongla | 39 | 11:00 | 178 | Ullon | 40 | 18:00
47 | Dhamrai | 92 | 15:00 | 113 | Motijheel | 30 | 18:30 | 179 | Uttara | 76 | 18:00
48 | Dhanmondi | 104.7 | 13:00 | 114 | Muktagacha | 42 | 18:30 | 180 | UttaraNew | 38 | 00:00
49 | Dohazari | 118 | 19:00 | 115 | Munshiganj | 110 | 00:00 | 181 | Zigatola | 59 | 18:30
50 | Faridpur | 162 | 19:00 | 116 | Muradnagar | 32 | 20:00
51 | Fatullah | 50 | 15:00 | 117 | Mymensingh | 228 | 19:00
52 | Fenchuganj | 39 | 00:00 | 118 | Naogaon | 142 | 21:00
53 | Feni | 118 | 19:00 | 119 | Narail | 63 | 19:00
54 | GPH | 100 | 08:00 | 120 | Narinda | 45 | 13:00
55 | Ghatail | 96 | 18:30 | 121 | Narshingdi | 138 | 00:00
56 | Ghorashal | 14 | 03:00 | 122 | Natore | 171 | 21:00
57 | Ghorashal-230 | 68 | 16:00 | 123 | Nawabganj | 56 | 00:00
58 | Goalpara | 30 | 00:00 | 124 | Netrakona | 137 | 18:30
59 | Gollamari | 76 | 23:00 | 125 | New | 49.2 | 15:00
60 | Gopalganj | 116 | 19:00 | 126 | Niamatpur | 124 | 22:00
61 | Gulshan | 94 | 13:00 | 127 | Noapara | 44 | 19:00
62 | Halishahar | 59 | 15:00 | 128 | PHP | 3 | 08:00
63 | HaripurSBU | 100 | 15:00 | 129 | Pabna | 115 | 19:00
64 | Hasnabad | 64 | 18:30 | 130 | Palashbari | 136 | 19:00
65 | Hathazari | 81 | 18:30 | 131 | Panchagarh | 57 | 19:00
66 | Ishurdi | 69 | 19:30 | 132 | Patuakhali | 83 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 05-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12952.5 | 0 |  | 12952.5
1:00 | 12698.5 | 0 |  | 12698.5
2:00 | 12301.5 | 0 |  | 12301.5
3:00 | 11966.5 | 0 |  | 11966.5
4:00 | 11677.5 | 0 |  | 11677.5
5:00 | 11389.5 | 0 |  | 11389.5
6:00 | 11012.31 | 0 |  | 11012.31
7:00 | 11099.92 | 0 |  | 11099.92
8:00 | 11307.67 | 0 |  | 11307.67
9:00 | 11599.12 | 0 |  | 11599.12
10:00 | 11740.82 | 0 |  | 11740.82
11:00 | 12075.51 | 0 |  | 12075.51
12:00 | 12607.04 | 0 |  | 12607.04
13:00 | 13100.74 | 0 |  | 13100.74
14:00 | 13280.24 | 0 |  | 13280.24
15:00 | 13355.74 | 0 |  | 13355.74
16:00 | 13037.67 | 0 |  | 13037.67
17:00 | 12664.53 | 0 |  | 12664.53
18:00 | 11503.8 | 0 |  | 11503.8
19:00 | 12775.2 | 0 |  | 12775.2
19:30 | 12184.2 | 0 |  | 12184.2
20:00 | 12240.2 | 0 |  | 12240.2
21:00 | 12893.92 | 0 |  | 12893.92
22:00 | 13146.49 | 0 |  | 13146.49
23:00 | 13234.36 | 0 |  | 13234.36
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 05-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7064.5 | 5888 | 12952.5 | DAILY GENERATION CURVE
00:30 | 7058.5 | 5767 | 12825.5
01:00 | 7052.5 | 5646 | 12698.5 | 05-04-2025
01:30 | 6968.5 | 5531.5 | 12500
02:00 | 6884.5 | 5417 | 12301.5
02:30 | 6829 | 5305 | 12134
03:00 | 6773.5 | 5193 | 11966.5
03:30 | 6685 | 5137 | 11822
04:00 | 6596.5 | 5081 | 11677.5
04:30 | 6480 | 5053.5 | 11533.5
05:00 | 6363.5 | 5026 | 11389.5
05:30 | 6276.105 | 4924.8 | 11200.905
06:00 | 6188.71 | 4823.6 | 11012.31
06:30 | 6223.535 | 4832.58 | 11056.115
07:00 | 6258.36 | 4841.56 | 11099.92
07:30 | 6318.94 | 4884.855 | 11203.795
08:00 | 6379.52 | 4928.15 | 11307.67
08:30 | 6499.34 | 4954.055 | 11453.395
09:00 | 6619.16 | 4979.96 | 11599.12
09:30 | 6650.845 | 5019.125 | 11669.97
10:00 | 6682.53 | 5058.29 | 11740.82
10:30 | 6762.935 | 5145.23 | 11908.165
11:00 | 6843.34 | 5232.17 | 12075.51
11:30 | 6905.765 | 5435.51 | 12341.275
12:00 | 6968.19 | 5638.85 | 12607.04
12:30 | 7055.435 | 5798.455 | 12853.89
13:00 | 7142.68 | 5958.06 | 13100.74
13:30 | 7030.8 | 6159.69 | 13190.49
14:00 | 6918.92 | 6361.32 | 13280.24
14:30 | 6955.17 | 6362.82 | 13317.99
15:00 | 6991.42 | 6364.32 | 13355.74
15:30 | 6988.785 | 6207.92 | 13196.705
16:00 | 6986.15 | 6051.52 | 13037.67
16:30 | 6939.035 | 5912.065 | 12851.1
17:00 | 6891.92 | 5772.61 | 12664.53
17:30 | 6647.545 | 5436.62 | 12084.165
18:00 | 6403.17 | 5100.63 | 11503.8
18:30 | 6777.685 | 5361.815 | 12139.5
19:00 | 7152.2 | 5623 | 12775.2
19:30 | 6808.2 | 5376 | 12184.2
20:00 | 6864.2 | 5376 | 12240.2
20:30 | 7108.7 | 5458.36 | 12567.06 |  | Executive Engineer
21:00 | 7353.2 | 5540.72 | 12893.92 |  | Network Operation Division
21:30 | 7306.7 | 5713.505 | 13020.205
22:00 | 7260.2 | 5886.29 | 13146.49
22:30 | 7195.2 | 5995.225 | 13190.425
23:00 | 7130.2 | 6104.16 | 13234.36

## En-Curve
QF-LDC-12
Date | 05-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3150 | 2517.5 | 899 | 0 | 30 | 1358 | 46 | 4034 | 0 | 124 | 794 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3168.5 | 2478 | 899.5 | 0 | 29 | 1363.5 | 46 | 3905.5 | 0 | 124 | 811.5 | 0 | 0 | 0 | 0 | 05-04-2025
01:00 | 3187 | 2438.5 | 900 | 0 | 28 | 1369 | 46 | 3777 | 0 | 124 | 829 | 0 | 0 | 0 | 0
01:30 | 3209 | 2454 | 900 | 0 | 28 | 1317.5 | 46 | 3688 | 0 | 112.5 | 745 | 0 | 0 | 0 | 0 | Energy Generated | 298.9359 |  | MKWHr
02:00 | 3231 | 2469.5 | 900 | 0 | 28 | 1266 | 46 | 3599 | 0 | 101 | 661 | 0 | 0 | 0 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3236.5 | 2457 | 900 | 0 | 27 | 1184.5 | 46 | 3551.5 | 0 | 95.5 | 636 | 0 | 0 | 0 | 0 | Total Energy Requirement | 298.9359 |  | MKWHr
03:00 | 3242 | 2444.5 | 900 | 0 | 26 | 1103 | 46 | 3504 | 0 | 90 | 611 | 0 | 0 | 0 | 0
03:30 | 3264 | 2437 | 901 | 0 | 26 | 1102.5 | 46 | 3404.5 | 0 | 80 | 561 | 0 | 0 | 0 | 0
04:00 | 3286 | 2429.5 | 902 | 0 | 26 | 1102 | 46 | 3305 | 0 | 70 | 511 | 0 | 0 | 0 | 0
04:30 | 3306 | 2415.5 | 906.5 | 0 | 26 | 1105.5 | 46 | 3226.5 | 0 | 52.5 | 449 | 0 | 0 | 0 | 0
05:00 | 3326 | 2401.5 | 911 | 0 | 26 | 1109 | 46 | 3148 | 0 | 35 | 387 | 0 | 0 | 0 | 0
05:30 | 3314.5 | 2329 | 911 | 0 | 25 | 1058 | 46 | 3089.5 | 0.905 | 38 | 389 | 0 | 0 | 0 | 0
06:00 | 3303 | 2256.5 | 911 | 0 | 24 | 1007 | 46 | 3031 | 1.81 | 41 | 391 | 0 | 0 | 0 | 0
06:30 | 3283 | 2241 | 911.5 | 0 | 26 | 1006.5 | 46 | 3024.5 | 42.115 | 55.5 | 420 | 0 | 0 | 0 | 0
07:00 | 3263 | 2225.5 | 912 | 0 | 28 | 1006 | 46 | 3018 | 82.42 | 70 | 449 | 0 | 0 | 0 | 0
07:30 | 3264.5 | 2213.5 | 903.5 | 0 | 28 | 1008.7 | 46 | 3022 | 152.095 | 97.5 | 468 | 0 | 0 | 0 | 0
08:00 | 3266 | 2201.5 | 895 | 0 | 28 | 1011.4 | 46 | 3026 | 221.77 | 125 | 487 | 0 | 0 | 0 | 0
08:30 | 3395.5 | 2163.25 | 880 | 0 | 28 | 1011.12 | 46 | 2925 | 298.525 | 141 | 565 | 0 | 0 | 0 | 0
09:00 | 3525 | 2125 | 865 | 0 | 28 | 1010.84 | 46 | 2824 | 375.28 | 157 | 643 | 0 | 0 | 0 | 0
09:30 | 3601 | 2212.25 | 889 | 0 | 27 | 977.695 | 46 | 2748.5 | 419.525 | 155 | 594 | 0 | 0 | 0 | 0
10:00 | 3677 | 2299.5 | 913 | 0 | 26 | 944.55 | 46 | 2673 | 463.77 | 153 | 545 | 0 | 0 | 0 | 0
10:30 | 3701 | 2361.5 | 913 | 0 | 27 | 931.15 | 43 | 2702.5 | 523.015 | 141 | 565 | 0 | 0 | 0 | 0
11:00 | 3725 | 2423.5 | 913 | 0 | 28 | 917.75 | 40 | 2732 | 582.26 | 129 | 585 | 0 | 0 | 0 | 0
11:30 | 3684 | 2436.5 | 913 | 0 | 31.5 | 1002.105 | 40 | 2889 | 588.17 | 148 | 606.5 | 0 | 0 | 2.5 | 0
12:00 | 3643 | 2449.5 | 913 | 0 | 35 | 1086.46 | 40 | 3046 | 594.08 | 167 | 628 | 0 | 0 | 5 | 0
12:30 | 3636 | 2446 | 913 | 0 | 35.5 | 1134.975 | 40 | 3184.5 | 590.315 | 167 | 701.6 | 0 | 0 | 5 | 0
13:00 | 3629 | 2442.5 | 913 | 0 | 36 | 1183.49 | 40 | 3323 | 586.55 | 167 | 775.2 | 0 | 0 | 5 | 0
13:30 | 3616 | 2317 | 914 | 0 | 36 | 1278.745 | 40 | 3403 | 545.045 | 171 | 862.7 | 0 | 0 | 7 | 0
14:00 | 3603 | 2191.5 | 915 | 0 | 36 | 1374 | 40 | 3483 | 503.54 | 175 | 950.2 | 0 | 0 | 9 | 0
14:30 | 3595 | 2186.25 | 915 | 0 | 34 | 1371 | 40 | 3522 | 438.54 | 190 | 1016.2 | 0 | 0 | 10 | 0
15:00 | 3587 | 2181 | 915 | 0 | 32 | 1368 | 40 | 3561 | 373.54 | 205 | 1082.2 | 0 | 0 | 11 | 0
15:30 | 3545.5 | 2178.25 | 915 | 0 | 35 | 1362 | 40 | 3597.5 | 296.255 | 205 | 1012.7 | 0 | 0 | 9.5 | 0
16:00 | 3504 | 2175.5 | 915 | 0 | 38 | 1356 | 40 | 3634 | 218.97 | 205 | 943.2 | 0 | 0 | 8 | 0
16:30 | 3529.5 | 2175.5 | 915 | 0 | 38 | 1363 | 40 | 3528.5 | 159 | 197.5 | 899.1 | 0 | 0 | 6 | 0
17:00 | 3555 | 2175.5 | 915 | 0 | 38 | 1370 | 40 | 3423 | 99.03 | 190 | 855 | 0 | 0 | 4 | 0
17:30 | 3340.5 | 2043.5 | 915 | 0 | 33 | 1287 | 40 | 3294.5 | 52.165 | 189 | 887 | 0 | 0 | 2.5 | 0
18:00 | 3126 | 1911.5 | 915 | 0 | 28 | 1204 | 40 | 3166 | 5.3 | 188 | 919 | 0 | 0 | 1 | 0
18:30 | 3291.5 | 2105.75 | 892 | 0 | 32 | 1258 | 40 | 3334.5 | 2.65 | 201.5 | 981.1 | 0 | 0 | 0.5 | 0
19:00 | 3457 | 2300 | 869 | 0 | 36 | 1312 | 40 | 3503 | 0 | 215 | 1043.2 | 0 | 0 | 0 | 0
19:30 | 3378 | 2195 | 868 | 0 | 34 | 1208 | 40 | 3332 | 0 | 168 | 961.2 | 0 | 0 | 0 | 0
20:00 | 3484 | 2213 | 868 | 0 | 36 | 1215 | 40 | 3334 | 0 | 140 | 910.2 | 0 | 0 | 0 | 0
20:30 | 3615 | 2357.5 | 891.5 | 0 | 36 | 1212.86 | 40 | 3370.5 | 0 | 140.5 | 903.2 | 0 | 0 | 0 | 0
21:00 | 3746 | 2502 | 915 | 0 | 36 | 1210.72 | 40 | 3407 | 0 | 141 | 896.2 | 0 | 0 | 0 | 0
21:30 | 3663.5 | 2510 | 914.5 | 0 | 36 | 1265.005 | 40 | 3546.5 | 0 | 151 | 893.7 | 0 | 0 | 0 | 0
22:00 | 3581 | 2518 | 914 | 0 | 36 | 1319.29 | 40 | 3686 | 0 | 161 | 891.2 | 0 | 0 | 0 | 0
22:30 | 3589.5 | 2529 | 914.5 | 0 | 36 | 1315.725 | 40 | 3729.5 | 0 | 161 | 875.2 | 0 | 0 | 0 | 0
23:00 | 3598 | 2540 | 915 | 0 | 36 | 1312.16 | 40 | 3773 | 0 | 161 | 859.2 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 05-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 07:00 | 392 | 14:00 | Payra | 419 | 07:00 | 409 | 23:00
Ashuganj | 408 | 6:00 | 389 | 14:00 | Rahanpur | 404 | 04:00 | 391 | 18:30
Bhulta | 406 | 19:30 | 388 | 15:00 | Rampal | 409 | 09:00 | 390 | 23:00
Bibiana | 390 | 07:00 | 380 | 13:00
BIPTC | 399 | 06:00 | 388 | 15:00
Bogura | 391 | 04:00 | 377 | 19:00
Gopalganj | 409 | 07:00 | 393 | 23:00
Kaliakoir | 379 | 07:00 | 367 | 18:30
Madunaghat | 403 | 07:00 | 397 | 00:00
Meghnaghat | 405 | 07:00 | 396 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 19:30 | 229 | 13:00 | Keranigonj | 235 | 07:00 | 226 | 15:00
AKSML | 235 | 07:00 | 227 | 00:00 | Khulna(S) | 232 | 06:00 | 218 | 23:00
Aminbazar | 239 | 18:30 | 230 | 14:00 | Madunaghat | 237 | 08:00 | 231 | 23:00
Ashuganj | 236 | 18:00 | 226 | 15:00 | Madunaghat-400 | 237 | 07:00 | 232 | 14:00
Ashuganj-400 | 236 | 18:00 | 226 | 15:00 | Maniknagar | 233 | 08:00 | 224 | 15:00
Baghabari | 234 | 06:00 | 225 | 18:00 | Meghnaghat | 241 | 08:00 | 232 | 15:00
Barapukuria | 223 | 04:00 | 218 | 13:00 | Meghnaghat-400 | 236 | 19:30 | 227 | 15:00
Barapukuria-230 | 223 | 04:00 | 218 | 13:00 | Mirsorai | 235 | 18:00 | 226 | 00:00
Barishal | 238 | 07:00 | 227 | 23:00 | Rajshahi | 233 | 04:00 | 218 | 20:00
Bheramara | 235 | 03:00 | 221 | 13:00 | Rampal | 234 | 09:00 | 219 | 23:00
Bhulta | 234 | 19:30 | 223 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 06:00 | 210 | 23:00 | Rampura | 232 | 07:00 | 222 | 15:00
BIPTC | 238 | 04:00 | 220 | 14:00 | Shikalbaha | 234 | 08:00 | 227 | 23:00
Bogura | 237 | 03:00 | 227 | 19:00 | Shyampur | 236 | 19:30 | 226 | 15:00
Bogura-400 | 237 | 04:00 | 228 | 19:00 | Siddhirganj | 236 | 19:30 | 226 | 15:00
Borhanuddin | 242 | 07:00 | 233 | 23:00 | Sirajgonj | 241 | 04:00 | 236 | 00:00
BSRM | 235 | 18:00 | 225 | 00:00 | Sreepur | 232 | 06:00 | 225 | 00:00
Cumilla(N) | 229 | 18:00 | 220 | 00:00 | Tongi | 235 | 18:00 | 224 | 13:00
Faridpur | 236 | 08:00 | 224 | 23:00
Fenchuganj | 227 | 07:00 | 219 | 00:00
Ghorashal | 238 | 19:30 | 230 | 08:00
Ghorashal-230 | 233 | 07:00 | 223 | 15:00
Gopalganj | 237 | 06:00 | 225 | 23:00
GPH | 235 | 18:00 | 228 | 23:00
Haripur | 233 | 06:00 | 225 | 15:00
Hasnabad | 235 | 18:00 | 227 | 14:00
Hathazari | 237 | 06:00 | 231 | 14:00
Ishurdi | 236 | 03:00 | 224 | 13:00
Jhenaidah | 230 | 09:00 | 210 | 20:00
Kaliakoir | 238 | 18:00 | 225 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 19:30 | 126 | 15:00 | Madunaghat | 135 | 06:00 | 131 | 23:00
Agargaon | 137 | 06:00 | 131 | 15:00 | Magura | 131 | 05:00 | 119 | 19:00
Agrabad | 134 | 07:00 | 130 | 13:00 | Mahasthangarh | 131 | 04:00 | 122 | 19:00
AKS | 132 | 03:00 | 128 | 12:00 | Manikganj | 132 | 07:00 | 124 | 00:00
Aminbazar | 138 | 18:30 | 130 | 22:00 | Maniknagar | 135 | 19:30 | 129 | 15:00
Amnura | 134 | 02:00 | 125 | 00:00 | Matarbari | 118 | 17:00 | 111 | 19:00
Ashuganj | 140 | 18:00 | 133 | 00:00 | Matuail | 138 | 19:30 | 131.3 | 15:00
Bagerhat | 131 | 07:00 | 116 | 23:00 | Millgate | 140 | 19:00 | 129 | 15:00
Bajitpur | 129 | 07:00 | 124 | 00:00 | Mirpur | 137 | 19:00 | 129 | 23:00
Bakulia | 136 | 18:00 | 131 | 13:00 | Mirzapur | 132 | 07:00 | 124 | 14:00
Banani | 133 | 19:30 | 126 | 14:00 | Mithapukur | 130 | 02:00 | 120 | 19:00
Bangabhaban | 135 | 19:30 | 128 | 15:00 | MI_Cement | 138.5 | 19:30 | 131.1 | 15:00
Barapukuria | 137 | 04:00 | 131 | 08:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 07:00 | 129 | 23:00 | Mogbazar | 135 | 07:00 | 126 | 15:00
Barishal | 133 | 10:00 | 125 | 00:00 | Mongla | 133 | 09:00 | 118 | 23:00
Barishal-230 | 133 | 07:00 | 124 | 22:00 | Motijheel | 135 | 19:30 | 128 | 15:00
Baroaulia | 135 | 18:00 | 131 | 03:00 | Muktagacha | 134 | 00:00 | 123 | 19:00
Baroirhat | 125 | 18:00 | 119 | 15:00 | Munshiganj | 138 | 19:30 | 131 | 13:00
Bashundhara | 140 | 19:00 | 125 | 13:00 | Muradnagar | 130 | 18:00 | 122 | 12:00
BashundharaCement | 138 | 00:00 | 132 | 01:00 | Mymensingh | 138 | 07:00 | 110 | 14:00
Beanibazar | 127 | 07:00 | 118 | 00:00 | Naogaon | 127 | 04:00 | 117 | 19:30
Benapole | 128 | 07:00 | 116 | 00:00 | Narail | 130 | 09:00 | 119 | 19:00
Bhaluka | 126 | 18:00 | 119 | 14:00 | Narinda | 135 | 19:30 | 129 | 15:00
Bhandaria | 127 | 08:00 | 114 | 23:00 | Narshingdi | 136 | 19:30 | 123 | 00:00
Bhangura | 132 | 18:00 | 126 | 19:00 | Natore | 131 | 09:00 | 122 | 19:00
Bheramara | 133 | 03:00 | 125 | 13:00 | Nawabganj | 137 | 19:30 | 129 | 13:00
Bheramara(GK) | 133 | 06:00 | 125 | 19:00 | Netrakona | 120 | 06:00 | 107 | 13:00
Bhulta | 134 | 19:30 | 128 | 00:00 | New | 141 | 19:00 | 130 | 12:00
Bog-Sherpur | 132 | 04:00 | 123 | 19:00 | Niamatpur | 134 | 05:00 | 130 | 14:00
Bogura | 132 | 04:00 | 126 | 18:30 | Noapara | 136 | 07:00 | 121 | 23:00
Bogura-230 | 133 | 03:00 | 126 | 19:00 | Pabna | 134 | 09:00 | 125 | 19:30
Brahmanbaria | 131 | 09:00 | 124 | 23:00 | Palashbari | 125 | 05:00 | 117 | 19:00
Cantonment | 138 | 19:00 | 131 | 15:00 | Panchagarh | 139 | 21:00 | 119 | 12:00
Chandpur | 127 | 09:00 | 114 | 15:00 | Patuakhali | 135 | 06:00 | 131 | 01:00
Chandraghona | 135 | 06:00 | 131 | 23:00 | Payra | 137 | 06:00 | 134 | 00:00
Chapai | 132 | 07:00 | 126 | 13:00 | PHP | 126 | 18:00 | 117 | 23:00
Charsaidpur | 138 | 20:00 | 131 | 15:00 | Postogola | 140 | 19:00 | 134 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 127 | 18:00 | 118 | 00:00 | Purbachal | 139 | 19:00 | 125 | 15:00
Chhatak | 130 | 19:30 | 116 | 00:00 | Purbasadipur | 132 | 21:00 | 116 | 13:00
Chowmuhani | 120 | 18:00 | 110 | 01:00 | Rahanpur | 136 | 11:00 | 132 | 18:30
Chuadanga | 127 | 04:00 | 116 | 19:00 | Rahanpur-400 | 137 | 03:00 | 133 | 00:00
Coxsbazar | 120 | 17:00 | 112 | 02:00 | Rahim | 137 | 20:00 | 131 | 15:00
Cumilla(N) | 131 | 18:00 | 124 | 12:00 | Rajbari | 131 | 09:00 | 123 | 00:00
Cumilla(S) | 134 | 01:00 | 121 | 12:00 | Rajendrapur | 139 | 19:00 | 122 | 15:00
Daudkandi | 131 | 20:00 | 121 | 12:00 | Rajshahi | 133 | 06:00 | 124 | 20:00
Dhaka | 134 | 07:00 | 126 | 13:00 | Rajshahi-230 | 139 | 12:00 | 118 | 14:00
Dhamrai | 139 | 19:00 | 128 | 15:00 | Ramganj | 121 | 09:00 | 109 | 15:00
Dhanmondi | 138 | 19:30 | 132 | 15:00 | Rampur | 133 | 05:00 | 130 | 13:00
Dohazari | 130 | 05:00 | 125 | 00:00 | Rampura | 134 | 07:00 | 126 | 14:00
Faridpur | 132 | 09:00 | 125 | 00:00 | Rangamati | 134 | 07:00 | 130 | 13:00
Fatullah | 138 | 06:00 | 133 | 14:00 | Rangpur | 129 | 03:00 | 120 | 19:00
Fenchuganj | 133 | 09:00 | 127 | 00:00 | Ruppur | 164 | 08:00 | 127 | 19:30
Feni | 126 | 18:00 | 118 | 23:00 | Saidpur | 132 | 04:00 | 120 | 08:00
Ghatail | 131 | 00:00 | 122 | 13:00 | Satkhira | 132 | 09:00 | 117 | 00:00
Ghorashal | 140 | 17:00 | 134 | 15:00 | Satmasjid | 138 | 07:00 | 131 | 14:00
Goalpara | 135 | 09:00 | 124 | 23:00 | Savar | 138 | 18:00 | 128 | 12:00
Gollamari | 135 | 06:00 | 125 | 23:00 | SevenRings | 141 | 18:00 | 133 | 15:00
Gopalganj | 136 | 09:00 | 126 | 23:00 | ShahCement | 138 | 20:00 | 131 | 15:00
Gopalganj-400 | 138 | 06:00 | 131 | 23:00 | Shahjadpur | 135 | 03:00 | 130 | 19:00
Gulshan | 133 | 07:00 | 125 | 15:00 | Shahjibazar | 131 | 07:00 | 124 | 22:00
Halishahar | 134 | 06:00 | 131 | 12:00 | Shahmirpur | 135 | 02:00 | 132 | 13:00
Haripur | 139 | 19:30 | 132 | 12:00 | Shariatpur | 135 | 07:00 | 126 | 23:00
HaripurSBU | 139 | 19:30 | 132 | 00:00 | Sherpur | 136 | 07:00 | 116 | 19:30
Hasnabad | 140 | 19:30 | 134 | 13:00 | Shikalbaha | 125 | 18:30 | 120 | 13:00
Hathazari | 137 | 05:00 | 132 | 13:00 | Shikalbaha-230 | 137 | 18:00 | 132 | 23:00
Ishurdi | 136 | 03:00 | 128 | 19:30 | Shitalakhya | 138.5 | 19:30 | 131.1 | 15:00
Jaldhaka | 131 | 04:00 | 116 | 08:00 | Sholosohor | 135 | 06:00 | 132 | 12:00
Jamalpur | 138 | 07:00 | 120 | 13:00 | Shyampur | 137 | 00:00 | 137 | 00:00
Jashore | 130 | 09:00 | 119 | 00:00 | Shyampur-230 | 138 | 07:00 | 132 | 15:00
Jhenaidah | 133 | 07:00 | 121 | 19:00 | Siddhirganj | 138 | 19:30 | 132 | 12:00
Jhenaidah-230 | 132 | 09:00 | 122 | 00:00 | Sirajganj | 130 | 05:00 | 123 | 19:00
Joydebpur | 140 | 18:00 | 128 | 15:00 | Sonargaon | 137 | 20:00 | 128 | 14:00
Joypurhat | 123 | 06:00 | 114 | 19:00 | Sreemongol | 131 | 08:00 | 123 | 00:00
Juldah | 135 | 17:00 | 133 | 00:00 | Sreepur | 129 | 03:00 | 123 | 14:00
Kabirpur | 139 | 19:00 | 127 | 15:00 | Srinagar | 136 | 19:00 | 129 | 14:00
Kachua | 126 | 09:00 | 116 | 12:00 | SSM | 138 | 11:00 | 133 | 00:00
Kaliakoir | 140 | 18:00 | 129 | 14:00 | Sunamganj | 126 | 09:00 | 117 | 00:00
Kallyanpur | 138 | 18:30 | 130 | 12:00 | Sylhet | 128 | 07:00 | 120 | 00:00
Kalurghat | 136 | 08:00 | 131 | 17:00 | Sylhet-132 | 129 | 07:00 | 122 | 00:00
Kamrangirchar | 137 | 19:30 | 130 | 13:00 | Tangail | 130 | 07:00 | 122 | 13:00
Kaptai | 134 | 16:00 | 122 | 19:00 | Thakurgaon | 137 | 21:00 | 117 | 12:00
Kasba | 129 | 18:00 | 121 | 14:00 | TK | 135 | 04:00 | 133 | 00:00
Kazla | 134 | 07:00 | 129 | 14:00 | Tongi | 140 | 18:00 | 132 | 13:00
Keranigonj | 137 | 19:30 | 129 | 15:00 | Ullahpara | 133 | 05:00 | 125 | 19:00
Khagrachori | 133 | 08:00 | 129 | 13:00 | Ullon | 134 | 07:00 | 126 | 15:00
Khulna | 134 | 09:00 | 122 | 23:00 | Uttara | 139 | 19:00 | 128 | 13:00
Khulna(S) | 136 | 09:00 | 125 | 23:00 | UttaraNew | 138 | 18:30 | 130 | 00:00
Khulshi | 133 | 18:00 | 129 | 12:00 | Zigatola | 137 | 19:30 | 130 | 13:00
Kishoreganj | 126 | 06:00 | 118 | 14:00
Kodda | 139 | 18:00 | 125 | 15:00
KSRM | 135 | 06:00 | 132 | 01:00
Kulaura | 132 | 09:00 | 126 | 00:00
Kurigram | 130 | 01:00 | 118 | 16:00
Kushtia | 132 | 04:00 | 123 | 13:00
Lalbag | 137 | 19:00 | 130 | 15:00
Lalmonirhat | 128 | 00:00 | 116 | 19:00
Madanganj | 137 | 19:30 | 131 | 16:00
Madaripur | 137 | 08:00 | 128 | 23:00
Madartek | 134 | 19:30 | 127 | 14:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division