## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-04-2025 | during | 07-04-2025 | during | 07-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 260 | 260 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 406 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 295 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 19 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 321 | 325 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23.5 | 25 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 22 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 79 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 34 | 34 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 20 | 101 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 120 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 1 | 35 | 55 | 55 | 35 | 35 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 400 | 584 | 584 | 584 | 584 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 500 | 500 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2821.5 | 3394 | 5269.9 | 5331.9 | 4333.12 | 4395.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 15 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 149 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 68 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 80 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 4 | 101 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 96 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 12 | 25 | 5 | 28 | 5 | 28 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.94 | 0 | 3.94 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 16 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1124 | 1222 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 160 | 156 | 155 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1593 | 2107 | 2987.66 | 3005.72 | 2987.66 | 3005.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 187 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 346 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 22 | 30 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 49 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 173 | 182 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 2 | 125 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 2 | 28 | 47 | 47 | 20 | 28 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 80 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 139 | 200 | 200 | 34 | 34 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 17.75 | 24.5 | 17.75 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 80 | 114 | 114 | 80 | 80 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 12 | 27 | 113 | 113 | 9 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 90 | 115 | 115 | 44 | 90 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 65 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1235.2 | 1528.2 | 2114.24 | 2060.99 | 1571.3 | 1591.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-04-2025 | during | 07-04-2025 | during | 07-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 108 | 97 | 210 | 210 | 210 | 210 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 107 | 163 | 200 | 200 | 170 | 170 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 66 | 105 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.66 | 0 | 45 | 0 | 45 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 331.66 | 412 | 648.4 | 601.5 | 608.4 | 561.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 37 | 36 | 36 | 36 | 33 | 33 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 136 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 21 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 354 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 220 | 220 | 230 | 230 | 230 | 230 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 986 | 936 | 1011 | 1011 | 973 | 973
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 916 | 868 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 93.05 | 0 | 94 | 0 | 94 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 760 | 1055 | 1234.2 | 1234.2 | 1200 | 1200 | Rev-01
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1769.05 | 1958 | 3614.2 | 3520.2 | 3065.01 | 2971.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 10 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1150 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.63 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1697.63 | 1737 | 2062.12 | 2061.12 | 2050.12 | 2049.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 38 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 189 | 159 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 153 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 167 | 153 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 324 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 110 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.63 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1323.05 | 1361.86 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 53.51 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 97 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2429.19 | 2530.86 | 3108.53 | 2942.53 | 3055.74 | 2889.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 57 | 55 | 0 | 0 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 164 | 160 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 70 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 155 | 0 | 160.7 | 0 | 160.7 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 518.7 | 443 | 599.3 | 402 | 654.3 | 457
System Total |  |  |  |  | 27566.2 | 28535.742 | 13381.93 | 15046.06 | 21415.35 | 20936.96 | 19298.65 | 18893.26
Forecast Scenario (07-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13550 |  | 0 |  | 13550
|  |  |  | 1:00 | 13410 |  | 0 |  | 13410
|  |  |  | 2:00 | 12850 |  | 0 |  | 12850
|  |  |  | 3:00 | 12500 |  | 0 |  | 12500
|  |  |  | 4:00 | 12310 |  | 0 |  | 12310
|  |  |  | 5:00 | 12100 |  | 0 |  | 12100
|  |  |  | 6:00 | 11650 |  | 0 |  | 11650
|  |  |  | 7:00 | 11830 |  | 0 |  | 11830
|  |  |  | 8:00 | 12010 |  | 0 |  | 12010
|  |  |  | 9:00 | 12490 |  | 0 |  | 12490
|  |  |  | 10:00 | 12770 |  | 0 |  | 12770
|  |  |  | 11:00 | 13130 |  | 0 |  | 13130
|  |  |  | 12:00 | 13580 |  | 0 |  | 13580
|  |  |  | 13:00 | 14080 |  | 0 |  | 14080
|  |  |  | 14:00 | 14350 |  | 0 |  | 14350
|  |  |  | 15:00 | 14380 |  | 0 |  | 14380
|  |  |  | 16:00 | 14320 |  | 0 |  | 14320
|  |  |  | 17:00 | 13930 |  | 0 |  | 13930
|  |  |  | 18:00 | 13360 |  | 0 |  | 13360
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 15220 |  | 0 |  | 15220
|  |  |  | 19:30 | 15270 |  | 0 |  | 15270
|  |  |  | 20:00 | 15280 |  | 0 |  | 15280
|  |  |  | 21:00 | 14960 |  | 0 |  | 14960
|  |  |  | 22:00 | 14900 |  | 0 |  | 14900
|  |  |  | 23:00 | 14700 |  | 0 |  | 14700
Probable Maximum Temperature: |  |  | 36.80°C
Probable Maximum Demand at Day Peak: |  |  | 13580.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15280.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15280.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 323.66 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:50 hrs on 07-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-04-2025 | [28 empty] | Date: | 06-04-2025 | [28 empty] | Date: | 06-04-2025 | [28 empty] | Date: | 06-04-2025 | [28 empty] | Date: | 06-04-2025 | [16 empty] | Date: | 06-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 14 | 380 | 297 | 583 | 0 | 17 | 0 | 328 | 0 | 0 | 0 | 90 | 11 | 14 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 98 | 36 | 0 | 40 | 0 | 29 | 187 | 0 | 0 | 0 | 8 | 19 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 182 | 0 | 355 | 0 | 51 | 183 | 34 | 34 | 50 | 163 | 11 | 20 | 80 | 36 | 52.2 | 0 | 20 | 0 | 220 | 300 | 35 | 39 | 0 | 153 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 183 | 0 | 0 | 12 | 7194.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 0 | 1355.79 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 211 | 0 | 171 | 0 | 384 | 0 | 0 | 0 | 165 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1244 | 0 | 6109.79 | 13303.99 | 83.69
01:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 20 | 0 | 0 | 80 | 0 | 0 | 0 | 35 | 0 | 28 | 380 | 291 | 500 | 0 | 17 | 0 | 329 | 0 | 0 | 0 | 90 | 11 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 98 | 36 | 0 | 40 | 0 | 33 | 157 | 0 | 0 | 0 | 8 | 35 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 183 | 0 | 355 | 0 | 51 | 182 | 34 | 19 | 51 | 84 | 8 | 20 | 80 | 34 | 52.2 | 0 | 20 | 0 | 220 | 300 | 37 | 39 | 0 | 151 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 183 | 0 | 0 | 12 | 7106.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1362.05 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 194 | 0 | 169 | 0 | 384 | 0 | 0 | 0 | 166 | 57 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 110 | 0 | 0 | 1244 | 0 | 6001.05 | 13107.25 | 83.68
02:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 380 | 303 | 500 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 52 | 11 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 98 | 12 | 0 | 40 | 0 | 35 | 157 | 0 | 0 | 0 | 8 | 51 | 150 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 183 | 0 | 355 | 0 | 51 | 187 | 34 | 16 | 51 | 34 | 9 | 20 | 98 | 30 | 52.2 | 0 | 20 | 0 | 220 | 300 | 37 | 39 | 0 | 151 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 45 | 75 | 184 | 0 | 0 | 12 | 6737.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1255.4 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 178 | 0 | 170 | 0 | 390 | 0 | 0 | 0 | 166 | 57 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 108 | 110 | 0 | 0 | 1244 | 0 | 5822.4 | 12559.6 | 83.67
03:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 380 | 305 | 500 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 52 | 11 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 98 | 12 | 0 | 40 | 0 | 35 | 157 | 0 | 0 | 0 | 8 | 17 | 150 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 183 | 0 | 355 | 0 | 51 | 186 | 34 | 17 | 51 | 34 | 0 | 20 | 70 | 30 | 52.2 | 0 | 20 | 0 | 220 | 300 | 37 | 39 | 0 | 151 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 45 | 75 | 153 | 0 | 0 | 12 | 6553.2 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1229.07 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 176 | 0 | 159 | 0 | 388 | 0 | 0 | 0 | 165 | 57 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 110 | 0 | 0 | 1180 | 0 | 5664.07 | 12217.27 | 83.66
04:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 380 | 305 | 500 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 52 | 11 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 12 | 0 | 40 | 0 | 35 | 156 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 173 | 0 | 356 | 0 | 51 | 203 | 34 | 18 | 50 | 34 | 0 | 20 | 70 | 32 | 52.2 | 0 | 20 | 0 | 220 | 300 | 37 | 39 | 0 | 157 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 45 | 75 | 154 | 0 | 0 | 12 | 6523.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 0 | 1111.9 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 197 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 167 | 57 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 116 | 110 | 0 | 0 | 1180 | 0 | 5519.9 | 12043.1 | 83.65
05:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 380 | 307 | 500 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 34 | 11 | 13 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 40 | 0 | 36 | 170 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 173 | 0 | 355 | 0 | 51 | 205 | 34 | 17 | 50 | 34 | 0 | 20 | 70 | 32 | 52.2 | 0 | 20 | 0 | 220 | 300 | 37 | 39 | 0 | 155 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 45 | 55 | 155 | 0 | 0 | 12 | 6459.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 0 | 1109.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 180 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 168 | 57 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 116 | 110 | 0 | 0 | 1126 | 0 | 5382.31 | 11841.51 | 83.64
06:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 380 | 291 | 500 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 11 | 13 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 39 | 215 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1050 | 1 | 51 | 0 | 173 | 0 | 300 | 0 | 51 | 192 | 34 | 17 | 45 | 34 | 0 | 20 | 70 | 30 | 52.2 | 1 | 20 | 0 | 220 | 300 | 37 | 39 | 0 | 152 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 45 | 55 | 155 | 0 | 0 | 12 | 6280.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 512 | 0 | 1101.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.66 | 214 | 0 | 160 | 0 | 135 | 0 | 339 | 0 | 0.03 | 0 | 166 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 250 | 10 | 112 | 110 | 0 | 0 | 1054 | 0 | 5140 | 11420.2 | 83.63
07:00 | 0 | 2 | 0 | 110 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 380 | 291 | 500 | 0 | 0 | 0 | 328 | 0 | 0 | 3 | 17 | 19 | 13 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 32 | 222 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 1050 | 2 | 51 | 0 | 173 | 0 | 300 | 0 | 51 | 191 | 34 | 17 | 45 | 34 | 1 | 20 | 70 | 34 | 52.2 | 11 | 21 | 0 | 220 | 300 | 37 | 39 | 0 | 157 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 87 | 152 | 0 | 6.77 | 12 | 6375.97 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.04 | 513 | 0 | 1212.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 2.59 | 214 | 0 | 158 | 0 | 119 | 0 | 331 | 0 | 0.24 | 0 | 167 | 57 | 0 | 3 | 0 | 0 | 0 | 0.6 | 20 | 0.07 | 0 | 250 | 10 | 112 | 110 | 0 | 0 | 1038 | 0 | 5255.85 | 11631.82 | 83.62
08:00 | 0 | 17 | 0 | 110 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 32 | 380 | 297 | 500 | 0 | 0 | 0 | 325 | 0 | 0 | 10 | 34 | 19 | 13 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 1 | 40 | 0 | 11 | 230 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1050 | 8 | 51 | 0 | 175 | 0 | 300 | 0 | 52 | 200 | 34 | 17 | 41 | 34 | 9 | 20 | 83 | 36 | 52.2 | 25 | 0 | 0 | 220 | 300 | 37 | 39 | 0 | 154 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 152 | 1 | 17.4 | 12 | 6465.6 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.83 | 505 | 0 | 1210.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 9.51 | 214 | 0 | 139 | 0 | 117 | 0 | 354 | 0 | 0.74 | 0 | 163 | 57 | 0 | 9 | 35 | 0 | 0 | 1.9 | 58 | 0.23 | 0 | 250 | 9 | 120 | 110 | 0 | 0 | 1043 | 0 | 5344.28 | 11809.88 | 83.61
09:00 | 0 | 17 | 8 | 110 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 286 | 500 | 0 | 0 | 0 | 328 | 0 | 0 | 19 | 70 | 19 | 13 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 12 | 3 | 39 | 0 | 9 | 157 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1050 | 14 | 51 | 0 | 175 | 0 | 355 | 0 | 51 | 186 | 34 | 25 | 45 | 34 | 9 | 20 | 70 | 38 | 52.2 | 42 | 0 | 0 | 220 | 325 | 38 | 39 | 0 | 156 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 151 | 1 | 27.65 | 12 | 6588.85 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.28 | 566 | 0 | 1207.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 29.66 | 214 | 0 | 147 | 0 | 148 | 0 | 386 | 0 | 2.12 | 0 | 161 | 57 | 35 | 16 | 70 | 0 | 0 | 3.5 | 89 | 0.27 | 0 | 307 | 9 | 110 | 110 | 0 | 0 | 1057 | 0 | 5710.01 | 12298.86 | 83.6
10:00 | 0 | 17 | 16 | 110 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 288 | 500 | 0 | 0 | 0 | 323 | 0 | 0 | 25 | 70 | 19 | 13 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 3 | 40 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1000 | 17 | 43 | 0 | 175 | 0 | 355 | 0 | 51 | 219 | 27 | 35 | 51 | 34 | 8 | 14 | 52 | 32 | 52.2 | 48 | 0 | 0 | 220 | 347 | 37 | 38 | 0 | 153 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 149 | 2 | 36.07 | 12 | 6613.27 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9 | 579 | 0 | 1210.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 44.28 | 214 | 0 | 173 | 0 | 193 | 0 | 387 | 0 | 3.68 | 0 | 163 | 57 | 35 | 23 | 70 | 0 | 0 | 0 | 118 | 0.53 | 0 | 307 | 9 | 108 | 110 | 0 | 0 | 1085 | 0 | 5964.67 | 12577.94 | 83.59
11:00 | 0 | 17 | 16 | 110 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 34 | 15 | 0 | 0 | 4 | 38 | 0 | 16 | 380 | 285 | 500 | 0 | 0 | 0 | 324 | 0 | 0 | 29 | 70 | 19 | 7 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 12 | 4 | 40 | 0 | 13 | 155 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1050 | 10 | 43 | 0 | 173 | 0 | 350 | 0 | 49 | 200 | 26 | 34 | 51 | 36 | 9 | 0 | 70 | 36 | 52.2 | 62 | 0 | 0 | 220 | 386 | 38 | 38 | 0 | 154 | 21 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 55 | 95 | 127 | 2 | 38.58 | 12 | 6719.78 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.35 | 661 | 0 | 1274.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 50.64 | 200 | 0 | 178 | 0 | 172 | 0 | 414 | 0 | 4.35 | 0 | 163 | 57 | 35 | 28 | 70 | 0 | 0 | 6 | 145 | 0.59 | 0 | 307 | 9 | 124 | 110 | 0 | 0 | 1110 | 0 | 6216.37 | 12936.15 | 83.58
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 1 | 34 | 16 | 0 | 0 | 55 | 120 | 0 | 20 | 380 | 296 | 500 | 0 | 0 | 0 | 321 | 0 | 0 | 30 | 108 | 23.5 | 15 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 76 | 12 | 4 | 40 | 0 | 12 | 160 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1124 | 17 | 43 | 2 | 173 | 0 | 346 | 0 | 48 | 200 | 22 | 34 | 70 | 34 | 12 | 20 | 70 | 42 | 52.2 | 65 | 2 | 0 | 220 | 388 | 37 | 39 | 0 | 153 | 21 | 0 | 81 | 30 | 0 | 17 | 0 | 0 | 66 | 107 | 108 | 2 | 36.66 | 12 | 6967.36 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.05 | 760 | 0 | 1323.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 53.51 | 189 | 0 | 181 | 0 | 167 | 0 | 414 | 0 | 4.63 | 0 | 164 | 57 | 35 | 31 | 70 | 0 | 0 | 6.7 | 155 | 0.63 | 0 | 307 | 10 | 120 | 110 | 0 | 0 | 1150 | 0 | 6414.57 | 13381.93 | 83.58
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 25 | 37 | 80 | 42 | 0 | 55 | 144 | 0 | 60 | 380 | 287 | 500 | 0 | 35 | 0 | 318 | 0 | 0 | 30 | 108 | 23.5 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 24 | 66 | 0 | 0 | 85 | 12 | 4 | 40 | 0 | 16 | 157 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1150 | 19 | 43 | 35 | 173 | 0 | 348 | 0 | 46 | 193 | 25 | 34 | 70 | 34 | 26 | 20 | 78 | 36 | 52.2 | 60 | 17 | 0 | 220 | 352 | 36 | 39 | 0 | 152 | 21 | 0 | 80 | 30 | 0 | 17 | 0 | 9 | 67 | 125 | 96 | 2 | 41.86 | 12 | 7372.56 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.22 | 763 | 0 | 1362.44 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 51.05 | 193 | 0 | 193 | 0 | 198 | 0 | 390 | 0 | 4.49 | 0 | 163 | 56 | 35 | 30 | 79 | 0 | 0 | 6.1 | 151 | 0.61 | 0 | 307 | 10 | 108 | 110 | 0 | 0 | 1180 | 0 | 6509.91 | 13882.47 | 83.57
14:00 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 70 | 80 | 60 | 0 | 55 | 144 | 0 | 80 | 380 | 294 | 500 | 0 | 35 | 0 | 316 | 0 | 0 | 11 | 125 | 23.5 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 37 | 63 | 0 | 0 | 98 | 12 | 3 | 40 | 0 | 14 | 155 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1150 | 17 | 43 | 70 | 173 | 0 | 345 | 0 | 45 | 199 | 28 | 34 | 70 | 34 | 26 | 20 | 78 | 42 | 52.2 | 53 | 29 | 0 | 220 | 354 | 36 | 38 | 0 | 149 | 21 | 0 | 80 | 30 | 0 | 17 | 0 | 54.5 | 67 | 125 | 96 | 2 | 37.27 | 12 | 7589.47 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.47 | 761 | 0 | 1359.52 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 42.08 | 184 | 0 | 177 | 0 | 182 | 0 | 331 | 0 | 3.69 | 0 | 163 | 56 | 70 | 26 | 113 | 0 | 0 | 5.5 | 131 | 0.34 | 0 | 307 | 9 | 120 | 110 | 0 | 0 | 1240 | 0 | 6566.6 | 14156.07 | 83.57
15:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 70 | 94 | 60 | 0 | 55 | 144 | 0 | 87 | 450 | 288 | 500 | 0 | 35 | 0 | 315 | 0 | 0 | 17 | 125 | 23.5 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 26 | 65 | 0 | 0 | 98 | 12 | 2 | 40 | 0 | 10 | 161 | 0 | 0 | 0 | 3 | 0 | 141 | 0 | 0 | 0 | 1150 | 12 | 43 | 80 | 180 | 0 | 331 | 0 | 40 | 202 | 25 | 34 | 70 | 34 | 26 | 8 | 78 | 44 | 52.2 | 39 | 28 | 0 | 220 | 385 | 35 | 38 | 0 | 146 | 21 | 0 | 79 | 30 | 0 | 17 | 0 | 0 | 67 | 125 | 96 | 1 | 27.77 | 12 | 7581.47 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.34 | 778 | 0 | 1366.13 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 29.31 | 201 | 0 | 182 | 0 | 175 | 0 | 400 | 0 | 2.69 | 0 | 162 | 55 | 70 | 20 | 113 | 0 | 0 | 4.4 | 95 | 0.41 | 0 | 307 | 10 | 120 | 110 | 0 | 0 | 1244 | 0 | 6599.28 | 14180.75 | 83.56
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 71 | 94 | 95 | 0 | 55 | 144 | 0 | 100 | 450 | 291 | 500 | 0 | 35 | 0 | 316 | 0 | 0 | 13 | 125 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 14 | 66 | 0 | 0 | 98 | 63 | 2 | 40 | 0 | 9 | 157 | 0 | 0 | 0 | 8 | 0 | 146 | 0 | 0 | 0 | 1157 | 8 | 43 | 93 | 180 | 0 | 348 | 0 | 41 | 182 | 23 | 40 | 70 | 44 | 26 | 20 | 78 | 38 | 52.2 | 24 | 28 | 0 | 220 | 351 | 35 | 37 | 0 | 151 | 23 | 0 | 79 | 30 | 0 | 17 | 0 | 9 | 67 | 134 | 96 | 1 | 15.42 | 12 | 7663.62 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.04 | 807 | 0 | 1369.91 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 19.06 | 191 | 0 | 185 | 0 | 186 | 0 | 321 | 0 | 1.6 | 0 | 166 | 56 | 115 | 12 | 109 | 0 | 0 | 2.5 | 57 | 0.25 | 0 | 307 | 10 | 88 | 110 | 0 | 0 | 1244 | 0 | 6459.36 | 14122.98 | 83.56
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 35 | 85 | 94 | 95 | 0 | 55 | 144 | 0 | 101 | 450 | 271 | 450 | 0 | 35 | 0 | 318 | 0 | 0 | 5 | 125 | 24 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 2 | 68 | 40 | 0 | 98 | 63 | 1 | 40 | 0 | 18 | 160 | 0 | 0 | 0 | 8 | 0 | 147 | 0 | 0 | 0 | 1100 | 2 | 43 | 103 | 180 | 0 | 351 | 0 | 43 | 182 | 25 | 51 | 70 | 39 | 27 | 20 | 80 | 38 | 52.2 | 11 | 28 | 0 | 220 | 314 | 35 | 37 | 0 | 134 | 23 | 0 | 79 | 30 | 0 | 17 | 0 | 36 | 67 | 143 | 96 | 0 | 5.52 | 12 | 7566.72 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.59 | 805 | 0 | 1359.88 | 0 | 0 | 0 | 113 | 4 | 0 | 0 | 0 | 0 | 14 | 0 | 3.05 | 169 | 0 | 158 | 0 | 158 | 0 | 320 | 0 | 0.27 | 0 | 167 | 56 | 115 | 5 | 113 | 0 | 0 | 1 | 34 | 0.1 | 0 | 250 | 9 | 88 | 110 | 0 | 0 | 1178 | 0 | 6163.89 | 13730.61 | 83.55
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 35 | 35 | 85 | 94 | 95 | 0 | 55 | 144 | 0 | 101 | 350 | 282 | 400 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 125 | 24 | 22 | 0 | 400 | 1 | 16 | 0 | 0 | 0 | 101 | 75 | 0 | 98 | 63 | 0 | 40 | 1 | 11 | 156 | 0 | 0 | 0 | 8 | 2 | 148 | 0 | 0 | 0 | 1020 | 0 | 43 | 110 | 145 | 0 | 300 | 0 | 47 | 186 | 23 | 67 | 80 | 53 | 27 | 20 | 80 | 34 | 52.2 | 1 | 28 | 0 | 220 | 323 | 35 | 38 | 0 | 131 | 23 | 0 | 80 | 30 | 0 | 17 | 0 | 36 | 105 | 162 | 96 | 0 | 0.27 | 12 | 7293.47 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 801 | 0 | 1267.61 | 0 | 0 | 0 | 113 | 4 | 49 | 0 | 7 | 0 | 0 | 10 | 0 | 152 | 0 | 144 | 0 | 143 | 0 | 325 | 0 | 0 | 0 | 165 | 56 | 115 | 1 | 113 | 0 | 0 | 0 | 2 | 0.01 | 0 | 200 | 9 | 120 | 110 | 0 | 0 | 1048 | 0 | 5872.02 | 13165.49 | 83.55
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 35 | 35 | 91 | 115 | 145 | 12 | 55 | 144 | 0 | 100 | 420 | 286 | 550 | 0 | 35 | 0 | 319 | 0 | 0 | 0 | 152 | 24 | 22 | 0 | 450 | 16 | 16 | 0 | 0 | 1 | 101 | 80 | 0 | 97 | 84 | 0 | 40 | 15 | 19 | 157 | 8 | 0 | 0 | 8 | 34 | 149 | 0 | 0 | 0 | 1215 | 0 | 51 | 122 | 172 | 0 | 355 | 0 | 49 | 183 | 24 | 90 | 80 | 135 | 27 | 20 | 80 | 36 | 52.2 | 0 | 28 | 0 | 220 | 350 | 36 | 38 | 0 | 145 | 23 | 0 | 81 | 30 | 0 | 17 | 0 | 36 | 104 | 163 | 97 | 0 | 0 | 12 | 8361.2 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963 | 15 | 1371.66 | 0 | 42 | 0 | 113 | 10 | 90 | 90 | 35 | 0 | 0 | 22 | 0 | 176 | 0 | 170 | 0 | 170 | 0 | 377 | 0 | 0 | 0 | 165 | 55 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1065 | 0 | 6569.66 | 14930.86 | 83.54
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 35 | 35 | 72 | 125 | 145 | 15 | 55 | 144 | 0 | 101 | 420 | 286 | 500 | 0 | 35 | 0 | 322 | 0 | 0 | 0 | 160 | 25 | 22 | 0 | 400 | 17 | 16 | 0 | 0 | 0 | 101 | 80 | 0 | 96 | 88 | 0 | 40 | 17 | 24 | 156 | 17 | 0 | 0 | 10 | 68 | 149 | 0 | 0 | 0 | 1222 | 0 | 51 | 125 | 179 | 0 | 355 | 0 | 49 | 181 | 28 | 90 | 80 | 135 | 27 | 20 | 80 | 36 | 52.2 | 0 | 28 | 0 | 220 | 350 | 36 | 38 | 0 | 133 | 23 | 0 | 81 | 30 | 0 | 17 | 0 | 36 | 104 | 163 | 97 | 0 | 0 | 12 | 8328.2 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 35 | 1363.07 | 0 | 42 | 0 | 113 | 20 | 97 | 109 | 35 | 0 | 0 | 22 | 0 | 167 | 0 | 160 | 0 | 162 | 0 | 319 | 0 | 0 | 0 | 163 | 55 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1200 | 0 | 6697.07 | 15025.27
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 35 | 35 | 79 | 125 | 145 | 19 | 55 | 144 | 0 | 101 | 420 | 295 | 500 | 0 | 35 | 0 | 325 | 0 | 0 | 0 | 160 | 25 | 22 | 0 | 400 | 17 | 16 | 0 | 0 | 0 | 101 | 80 | 0 | 96 | 88 | 0 | 40 | 17 | 25 | 156 | 17 | 0 | 0 | 15 | 68 | 149 | 0 | 0 | 0 | 1222 | 0 | 51 | 125 | 182 | 0 | 354 | 0 | 49 | 187 | 30 | 90 | 80 | 139 | 27 | 20 | 80 | 34 | 52.2 | 0 | 28 | 0 | 220 | 354 | 36 | 38 | 0 | 136 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 35 | 105 | 163 | 97 | 0 | 0 | 12 | 8377.2 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 35 | 1361.86 | 0 | 0 | 0 | 113 | 0 | 97 | 110 | 38 | 0 | 0 | 22 | 0 | 159 | 0 | 153 | 0 | 153 | 0 | 324 | 0 | 0 | 0 | 160 | 55 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1200 | 0 | 6668.86 | 15046.06 | 83.54
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 35 | 35 | 65 | 108 | 45 | 30 | 55 | 144 | 0 | 101 | 420 | 288 | 500 | 0 | 35 | 0 | 328 | 0 | 0 | 0 | 125 | 25 | 22 | 0 | 400 | 17 | 16 | 0 | 0 | 0 | 101 | 80 | 0 | 86 | 48 | 0 | 40 | 17 | 16 | 157 | 0 | 0 | 0 | 8 | 68 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 180 | 0 | 355 | 0 | 50 | 181 | 32 | 90 | 80 | 140 | 27 | 20 | 80 | 36 | 52.2 | 0 | 28 | 0 | 220 | 350 | 36 | 39 | 0 | 141 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 35 | 105 | 172 | 67 | 0 | 0 | 12 | 8119.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 35 | 1358 | 0 | 0 | 0 | 113 | 0 | 97 | 70 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 153 | 0 | 153 | 0 | 376 | 0 | 0 | 0 | 159 | 54 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1237 | 0 | 6645 | 14764.2 | 83.53
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 35 | 50 | 78 | 0 | 24 | 35 | 72 | 0 | 92 | 420 | 287 | 500 | 0 | 35 | 0 | 330 | 0 | 0 | 0 | 125 | 23.8 | 22 | 0 | 400 | 0 | 30 | 0 | 0 | 1 | 101 | 80 | 0 | 86 | 12 | 0 | 40 | 17 | 19 | 158 | 0 | 0 | 0 | 8 | 51 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 180 | 0 | 356 | 0 | 51 | 181 | 29 | 72 | 80 | 140 | 27 | 20 | 80 | 36 | 52.2 | 0 | 28 | 0 | 220 | 350 | 36 | 38 | 0 | 152 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 35 | 105 | 172 | 69 | 0 | 0 | 12 | 7800 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 35 | 1362 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 169 | 0 | 168 | 0 | 321 | 0 | 0 | 0 | 160 | 56 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 110 | 110 | 0 | 0 | 1237 | 0 | 6470 | 14270 | 83.53
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 35 | 50 | 32 | 0 | 0 | 17 | 35 | 0 | 76 | 420 | 280 | 500 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 108 | 0 | 22 | 0 | 400 | 0 | 30 | 0 | 0 | 1 | 85 | 80 | 0 | 70 | 0 | 0 | 40 | 0 | 29 | 158 | 0 | 0 | 0 | 8 | 51 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 24 | 180 | 0 | 355 | 0 | 49 | 181 | 33 | 47 | 80 | 139 | 28 | 20 | 80 | 36 | 52.2 | 0 | 28 | 0 | 220 | 344 | 36 | 38 | 0 | 152 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 35 | 55 | 120 | 69 | 0 | 0 | 0 | 7310.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 17 | 1374 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 172 | 0 | 171 | 0 | 321 | 0 | 0 | 0 | 165 | 56 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1244 | 0 | 6257 | 13567.2 | 83.52
Total KWH | 0 | 511680 | 254400 | 1309500 | 0 | 0 | 0 | 0 | 9313200 | 0 | 0 | 324000 | 405000 | 944640 | 1076160 | 835025 | 94139 | 585541 | 1560960 | 0 | 1320960 | 9473500 | 7003375 | 11847727 | 0 | 392169 | 0 | 7721940 | 0 | 0 | 198795 | 2184000 | 441600 | 413280 | 0 | 11123181 | 57709 | 107891 | 0 | 0 | 104160 | 1056837 | 501667 | 0 | 2013120 | 620160 | 27242 | 947940 | 78618 | 522720 | 3803636.36 | 16727 | 0 | 0 | 158018.4 | 458327 | 3514487 | 0 | 0 | 0 | 27092725 | 117720 | 1022804 | 1037090 | 4215272.63 | 0 | 8585900 | 0 | 1164000 | 4705000 | 722592 | 958080 | 1471670 | 1543680 | 382200 | 424830 | 1836540 | 859200 | 1246901 | 437836 | 472768 | 0 | 5258300 | 8372000 | 860000 | 902040 | 0 | 3584864 | 524688 | 0 | 1950720 | 714816 | 0 | 420000 | 0 | 416520 | 1641600 | 2728800 | 2839680 | 12300 | 277410 | 280320 | 172404898.39 | 21969454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 666000 | 17607268 | 135360 | 30798855.34 | 0 | 41968 | 0 | 1324224 | 24081 | 294136 | 287808 | 84067 | 0 | 668330 | 54480 | 332248 | 4700364 | 0 | 4304745 | 0 | 4129627 | 0 | 8887200 | 0 | 26640 | 0 | 4002000 | 1294690 | 1339467 | 207871 | 1756368 | 0 | 0 | 37695.6 | 1056240 | 3930 | 0 | 6720000 | 235297 | 2703000 | 2647300 | 0 | 0 | 28289454.55 | 0 | 146630168.49 | 319035066.88

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13381.93 | MW | 12:00 Hr. | Energy Generated |  |  | 319.0351 |  | MKWHr.
| Day Peak Demand |  |  | 13381.93 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.552 |  | MKWHr.
| Evening Peak Generation |  |  | 15046.06 | MW | 20:00 Hr. | Energy Demand |  |  | 319.5871 |  | MKWHr.
| Evening Peak Demand |  |  | 15075.43 | MW | 19:30 Hr. | Maximum Temperature |  |  | 36.1 |  | °C
| Minimum Generation of the Day |  |  | 11420.2 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 976.74 |  | MMCFD
| Maximum Generation of the Day |  |  | 15046.06 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.3507 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 58.6473 | 0 | 10.4887 | 0 | 0 | 0.19879 | 0 | 0 | 69.3348 | Gas | 138.0312 | Gas | 451927920.5345
| Chattogram Zone |  |  | 4.0372 | 30.8964 | 5.0691 | 0 | 0.94794 | 0.14496 | 0 | 0.10416 | 41.1997 | Coal | 88.8098 | Coal | 637867093.6853
| Cumilla Zone |  |  | 22.3121 | 0 | 7.4773 | 0 | 0 | 0.43784 | 0.8592 | 0 | 31.0864 | HFO | 33.4442 | HFO | 581132582.718
| Mymensingh Zone |  |  | 2.8397 | 0 | 5.0672 | 0 | 0 | 0.28971 | 0 | 0 | 8.1966 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 22.5874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5874 | Hydro | 0.94794 | Hydro | 94794
| Khulna Zone |  |  | 0 | 17.6073 | 0.13536 | 0 | 0 | 0.666 | 21.9695 | 0 | 40.3781 | Solar | 4.0703 | Solar | 66020976.056
| Barishal Zone |  |  | 5.5856 | 35.0095 | 0 | 0 | 0 | 0.00393 | 0 | 0 | 40.599 | Import | 53.6275 | Import | 287512586.312
| Rajshahi Zone |  |  | 22.0219 | 0 | 2.1108 | 0 | 0 | 1.0272 | 30.7989 | 0 | 55.9588 | Wind | 0.10416 | Wind | 1524902.4
| Rangpur Zone |  |  | 0 | 5.2967 | 3.0958 | 0 | 0 | 1.3018 | 0 | 0 | 9.6943
| Total |  |  | 138.0312 | 88.8098 | 33.4442 | 0 | 0.94794 | 4.0703 | 53.6275 | 0.10416 | 319.0351
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 451927920.5345 |  | Hydro | 94794
|  |  |  | Coal | 637867093.6853 |  | Solar | 66020976.056
|  |  |  | HFO | 581132582.718 |  | Import | 287512586.312
|  |  |  | HSD | 0 |  | Wind | 1524902.4
[5 empty] | Total: | 202,60,80,855 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9695 | Peak Hr Flow | 868.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9531290.96 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.7989 | Peak Hr Flow | 1361.86 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 698 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8592 | Peak Hr Flow | 34.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 884 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.6275 | Peak Hr Flow | 2263.86 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4548
|  |  |  | Chattogram |  | 0 |  | 1516
|  |  |  | Cumilla |  | 0 |  | 1496
|  |  |  | Mymensingh |  | 0 |  | 1332
|  |  |  | Sylhet |  | 0 |  | 560
|  |  |  | Khulna |  | 0 |  | 1865
|  |  |  | Barishal |  | 0 |  | 471
|  |  |  | Rajshahi |  | 0 |  | 1600
|  |  |  | Rangpur |  | 0 |  | 966
|  |  |  | Total |  | 0 |  | 14354
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:32 | 11:21 | Chauddagram 132/33kV S/S 132 kv T-2 LT Scheduled S/D Due to Cumilla PBS-2 Taken S/D due | [7 empty] | 23.0MW load
|  |  | to loop connection Red-hot maintenance. | [7 empty] | interrup.
| 08:33 | 11:21 | Chauddagram 132/33kV S/S 132 kv T-2 HT Scheduled S/D Due to Cumilla PBS-2 Taken S/D due | [7 empty] | 23.0MW load
|  |  | to loop connection Red-hot maintenance. | [7 empty] | interrup.
| 08:39 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 KV Ckt-1 Tripped showing Main-01, Main-02
relays Due to Line Fault
| 08:39 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 KV Ckt-2 Tripped showing No any signal relays
Due to TIE
| 08:55 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
| 09:04 | 12:05 | Thakurgaon 132/33kV S/S T-3(432T) HT Scheduled S/D
| 09:04 | 12:05 | Thakurgaon 132/33kV S/S T-3(432T) LT Scheduled S/D
| 11:34 |  | Ghorashal Unit-7 was shutdown at 11:34hr due to gas shortage.
| 12:00 |  | Day peak Generation is 13378 MW
| 12:24 | 13:56 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Conductor | [7 empty] | 30.0MW load
|  |  | armaring. | [7 empty] | interrup. Kabirpur
132/33kV end
| 16:38 | 01:05 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Isulator (Q3) T-Phase High temp. Maintenance works
| 19:15 | 06:33 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Forced S/D Due to 230/132 kV T03 Transformer DS
803M red hot.
|  | 19:43 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 HT is restored.
|  | 19:50 | Cantonment 132/33kV S/S Transformer-1 (T-1) HT is restored.
|  | 19:51 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-1 LT is restored.
| 20:00 |  | Evening Peak: 15045 MW.
|  | 20:01 | Cantonment 132/33kV S/S Transformer-1 (T-1) LT is restored.
| 21:10 | 06:32 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT Forced S/D
| 21:38 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is ON with remarks:-
| 23:19 | 00:24 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Kabirpur 132/33kV end showing Distance relay
relays Due to Earth fault and from Tongi 230/132/33kV end showing Distance relay relays
Due to Bad weather
| 23:38 |  | Ghorasal-Joydeb-B 132kV Ckt-1 Tripped from Joydebpur 132/33kV end showing Main
Protection Trip. MVTR Trip relays Due to Grid Fail
| 23:40 | 23:59 | Bashundhara-Rampura 132 kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance
protection 21/1 Z1 AN relays Due to Heavy Thunderstorm.
| 23:40 | 23:49 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance
protection 21/1 Z1 AN relays Due to Heavy Thunderstorm.
| 23:44 |  | Gulshan 132/33kV S/S MT-2 HT Tripped showing REC 316*4 relays Due to Trip
| 00:25 | 00:51 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing DIR O/C & E/F relay relays Due to 33 kv | [7 empty] | 20.0MW load
|  |  | side feeder fault Astha feed feeder Auxiliary Transformer -01 drop out fuse R,Y phase | [7 empty] | interrup.
burn
|  | 00:51 | Sonargaon 132/33kV S/S Tr-1 LT is restored.
| 00:52 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Tripped from Joydebpur 132/33kV end showing Main
Protection Trip, MVTR Trip relays.
| 05:00 |  | Minimum generation: 9267 MW
| 06:32 |  | Bhulta 132/33kV S/S GT2 LT Scheduled S/D Due to Red hot maintenace
| 06:33 | 07:58 | Bhulta 132/33kV S/S GT2 HT Scheduled S/D Due to Red hot maintenace
| 06:36 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Scheduled S/D Due to Maintenance for high
temperature issue at B phase of bushing
| 06:36 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT Scheduled S/D Due to Maintenance for high
temperature issue at B phase of bushing
| 07:10 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 LT Scheduled S/D Due to Painting
Work.
| 07:13 |  | Cantonment 132/33kV S/S Transformer-2 (T-2) LT Scheduled S/D Due to Painting Work.
| 07:14 |  | Cantonment 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Painting Work.
| 07:17 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 HT Scheduled S/D Due to Painting
Work.
| 07:48 |  | Savar 132/33kV S/S Main Bus-I Scheduled S/D Due to Corrective maintenance work
| 07:52 |  | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Corrective
maintenance work.
| 07:59 |  | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to REB-2 feeder Red Hot maintenance
| 08:00 |  | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to REB-2 feeder Red Hot maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 1309500 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 406 | 9313200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9473500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 295 | 7003375 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 19 | 94139 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 325 | 7721940 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 1076160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 585541 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 392169 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 25 | 441600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 413280 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 254400 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 835025 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 79 | 944640 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 511680 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 101 | 1320960 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1560960 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 198795 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 405000 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 11123181 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 500 | 11847727 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2184000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3394 | 69334772
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 15 | 158018.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117720 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 947940 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3514487 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 458327 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 80 | 501667 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 101 | 1056837 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 96 | 2013120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 522720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 27242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 16 | 107891 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 78618 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 620160 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 57709 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 16727 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1222 | 27092725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 104160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 156 | 3803636.36 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2107 | 41199704.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 187 | 4705000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8585900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 30 | 722592 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1164000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 4215272.63 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1022804 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 1037090 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 28 | 472768 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1471670 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 139 | 1543680 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 34 | 859200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1246901 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 424830 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1836540 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 27 | 382200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 958080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 437836 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1528.2 | 31086363.63
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 97 | 2839680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2728800 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1641600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 277410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 280320 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 416520 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 412 | 8196630
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 860000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 902040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 136 | 3584864 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 714816 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1950720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 0 | 0 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 420000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 524688 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 354 | 8372000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 220 | 5258300 | Due to GBC Problem
Sylhet Area Total |  |  |  |  | 2368.568 | 936 | 22587428
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 868 | 21969454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 135360 | Under Maintenance
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 666000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1055 | 17607268 | U#1 Under Reserve shut down
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1958 | 40378082
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 235297 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2703000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 28289454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2647300 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6720000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3930 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1737 | 40598981.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 41968 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 24081 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 38 | 84067 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 159 | 4700364 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 153 | 4304745 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 153 | 4129627 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 324 | 8887200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 54480 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 294136 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1324224 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 110 | 287808 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1361.86 | 30798855.34 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 332248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 668330 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2530.86 | 55958773.34
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 55 | 1294690 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 4002000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1756368 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37695.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1339467 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 207871 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1056240 | -
Rangpur Area Total |  |  |  |  | 950 | 443 | 9694331.6
Eastern Grid Total |  |  |  |  | 16921.242 | 8377.2 | 172404898.39
Western Grid Total |  |  |  |  | 11614.5 | 6668.86 | 146630168.49
National Grid Total |  |  |  |  | 28535.742 | 15046.06 | 319035066.88
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-04-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9451.93 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4901.9 | MW
i) Dhaka area |  |  | 4547.63 |  | MW | i) Khulna area |  |  |  | 1865 | MW
ii) Chattogram area |  |  | 1516.3 |  | MW | ii) Barishal area |  |  |  | 470.7 | MW
iii) Cumilla area |  |  | 1496 |  | MW | iii) Rajshahi area |  |  |  | 1600.2 | MW
iv) Mymensingh area |  |  | 1332 |  | MW | iv) Rangpur area |  |  |  | 966 | MW
v) Sylhet area |  |  | 560 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14353.83 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 23:00 | 67 | Jaldhaka | 84 | 19:00 | 133 | Payra | 34 | 00:00
2 | AKSML | 121.7 | 11:00 | 68 | Jamalpur | 146 | 19:00 | 134 | Postogola | 44 | 18:00
3 | Aftabnagar | 36 | 15:00 | 69 | Jashore | 159 | 19:30 | 135 | Purbachal | 18 | 21:00
4 | Agargaon | 125 | 13:00 | 70 | Jhenaidah | 157 | 19:00 | 136 | Purbasadipur | 133 | 13:00
5 | Agrabad | 86 | 15:00 | 71 | Joydebpur | 128 | 18:30 | 137 | Rahanpur | 34 | 21:00
6 | Amnura | 59 | 21:00 | 72 | Joypurhat | 80 | 21:00 | 138 | Rahim | 29 | 23:00
7 | Ashuganj | 84 | 23:00 | 73 | Juldah | 15 | 00:00 | 139 | Rajbari | 88 | 21:00
8 | BSRM | 167 | 21:00 | 74 | KSRM | 13 | 13:00 | 140 | Rajendrapur | 131 | 19:00
9 | Bagerhat | 92 | 22:00 | 75 | Kabirpur | 205 | 20:00 | 141 | Rajshahi | 128 | 14:00
10 | Bajitpur | 56 | 19:00 | 76 | Kachua | 92 | 20:00 | 142 | Rajshahi-230 | 94 | 12:00
11 | Bakulia | 84 | 19:00 | 77 | Kallyanpur | 102 | 18:30 | 143 | Ramganj | 120 | 18:30
12 | Banani | 68.8 | 13:00 | 78 | Kalurghat | 38 | 15:00 | 144 | Rampur | 40 | 23:00
13 | Bangabhaban | 20 | 10:00 | 79 | Kamrangirchar | 47 | 19:30 | 145 | Rangamati | 18 | 18:30
14 | Barapukuria | 76 | 19:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 145 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kasba | 41 | 23:00 | 147 | Ruppur | 7.4 | 15:00
16 | Barishal | 111 | 14:00 | 82 | Kazla | 78 | 23:00 | 148 | SSM | 2 | 22:00
17 | Barishal-230 | 106 | 00:00 | 83 | Keranigonj | 64 | 21:00 | 149 | Saidpur | 119 | 14:00
18 | Baroaulia | 56 | 19:00 | 84 | Khagrachori | 34 | 18:30 | 150 | Satkhira | 146 | 22:00
19 | Baroirhat | 65 | 19:30 | 85 | Khulna | 97 | 13:00 | 151 | Satmasjid | 102 | 19:00
20 | Bashundhara | 179 | 14:00 | 86 | Khulshi | 171 | 19:00 | 152 | Savar | 173 | 21:00
21 | BashundharaCement | 6 | 02:00 | 87 | Kishoreganj | 156 | 19:30 | 153 | SevenRings | 11.07 | 00:00
22 | Beanibazar | 62 | 00:00 | 88 | Kodda | 224 | 21:00 | 154 | ShahCement | 15 | 15:00
23 | Benapole | 76 | 20:00 | 89 | Kulaura | 42 | 00:00 | 155 | Shahjadpur | 85 | 20:00
24 | Bhaluka | 173 | 16:00 | 90 | Kurigram | 71 | 19:00 | 156 | Shahjibazar | 132 | 21:00
25 | Bhandaria | 57 | 00:00 | 91 | Kushtia | 152 | 21:00 | 157 | Shahmirpur | 69 | 00:00
26 | Bhangura | 44 | 14:00 | 92 | Lalbag | 34 | 17:00 | 158 | Shariatpur | 94 | 22:00
27 | Bheramara(GK) | 68 | 21:00 | 93 | Lalmonirhat | 66 | 19:00 | 159 | Sherpur | 184 | 19:00
28 | Bhulta | 179 | 21:00 | 94 | MI_Cement | 10.8 | 19:00 | 160 | Shikalbaha | 30 | 16:00
29 | Bog-Sherpur | 70 | 21:00 | 95 | Madanganj | 46 | 19:00 | 161 | Shitalakhya | 69.2 | 13:00
30 | Bogura | 178 | 19:00 | 96 | Madaripur | 121 | 00:00 | 162 | Sholosohor | 38 | 15:00
31 | Borhanuddin | 92 | 21:00 | 97 | Madartek | 84.71 | 23:00 | 163 | Shyampur | 84 | 13:00
32 | Brahmanbaria | 145 | 19:00 | 98 | Madunaghat | 53 | 19:00 | 164 | Siddhirganj | 94 | 21:00
33 | Cantonment | 82 | 13:00 | 99 | Magura | 78 | 19:00 | 165 | Sirajganj | 116 | 19:30
34 | Chandpur | 74 | 22:00 | 100 | Mahasthangarh | 88 | 20:00 | 166 | Sonargaon | 90 | 21:00
35 | Chandraghona | 37 | 18:30 | 101 | Manikganj | 138 | 22:00 | 167 | Sreemongol | 82 | 18:30
36 | Chapai | 74 | 20:00 | 102 | Maniknagar | 66 | 13:00 | 168 | Sreepur | 99 | 19:00
37 | Charsaidpur | 31 | 19:30 | 103 | Matarbari | 52 | 18:30 | 169 | Srinagar | 49.6 | 20:00
38 | Chauddagram | 82 | 18:30 | 104 | Matuail | 48 | 12:00 | 170 | Sunamganj | 54 | 19:00
39 | Chhatak | 31 | 19:00 | 105 | Millgate | 67 | 14:00 | 171 | Sylhet | 39 | 18:30
40 | Chowmuhani | 234 | 19:00 | 106 | Mirpur | 128 | 21:00 | 172 | Sylhet-132 | 108 | 16:00
41 | Chuadanga | 111 | 00:00 | 107 | Mirsorai | 9 | 15:00 | 173 | TK | 24 | 23:00
42 | Coxsbazar | 139 | 18:30 | 108 | Mirzapur | 50 | 18:30 | 174 | Tangail | 204 | 18:30
43 | Cumilla(N) | 192 | 21:00 | 109 | Mithapukur | 74 | 19:00 | 175 | Thakurgaon | 109 | 19:30
44 | Cumilla(S) | 157 | 16:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 100 | 15:00
45 | Daudkandi | 162 | 20:00 | 111 | Mogbazar | 136.9 | 13:00 | 177 | Ullahpara | 43 | 19:00
46 | Dhaka | 52 | 12:00 | 112 | Mongla | 31 | 14:00 | 178 | Ullon | 46 | 23:00
47 | Dhamrai | 108 | 19:00 | 113 | Motijheel | 38 | 13:00 | 179 | Uttara | 87 | 15:00
48 | Dhanmondi | 143 | 13:00 | 114 | Muktagacha | 42 | 19:00 | 180 | UttaraNew | 46 | 23:00
49 | Dohazari | 122 | 19:00 | 115 | Munshiganj | 122 | 23:00 | 181 | Zigatola | 62 | 18:30
50 | Faridpur | 171 | 19:00 | 116 | Muradnagar | 30 | 19:00
51 | Fatullah | 62 | 15:00 | 117 | Mymensingh | 223 | 20:00
52 | Fenchuganj | 35 | 00:00 | 118 | Naogaon | 140 | 00:00
53 | Feni | 121 | 18:30 | 119 | Narail | 70 | 19:00
54 | GPH | 97 | 05:00 | 120 | Narinda | 56 | 13:00
55 | Ghatail | 96 | 19:00 | 121 | Narshingdi | 162 | 21:00
56 | Ghorashal | 14 | 19:30 | 122 | Natore | 164 | 14:00
57 | Ghorashal-230 | 80 | 20:00 | 123 | Nawabganj | 63.8 | 22:00
58 | Goalpara | 32 | 22:00 | 124 | Netrakona | 135 | 23:00
59 | Gollamari | 84 | 20:00 | 125 | New | 61.9 | 14:00
60 | Gopalganj | 115 | 21:00 | 126 | Niamatpur | 125 | 21:00
61 | Gulshan | 130 | 14:00 | 127 | Noapara | 47 | 19:30
62 | Halishahar | 73 | 15:00 | 128 | PHP | 5 | 21:00
63 | HaripurSBU | 104 | 20:00 | 129 | Pabna | 125 | 21:00
64 | Hasnabad | 70 | 00:00 | 130 | Palashbari | 136 | 21:00
65 | Hathazari | 82 | 18:00 | 131 | Panchagarh | 59 | 19:00
66 | Ishurdi | 72 | 13:00 | 132 | Patuakhali | 81.4 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13303.99 | 50 |  | 13356.24
1:00 | 13107.25 | 98 |  | 13209.66
2:00 | 12559.6 | 87 |  | 12650.6
3:00 | 12217.27 | 79 |  | 12300.27
4:00 | 12043.1 | 65 |  | 12111.1
5:00 | 11841.51 | 56 |  | 11900.51
6:00 | 11420.2 | 31 |  | 11452.6
7:00 | 11631.82 | 0 |  | 11631.82
8:00 | 11809.88 | 0 |  | 11809.88
9:00 | 12298.86 | 0 |  | 12298.86
10:00 | 12577.94 | 0 |  | 12577.94
11:00 | 12936.15 | 0 |  | 12936.15
12:00 | 13381.93 | 0 |  | 13381.93
13:00 | 13882.47 | 0 |  | 13882.47
14:00 | 14156.07 | 0 |  | 14156.07
15:00 | 14180.75 | 0 |  | 14180.75
16:00 | 14122.98 | 0 |  | 14122.98
17:00 | 13730.61 | 0 |  | 13730.61
18:00 | 13165.49 | 0 |  | 13165.49
19:00 | 14930.86 | 86 |  | 15020.86
19:30 | 15025.27 | 48 |  | 15075.43
20:00 | 15046.06 | 0 |  | 15046.06
21:00 | 14764.2 | 0 |  | 14764.2
22:00 | 14270 | 0 |  | 14270
23:00 | 13567.2 | 0 |  | 13567.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7194.2 | 6109.79 | 13303.99 | DAILY GENERATION CURVE
00:30 | 7150.2 | 6055.42 | 13205.62
01:00 | 7106.2 | 6001.05 | 13107.25 | 06-04-2025
01:30 | 6921.7 | 5911.725 | 12833.425
02:00 | 6737.2 | 5822.4 | 12559.6
02:30 | 6645.2 | 5743.235 | 12388.435
03:00 | 6553.2 | 5664.07 | 12217.27
03:30 | 6538.2 | 5591.985 | 12130.185
04:00 | 6523.2 | 5519.9 | 12043.1
04:30 | 6491.2 | 5451.105 | 11942.305
05:00 | 6459.2 | 5382.31 | 11841.51
05:30 | 6369.7 | 5261.155 | 11630.855
06:00 | 6280.2 | 5140 | 11420.2
06:30 | 6328.085 | 5197.925 | 11526.01
07:00 | 6375.97 | 5255.85 | 11631.82
07:30 | 6420.785 | 5300.065 | 11720.85
08:00 | 6465.6 | 5344.28 | 11809.88
08:30 | 6527.225 | 5527.145 | 12054.37
09:00 | 6588.85 | 5710.01 | 12298.86
09:30 | 6601.06 | 5837.34 | 12438.4
10:00 | 6613.27 | 5964.67 | 12577.94
10:30 | 6666.525 | 6090.52 | 12757.045
11:00 | 6719.78 | 6216.37 | 12936.15
11:30 | 6843.57 | 6315.47 | 13159.04
12:00 | 6967.36 | 6414.57 | 13381.93
12:30 | 7169.96 | 6462.24 | 13632.2
13:00 | 7372.56 | 6509.91 | 13882.47
13:30 | 7481.015 | 6538.255 | 14019.27
14:00 | 7589.47 | 6566.6 | 14156.07
14:30 | 7585.47 | 6582.94 | 14168.41
15:00 | 7581.47 | 6599.28 | 14180.75
15:30 | 7622.545 | 6529.32 | 14151.865
16:00 | 7663.62 | 6459.36 | 14122.98
16:30 | 7615.17 | 6311.625 | 13926.795
17:00 | 7566.72 | 6163.89 | 13730.61
17:30 | 7430.095 | 6017.955 | 13448.05
18:00 | 7293.47 | 5872.02 | 13165.49
18:30 | 7827.335 | 6220.84 | 14048.175
19:00 | 8361.2 | 6569.66 | 14930.86
19:30 | 8328.2 | 6697.07 | 15025.27
20:00 | 8377.2 | 6668.86 | 15046.06
20:30 | 8248.2 | 6656.93 | 14905.13 |  | Executive Engineer
21:00 | 8119.2 | 6645 | 14764.2 |  | Network Operation Division
21:30 | 7959.6 | 6557.5 | 14517.1
22:00 | 7800 | 6470 | 14270
22:30 | 7555.1 | 6363.5 | 13918.6
23:00 | 7310.2 | 6257 | 13567.2

## En-Curve
QF-LDC-12
Date | 06-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3529 | 2496 | 915 | 0 | 36 | 1355.79 | 40 | 3801 | 0 | 161 | 970.2 | 0 | 0 | 0 | 50 | DAILY ENERGY CURVE
00:30 | 3519.5 | 2451.5 | 915 | 0 | 35 | 1358.92 | 40 | 3788 | 0 | 201 | 896.7 | 0 | 0 | 0 | 74 | 06-04-2025
01:00 | 3510 | 2407 | 915 | 0 | 34 | 1362.05 | 40 | 3775 | 0 | 241 | 823.2 | 0 | 0 | 0 | 98
01:30 | 3499 | 2414 | 915.5 | 0 | 32 | 1308.725 | 40 | 3709.5 | 0 | 165 | 749.7 | 0 | 0 | 0 | 92.5 | Energy Generated | 319.0351 |  | MKWHr
02:00 | 3488 | 2421 | 916 | 0 | 30 | 1255.4 | 40 | 3644 | 0 | 89 | 676.2 | 0 | 0 | 0 | 87 | Energy not Served | 0.552 |  | MKWHr
02:30 | 3453.5 | 2422 | 916.5 | 0 | 30 | 1242.235 | 40 | 3586.5 | 0 | 89 | 608.7 | 0 | 0 | 0 | 83 | Total Energy Requirement | 319.5871 |  | MKWHr
03:00 | 3419 | 2423 | 917 | 0 | 30 | 1229.07 | 40 | 3529 | 0 | 89 | 541.2 | 0 | 0 | 0 | 79
03:30 | 3439 | 2421 | 916.5 | 0 | 31 | 1170.485 | 40 | 3498.5 | 0 | 80.5 | 533.2 | 0 | 0 | 0 | 72
04:00 | 3459 | 2419 | 916 | 0 | 32 | 1111.9 | 40 | 3468 | 0 | 72 | 525.2 | 0 | 0 | 0 | 65
04:30 | 3445.5 | 2419.5 | 916 | 0 | 32 | 1110.605 | 40 | 3448.5 | 0 | 63 | 467.2 | 0 | 0 | 0 | 60.5
05:00 | 3432 | 2420 | 916 | 0 | 32 | 1109.31 | 40 | 3429 | 0 | 54 | 409.2 | 0 | 0 | 0 | 56
05:30 | 3345.5 | 2387 | 916 | 0 | 31 | 1105.485 | 40 | 3366.5 | 2.67 | 45.5 | 391.2 | 0 | 0 | 0 | 43.5
06:00 | 3259 | 2354 | 916 | 0 | 30 | 1101.66 | 40 | 3304 | 5.34 | 37 | 373.2 | 0 | 0 | 0 | 31
06:30 | 3238.5 | 2357 | 916 | 0 | 32 | 1156.985 | 40 | 3300.5 | 38.325 | 46.5 | 400.2 | 0 | 0 | 0 | 15.5
07:00 | 3218 | 2360 | 916 | 0 | 34 | 1212.31 | 40 | 3297 | 71.31 | 56 | 427.2 | 0 | 0 | 0 | 0
07:30 | 3231.5 | 2352 | 892 | 0 | 35 | 1211.19 | 40 | 3297.5 | 141.96 | 61.5 | 458.2 | 0 | 0 | 0 | 0
08:00 | 3245 | 2344 | 868 | 0 | 36 | 1210.07 | 40 | 3298 | 212.61 | 67 | 489.2 | 0 | 0 | 0 | 0
08:30 | 3335.5 | 2338 | 867.5 | 0 | 37 | 1208.625 | 39.5 | 3326.5 | 289.045 | 89 | 523.7 | 0 | 0 | 0 | 0
09:00 | 3426 | 2332 | 867 | 0 | 38 | 1207.18 | 39 | 3355 | 365.48 | 111 | 558.2 | 0 | 0 | 0 | 0
09:30 | 3486.5 | 2320 | 891 | 0 | 35 | 1208.73 | 39.5 | 3350.5 | 422.97 | 115 | 569.2 | 0 | 0 | 0 | 0
10:00 | 3547 | 2308 | 915 | 0 | 32 | 1210.28 | 40 | 3346 | 480.46 | 119 | 580.2 | 0 | 0 | 0 | 0
10:30 | 3548.5 | 2301.5 | 915 | 0 | 34 | 1242.36 | 40 | 3424.5 | 521.485 | 118.5 | 611.2 | 0 | 0 | 0 | 0
11:00 | 3550 | 2295 | 915 | 0 | 36 | 1274.44 | 40 | 3503 | 562.51 | 118 | 642.2 | 0 | 0 | 0 | 0
11:30 | 3482 | 2315.25 | 915.5 | 0 | 39 | 1298.745 | 40 | 3612.5 | 579.345 | 149.5 | 727.2 | 0 | 0 | 0 | 0
12:00 | 3414 | 2335.5 | 916 | 0 | 42 | 1323.05 | 40 | 3722 | 596.18 | 181 | 812.2 | 0 | 0 | 0 | 0
12:30 | 3392.5 | 2334.5 | 915.5 | 0 | 39 | 1342.745 | 40 | 3749 | 588.255 | 251.5 | 967.2 | 0 | 0 | 12 | 0
13:00 | 3371 | 2333.5 | 915 | 0 | 36 | 1362.44 | 40 | 3776 | 580.33 | 322 | 1122.2 | 0 | 0 | 24 | 0
13:30 | 3330 | 2333.5 | 915.5 | 0 | 39 | 1360.98 | 40 | 3804 | 535.84 | 339 | 1290.95 | 0 | 0 | 30.5 | 0
14:00 | 3289 | 2333.5 | 916 | 0 | 42 | 1359.52 | 40 | 3832 | 491.35 | 356 | 1459.7 | 0 | 0 | 37 | 0
14:30 | 3336.5 | 2357 | 915.5 | 0 | 43 | 1362.825 | 40 | 3844.5 | 434.135 | 354.5 | 1448.95 | 0 | 0 | 31.5 | 0
15:00 | 3384 | 2380.5 | 915 | 0 | 44 | 1366.13 | 40 | 3857 | 376.92 | 353 | 1438.2 | 0 | 0 | 26 | 0
15:30 | 3313.5 | 2391.25 | 915 | 0 | 41 | 1368.02 | 40 | 3875.5 | 303.395 | 349.5 | 1534.7 | 0 | 0 | 20 | 0
16:00 | 3243 | 2402 | 915 | 0 | 38 | 1369.91 | 40 | 3894 | 229.87 | 346 | 1631.2 | 0 | 0 | 14 | 0
16:30 | 3189.5 | 2364 | 915 | 0 | 38 | 1364.895 | 40 | 3805 | 165.2 | 369 | 1668.2 | 0 | 0 | 8 | 0
17:00 | 3136 | 2326 | 915 | 0 | 38 | 1359.88 | 40 | 3716 | 100.53 | 392 | 1705.2 | 0 | 0 | 2 | 0
17:30 | 3075 | 2211.5 | 915 | 0 | 36 | 1313.745 | 40 | 3581 | 53.605 | 459 | 1762.2 | 0 | 0 | 1 | 0
18:00 | 3014 | 2097 | 915 | 0 | 34 | 1267.61 | 40 | 3446 | 6.68 | 526 | 1819.2 | 0 | 0 | 0 | 0
18:30 | 3161 | 2264.5 | 895 | 0 | 35 | 1319.635 | 40 | 3686.5 | 3.34 | 634.5 | 2008.2 | 0 | 0 | 0.5 | 43
19:00 | 3308 | 2432 | 875 | 0 | 36 | 1371.66 | 40 | 3927 | 0 | 743 | 2197.2 | 0 | 0 | 1 | 86
19:30 | 3227 | 2333 | 868 | 0 | 36 | 1363.07 | 40 | 4105 | 0 | 778 | 2275.2 | 0 | 0 | 0 | 48
20:00 | 3222 | 2350 | 868 | 0 | 34 | 1361.86 | 40 | 4155 | 0 | 719 | 2296.2 | 0 | 0 | 0 | 0
20:30 | 3233.5 | 2344 | 891.5 | 0 | 35 | 1359.93 | 40 | 4146.5 | 0 | 663 | 2191.7 | 0 | 0 | 0 | 0
21:00 | 3245 | 2338 | 915 | 0 | 36 | 1358 | 40 | 4138 | 0 | 607 | 2087.2 | 0 | 0 | 0 | 0
21:30 | 3239 | 2343.9 | 915.5 | 0 | 36 | 1360 | 40 | 4160 | 0 | 543.5 | 1878.7 | 0 | 0 | 0.5 | 0
22:00 | 3233 | 2349.8 | 916 | 0 | 36 | 1362 | 40 | 4182 | 0 | 480 | 1670.2 | 0 | 0 | 1 | 0
22:30 | 3236.5 | 2338.9 | 915.5 | 0 | 36 | 1368 | 40 | 4155.5 | 0 | 440.5 | 1386.7 | 0 | 0 | 1 | 0
23:00 | 3240 | 2328 | 915 | 0 | 36 | 1374 | 40 | 4129 | 0 | 401 | 1103.2 | 0 | 0 | 1 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 06:00 | 361 | 17:00 | Payra | 416 | 08:00 | 410 | 00:00
Ashuganj | 405 | 5:00 | 383 | 11:00 | Rahanpur | 402 | 04:00 | 387 | 12:00
Bhulta | 401 | 06:00 | 383 | 12:00 | Rampal | 405 | 18:00 | 393 | 00:00
Bibiana | 390 | 05:00 | 379 | 12:00
BIPTC | 398 | 06:00 | 388 | 15:00
Bogura | 391 | 04:00 | 373 | 12:00
Gopalganj | 404 | 06:00 | 394 | 00:00
Kaliakoir | 378 | 23:00 | 358 | 12:00
Madunaghat | 401 | 18:00 | 394 | 00:00
Meghnaghat | 403 | 06:00 | 393 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 06:00 | 226 | 12:00 | Keranigonj | 233 | 07:00 | 224 | 12:00
AKSML | 236 | 18:00 | 225 | 12:00 | Khulna(S) | 230 | 09:00 | 219 | 00:00
Aminbazar | 235 | 07:00 | 227 | 12:00 | Madunaghat | 238 | 18:00 | 229 | 12:00
Ashuganj | 233 | 05:00 | 224 | 15:00 | Madunaghat-400 | 237 | 18:00 | 231 | 12:00
Ashuganj-400 | 233 | 05:00 | 224 | 15:00 | Maniknagar | 231 | 04:00 | 221 | 12:00
Baghabari | 233 | 17:00 | 227 | 10:00 | Meghnaghat | 240 | 00:00 | 231 | 14:00
Barapukuria | 223 | 00:00 | 216 | 07:00 | Meghnaghat-400 | 234 | 06:00 | 225 | 12:00
Barapukuria-230 | 223 | 00:00 | 216 | 07:00 | Mirsorai | 230 | 01:00 | 224 | 12:00
Barishal | 235 | 06:00 | 228 | 00:00 | Rajshahi | 233 | 17:00 | 220 | 12:00
Bheramara | 235 | 04:00 | 222 | 12:00 | Rampal | 230 | 18:00 | 220 | 00:00
Bhulta | 230 | 05:00 | 220 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 04:00 | 216 | 15:00 | Rampura | 229 | 06:00 | 218 | 15:00
BIPTC | 236 | 04:00 | 222 | 12:00 | Shikalbaha | 233 | 18:00 | 225 | 12:00
Bogura | 237 | 04:00 | 226 | 12:00 | Shyampur | 233 | 06:00 | 224 | 12:00
Bogura-400 | 236 | 04:00 | 227 | 12:00 | Siddhirganj | 233 | 05:00 | 227 | 18:00
Borhanuddin | 240 | 08:00 | 233 | 00:00 | Sirajgonj | 240 | 03:00 | 234 | 11:00
BSRM | 231 | 03:00 | 224 | 12:00 | Sreepur | 230 | 03:00 | 224 | 11:00
Cumilla(N) | 226 | 06:00 | 217 | 22:00 | Tongi | 230 | 23:00 | 215 | 12:00
Faridpur | 234 | 09:00 | 222 | 22:00
Fenchuganj | 226 | 05:00 | 219 | 21:00
Ghorashal | 240 | 23:00 | 230 | 00:00
Ghorashal-230 | 230 | 06:00 | 218 | 12:00
Gopalganj | 232 | 06:00 | 225 | 00:00
GPH | 234 | 18:00 | 226 | 15:00
Haripur | 231 | 07:00 | 221 | 11:00
Hasnabad | 233 | 07:00 | 225 | 12:00
Hathazari | 235 | 19:30 | 228 | 12:00
Ishurdi | 236 | 04:00 | 225 | 12:00
Jhenaidah | 226 | 07:00 | 211 | 00:00
Kaliakoir | 233 | 06:00 | 220 | 03:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 04:00 | 124 | 12:00 | Madunaghat | 136 | 18:00 | 130 | 12:00
Agargaon | 135 | 04:00 | 129 | 12:00 | Magura | 133 | 09:00 | 126 | 12:00
Agrabad | 135 | 18:00 | 127 | 11:00 | Mahasthangarh | 132 | 17:00 | 123 | 07:00
AKS | 133 | 18:00 | 127 | 14:00 | Manikganj | 128 | 06:00 | 124 | 11:00
Aminbazar | 134 | 03:00 | 128 | 12:00 | Maniknagar | 133 | 04:00 | 126 | 12:00
Amnura | 137 | 19:30 | 124 | 12:00 | Matarbari | 122 | 18:00 | 109 | 12:00
Ashuganj | 137 | 07:00 | 133 | 12:00 | Matuail | 135.5 | 06:00 | 129.4 | 12:00
Bagerhat | 130 | 09:00 | 118 | 00:00 | Millgate | 135 | 04:00 | 125 | 12:00
Bajitpur | 129 | 05:00 | 123 | 12:00 | Mirpur | 133 | 06:00 | 128 | 10:00
Bakulia | 136 | 17:00 | 128 | 12:00 | Mirzapur | 134 | 23:00 | 123 | 12:00
Banani | 131 | 02:00 | 123 | 12:00 | Mithapukur | 130 | 01:00 | 121 | 07:00
Bangabhaban | 133 | 05:00 | 126 | 12:00 | MI_Cement | 135.8 | 06:00 | 130 | 12:00
Barapukuria | 137 | 00:00 | 129 | 08:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 135 | 08:00 | 130 | 00:00 | Mogbazar | 133 | 04:00 | 124 | 12:00
Barishal | 130 | 05:00 | 125 | 00:00 | Mongla | 130 | 18:00 | 118 | 00:00
Barishal-230 | 131 | 07:00 | 124 | 00:00 | Motijheel | 133 | 05:00 | 126 | 12:00
Baroaulia | 134 | 18:00 | 129 | 12:00 | Muktagacha | 133 | 23:00 | 125 | 11:00
Baroirhat | 125 | 18:00 | 118 | 12:00 | Munshiganj | 136 | 05:00 | 129 | 12:00
Bashundhara | 133 | 01:00 | 123 | 15:00 | Muradnagar | 128 | 06:00 | 120 | 12:00
BashundharaCement | 135 | 06:00 | 130 | 11:00 | Mymensingh | 136 | 23:00 | 109 | 18:30
Beanibazar | 128 | 07:00 | 119 | 14:00 | Naogaon | 128 | 18:00 | 120 | 00:00
Benapole | 130 | 05:00 | 118 | 00:00 | Narail | 134 | 05:00 | 123 | 18:30
Bhaluka | 124 | 04:00 | 117 | 11:00 | Narinda | 133 | 04:00 | 126 | 12:00
Bhandaria | 126 | 07:00 | 115 | 00:00 | Narshingdi | 131 | 02:00 | 122 | 18:00
Bhangura | 134 | 22:00 | 127 | 12:00 | Natore | 133 | 17:00 | 125 | 00:00
Bheramara | 137 | 04:00 | 129 | 12:00 | Nawabganj | 136 | 00:00 | 127 | 12:00
Bheramara(GK) | 136 | 17:00 | 128 | 18:30 | Netrakona | 116 | 04:00 | 107 | 15:00
Bhulta | 130 | 18:00 | 123 | 12:00 | New | 138 | 23:00 | 126 | 12:00
Bog-Sherpur | 132 | 18:00 | 126 | 07:00 | Niamatpur | 133 | 18:00 | 129 | 14:00
Bogura | 135 | 17:00 | 127 | 00:00 | Noapara | 132 | 18:00 | 122 | 00:00
Bogura-230 | 135 | 18:00 | 128 | 07:00 | Pabna | 134 | 04:00 | 128 | 12:00
Brahmanbaria | 130 | 07:00 | 123 | 18:30 | Palashbari | 129 | 20:00 | 119 | 08:00
Cantonment | 136 | 06:00 | 128 | 15:00 | Panchagarh | 138 | 00:00 | 117 | 07:00
Chandpur | 123 | 18:00 | 113 | 15:00 | Patuakhali | 135 | 04:00 | 130 | 21:00
Chandraghona | 136 | 18:00 | 130 | 12:00 | Payra | 137 | 18:00 | 134 | 00:00
Chapai | 131 | 18:00 | 125 | 23:00 | PHP | 123 | 18:00 | 116 | 12:00
Charsaidpur | 136 | 07:00 | 130 | 12:00 | Postogola | 138 | 04:00 | 132 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 124 | 18:00 | 116 | 12:00 | Purbachal | 135 | 05:00 | 123 | 10:00
Chhatak | 127 | 07:00 | 116 | 18:30 | Purbasadipur | 133 | 00:00 | 117 | 07:00
Chowmuhani | 119 | 18:00 | 110 | 12:00 | Rahanpur | 136 | 04:00 | 131 | 12:00
Chuadanga | 134 | 04:00 | 120 | 18:30 | Rahanpur-400 | 137 | 04:00 | 131 | 12:00
Coxsbazar | 120 | 16:00 | 107 | 12:00 | Rahim | 135 | 06:00 | 129 | 12:00
Cumilla(N) | 129 | 05:00 | 123 | 14:00 | Rajbari | 134 | 18:00 | 123 | 00:00
Cumilla(S) | 133 | 00:00 | 121 | 13:00 | Rajendrapur | 133 | 18:00 | 120 | 12:00
Daudkandi | 128 | 05:00 | 120 | 12:00 | Rajshahi | 134 | 17:00 | 126 | 12:00
Dhaka | 132 | 04:00 | 124 | 10:00 | Rajshahi-230 | 133 | 03:00 | 116 | 12:00
Dhamrai | 134 | 00:00 | 127 | 12:00 | Ramganj | 119 | 18:00 | 107 | 14:00
Dhanmondi | 136 | 06:00 | 130 | 12:00 | Rampur | 135 | 18:00 | 128 | 11:00
Dohazari | 131 | 12:00 | 123 | 11:00 | Rampura | 132 | 06:00 | 124 | 10:00
Faridpur | 135 | 18:00 | 125 | 00:00 | Rangamati | 134 | 18:00 | 128 | 12:00
Fatullah | 137 | 06:00 | 131 | 12:00 | Rangpur | 130 | 01:00 | 117 | 08:00
Fenchuganj | 133 | 03:00 | 127 | 14:00 | Ruppur | 137 | 05:00 | 131 | 00:00
Feni | 123 | 02:00 | 114 | 18:30 | Saidpur | 132 | 01:00 | 118 | 08:00
Ghatail | 132 | 23:00 | 121 | 16:00 | Satkhira | 130 | 10:00 | 117 | 00:00
Ghorashal | 141 | 23:00 | 131 | 12:00 | Satmasjid | 135 | 04:00 | 129 | 11:00
Goalpara | 133 | 05:00 | 124 | 00:00 | Savar | 134 | 18:00 | 126 | 10:00
Gollamari | 134 | 05:00 | 126 | 00:00 | SevenRings | 137 | 04:00 | 131 | 12:00
Gopalganj | 134 | 06:00 | 127 | 00:00 | ShahCement | 136 | 07:00 | 130 | 12:00
Gopalganj-400 | 137 | 18:00 | 132 | 00:00 | Shahjadpur | 137 | 23:00 | 130 | 11:00
Gulshan | 131 | 05:00 | 122 | 10:00 | Shahjibazar | 131 | 08:00 | 124 | 13:00
Halishahar | 135 | 18:00 | 128 | 12:00 | Shahmirpur | 137 | 18:00 | 129 | 12:00
Haripur | 136 | 06:00 | 130 | 12:00 | Shariatpur | 134 | 08:00 | 126 | 00:00
HaripurSBU | 136 | 06:00 | 129 | 12:00 | Sherpur | 130 | 22:00 | 119 | 15:00
Hasnabad | 139 | 23:00 | 132 | 11:00 | Shikalbaha | 125 | 17:00 | 118 | 12:00
Hathazari | 136 | 19:30 | 131 | 12:00 | Shikalbaha-230 | 137 | 18:00 | 130 | 12:00
Ishurdi | 138 | 04:00 | 131 | 12:00 | Shitalakhya | 135.8 | 06:00 | 130 | 12:00
Jaldhaka | 132 | 01:00 | 115 | 08:00 | Sholosohor | 135 | 18:00 | 130 | 12:00
Jamalpur | 135 | 22:00 | 124 | 05:00 | Shyampur | 137 | 00:00 | 132 | 16:00
Jashore | 130 | 05:00 | 120 | 00:00 | Shyampur-230 | 136 | 04:00 | 131 | 12:00
Jhenaidah | 136 | 04:00 | 126 | 18:30 | Siddhirganj | 135 | 01:00 | 130 | 12:00
Jhenaidah-230 | 136 | 04:00 | 127 | 00:00 | Sirajganj | 131 | 17:00 | 126 | 00:00
Joydebpur | 133 | 18:00 | 126 | 12:00 | Sonargaon | 133 | 05:00 | 127 | 12:00
Joypurhat | 125 | 18:00 | 116 | 00:00 | Sreemongol | 130 | 05:00 | 124 | 14:00
Juldah | 135 | 00:00 | 131 | 14:00 | Sreepur | 129 | 03:00 | 122 | 15:00
Kabirpur | 135 | 23:00 | 124 | 10:00 | Srinagar | 134 | 05:00 | 127 | 12:00
Kachua | 126 | 18:00 | 114 | 14:00 | SSM | 140 | 18:00 | 132 | 12:00
Kaliakoir | 138 | 23:00 | 128 | 12:00 | Sunamganj | 125 | 07:00 | 117 | 14:00
Kallyanpur | 134 | 18:00 | 129 | 10:00 | Sylhet | 128 | 08:00 | 120 | 15:00
Kalurghat | 136 | 18:00 | 130 | 12:00 | Sylhet-132 | 129 | 06:00 | 121 | 15:00
Kamrangirchar | 134 | 07:00 | 128 | 15:00 | Tangail | 133 | 23:00 | 119 | 12:00
Kaptai | 134 | 6:00 | 122 | 19:00 | Thakurgaon | 137 | 00:00 | 113 | 08:00
Kasba | 127 | 07:00 | 120 | 12:00 | TK | 137 | 18:00 | 132 | 10:00
Kazla | 133 | 06:00 | 127 | 12:00 | Tongi | 136 | 04:00 | 128 | 12:00
Keranigonj | 134 | 06:00 | 128 | 12:00 | Ullahpara | 134 | 22:00 | 128 | 00:00
Khagrachori | 133 | 18:00 | 127 | 12:00 | Ullon | 131 | 05:00 | 123 | 12:00
Khulna | 132 | 06:00 | 122 | 00:00 | Uttara | 134 | 06:00 | 125 | 12:00
Khulna(S) | 134 | 09:00 | 126 | 00:00 | UttaraNew | 134 | 17:00 | 128 | 10:00
Khulshi | 134 | 17:00 | 123 | 10:00 | Zigatola | 134 | 06:00 | 129 | 12:00
Kishoreganj | 126 | 06:00 | 118 | 15:00
Kodda | 135 | 23:00 | 124 | 12:00
KSRM | 137 | 18:00 | 129 | 12:00
Kulaura | 131 | 05:00 | 126 | 15:00
Kurigram | 128 | 00:00 | 115 | 07:00
Kushtia | 134 | 17:00 | 126 | 00:00
Lalbag | 134 | 07:00 | 127 | 15:00
Lalmonirhat | 128 | 00:00 | 119 | 12:00
Madanganj | 135 | 06:00 | 130 | 11:00
Madaripur | 135 | 06:00 | 129 | 00:00
Madartek | 132 | 06:00 | 123 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division