## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-04-2025 | [28 empty] | Date: | 07-04-2025 | [28 empty] | Date: | 07-04-2025 | [28 empty] | Date: | 07-04-2025 | [28 empty] | Date: | 07-04-2025 | [16 empty] | Date: | 07-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 304 | 300 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 52 | 15 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 31 | 157 | 0 | 0 | 0 | 8 | 0 | 148 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 86 | 0 | 300 | 0 | 50 | 208 | 33 | 34 | 80 | 139 | 14 | 18 | 80 | 38 | 52.2 | 0 | 29 | 0 | 220 | 343 | 36 | 39 | 0 | 139 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 35 | 45 | 95 | 69 | 0 | 0 | 0 | 5958.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 856 | 0 | 1327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 164 | 0 | 161 | 0 | 250 | 0 | 0 | 0 | 163 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 130 | 110 | 0 | 0 | 1000 | 0 | 5562 | 11520.2 | 83.52
01:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 295 | 400 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15.8 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 29 | 158 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 970 | 0 | 51 | 0 | 88 | 0 | 300 | 0 | 49 | 193 | 34 | 20 | 80 | 60 | 9 | 0 | 80 | 36 | 52.2 | 0 | 30 | 0 | 220 | 303 | 36 | 39 | 0 | 135 | 23 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 8 | 24 | 72 | 0 | 0 | 0 | 5641 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 859 | 0 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 160 | 0 | 162 | 0 | 337 | 0 | 0 | 0 | 163 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 110 | 110 | 0 | 0 | 900 | 0 | 5429 | 11070 | 83.51
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 300 | 400 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 23 | 157 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 907 | 0 | 51 | 0 | 88 | 0 | 353 | 0 | 48 | 199 | 34 | 17 | 70 | 35 | 9 | 0 | 80 | 32 | 52.2 | 0 | 0 | 0 | 220 | 321 | 36 | 39 | 0 | 138 | 0 | 0 | 82 | 30 | 0 | 17 | 0 | 0 | 8 | 24 | 72 | 0 | 0 | 0 | 5710.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 0 | 1010 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 165 | 0 | 168 | 0 | 348 | 0 | 0 | 0 | 161 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 110 | 110 | 0 | 0 | 900 | 0 | 5160 | 10870.2 | 83.51
03:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 277 | 400 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 23 | 158 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 88 | 0 | 356 | 0 | 40 | 182 | 34 | 17 | 70 | 35 | 0 | 18 | 70 | 32 | 52.2 | 0 | 0 | 0 | 220 | 289 | 36 | 29 | 0 | 132 | 0 | 0 | 11 | 30 | 0 | 17 | 0 | 0 | 8 | 8 | 72 | 0 | 0 | 0 | 5470.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 0 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 151 | 0 | 148 | 0 | 319 | 0 | 0 | 0 | 165 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 110 | 110 | 0 | 0 | 800 | 0 | 4893 | 10363.2 | 83.5
04:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 282 | 350 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 17.5 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 23 | 159 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 730 | 0 | 51 | 0 | 88 | 0 | 300 | 0 | 20 | 180 | 34 | 17 | 70 | 34 | 0 | 0 | 70 | 20 | 52.2 | 0 | 0 | 0 | 220 | 290 | 36 | 29 | 0 | 132 | 0 | 0 | 11 | 30 | 0 | 17 | 0 | 0 | 8 | 12 | 72 | 0 | 0 | 0 | 5099.7 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 147 | 0 | 145 | 0 | 320 | 0 | 0 | 0 | 167 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 110 | 110 | 0 | 0 | 618 | 0 | 4562 | 9661.7 | 83.5
05:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 291 | 300 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 23 | 156 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 640 | 0 | 51 | 0 | 88 | 0 | 300 | 0 | 20 | 183 | 34 | 0 | 70 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 220 | 290 | 36 | 29 | 0 | 132 | 0 | 0 | 11 | 30 | 0 | 17 | 0 | 0 | 8 | 32 | 72 | 0 | 0 | 0 | 4767.5 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 148 | 0 | 147 | 0 | 323 | 0 | 0 | 0 | 168 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 108 | 110 | 0 | 0 | 560 | 0 | 4500 | 9267.5 | 83.49
06:00 | 0 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 36 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 295 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 17.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 26 | 157 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 608 | 0 | 51 | 0 | 88 | 0 | 300 | 0 | 20 | 190 | 34 | 0 | 70 | 0 | 0 | 0 | 0 | 26 | 0 | 1 | 0 | 0 | 220 | 290 | 36 | 29 | 0 | 134 | 0 | 0 | 11 | 30 | 0 | 17 | 0 | 0 | 15 | 60 | 72 | 0 | 0.89 | 0 | 4857.39 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13 | 808 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36 | 187 | 0 | 162 | 0 | 157 | 0 | 336 | 0 | 0 | 0 | 167 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 108 | 110 | 0 | 0 | 548 | 0 | 4536.49 | 9393.88 | 83.49
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 14 | 82 | 114 | 0 | 0 | 4 | 0 | 0 | 0 | 330 | 313 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 3 | 0 | 24.5 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 23 | 159 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 4 | 51 | 0 | 88 | 0 | 300 | 0 | 20 | 208 | 35 | 0 | 70 | 0 | 1 | 0 | 0 | 28 | 0 | 11 | 0 | 0 | 220 | 320 | 36 | 29 | 0 | 136 | 11 | 0 | 11 | 30 | 0 | 17 | 0 | 0 | 66 | 120 | 72 | 0 | 7.15 | 0 | 5165.65 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.25 | 809 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 4.29 | 188 | 0 | 167 | 0 | 157 | 0 | 369 | 0 | 0 | 0 | 168 | 57 | 0 | 3 | 0 | 0 | 0 | 0.5 | 11 | 0.05 | 0 | 150 | 7 | 120 | 110 | 0 | 0 | 545 | 0 | 4631.09 | 9796.74 | 83.48
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 35 | 115 | 114 | 0 | 0 | 55 | 0 | 0 | 0 | 330 | 302 | 400 | 0 | 0 | 0 | 300 | 0 | 0 | 7 | 35 | 22.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 60 | 0 | 2 | 40 | 0 | 15 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 607 | 8 | 51 | 0 | 88 | 0 | 300 | 0 | 20 | 201 | 36 | 0 | 70 | 0 | 9 | 20 | 0 | 32 | 0 | 27 | 0 | 0 | 220 | 320 | 36 | 29 | 0 | 144 | 16 | 0 | 11 | 30 | 0 | 17 | 0 | 0 | 69 | 120 | 72 | 1 | 22.4 | 0 | 5537.9 | 862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.94 | 808 | 0 | 822.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 10.55 | 198 | 0 | 178 | 0 | 165 | 0 | 414 | 0 | 0.75 | 0 | 164 | 57 | 35 | 8 | 20 | 0 | 0 | 1.6 | 37 | 0.23 | 0 | 150 | 6 | 120 | 110 | 0 | 0 | 549 | 0 | 4793.3 | 10331.2 | 83.48
09:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 132 | 112 | 0 | 0 | 52 | 0 | 0 | 0 | 420 | 302 | 400 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 0 | 3 | 40 | 0 | 6 | 158 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 611 | 9 | 51 | 0 | 88 | 0 | 300 | 0 | 20 | 203 | 35 | 0 | 70 | 5 | 9 | 20 | 0 | 34 | 0 | 42 | 0 | 0 | 220 | 334 | 36 | 30 | 0 | 140 | 0 | 0 | 11 | 30 | 0 | 17 | 0 | 0 | 39 | 95 | 71 | 1 | 33.35 | 1 | 5694.35 | 862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.11 | 807 | 0 | 828.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 33.32 | 196 | 0 | 175 | 0 | 163 | 0 | 414 | 0 | 2.57 | 0 | 163 | 57 | 35 | 18 | 45 | 0 | 0 | 3.4 | 99 | 0.39 | 0 | 150 | 6 | 120 | 110 | 0 | 0 | 580 | 0 | 4989.91 | 10684.26 | 83.47
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 36 | 95 | 31 | 0 | 0 | 35 | 0 | 0 | 0 | 420 | 293 | 520 | 0 | 0 | 0 | 331 | 0 | 0 | 28 | 0 | 18 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 9 | 3 | 40 | 0 | 6 | 158 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 650 | 17 | 51 | 0 | 150 | 0 | 355 | 0 | 22 | 184 | 29 | 24 | 70 | 26 | 9 | 20 | 17 | 30 | 0 | 52 | 0 | 0 | 220 | 383 | 36 | 30 | 0 | 153 | 0 | 0 | 80 | 30 | 0 | 17 | 0 | 0 | 39 | 95 | 72 | 2 | 41.93 | 8 | 6073.93 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.82 | 805 | 0 | 821.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 45.69 | 202 | 0 | 188 | 0 | 171 | 0 | 393 | 0 | 4.12 | 0 | 166 | 57 | 35 | 24 | 50 | 0 | 0 | 4.8 | 133 | 0.51 | 0 | 196 | 5 | 108 | 110 | 0 | 0 | 602 | 0 | 5193.09 | 11267.02 | 83.47
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 36 | 50 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 420 | 295 | 520 | 0 | 0 | 0 | 326 | 0 | 0 | 29 | 0 | 17 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 63 | 36 | 4 | 40 | 0 | 3 | 158 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 800 | 16 | 51 | 0 | 172 | 0 | 354 | 0 | 42 | 202 | 28 | 51 | 50 | 50 | 9 | 18 | 17 | 40 | 8 | 59 | 0 | 0 | 220 | 383 | 36 | 20 | 0 | 157 | 0 | 0 | 80 | 30 | 0 | 17 | 0 | 37 | 39 | 65 | 65 | 2 | 47.48 | 12 | 6322.48 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.45 | 810 | 0 | 869.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 52.83 | 202 | 0 | 186 | 0 | 174 | 0 | 414 | 0 | 4.75 | 0 | 166 | 57 | 35 | 30 | 50 | 0 | 0 | 5.5 | 157 | 0.62 | 0 | 253 | 6 | 120 | 110 | 0 | 0 | 689 | 0 | 5481.26 | 11803.74 | 83.46
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 36 | 34 | 50 | 0 | 0 | 55 | 13 | 0 | 0 | 420 | 295 | 520 | 0 | 0 | 0 | 322 | 0 | 0 | 30 | 30 | 18 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 63 | 45 | 4 | 40 | 0 | 7 | 156 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 900 | 16 | 51 | 0 | 172 | 0 | 355 | 0 | 46 | 200 | 30 | 51 | 50 | 51 | 9 | 12 | 55 | 38 | 18 | 66 | 0 | 0 | 220 | 385 | 36 | 20 | 0 | 158 | 0 | 0 | 80 | 30 | 0 | 17 | 0 | 32 | 67 | 90 | 60 | 2 | 49.8 | 12 | 6615.8 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.92 | 808 | 0 | 1042.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 55.44 | 198 | 0 | 194 | 0 | 169 | 0 | 414 | 0 | 5.03 | 0 | 165 | 56 | 35 | 31 | 49 | 0 | 0 | 6.3 | 167 | 0.62 | 0 | 307 | 6 | 120 | 110 | 0 | 0 | 946 | 0 | 5986.14 | 12601.94 | 83.46
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 36 | 60 | 66 | 0 | 0 | 55 | 72 | 0 | 40 | 380 | 288 | 520 | 0 | 0 | 0 | 319 | 0 | 0 | 29 | 35 | 22 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 9 | 50 | 0 | 0 | 75 | 50 | 4 | 40 | 0 | 10 | 157 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 950 | 16 | 51 | 30 | 175 | 0 | 356 | 0 | 46 | 188 | 31 | 57 | 50 | 51 | 0 | 12 | 70 | 42 | 25 | 60 | 0 | 0 | 220 | 385 | 36 | 20 | 0 | 152 | 15 | 0 | 82 | 30 | 0 | 17 | 0 | 54.5 | 68 | 105 | 44 | 2 | 47.48 | 12 | 6891.98 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.14 | 808 | 0 | 1303.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 55.13 | 174 | 0 | 0 | 0 | 174 | 0 | 386 | 0 | 4.83 | 0 | 165 | 56 | 35 | 31 | 50 | 0 | 0 | 5.8 | 162 | 0.58 | 0 | 307 | 6 | 120 | 110 | 0 | 0 | 1185 | 0 | 6234.52 | 13126.5 | 83.45
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 36 | 83 | 90 | 0 | 0 | 55 | 72 | 0 | 63 | 380 | 285 | 520 | 0 | 0 | 0 | 316 | 0 | 0 | 26 | 70 | 0 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 14 | 45 | 0 | 0 | 75 | 62 | 3 | 40 | 0 | 8 | 157 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1050 | 15 | 51 | 70 | 185 | 0 | 354 | 0 | 47 | 197 | 28 | 86 | 50 | 51 | 6 | 15 | 70 | 36 | 25 | 52 | 25 | 0 | 220 | 359 | 36 | 0 | 0 | 151 | 15 | 0 | 81 | 30 | 0 | 17 | 0 | 54.5 | 68 | 106 | 30 | 2 | 42.56 | 12 | 7110.06 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.08 | 865 | 0 | 1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 48.32 | 172 | 0 | 0 | 0 | 183 | 0 | 342 | 0 | 4.27 | 0 | 166 | 56 | 60 | 27 | 49 | 0 | 0 | 5.2 | 142 | 0.51 | 0 | 307 | 8 | 120 | 110 | 0 | 0 | 1225 | 0 | 6326.38 | 13436.44 | 83.45
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 47 | 119 | 140 | 0 | 0 | 35 | 122 | 0 | 76 | 380 | 283 | 520 | 0 | 0 | 0 | 314 | 0 | 0 | 21 | 108 | 0 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 22 | 48 | 0 | 0 | 75 | 62 | 2 | 40 | 0 | 0 | 157 | 0 | 0 | 0 | 2 | 0 | 143 | 0 | 0 | 0 | 1100 | 9 | 51 | 70 | 185 | 0 | 351 | 0 | 49 | 186 | 28 | 90 | 70 | 51 | 8 | 16 | 70 | 38 | 25 | 39 | 25 | 0 | 220 | 355 | 36 | 0 | 0 | 148 | 8 | 0 | 81 | 30 | 0 | 17 | 70 | 54.5 | 67 | 106 | 29 | 2 | 33.04 | 12 | 7350.54 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.97 | 863 | 0 | 1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 36.52 | 180 | 0 | 6 | 0 | 174 | 0 | 382 | 0 | 3.45 | 0 | 166 | 57 | 70 | 21 | 49 | 0 | 0 | 3.9 | 108 | 0.39 | 0 | 307 | 6 | 120 | 110 | 0 | 0 | 1117 | 0 | 6181.23 | 13531.77 | 83.44
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 54 | 132 | 140 | 0 | 0 | 26 | 126 | 0 | 96 | 380 | 272 | 520 | 0 | 0 | 0 | 313 | 0 | 0 | 13 | 108 | 24 | 22 | 0 | 440 | 0 | 0 | 0 | 0 | 25 | 48 | 0 | 0 | 88 | 74 | 1 | 40 | 0 | 6 | 157 | 0 | 0 | 0 | 8 | 0 | 146 | 0 | 0 | 0 | 1102 | 6 | 51 | 70 | 185 | 0 | 355 | 0 | 49 | 183 | 28 | 90 | 70 | 51 | 8 | 16 | 70 | 34 | 25 | 23 | 20 | 0 | 220 | 350 | 36 | 0 | 0 | 151 | 8 | 0 | 81 | 30 | 0 | 17 | 100 | 54.5 | 67 | 106 | 33 | 1 | 21.05 | 12 | 7443.55 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.81 | 864 | 0 | 1369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 23.15 | 180 | 0 | 55 | 0 | 182 | 0 | 376 | 0 | 2.13 | 0 | 163 | 58 | 70 | 12 | 49 | 0 | 0 | 2.8 | 63 | 0.24 | 0 | 307 | 7 | 110 | 110 | 0 | 0 | 1117 | 0 | 6107.13 | 13550.68 | 83.44
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 54 | 131 | 140 | 0 | 0 | 35 | 126 | 0 | 84 | 380 | 285 | 520 | 0 | 0 | 0 | 315 | 0 | 0 | 5 | 108 | 24 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 21 | 50 | 0 | 0 | 88 | 36 | 0 | 40 | 0 | 8 | 157 | 0 | 0 | 0 | 8 | 0 | 146 | 0 | 0 | 0 | 1100 | 2 | 51 | 70 | 177 | 0 | 351 | 0 | 46 | 196 | 29 | 90 | 70 | 51 | 8 | 16 | 70 | 34 | 25 | 8 | 20 | 0 | 220 | 373 | 36 | 0 | 0 | 152 | 0 | 0 | 81 | 30 | 0 | 17 | 0 | 54.5 | 68 | 124 | 34 | 0 | 8.56 | 12 | 7269.06 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.18 | 917 | 4 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8.85 | 177 | 0 | 99 | 0 | 179 | 0 | 337 | 0 | 0.8 | 0 | 164 | 57 | 50 | 5 | 49 | 0 | 0 | 0.9 | 25 | 0.1 | 0 | 250 | 6 | 110 | 110 | 0 | 0 | 1111 | 0 | 5921.83 | 13190.89 | 83.43
18:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35 | 54 | 131 | 140 | 45 | 0 | 35 | 90 | 0 | 66 | 350 | 292 | 420 | 0 | 17 | 0 | 315 | 0 | 0 | 0 | 108 | 23 | 22 | 0 | 400 | 0 | 15 | 0 | 0 | 20 | 50 | 11 | 0 | 70 | 36 | 0 | 40 | 12 | 4 | 156 | 0 | 0 | 0 | 8 | 16 | 146 | 0 | 0 | 0 | 1057 | 0 | 51 | 70 | 138 | 0 | 300 | 0 | 49 | 199 | 32 | 90 | 70 | 76 | 19 | 16 | 52 | 34 | 25 | 1 | 20 | 0 | 220 | 333 | 36 | 0 | 0 | 139 | 0 | 0 | 82 | 30 | 0 | 17 | 80 | 54.5 | 106 | 126 | 32 | 0 | 0.74 | 12 | 7080.24 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.29 | 914 | 17 | 1271 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 0.45 | 169 | 0 | 140 | 0 | 163 | 0 | 379 | 0 | 0.07 | 0 | 165 | 57 | 50 | 1 | 70 | 0 | 0 | 0.1 | 3 | 0.01 | 0 | 200 | 6 | 120 | 110 | 0 | 0 | 1050 | 0 | 5837.92 | 12918.16 | 83.43
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 37 | 131 | 141 | 110 | 6 | 35 | 144 | 0 | 93 | 400 | 252 | 420 | 0 | 35 | 0 | 310 | 0 | 0 | 0 | 142 | 23 | 19 | 0 | 400 | 0 | 15 | 0 | 0 | 13 | 50 | 53 | 0 | 100 | 88 | 0 | 40 | 30 | 13 | 157 | 0 | 0 | 0 | 8 | 40 | 146 | 0 | 0 | 0 | 1144 | 0 | 51 | 85 | 182 | 0 | 355 | 0 | 50 | 182 | 33 | 90 | 70 | 132 | 29 | 16 | 80 | 34 | 52.2 | 0 | 28 | 0 | 220 | 314 | 36 | 0 | 0 | 149 | 0 | 0 | 82 | 30 | 0 | 17 | 100 | 54.5 | 115 | 145 | 34 | 0 | 0 | 12 | 7841.7 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 35 | 1355 | 0 | 0 | 0 | 55 | 0 | 99 | 50 | 35 | 0 | 0 | 22 | 0 | 182 | 0 | 210 | 0 | 179 | 0 | 414 | 0 | 0 | 0 | 164 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 108 | 110 | 0 | 0 | 1160 | 0 | 6866 | 14707.7 | 83.42
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 0 | 0 | 54 | 131 | 141 | 110 | 15 | 35 | 144 | 0 | 99 | 350 | 275 | 420 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 125 | 23.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 17 | 34 | 82 | 0 | 100 | 88 | 0 | 40 | 0 | 13 | 157 | 0 | 0 | 0 | 8 | 17 | 150 | 0 | 0 | 0 | 1195 | 0 | 51 | 80 | 182 | 0 | 355 | 0 | 51 | 182 | 34 | 90 | 70 | 132 | 29 | 12 | 80 | 34 | 52.2 | 0 | 28 | 0 | 220 | 348 | 36 | 0 | 0 | 152 | 0 | 0 | 82 | 30 | 0 | 17 | 100 | 17 | 115 | 145 | 34 | 0 | 0 | 12 | 7818.7 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239 | 35 | 1364 | 0 | 0 | 0 | 35 | 0 | 99 | 0 | 28 | 0 | 0 | 22 | 0 | 174 | 0 | 209 | 0 | 170 | 0 | 414 | 0 | 0 | 0 | 160 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 5 | 108 | 110 | 0 | 0 | 1200 | 0 | 6827 | 14645.7
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 | 54 | 131 | 143 | 110 | 15 | 35 | 144 | 0 | 100 | 350 | 301 | 420 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 125 | 23.5 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 32 | 34 | 81 | 0 | 100 | 62 | 0 | 40 | 0 | 15 | 156 | 0 | 0 | 0 | 8 | 17 | 148 | 0 | 0 | 0 | 1155 | 0 | 51 | 80 | 182 | 0 | 354 | 0 | 51 | 200 | 34 | 90 | 70 | 128 | 27 | 12 | 80 | 36 | 52.2 | 0 | 28 | 0 | 220 | 381 | 36 | 0 | 0 | 152 | 15 | 0 | 82 | 30 | 0 | 17 | 100 | 24 | 115 | 145 | 33 | 0 | 0 | 12 | 7857.7 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1235 | 40 | 1360 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 163 | 0 | 171 | 0 | 414 | 0 | 0 | 0 | 162 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 5 | 108 | 110 | 0 | 0 | 1220 | 0 | 6647 | 14504.7 | 83.42
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 16 | 54 | 131 | 127 | 110 | 15 | 35 | 144 | 0 | 100 | 350 | 283 | 420 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 125 | 23.8 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 25 | 34 | 81 | 0 | 100 | 62 | 0 | 40 | 0 | 16 | 156 | 0 | 0 | 0 | 8 | 17 | 149 | 0 | 0 | 0 | 1152 | 0 | 51 | 80 | 182 | 0 | 355 | 0 | 51 | 182 | 34 | 90 | 70 | 120 | 27 | 12 | 80 | 36 | 52.2 | 0 | 28 | 0 | 220 | 350 | 36 | 0 | 0 | 153 | 0 | 0 | 82 | 30 | 0 | 17 | 100 | 17 | 115 | 145 | 33 | 0 | 0 | 12 | 7756 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242 | 86 | 1358.15 | 0 | 0 | 0 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 169 | 0 | 180 | 0 | 414 | 0 | 0 | 0 | 163 | 57 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 108 | 110 | 0 | 0 | 1230 | 0 | 6742.15 | 14498.15 | 83.41
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 36 | 54 | 131 | 136 | 110 | 7 | 0 | 144 | 0 | 100 | 350 | 296 | 420 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 125 | 22 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 34 | 81 | 0 | 100 | 62 | 0 | 40 | 0 | 18 | 157 | 0 | 0 | 0 | 8 | 17 | 150 | 0 | 0 | 0 | 1154 | 0 | 51 | 80 | 185 | 0 | 355 | 0 | 52 | 190 | 35 | 90 | 70 | 125 | 29 | 14 | 80 | 38 | 52.2 | 0 | 29 | 0 | 152 | 355 | 36 | 0 | 0 | 151 | 0 | 0 | 82 | 30 | 0 | 17 | 100 | 17 | 115 | 145 | 33 | 0 | 0 | 12 | 7706.2 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239 | 88 | 1361.42 | 0 | 0 | 0 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 175 | 0 | 174 | 0 | 324 | 0 | 0 | 0 | 165 | 57 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 108 | 110 | 0 | 0 | 1230 | 0 | 6649.42 | 14355.62 | 83.41
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 35 | 36 | 131 | 138 | 110 | 0 | 0 | 144 | 0 | 96 | 350 | 301 | 350 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 125 | 22 | 22 | 0 | 350 | 0 | 0 | 0 | 0 | 10 | 34 | 80 | 0 | 100 | 72 | 0 | 40 | 0 | 23 | 156 | 0 | 0 | 0 | 8 | 19 | 150 | 0 | 0 | 0 | 1156 | 0 | 51 | 88 | 185 | 0 | 355 | 0 | 52 | 199 | 35 | 90 | 70 | 120 | 29 | 14 | 80 | 38 | 52.2 | 0 | 29 | 0 | 15 | 378 | 36 | 0 | 0 | 152 | 12 | 0 | 82 | 30 | 0 | 17 | 100 | 17 | 115 | 145 | 33 | 0 | 0 | 12 | 7498.2 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1243 | 98 | 1357.71 | 0 | 0 | 0 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 181 | 0 | 178 | 0 | 414 | 0 | 0 | 0 | 164 | 55 | 75 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 110 | 0 | 0 | 1230 | 0 | 6825.71 | 14323.91 | 83.4
Total KWH | 0 | 656640 | 228480 | 0 | 0 | 0 | 0 | 0 | 9489600 | 0 | 0 | 309600 | 753480 | 2059200 | 1955040 | 694265 | 50997 | 605896 | 1431360 | 0 | 931200 | 8883000 | 6959215 | 10359545 | 0 | 58911 | 0 | 7647503 | 0 | 0 | 207766 | 1326000 | 444600 | 463320 | 0 | 9741818 | 0 | 30109 | 0 | 0 | 202560 | 901352 | 432358 | 0 | 1869120 | 810240 | 26039 | 946520 | 51855 | 377280 | 3607272.73 | 0 | 0 | 0 | 133149.6 | 204909 | 3451920 | 0 | 0 | 0 | 21959998 | 118935 | 1111432 | 961818 | 3328727.27 | 0 | 8452100 | 0 | 961440 | 4721000 | 788184 | 1256640 | 1609990 | 1416960 | 272160 | 302520 | 1272240 | 799680 | 705077 | 442436 | 314272 | 0 | 4939300 | 8495000 | 853000 | 369960 | 0 | 3505827 | 133392 | 0 | 1483200 | 717504 | 0 | 418000 | 768330 | 569520 | 1518000 | 2304000 | 1198080 | 15200 | 351810 | 182160 | 156920012.6 | 21854720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 669240 | 22130910 | 401760 | 26898981 | 0 | 0 | 0 | 358848 | 0 | 343632 | 27648 | 39499 | 0 | 713480 | 32944 | 381000 | 4453636 | 0 | 3627436 | 0 | 4262400 | 0 | 9017672.7 | 0 | 33480 | 0 | 4000000 | 1324800 | 1131326 | 213136 | 1240003 | 0 | 0 | 40193.4 | 1114560 | 4123.5 | 0 | 5629000 | 191461 | 2757000 | 2635000 | 0 | 0 | 23022545.45 | 0 | 138550435.05 | 295470447.65

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-04-2025 | during | 08-04-2025 | during | 08-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 252 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 6 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 310 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 50 | 141 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 35 | 55 | 55 | 35 | 35 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 23 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 19 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 110 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 131 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 17 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 93 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 13 | 144 | 162 | 162 | 144 | 144 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 36 | 37 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 440 | 400 | 584 | 584 | 584 | 584 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 520 | 420 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 30 | 142 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2739 | 3167 | 5269.9 | 5331.9 | 4038.13 | 4135.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 146 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 40 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 53 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 39 | 50 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 63 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 7 | 13 | 8 | 25 | 8 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.79 | 0 | 3.79 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 30 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 45 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 900 | 1144 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 13 | 2 | 0 | 2 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 156 | 157 | 155 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1414 | 1897 | 2990.51 | 3002.72 | 2990.51 | 3002.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 182 | 0 | 0 | 0 | 0 | -
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 33 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 172 | 182 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 85 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 28 | 47 | 47 | 47 | 47 | -
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 0 | 0 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 51 | 132 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 18 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 16 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 55 | 80 | 114 | 114 | 80 | 80 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 9 | 27 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 90 | 115 | 115 | 34 | 90 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1204 | 1469.2 | 1741.99 | 1676.99 | 1511.05 | 1520.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-04-2025 | during | 08-04-2025 | during | 08-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 60 | 34 | 157.5 | 157.5 | 100 | 100 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 1.9 | 0 | 1.9 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 90 | 145 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 115 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.8 | 0 | 47.5 | 0 | 47.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 32 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 312.8 | 360.5 | 598.4 | 549 | 540.9 | 491.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 36 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 158 | 149 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 82 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 0 | 100 | 100 | 100 | 100 | 100 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 314 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 220 | 220 | 220 | 220 | 230 | 230 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 946 | 948 | 999 | 999 | 974 | 974
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 907 | 864 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105 | 86 | 86 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94.92 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 808 | 1224 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1809.92 | 2123 | 3615.2 | 3520.2 | 3081.01 | 2986.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 100 | 165 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 8 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 108 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 946 | 1160 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 110 | 110 | 110 | 110 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.62 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1489.62 | 1693 | 2162.12 | 2226.12 | 2050.12 | 2049.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Low gas pressure
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 22 | 22 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 198 | 182 | 214 | 214 | 214 | 214 | -
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 194 | 210 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 169 | 179 | 220 | 220 | 220 | 220 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 0 | 0 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 99 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 55 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.03 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1042.83 | 1355 | 748 | 748 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 55.44 | 0 | 62 | 0 | 62 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 99 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2177.3 | 2601 | 2510.14 | 2342.99 | 3034.89 | 2867.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 57 | 68 | 68 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 165 | 164 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.3 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 167 | 0 | 162.06 | 0 | 162.06 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 509.3 | 449 | 654.46 | 456 | 641.46 | 443
System Total |  |  |  |  | 27566.2 | 28535.742 | 12601.94 | 14707.7 | 20541.72 | 20104.92 | 18862.07 | 18469.27
Forecast Scenario (08-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13250 |  | 0 |  | 13250
|  |  |  | 1:00 | 13110 |  | 0 |  | 13110
|  |  |  | 2:00 | 12550 |  | 0 |  | 12550
|  |  |  | 3:00 | 12200 |  | 0 |  | 12200
|  |  |  | 4:00 | 12010 |  | 0 |  | 12010
|  |  |  | 5:00 | 11800 |  | 0 |  | 11800
|  |  |  | 6:00 | 11350 |  | 0 |  | 11350
|  |  |  | 7:00 | 11530 |  | 0 |  | 11530
|  |  |  | 8:00 | 11710 |  | 0 |  | 11710
|  |  |  | 9:00 | 12190 |  | 0 |  | 12190
|  |  |  | 10:00 | 12470 |  | 0 |  | 12470
|  |  |  | 11:00 | 12830 |  | 0 |  | 12830
|  |  |  | 12:00 | 13280 |  | 0 |  | 13280
|  |  |  | 13:00 | 13780 |  | 0 |  | 13780
|  |  |  | 14:00 | 14050 |  | 0 |  | 14050
|  |  |  | 15:00 | 14080 |  | 0 |  | 14080
|  |  |  | 16:00 | 14020 |  | 0 |  | 14020
|  |  |  | 17:00 | 13630 |  | 0 |  | 13630
|  |  |  | 18:00 | 13060 |  | 0 |  | 13060
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 14920 |  | 0 |  | 14920
|  |  |  | 19:30 | 14970 |  | 0 |  | 14970
|  |  |  | 20:00 | 14940 |  | 0 |  | 14940
|  |  |  | 21:00 | 14660 |  | 0 |  | 14660
|  |  |  | 22:00 | 14170 |  | 0 |  | 14170
|  |  |  | 23:00 | 13460 |  | 0 |  | 13460
Probable Maximum Temperature: |  |  | 37.40°C
Probable Maximum Demand at Day Peak: |  |  | 13280.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14970.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14970.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 315.05 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:23 hrs on 08-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12601.94 | MW | 12:00 Hr. | Energy Generated |  |  | 295.4704 |  | MKWHr.
| Day Peak Demand |  |  | 12601.94 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.911 |  | MKWHr.
| Evening Peak Generation |  |  | 14707.7 | MW | 19:00 Hr. | Energy Demand |  |  | 296.3814 |  | MKWHr.
| Evening Peak Demand |  |  | 14800.7 | MW | 19:00 Hr. | Maximum Temperature |  |  | 35.5 |  | °C
| Minimum Generation of the Day |  |  | 9267.5 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 978.2 |  | MMCFD
| Maximum Generation of the Day |  |  | 14707.7 | MW | 19:00 Hr. | Production Cost per KWHr |  |  | 6.351 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 53.9886 | 0 | 11.0611 | 0 | 0 | 0.20777 | 0 | 0 | 65.2574 | Gas | 128.9194 | Gas | 418315983.3205
| Chattogram Zone |  |  | 3.8292 | 25.5673 | 4.4331 | 0 | 0.94652 | 0.14497 | 0 | 0.20256 | 35.1236 | Coal | 81.6745 | Coal | 594837896.8569
| Cumilla Zone |  |  | 21.2754 | 0 | 6.1992 | 0 | 0 | 0.44244 | 0.79968 | 0 | 28.7167 | HFO | 29.8427 | HFO | 533515570.542
| Mymensingh Zone |  |  | 1.1981 | 0 | 4.5737 | 0 | 0 | 0.36701 | 0 | 0 | 6.1388 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 21.6835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6835 | Hydro | 0.94652 | Hydro | 94652
| Khulna Zone |  |  | 0 | 22.1309 | 0.40176 | 0 | 0 | 0.66924 | 21.8547 | 0 | 45.0566 | Solar | 4.3314 | Solar | 70475248.069
| Barishal Zone |  |  | 5.5835 | 28.6515 | 0 | 0 | 0 | 0.0041235 | 0 | 0 | 34.2391 | Import | 49.5534 | Import | 256337037.4
| Rajshahi Zone |  |  | 21.3611 | 0 | 0.80257 | 0 | 0 | 1.128 | 26.899 | 0 | 50.1907 | Wind | 0.20256 | Wind | 2965478.4
| Rangpur Zone |  |  | 0 | 5.3248 | 2.3713 | 0 | 0 | 1.3679 | 0 | 0 | 9.064
| Total |  |  | 128.9194 | 81.6745 | 29.8427 | 0 | 0.94652 | 4.3314 | 49.5534 | 0.20256 | 295.4704
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 418315983.3205 |  | Hydro | 94652
|  |  |  | Coal | 594837896.8569 |  | Solar | 70475248.069
|  |  |  | HFO | 533515570.542 |  | Import | 256337037.4
|  |  |  | HSD | 0 |  | Wind | 2965478.4
[5 empty] | Total: | 187,65,41,866 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8547 | Peak Hr Flow | 864.00 MW at 19:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 27932181.87 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.899 | Peak Hr Flow | 1355.00 MW at 19:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 504 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.79968 | Peak Hr Flow | 34.00 MW at 19:00 hrs.
Maximum Power Flow: |  |  | MW: | 706 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.5534 | Peak Hr Flow | 2253.00 MW at 19:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 29 |  | 4537
|  |  |  | Chattogram |  | 0 |  | 1459
|  |  |  | Cumilla |  | 10 |  | 1468
|  |  |  | Mymensingh |  | 50 |  | 1274
|  |  |  | Sylhet |  | 0 |  | 513
|  |  |  | Khulna |  | 0 |  | 1887
|  |  |  | Barishal |  | 0 |  | 461
|  |  |  | Rajshahi |  | 0 |  | 1609
|  |  |  | Rangpur |  | 0 |  | 1062
|  |  |  | Total |  | 89 |  | 14270
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 | 09:33 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to REB-2 feeder Red Hot maintenance
|  | 08:02 | Bhulta 132/33kV S/S GT2 LT is restored.
| 08:14 | 18:05 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast wall Construction
| 08:14 | 18:06 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast wall Construction
|  | 08:21 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT is restored.
|  | 08:21 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT is restored.
|  | 08:34 | Ashuganj 230/132/33kV S/S TR-OAT-11 LT is restored.
| 08:43 | 10:26 | Bhulta-Haripur 132 kV Ckt-1 Scheduled S/D from Bhulta 132/33kV end Due to Red hot
maintenace
|  | 08:55 | Gulshan 132/33kV S/S MT-2 HT is restored.
|  | 09:01 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 is restored.
| 09:02 | 09:47 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Corrective
maintenance work.
|  | 09:33 | Kulaura 132/33kV S/S TR-1 LT is restored.
| 09:39 | 13:15 | Jashore 132/33kV S/S T-3 LT Forced S/D Due to T3 Tx Abnormal Sound Remove
| 09:40 | 13:13 | Jashore 132/33kV S/S T-3 HT Forced S/D Due to T3 Tx Abnormal Sound Remove
| 09:46 | 13:00 | Barishal 230/132kV S/S ATR-2 LT Scheduled S/D Due to Oil leakage repair of Ate 2 oltc
| 09:47 | 13:03 | Barishal 230/132kV S/S ATR-2 HT Scheduled S/D Due to oil leakage repair oltc
| 10:36 | 15:21 | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end Due to
Shutdown taken by NLDC
| 10:43 | 16:15 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end.
| 10:48 | 14:05 | Savar 132/33kV S/S T-4 HT Scheduled S/D Due to Corrective maintenance work
| 10:48 | 14:05 | Savar 132/33kV S/S T-4 LT Scheduled S/D Due to Corrective maintenance work
|  | 10:50 | Savar 132/33kV S/S Main Bus-I is restored.
| 11:35 | 13:59 | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to Corrective maintenance work
| 11:40 | 16:32 | BIPTC S/S 20DF11 Scheduled S/D
| 12:04 | 16:21 | Chowmuhani-Feni 132 kV Ckt-1 Tripped from Chowmuhani 132/33kV end showing Distance Relay | [7 empty] | 51.0MW load
|  |  | Zone-1, B & C Phase. relays Due to Distance Relay Zone-1, B & C Phase. | [7 empty] | interrup.
Chowmuhani 132/33kV
end
| 12:04 | 12:28 | Chowmuhani-Ramganj 132 kV Ckt-2 Tripped from Ramganj 132/33kV end showing Trip relay K34X
for P743 relays Due to Distance Trip, Zone-2 Phase A B C
| 12:04 |  | Sirajgonj 225MW CCPP Unit-2 Tripped with remarks:- GT
| 12:04 | 12:49 | Chowmuhani-Ramganj 132 kV Ckt-1 Tripped from Ramganj 132/33kV end showing Trip relay K34X | [7 empty] | 42.0MW load
|  |  | for P743 relays Due to Overcurrent A B C Trip | [7 empty] | interrup. Ramganj
132/33kV end
| 12:28 | 16:21 | Chowmuhani-Feni 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end Due to Maintenance
Work (SOTF shown by Feni S/S)
| 12:31 | 17:56 | Ishwardi-Natore 132kV Ckt-1 Project Work S/D from Ishurdi 132/33kV end Due to
Reconducting
| 12:43 | 14:41 | Chowmuhani-Ramganj 132 kV Ckt-1 Forced S/D from Chowmuhani 132/33kV end Due to 789BP
Flashing shown and from Ramganj 132/33kV end Due to Line Fault
| 14:13 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 14:33 | 15:45 | Sonargaon 132/33kV S/S Tr-1 LT Forced S/D Due to Due to 33kV PBS Astafeed feeder E/F, R&B | [7 empty] | 35.0MW load
|  |  | phase Fuse barrel bursts at Auxiliary Transformer-1. | [7 empty] | interrup.
| 14:33 | 15:45 | Sonargaon 132/33kV S/S Tr-1 HT Forced S/D Due to Due to 33kV PBS Astafeed feeder E/F, R&B | [7 empty] | 35.0MW load
|  |  | phase Fuse barrel bursts at Auxiliary Transformer-1. | [7 empty] | interrup.
| 15:46 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- ST
| 16:19 |  | Ghorasal-Joydeb-B 132kV Ckt-1 Forced S/D from Joydebpur 132/33kV end.
| 16:25 | 21:17 | Ghorasal-Joydeb-B 132kV Ckt-2 Forced S/D from Joydebpur 132/33kV end.
| 18:13 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:-
|  | 18:35 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 HT is restored.
|  | 18:39 | Cantonment 132/33kV S/S Transformer-2 (T-2) HT is restored.
|  | 18:40 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 LT is restored.
| 19:00 |  | Evening peak Generation is 14707 MW
| 19:39 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is ON with remarks:- FGMO Minimum @ 19:37 hrs Executed
by Mr. shawkat, SDE, NLDC
| 21:14 |  | Joydebpur-Kodda B 132 kV Ckt-1 Forced S/D from Joydebpur 132/33kV end.
| 21:17 |  | Joydebpur-Kodda B 132 kV Ckt-2 Forced S/D from Joydebpur 132/33kV end.
| 21:34 | 22:22 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D Due to Red Hot Removing | [7 empty] | 15.0MW load
interrup.
| 21:38 | 22:19 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D Due to Red Hot Removing | [7 empty] | 15.0MW load
interrup.
| 02:19 | 02:34 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing REF630 relays Due to | [7 empty] | 40.0MW load
|  |  | Benapole Feeder & Sharsha Feeder Fault Simultaniously . | [7 empty] | interrup.
| 05:55 | 07:34 | Ashuganj 230/132/33kV S/S TR-OAT-11 LT Scheduled S/D Due to 132kv CB hand isolator lower
clamp(transformer side) B-phase temperature 230 C @1040 amp.
| 05:57 | 07:43 | Ashuganj 230/132/33kV S/S TR-OAT-11 HT Scheduled S/D Due to 132kv CB hand isolator lower
clamp(transformer side) B-phase temperature 230 C @1040 amp.
| 06:00 |  | Minimum generation: 11984 MW
| 06:53 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ghorashal 230kV end Due to Manikganj
132/33 Kv Grid For ERS work at Ishwardi line-1 and from Ishurdi 230/132kV end Due to
Manikganj for project work
| 07:11 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 LT Scheduled S/D Due to Painting
Work.
| 07:12 |  | Cantonment 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to Painting Work.
| 07:18 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 HT Scheduled S/D Due to Painting
Work.
| 07:29 |  | Jhenaidah 132/33kV S/S Transformer T-2 LT Scheduled S/D Due to 33kV WZPDCL Bus Section | [7 empty] | 30.0MW load
|  |  | 1&2 B Phase Red Hot Maintenance. | [7 empty] | interrup.
| 07:30 |  | Jhenaidah 132/33kV S/S Transformer T-2 HT Scheduled S/D Due to 33kV WZPDCL Bus Section | [7 empty] | 30.0MW load
|  |  | 1&2 B Phase Red Hot Maintenance Work. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9489600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8883000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 252 | 6959215 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 6 | 50997 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 310 | 7647503 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 309600 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 141 | 1955040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 605896 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 58911 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 444600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 19 | 463320 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 228480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 110 | 694265 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2059200 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 656640 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 93 | 931200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1431360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 207766 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 37 | 753480 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9741818 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 420 | 10359545 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1326000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3167 | 65257436
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 133149.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 118935 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 946520 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3451920 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 40 | 204909 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 53 | 432358 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 50 | 901352 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1869120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 377280 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26039 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 30109 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 30 | 51855 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 810240 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1144 | 21959998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 202560 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 157 | 3607272.73 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1897 | 35123617.33
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4721000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8452100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 788184 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 961440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 182 | 3328727.27 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1111432 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 85 | 961818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 28 | 314272 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1609990 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 132 | 1416960 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 34 | 799680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 705077 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 302520 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1272240 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 272160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1256640 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 442436 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1469.2 | 28716676.27
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 34 | 1198080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 145 | 2304000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 115 | 1518000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 351810 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 182160 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 569520 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 360.5 | 6138770
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 853000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 369960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3505827 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 717504 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1483200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 100 | 768330 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 418000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 133392 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 314 | 8495000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 220 | 4939300 | Partial Shutdown due to maintenance
Sylhet Area Total |  |  |  |  | 2368.568 | 948 | 21683513
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 864 | 21854720 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 401760 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 669240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1224 | 22130910 | Rev-01
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2123 | 45056630
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | Partial Shutdown due to maintenance
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 8 | 191461 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 108 | 2757000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1160 | 23022545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2635000 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5629000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4123.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1693 | 34239129.95
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 39499 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4453636 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 210 | 3627436 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 179 | 4262400 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9017672.7 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 32944 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 343632 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 55 | 358848 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 27648 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33480 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1355 | 26898981 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 381000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 713480 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2601 | 50190656.7
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1324800 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 4000000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1240003 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40193.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1131326 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 213136 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1114560 | -
Rangpur Area Total |  |  |  |  | 950 | 449 | 9064018.4
Eastern Grid Total |  |  |  |  | 16921.242 | 7841.7 | 156920012.6
Western Grid Total |  |  |  |  | 11614.5 | 6866 | 138550435.05
National Grid Total |  |  |  |  | 28535.742 | 14707.7 | 295470447.65
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-04-2025
Zone Total Scenario at Evening Peak Hour (19:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9162.18 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5019.2 | MW
i) Dhaka area |  |  | 4508.08 |  | MW | i) Khulna area |  |  |  | 1887.2 | MW
ii) Chattogram area |  |  | 1458.6 |  | MW | ii) Barishal area |  |  |  | 461 | MW
iii) Cumilla area |  |  | 1458.5 |  | MW | iii) Rajshahi area |  |  |  | 1609 | MW
iv) Mymensingh area |  |  | 1224 |  | MW | iv) Rangpur area |  |  |  | 1062 | MW
v) Sylhet area |  |  | 513 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14181.38 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 12 | 11:00 | 67 | Jaldhaka | 84 | 19:00 | 133 | Payra | 34 | 00:00
2 | AKSML | 118 | 23:00 | 68 | Jamalpur | 142 | 19:30 | 134 | Postogola | 43 | 23:00
3 | Aftabnagar | 32 | 18:30 | 69 | Jashore | 164 | 19:00 | 135 | Purbachal | 17 | 20:00
4 | Agargaon | 118 | 13:00 | 70 | Jhenaidah | 138 | 19:30 | 136 | Purbasadipur | 130 | 13:00
5 | Agrabad | 100 | 14:00 | 71 | Joydebpur | 126 | 19:30 | 137 | Rahanpur | 34 | 00:00
6 | Amnura | 56 | 22:00 | 72 | Joypurhat | 75 | 19:00 | 138 | Rahim | 44 | 17:00
7 | Ashuganj | 84 | 00:00 | 73 | Juldah | 17 | 15:00 | 139 | Rajbari | 85 | 19:00
8 | BSRM | 178 | 17:00 | 74 | KSRM | 14 | 23:00 | 140 | Rajendrapur | 112 | 23:00
9 | Bagerhat | 86 | 01:00 | 75 | Kabirpur | 214 | 19:00 | 141 | Rajshahi | 122 | 19:00
10 | Bajitpur | 53 | 00:00 | 76 | Kachua | 88 | 00:00 | 142 | Rajshahi-230 | 81 | 13:00
11 | Bakulia | 91 | 19:00 | 77 | Kallyanpur | 102 | 23:00 | 143 | Ramganj | 120 | 18:30
12 | Banani | 63.4 | 13:00 | 78 | Kalurghat | 40 | 10:00 | 144 | Rampur | 40 | 00:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kamrangirchar | 50.9 | 19:30 | 145 | Rangamati | 18 | 19:00
14 | Barapukuria | 74 | 19:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 153 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kasba | 41 | 20:00 | 147 | Ruppur | 6.8 | 15:00
16 | Barishal | 110 | 00:00 | 82 | Kazla | 87 | 22:00 | 148 | SSM | 10 | 03:00
17 | Barishal-230 | 104 | 21:00 | 83 | Keranigonj | 69 | 01:00 | 149 | Saidpur | 120 | 14:00
18 | Baroaulia | 58 | 11:00 | 84 | Khagrachori | 34 | 18:30 | 150 | Satkhira | 143 | 19:00
19 | Baroirhat | 64 | 21:00 | 85 | Khulna | 77 | 13:00 | 151 | Satmasjid | 96 | 19:00
20 | Bashundhara | 168 | 15:00 | 86 | Khulshi | 173 | 19:00 | 152 | Savar | 180 | 19:00
21 | BashundharaCement | 13 | 11:00 | 87 | Kishoreganj | 152 | 00:00 | 153 | SevenRings | 13.27 | 17:00
22 | Beanibazar | 69 | 18:30 | 88 | Kodda | 234 | 22:00 | 154 | ShahCement | 16 | 10:00
23 | Benapole | 76 | 19:00 | 89 | Kulaura | 46 | 18:30 | 155 | Shahjadpur | 84 | 21:00
24 | Bhaluka | 169 | 19:00 | 90 | Kurigram | 72 | 19:30 | 156 | Shahjibazar | 131 | 00:00
25 | Bhandaria | 57 | 23:00 | 91 | Kushtia | 150 | 19:00 | 157 | Shahmirpur | 61 | 21:00
26 | Bhangura | 41 | 19:30 | 92 | Lalbag | 43 | 19:00 | 158 | Shariatpur | 92 | 00:00
27 | Bheramara(GK) | 69 | 19:00 | 93 | Lalmonirhat | 64 | 19:00 | 159 | Sherpur | 156 | 19:30
28 | Bhulta | 184 | 23:00 | 94 | MI_Cement | 11 | 07:00 | 160 | Shikalbaha | 28 | 00:00
29 | Bog-Sherpur | 70 | 19:00 | 95 | Madanganj | 46 | 13:00 | 161 | Shitalakhya | 72.5 | 16:00
30 | Bogura | 176 | 19:30 | 96 | Madaripur | 112 | 22:00 | 162 | Sholosohor | 40 | 16:00
31 | Borhanuddin | 92 | 22:00 | 97 | Madartek | 77.15 | 22:00 | 163 | Shyampur | 88 | 18:00
32 | Brahmanbaria | 139 | 20:00 | 98 | Madunaghat | 52 | 00:00 | 164 | Siddhirganj | 104 | 23:00
33 | Cantonment | 81 | 14:00 | 99 | Magura | 75 | 19:30 | 165 | Sirajganj | 112 | 19:30
34 | Chandpur | 76 | 19:00 | 100 | Mahasthangarh | 82 | 00:00 | 166 | Sonargaon | 81 | 19:00
35 | Chandraghona | 37 | 19:30 | 101 | Manikganj | 126 | 20:00 | 167 | Sreemongol | 76 | 00:00
36 | Chapai | 73 | 20:00 | 102 | Maniknagar | 61 | 13:00 | 168 | Sreepur | 105 | 12:00
37 | Charsaidpur | 26 | 01:00 | 103 | Matarbari | 51 | 19:00 | 169 | Srinagar | 50.6 | 00:00
38 | Chauddagram | 79 | 18:30 | 104 | Matuail | 56 | 16:00 | 170 | Sunamganj | 50 | 00:00
39 | Chhatak | 30 | 20:00 | 105 | Millgate | 74 | 14:00 | 171 | Sylhet | 38 | 00:00
40 | Chowmuhani | 237 | 21:00 | 106 | Mirpur | 133 | 18:30 | 172 | Sylhet-132 | 112 | 15:00
41 | Chuadanga | 120 | 19:00 | 107 | Mirsorai | 9 | 15:00 | 173 | TK | 23.4 | 22:00
42 | Coxsbazar | 131 | 14:00 | 108 | Mirzapur | 50 | 23:00 | 174 | Tangail | 186 | 18:30
43 | Cumilla(N) | 185 | 18:30 | 109 | Mithapukur | 72 | 19:00 | 175 | Thakurgaon | 111 | 19:00
44 | Cumilla(S) | 159 | 18:30 | 110 | Modern | N/A | N/A | 176 | Tongi | 108 | 15:00
45 | Daudkandi | 161 | 20:00 | 111 | Mogbazar | 135.3 | 15:00 | 177 | Ullahpara | 45 | 19:00
46 | Dhaka | 48 | 12:00 | 112 | Mongla | 36 | 23:00 | 178 | Ullon | 43 | 21:00
47 | Dhamrai | 116 | 19:00 | 113 | Motijheel | 34 | 13:00 | 179 | Uttara | 81 | 16:00
48 | Dhanmondi | 135 | 13:00 | 114 | Muktagacha | 33 | 14:00 | 180 | UttaraNew | 42 | 23:00
49 | Dohazari | 114 | 19:00 | 115 | Munshiganj | 122 | 00:00 | 181 | Zigatola | 60 | 19:30
50 | Faridpur | 170 | 00:00 | 116 | Muradnagar | 32 | 13:00
51 | Fatullah | 72 | 15:00 | 117 | Mymensingh | 213 | 19:30
52 | Fenchuganj | 33 | 00:00 | 118 | Naogaon | 141 | 21:00
53 | Feni | 118 | 19:00 | 119 | Narail | 65 | 19:30
54 | GPH | 96 | 05:00 | 120 | Narinda | 54 | 14:00
55 | Ghatail | 84 | 22:00 | 121 | Narshingdi | 150 | 22:00
56 | Ghorashal | 14 | 14:00 | 122 | Natore | 163 | 19:30
57 | Ghorashal-230 | 76 | 20:00 | 123 | Nawabganj | 59 | 00:00
58 | Goalpara | 32 | 00:00 | 124 | Netrakona | 143 | 00:00
59 | Gollamari | 84 | 00:00 | 125 | New | 70 | 14:00
60 | Gopalganj | 115.2 | 19:00 | 126 | Niamatpur | 118 | 22:00
61 | Gulshan | 118 | 15:00 | 127 | Noapara | 52 | 14:00
62 | Halishahar | 77 | 08:00 | 128 | PHP | 6 | 03:00
63 | HaripurSBU | 126 | 22:00 | 129 | Pabna | 122 | 19:00
64 | Hasnabad | 70 | 19:00 | 130 | Palashbari | 138 | 19:00
65 | Hathazari | 87 | 19:00 | 131 | Panchagarh | 55 | 19:30
66 | Ishurdi | 75 | 19:00 | 132 | Patuakhali | 83 | 23:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11520.2 | 0 |  | 11520.2
1:00 | 11070 | 0 |  | 11070
2:00 | 10870.2 | 0 |  | 10870.2
3:00 | 10363.2 | 0 |  | 10363.2
4:00 | 9661.7 | 0 |  | 9661.7
5:00 | 9267.5 | 0 |  | 9267.5
6:00 | 9393.88 | 0 |  | 9393.88
7:00 | 9796.74 | 0 |  | 9796.74
8:00 | 10331.2 | 0 |  | 10331.2
9:00 | 10684.26 | 0 |  | 10684.26
10:00 | 11267.02 | 0 |  | 11267.02
11:00 | 11803.74 | 0 |  | 11803.74
12:00 | 12601.94 | 0 |  | 12601.94
13:00 | 13126.5 | 70 |  | 13199.5
14:00 | 13436.44 | 92 |  | 13532.44
15:00 | 13531.77 | 136 |  | 13673.77
16:00 | 13550.68 | 164 |  | 13721.68
17:00 | 13190.89 | 127 |  | 13323.89
18:00 | 12918.16 | 90 |  | 13012.16
19:00 | 14707.7 | 89 |  | 14800.7
19:30 | 14645.7 | 72 |  | 14720.7
20:00 | 14504.7 | 73 |  | 14580.7
21:00 | 14498.15 | 70 |  | 14571.15
22:00 | 14355.62 | 0 |  | 14355.62
23:00 | 14323.91 | 0 |  | 14323.91
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 5958.2 | 5562 | 11520.2 | DAILY GENERATION CURVE
00:30 | 5799.6 | 5495.5 | 11295.1
01:00 | 5641 | 5429 | 11070 | 07-04-2025
01:30 | 5675.6 | 5294.5 | 10970.1
02:00 | 5710.2 | 5160 | 10870.2
02:30 | 5590.2 | 5026.5 | 10616.7
03:00 | 5470.2 | 4893 | 10363.2
03:30 | 5284.95 | 4727.5 | 10012.45
04:00 | 5099.7 | 4562 | 9661.7
04:30 | 4933.6 | 4531 | 9464.6
05:00 | 4767.5 | 4500 | 9267.5
05:30 | 4812.445 | 4518.245 | 9330.69
06:00 | 4857.39 | 4536.49 | 9393.88
06:30 | 5011.52 | 4583.79 | 9595.31
07:00 | 5165.65 | 4631.09 | 9796.74
07:30 | 5351.775 | 4712.195 | 10063.97
08:00 | 5537.9 | 4793.3 | 10331.2
08:30 | 5616.125 | 4891.605 | 10507.73
09:00 | 5694.35 | 4989.91 | 10684.26
09:30 | 5884.14 | 5091.5 | 10975.64
10:00 | 6073.93 | 5193.09 | 11267.02
10:30 | 6198.205 | 5337.175 | 11535.38
11:00 | 6322.48 | 5481.26 | 11803.74
11:30 | 6469.14 | 5733.7 | 12202.84
12:00 | 6615.8 | 5986.14 | 12601.94
12:30 | 6753.89 | 6110.33 | 12864.22
13:00 | 6891.98 | 6234.52 | 13126.5
13:30 | 7001.02 | 6280.45 | 13281.47
14:00 | 7110.06 | 6326.38 | 13436.44
14:30 | 7230.3 | 6253.805 | 13484.105
15:00 | 7350.54 | 6181.23 | 13531.77
15:30 | 7397.045 | 6144.18 | 13541.225
16:00 | 7443.55 | 6107.13 | 13550.68
16:30 | 7356.305 | 6014.48 | 13370.785
17:00 | 7269.06 | 5921.83 | 13190.89
17:30 | 7174.65 | 5879.875 | 13054.525
18:00 | 7080.24 | 5837.92 | 12918.16
18:30 | 7460.97 | 6351.96 | 13812.93
19:00 | 7841.7 | 6866 | 14707.7
19:30 | 7818.7 | 6827 | 14645.7
20:00 | 7857.7 | 6647 | 14504.7
20:30 | 7806.85 | 6694.575 | 14501.425 |  | Executive Engineer
21:00 | 7756 | 6742.15 | 14498.15 |  | Network Operation Division
21:30 | 7731.1 | 6695.785 | 14426.885
22:00 | 7706.2 | 6649.42 | 14355.62
22:30 | 7602.2 | 6737.565 | 14339.765
23:00 | 7498.2 | 6825.71 | 14323.91

## En-Curve
QF-LDC-12
Date | 07-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2998 | 1819 | 915 | 0 | 38 | 1327 | 40 | 3583 | 0 | 159 | 641.2 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3032 | 1903.4 | 915 | 0 | 37 | 1265.5 | 40 | 3445 | 0 | 136.5 | 520.7 | 0 | 0 | 0 | 0 | 07-04-2025
01:00 | 3066 | 1987.8 | 915 | 0 | 36 | 1204 | 40 | 3307 | 0 | 114 | 400.2 | 0 | 0 | 0 | 0
01:30 | 3151 | 2037.4 | 915.5 | 0 | 34 | 1107 | 40 | 3251.5 | 0 | 82 | 351.7 | 0 | 0 | 0 | 0 | Energy Generated | 295.4704 |  | MKWHr
02:00 | 3236 | 2087 | 916 | 0 | 32 | 1010 | 40 | 3196 | 0 | 50 | 303.2 | 0 | 0 | 0 | 0 | Energy not Served | 0.911 |  | MKWHr
02:30 | 3183 | 2042 | 916 | 0 | 32 | 963 | 40 | 3095 | 0 | 58.5 | 287.2 | 0 | 0 | 0 | 0 | Total Energy Requirement | 296.3814 |  | MKWHr
03:00 | 3130 | 1997 | 916 | 0 | 32 | 916 | 40 | 2994 | 0 | 67 | 271.2 | 0 | 0 | 0 | 0
03:30 | 3083 | 1885.75 | 916 | 0 | 26 | 866.5 | 40 | 2848.5 | 0 | 67 | 279.7 | 0 | 0 | 0 | 0
04:00 | 3036 | 1774.5 | 916 | 0 | 20 | 817 | 40 | 2703 | 0 | 67 | 288.2 | 0 | 0 | 0 | 0
04:30 | 3012.5 | 1764 | 916 | 0 | 20 | 817.5 | 40 | 2623 | 0 | 59 | 212.6 | 0 | 0 | 0 | 0
05:00 | 2989 | 1753.5 | 916 | 0 | 20 | 818 | 40 | 2543 | 0 | 51 | 137 | 0 | 0 | 0 | 0
05:30 | 3004.5 | 1758 | 916 | 0 | 23 | 820 | 40 | 2519 | 1.19 | 91 | 158 | 0 | 0 | 0 | 0
06:00 | 3020 | 1762.5 | 916 | 0 | 26 | 822 | 40 | 2495 | 2.38 | 131 | 179 | 0 | 0 | 0 | 0
06:30 | 3070 | 1779.5 | 916 | 0 | 27 | 819.5 | 40 | 2497.5 | 39.31 | 143.5 | 263 | 0 | 0 | 0 | 0
07:00 | 3120 | 1796.5 | 916 | 0 | 28 | 817 | 40 | 2500 | 76.24 | 156 | 347 | 0 | 0 | 0 | 0
07:30 | 3165 | 1877 | 889 | 0 | 30 | 819.615 | 40 | 2497.5 | 139.355 | 173.5 | 432.5 | 0 | 0 | 0.5 | 0
08:00 | 3210 | 1957.5 | 862 | 0 | 32 | 822.23 | 40 | 2495 | 202.47 | 191 | 518 | 0 | 0 | 1 | 0
08:30 | 3251.5 | 1988.75 | 862 | 0 | 33 | 825.175 | 40 | 2510.5 | 293.305 | 189.5 | 513.5 | 0 | 0 | 0.5 | 0
09:00 | 3293 | 2020 | 862 | 0 | 34 | 828.12 | 40 | 2526 | 384.14 | 188 | 509 | 0 | 0 | 0 | 0
09:30 | 3330.5 | 2165 | 884.5 | 0 | 32 | 824.635 | 40 | 2580 | 452.505 | 143 | 523.5 | 0 | 0 | 0 | 0
10:00 | 3368 | 2310 | 907 | 0 | 30 | 821.15 | 40 | 2634 | 520.87 | 98 | 538 | 0 | 0 | 0 | 0
10:30 | 3371.5 | 2331.5 | 907 | 0 | 35 | 845.13 | 40 | 2783.5 | 555.75 | 90.5 | 575.5 | 0 | 0 | 0 | 0
11:00 | 3375 | 2353 | 907 | 0 | 40 | 869.11 | 40 | 2933 | 590.63 | 83 | 613 | 0 | 0 | 0 | 0
11:30 | 3371.5 | 2355 | 907 | 0 | 39 | 955.97 | 40 | 3135.5 | 608.87 | 126 | 664 | 0 | 0 | 0 | 0
12:00 | 3368 | 2357 | 907 | 0 | 38 | 1042.83 | 40 | 3338 | 627.11 | 169 | 715 | 0 | 0 | 0 | 0
12:30 | 3232 | 2344 | 907 | 0 | 40 | 1172.935 | 40 | 3483 | 617.035 | 185 | 838.75 | 0 | 0 | 4.5 | 35
13:00 | 3096 | 2331 | 907 | 0 | 42 | 1303.04 | 40 | 3628 | 606.96 | 201 | 962.5 | 0 | 0 | 9 | 70
13:30 | 3047 | 2324.5 | 906.5 | 0 | 39 | 1334.02 | 40 | 3727 | 569.95 | 240.5 | 1041.5 | 0 | 0 | 11.5 | 81
14:00 | 2998 | 2318 | 906 | 0 | 36 | 1365 | 40 | 3826 | 532.94 | 280 | 1120.5 | 0 | 0 | 14 | 92
14:30 | 3055 | 2308.5 | 906.5 | 0 | 37 | 1366.5 | 40 | 3796.5 | 469.105 | 313 | 1174 | 0 | 0 | 18 | 114
15:00 | 3112 | 2299 | 907 | 0 | 38 | 1368 | 40 | 3767 | 405.27 | 346 | 1227.5 | 0 | 0 | 22 | 136
15:30 | 3148.5 | 2310.5 | 907 | 0 | 36 | 1368.5 | 40 | 3767.5 | 326.725 | 343.5 | 1269.5 | 0 | 0 | 23.5 | 150
16:00 | 3185 | 2322 | 907 | 0 | 34 | 1369 | 40 | 3768 | 248.18 | 341 | 1311.5 | 0 | 0 | 25 | 164
16:30 | 3153 | 2300 | 907 | 0 | 34 | 1344 | 40 | 3762 | 173.785 | 342 | 1292 | 0 | 0 | 23 | 145.5
17:00 | 3121 | 2278 | 907 | 0 | 34 | 1319 | 40 | 3756 | 99.39 | 343 | 1272.5 | 0 | 0 | 21 | 127
17:30 | 3131.5 | 2190 | 907 | 0 | 34 | 1295 | 40 | 3677.5 | 54.525 | 353.5 | 1351 | 0 | 0 | 20.5 | 108.5
18:00 | 3142 | 2102 | 907 | 0 | 34 | 1271 | 40 | 3599 | 9.66 | 364 | 1429.5 | 0 | 0 | 20 | 90
18:30 | 3241.5 | 2138.5 | 885.5 | 0 | 34 | 1313 | 40 | 3906 | 4.83 | 501 | 1732.1 | 0 | 0 | 16.5 | 89.5
19:00 | 3341 | 2175 | 864 | 0 | 34 | 1355 | 40 | 4213 | 0 | 638 | 2034.7 | 0 | 0 | 13 | 89
19:30 | 3386 | 2148.5 | 863 | 0 | 34 | 1364 | 40 | 4315 | 0 | 627 | 1851.2 | 0 | 0 | 17 | 72
20:00 | 3385 | 2191.5 | 864 | 0 | 36 | 1360 | 40 | 4235 | 0 | 529 | 1832.2 | 0 | 0 | 32 | 73
20:30 | 3374 | 2178.65 | 888 | 0 | 36 | 1359.075 | 40 | 4242.5 | 0 | 521.5 | 1833.2 | 0 | 0 | 28.5 | 71.5
21:00 | 3363 | 2165.8 | 912 | 0 | 36 | 1358.15 | 40 | 4250 | 0 | 514 | 1834.2 | 0 | 0 | 25 | 70
21:30 | 3291.5 | 2174.4 | 911.5 | 0 | 37 | 1359.785 | 40 | 4251 | 0 | 519 | 1827.2 | 0 | 0 | 15.5 | 35
22:00 | 3220 | 2183 | 911 | 0 | 38 | 1361.42 | 40 | 4252 | 0 | 524 | 1820.2 | 0 | 0 | 6 | 0
22:30 | 3222.5 | 2134.5 | 911 | 0 | 38 | 1359.565 | 40 | 4281.5 | 0 | 524.5 | 1820.2 | 0 | 0 | 8 | 0
23:00 | 3225 | 2086 | 911 | 0 | 38 | 1357.71 | 40 | 4311 | 0 | 525 | 1820.2 | 0 | 0 | 10 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 408 | 05:00 | 392 | 23:00 | Payra | 420 | 05:00 | 410 | 22:00
Ashuganj | 418 | 3:00 | 394 | 15:00 | Rahanpur | 405 | 04:00 | 387 | 14:00
Bhulta | 414 | 04:00 | 393 | 12:00 | Rampal | 410 | 05:00 | 394 | 19:00
Bibiana | 398 | 08:00 | 382 | 16:00
BIPTC | 399 | 05:00 | 389 | 13:00
Bogura | 391 | 05:00 | 372 | 14:00
Gopalganj | 411 | 05:00 | 394 | 23:00
Kaliakoir | 397 | 07:00 | 365 | 10:00
Madunaghat | 406 | 05:00 | 397 | 12:00
Meghnaghat | 410 | 06:00 | 396 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 241 | 08:00 | 229 | 12:00 | Keranigonj | 238 | 04:00 | 227 | 12:00
AKSML | 239 | 05:00 | 228 | 00:00 | Khulna(S) | 235 | 05:00 | 219 | 20:00
Aminbazar | 241 | 05:00 | 230 | 11:00 | Madunaghat | 238 | 06:00 | 232 | 00:00
Ashuganj | 241 | 05:00 | 229 | 13:00 | Madunaghat-400 | 240 | 05:00 | 232 | 12:00
Ashuganj-400 | 241 | 05:00 | 229 | 13:00 | Maniknagar | 237 | 06:00 | 225 | 12:00
Baghabari | 237 | 04:00 | 227 | 13:00 | Meghnaghat | 244 | 04:00 | 232 | 23:00
Barapukuria | 224 | 05:00 | 215 | 13:00 | Meghnaghat-400 | 239 | 05:00 | 229 | 12:00
Barapukuria-230 | 224 | 05:00 | 215 | 13:00 | Mirsorai | 237 | 05:00 | 225 | 00:00
Barishal | 239 | 06:00 | 227 | 23:00 | Rajshahi | 234 | 03:00 | 222 | 12:00
Bheramara | 234 | 02:00 | 222 | 12:00 | Rampal | 234 | 05:00 | 220 | 19:00
Bhulta | 238 | 04:00 | 225 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 04:00 | 219 | 14:00 | Rampura | 238 | 05:00 | 224 | 12:00
BIPTC | 236 | 02:00 | 222 | 12:00 | Shikalbaha | 236 | 06:00 | 229 | 11:00
Bogura | 238 | 05:00 | 226 | 14:00 | Shyampur | 239 | 05:00 | 227 | 12:00
Bogura-400 | 237 | 04:00 | 227 | 13:00 | Siddhirganj | 259 | 16:00 | 228 | 12:00
Borhanuddin | 242 | 05:00 | 234 | 22:00 | Sirajgonj | 243 | 03:00 | 236 | 13:00
BSRM | 238 | 05:00 | 225 | 12:00 | Sreepur | 239 | 04:00 | 224 | 13:00
Cumilla(N) | 236 | 05:00 | 220 | 12:00 | Tongi | 235 | 00:00 | 222 | 13:00
Faridpur | 234 | 06:00 | 222 | 23:00
Fenchuganj | 235 | 04:00 | 220 | 18:30
Ghorashal | 240 | 00:00 | 240 | 00:00
Ghorashal-230 | 237 | 04:00 | 223 | 13:00
Gopalganj | 235 | 05:00 | 224 | 23:00
GPH | 238 | 05:00 | 228 | 12:00
Haripur | 238 | 03:00 | 225 | 12:00
Hasnabad | 239 | 05:00 | 228 | 12:00
Hathazari | 239 | 05:00 | 230 | 12:00
Ishurdi | 237 | 02:00 | 225 | 12:00
Jhenaidah | 229 | 05:00 | 212 | 19:00
Kaliakoir | 238 | 04:00 | 73 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 00:00 | 127 | 15:00 | Madunaghat | 135 | 04:00 | 132 | 00:00
Agargaon | 139 | 05:00 | 131 | 12:00 | Magura | 137 | 06:00 | 124 | 20:00
Agrabad | 135 | 05:00 | 130 | 00:00 | Mahasthangarh | 134 | 05:00 | 125 | 13:00
AKS | 132 | 05:00 | 129 | 00:00 | Manikganj | 135 | 08:00 | 122 | 11:00
Aminbazar | 138 | 01:00 | 130 | 23:00 | Maniknagar | 137 | 04:00 | 129 | 12:00
Amnura | 136 | 02:00 | 124 | 00:00 | Matarbari | 122 | 19:00 | 111 | 00:00
Ashuganj | 142 | 04:00 | 135 | 12:00 | Matuail | 139 | 03:00 | 131.5 | 11:00
Bagerhat | 133 | 08:00 | 120 | 19:30 | Millgate | 139 | 00:00 | 127 | 14:00
Bajitpur | 140 | 02:00 | 126 | 00:00 | Mirpur | 136 | 03:00 | 130 | 12:00
Bakulia | 137 | 05:00 | 131 | 12:00 | Mirzapur | 138 | 07:00 | 124 | 12:00
Banani | 138 | 03:00 | 127 | 12:00 | Mithapukur | 131 | 05:00 | 122 | 13:00
Bangabhaban | 138 | 02:00 | 129 | 12:00 | MI_Cement | 140 | 04:00 | 132 | 12:00
Barapukuria | 137 | 05:00 | 129 | 13:00 | Modern | N/A | N/A | N/A | N/A
Barguna | 137 | 08:00 | 129 | 23:00 | Mogbazar | 141 | 06:00 | 128 | 13:00
Barishal | 132 | 05:00 | 125 | 20:00 | Mongla | 134 | 08:00 | 121 | 18:30
Barishal-230 | 134 | 06:00 | 125 | 23:00 | Motijheel | 138 | 02:00 | 129 | 12:00
Baroaulia | 134 | 06:00 | 131 | 00:00 | Muktagacha | 158 | 04:00 | 126 | 13:00
Baroirhat | 134 | 05:00 | 119 | 00:00 | Munshiganj | 137 | 00:00 | 131 | 12:00
Bashundhara | 139 | 04:00 | 127 | 13:00 | Muradnagar | 138 | 05:00 | 123 | 12:00
BashundharaCement | 138 | 01:00 | 131 | 12:00 | Mymensingh | 137 | 09:00 | 113 | 14:00
Beanibazar | 141 | 03:00 | 124 | 00:00 | Naogaon | 130 | 05:00 | 120 | 20:00
Benapole | 133 | 06:00 | 118 | 20:00 | Narail | 139 | 05:00 | 122 | 22:00
Bhaluka | 132 | 06:00 | 119 | 14:00 | Narinda | 136 | 7:00 | 129 | 15:00
Bhandaria | 126 | 08:00 | 115 | 22:00 | Narshingdi | 139 | 03:00 | 125 | 22:00
Bhangura | 136 | 05:00 | 127 | 23:00 | Natore | 134 | 04:00 | 126 | 19:30
Bheramara | 137 | 04:00 | 129 | 23:00 | Nawabganj | 137 | 06:00 | 128 | 14:00
Bheramara(GK) | 137 | 04:00 | 129 | 20:00 | Netrakona | 130 | 05:00 | 110 | 18:30
Bhulta | 135 | 01:00 | 126 | 09:00 | New | 139 | 00:00 | 127 | 15:00
Bog-Sherpur | 135 | 05:00 | 127 | 19:30 | Niamatpur | 137 | 08:00 | 128 | 14:00
Bogura | 136 | 05:00 | 129 | 13:00 | Noapara | 135 | 06:00 | 123 | 19:00
Bogura-230 | 137 | 05:00 | 129 | 13:00 | Pabna | 136 | 04:00 | 127 | 23:00
Brahmanbaria | 140 | 03:00 | 126 | 23:00 | Palashbari | 129 | 04:00 | 119 | 13:00
Cantonment | 139 | 05:00 | 131 | 12:00 | Panchagarh | 135 | 23:00 | 117 | 07:00
Chandpur | 126 | 05:00 | 118 | 00:00 | Patuakhali | 136 | 09:00 | 131 | 23:00
Chandraghona | 138 | 06:00 | 132 | 00:00 | Payra | 139 | 00:00 | 134 | 23:00
Chapai | 135 | 04:00 | 124 | 14:00 | PHP | 135 | 05:00 | 117 | 17:00
Charsaidpur | 140 | 04:00 | 132 | 12:00 | Postogola | 141 | 07:00 | 135 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Chauddagram | 135 | 05:00 | 118 | 11:00 | Purbachal | 139 | 04:00 | 126 | 15:00
Chhatak | 141 | 03:00 | 122 | 00:00 | Purbasadipur | 130 | 23:00 | 116 | 13:00
Chowmuhani | 131 | 05:00 | 109 | 00:00 | Rahanpur | 137 | 06:00 | 131 | 13:00
Chuadanga | 137 | 04:00 | 121 | 23:00 | Rahanpur-400 | 139 | 04:00 | 131 | 14:00
Coxsbazar | 117 | 06:00 | 113 | 00:00 | Rahim | 139 | 04:00 | 132 | 12:00
Cumilla(N) | 139 | 05:00 | 125 | 14:00 | Rajbari | 137 | 06:00 | 129 | 22:00
Cumilla(S) | 137 | 05:00 | 122 | 15:00 | Rajendrapur | 139 | 08:00 | 122 | 12:00
Daudkandi | 135 | 05:00 | 123 | 12:00 | Rajshahi | 135 | 06:00 | 127 | 13:00
Dhaka | 139 | 03:00 | 128 | 12:00 | Rajshahi-230 | 135 | 03:00 | 118 | 14:00
Dhamrai | 138 | 00:00 | 127 | 16:00 | Ramganj | 132 | 05:00 | 110 | 17:00
Dhanmondi | 139 | 00:00 | 132 | 12:00 | Rampur | 136 | 06:00 | 130 | 00:00
Dohazari | 130 | 04:00 | 125 | 00:00 | Rampura | 138 | 00:00 | 128 | 12:00
Faridpur | 138 | 06:00 | 131 | 23:00 | Rangamati | 137 | 06:00 | 130 | 11:00
Fatullah | 140 | 05:00 | 133 | 12:00 | Rangpur | 129 | 05:00 | 121 | 08:00
Fenchuganj | 141 | 03:00 | 130 | 14:00 | Ruppur | 137 | 05:00 | 131 | 20:00
Feni | 137 | 06:00 | 117 | 11:00 | Saidpur | 131 | 22:00 | 120 | 13:00
Ghatail | 132 | 01:00 | 119 | 08:00 | Satkhira | 132 | 05:00 | 118 | 19:00
Ghorashal | 144 | 01:00 | 135 | 22:00 | Satmasjid | 139 | 08:00 | 131 | 12:00
Goalpara | 137 | 08:00 | 124 | 19:00 | Savar | 136 | 07:00 | 129 | 11:00
Gollamari | 137 | 05:00 | 126 | 20:00 | SevenRings | 144 | 03:00 | 135 | 22:00
Gopalganj | 138 | 06:00 | 128 | 19:00 | ShahCement | 140 | 04:00 | 132 | 12:00
Gopalganj-400 | 140 | 05:00 | 133 | 22:00 | Shahjadpur | 138 | 01:00 | 132 | 21:00
Gulshan | 138 | 05:00 | 127 | 13:00 | Shahjibazar | 139 | 03:00 | 127 | 23:00
Halishahar | 136 | 05:00 | 129 | 00:00 | Shahmirpur | 136 | 19:00 | 132 | 00:00
Haripur | 139 | 07:00 | 133 | 12:00 | Shariatpur | 138 | 07:00 | 128 | 23:00
HaripurSBU | 140 | 05:00 | 133 | 12:00 | Sherpur | 138 | 01:00 | 124 | 19:30
Hasnabad | 141 | 05:00 | 135 | 11:00 | Shikalbaha | 126 | 04:00 | 120 | 11:00
Hathazari | 137 | 04:00 | 133 | 00:00 | Shikalbaha-230 | 137 | 05:00 | 133 | 00:00
Ishurdi | 139 | 06:00 | 131 | 20:00 | Shitalakhya | 140 | 04:00 | 132 | 12:00
Jaldhaka | 130 | 02:00 | 117 | 13:00 | Sholosohor | 137 | 05:00 | 132 | 00:00
Jamalpur | 139 | 02:00 | 126 | 13:00 | Shyampur | 139 | 04:00 | 134 | 14:00
Jashore | 135 | 06:00 | 121 | 19:30 | Shyampur-230 | 140 | 04:00 | 133 | 12:00
Jhenaidah | 140 | 06:00 | 126 | 19:30 | Siddhirganj | 139 | 05:00 | 132 | 08:00
Jhenaidah-230 | 140 | 04:00 | 127 | 19:30 | Sirajganj | 134 | 04:00 | 125 | 20:00
Joydebpur | 137 | 07:00 | 123 | 02:00 | Sonargaon | 139 | 05:00 | 128 | 12:00
Joypurhat | 126 | 04:00 | 116 | 20:00 | Sreemongol | 140 | 03:00 | 128 | 00:00
Juldah | 135 | 18:30 | 131 | 11:00 | Sreepur | 134 | 04:00 | 123 | 13:00
Kabirpur | 140 | 04:00 | 123 | 15:00 | Srinagar | 137 | 04:00 | 129 | 13:00
Kachua | 132 | 05:00 | 11 | 00:00 | SSM | 140 | 06:00 | 136 | 00:00
Kaliakoir | 139 | 03:00 | 128 | 10:00 | Sunamganj | 139 | 03:00 | 120 | 00:00
Kallyanpur | 138 | 07:00 | 130 | 12:00 | Sylhet | 139 | 03:00 | 124 | 00:00
Kalurghat | 137 | 21:00 | 131 | 11:00 | Sylhet-132 | 140 | 03:00 | 126 | 00:00
Kamrangirchar | 137 | 04:00 | 130 | 12:00 | Tangail | 132 | 09:00 | 117 | 08:00
Kaptai | 137 | 6:00 | 135 | 1:00 | Thakurgaon | 134 | 23:00 | 116 | 07:00
Kasba | 138 | 05:00 | 123 | 12:00 | TK | 139 | 18:00 | 132 | 11:00
Kazla | 137 | 05:00 | 129 | 12:00 | Tongi | 142 | 00:00 | 129 | 15:00
Keranigonj | 137 | 04:00 | 130 | 12:00 | Ullahpara | 136 | 05:00 | 127 | 23:00
Khagrachori | 137 | 05:00 | 129 | 12:00 | Ullon | 139 | 01:00 | 127 | 13:00
Khulna | 136 | 06:00 | 124 | 20:00 | Uttara | 139 | 00:00 | 125 | 16:00
Khulna(S) | 138 | 06:00 | 127 | 19:00 | UttaraNew | 136 | 00:00 | 129 | 12:00
Khulshi | 134 | 05:00 | 13 | 16:00 | Zigatola | 138 | 05:00 | 130 | 12:00
Kishoreganj | 136 | 05:00 | 120 | 18:30
Kodda | 135 | 19:00 | 120 | 15:00
KSRM | 136 | 07:00 | 130 | 17:00
Kulaura | 141 | 03:00 | 128 | 00:00
Kurigram | 130 | 03:00 | 116 | 13:00
Kushtia | 138 | 06:00 | 127 | 19:30
Lalbag | 137 | 04:00 | 129 | 12:00
Lalmonirhat | 129 | 22:00 | 120 | 07:00
Madanganj | 138 | 01:00 | 131 | 12:00
Madaripur | 138 | 07:00 | 131 | 00:00
Madartek | 138 | 04:00 | 127 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division