## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-04-2025 | during | 09-04-2025 | during | 09-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 140 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 323 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 98 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 117 | 145 | 149.36 | 149.36 | 138 | 138 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 16.5 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 42 | 52.19 | 52.19 | 8 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 295 | 238 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 130 | 149 | 149 | 131 | 131 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 34 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 76 | 84 | 104 | 104 | 84 | 84 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 280 | 584 | 584 | 584 | 584 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 250 | 250 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 3151.5 | 3245.5 | 5270.9 | 5331.9 | 4036.77 | 4123.77
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 20 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 148 | 150 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 105 | 68 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 72 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 68 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 89 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 22 | 5 | 28 | 5 | 28 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 108 | 108 | 50 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 3.83 | 0 | 3.83 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 41 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 62 | 60 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 3 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 35 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 5 | 3 | 5 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 157 | 222 | 155 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1948 | 2366.5 | 2992.55 | 3008.72 | 2934.55 | 2950.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 208 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 34 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 49 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 177 | 187 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 127 | 135 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 20 | 36 | 47 | 47 | 30 | 30 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 156 | 200 | 200 | 125 | 125 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 80 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 37 | 113 | 113 | 9 | 9 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 72 | 115 | 115 | 51 | 51 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 33 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1393 | 1564.2 | 2125.99 | 2060.99 | 1746.05 | 1681.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-04-2025 | during | 09-04-2025 | during | 09-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 27 | 17 | 157.5 | 157.5 | 70 | 70 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 134 | 200 | 200 | 126 | 126 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 113 | 115 | 115 | 67 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 42.87 | 0 | 49.5 | 0 | 49.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 5 | 34 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 280.87 | 310 | 600.5 | 549 | 381 | 377.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 36 | 36 | 36 | 36 | 36 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 39 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 152 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 100 | 100 | 100 | 100 | 100 | 100 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 22 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 350 | 385 | 385 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 60 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 837 | 1131 | 1199 | 1199 | 1159 | 1159
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 911 | 910 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 30 | 46 | 46 | 46 | 46 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 49 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 55 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 95.93 | 0 | 94.75 | 0 | 94.75 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1108 | 1234 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2114.93 | 2278 | 3610.95 | 3516.2 | 3095.76 | 3001.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 0 | 165 | 165 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 112 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 995 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 110 | 220 | 220 | 110 | 110 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.2 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1433.2 | 1834 | 2337.12 | 2336.12 | 2050.12 | 2049.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 49 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 20 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 27 | 27 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 198 | 177 | 214 | 214 | 192.6 | 192.6 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 200 | 207 | 220 | 220 | 220 | 220 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 196 | 220 | 220 | 198 | 198 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 375 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 98 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.05 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 756 | 759.39 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 38.22 | 0 | 62 | 0 | 62 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2203.27 | 2208.59 | 2509.99 | 2342.99 | 2413.8 | 2246.8
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 57 | 56 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 167 | 164 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.4 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 98 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 107 | 0 | 159.41 | 0 | 159.41 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 577.4 | 463 | 672.81 | 477 | 672.81 | 477
System Total |  |  |  |  | 27566.2 | 28535.742 | 13939.17 | 15400.79 | 21319.81 | 20821.92 | 18489.86 | 18065.97
Forecast Scenario (09-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14270 |  | 0 |  | 14270
|  |  |  | 1:00 | 13840 |  | 0 |  | 13840
|  |  |  | 2:00 | 13340 |  | 0 |  | 13340
|  |  |  | 3:00 | 12930 |  | 0 |  | 12930
|  |  |  | 4:00 | 12460 |  | 0 |  | 12460
|  |  |  | 5:00 | 12390 |  | 0 |  | 12390
|  |  |  | 6:00 | 11980 |  | 0 |  | 11980
|  |  |  | 7:00 | 12210 |  | 0 |  | 12210
|  |  |  | 8:00 | 12480 |  | 0 |  | 12480
|  |  |  | 9:00 | 12780 |  | 0 |  | 12780
|  |  |  | 10:00 | 13450 |  | 0 |  | 13450
|  |  |  | 11:00 | 13910 |  | 0 |  | 13910
|  |  |  | 12:00 | 14100 |  | 0 |  | 14100
|  |  |  | 13:00 | 14450 |  | 0 |  | 14450
|  |  |  | 14:00 | 14550 |  | 0 |  | 14550
|  |  |  | 15:00 | 14650 |  | 0 |  | 14650
|  |  |  | 16:00 | 14480 |  | 0 |  | 14480
|  |  |  | 17:00 | 14250 |  | 0 |  | 14250
|  |  |  | 18:00 | 13720 |  | 0 |  | 13720
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 15310 |  | 0 |  | 15310
|  |  |  | 19:30 | 15460 |  | 0 |  | 15460
|  |  |  | 20:00 | 15480 |  | 0 |  | 15480
|  |  |  | 21:00 | 15500 |  | 0 |  | 15500
|  |  |  | 22:00 | 15300 |  | 0 |  | 15300
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 35.9°C
Probable Maximum Demand at Day Peak: |  |  | 14100.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 333.03 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:29 hrs on 09-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-04-2025 | [28 empty] | Date: | 08-04-2025 | [28 empty] | Date: | 08-04-2025 | [28 empty] | Date: | 08-04-2025 | [28 empty] | Date: | 08-04-2025 | [16 empty] | Date: | 08-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 35 | 36 | 131 | 138 | 160 | 0 | 0 | 144 | 0 | 75 | 450 | 295 | 300 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 125 | 22.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 34 | 78 | 0 | 100 | 88 | 0 | 40 | 0 | 18 | 157 | 0 | 0 | 0 | 8 | 51 | 152 | 0 | 0 | 0 | 1151 | 0 | 51 | 112 | 185 | 0 | 355 | 0 | 51 | 182 | 35 | 90 | 70 | 120 | 10 | 17 | 80 | 38 | 52.2 | 0 | 30 | 0 | 15 | 348 | 36 | 0 | 0 | 152 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 17 | 115 | 145 | 33 | 0 | 0 | 12 | 7483.7 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 105 | 1370.04 | 0 | 0 | 0 | 95 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 178 | 0 | 173 | 0 | 383 | 0 | 0 | 0 | 160 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1120 | 0 | 6790.04 | 14273.74 | 83.4
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 23 | 17 | 131 | 138 | 95 | 0 | 0 | 144 | 0 | 65 | 450 | 290 | 300 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 125 | 23 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 34 | 70 | 0 | 100 | 88 | 0 | 40 | 0 | 23 | 157 | 0 | 0 | 0 | 8 | 51 | 152 | 0 | 0 | 0 | 1152 | 0 | 51 | 135 | 185 | 0 | 355 | 0 | 51 | 182 | 36 | 86 | 50 | 121 | 9 | 17 | 80 | 36 | 52.2 | 0 | 30 | 0 | 15 | 349 | 36 | 0 | 0 | 133 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 17 | 48 | 96 | 33 | 0 | 0 | 12 | 7231.2 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239 | 105 | 1352.02 | 0 | 0 | 0 | 70 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 172 | 0 | 167 | 0 | 315 | 0 | 0 | 0 | 161 | 57 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 110 | 110 | 0 | 0 | 1120 | 0 | 6570.02 | 13801.22 | 83.39
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 0 | 17 | 17 | 131 | 138 | 60 | 0 | 0 | 54 | 0 | 65 | 450 | 290 | 300 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 52 | 23 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 70 | 0 | 100 | 88 | 0 | 40 | 0 | 23 | 157 | 0 | 0 | 0 | 0 | 51 | 153 | 0 | 0 | 0 | 1151 | 0 | 51 | 137 | 185 | 0 | 355 | 0 | 51 | 182 | 36 | 52 | 50 | 121 | 9 | 17 | 80 | 36 | 52.2 | 0 | 30 | 0 | 15 | 290 | 36 | 0 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 0 | 48 | 96 | 33 | 0 | 0 | 12 | 6903.2 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1210 | 70 | 1359.2 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 160 | 0 | 167 | 0 | 315 | 0 | 0 | 0 | 161 | 57 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 110 | 110 | 0 | 0 | 1115 | 0 | 6407.2 | 13310.4 | 83.39
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 17 | 131 | 138 | 0 | 0 | 0 | 35 | 0 | 16 | 450 | 293 | 300 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 23.5 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 46 | 0 | 100 | 60 | 0 | 40 | 0 | 23 | 157 | 0 | 0 | 0 | 0 | 51 | 153 | 0 | 0 | 0 | 1150 | 0 | 51 | 138 | 185 | 0 | 355 | 0 | 52 | 183 | 36 | 52 | 50 | 60 | 0 | 17 | 80 | 34 | 52.2 | 0 | 30 | 0 | 44 | 294 | 36 | 0 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 0 | 48 | 97 | 33 | 0 | 0 | 12 | 6637.7 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 1357.93 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 154 | 0 | 168 | 0 | 316 | 0 | 0 | 0 | 160 | 57 | 35 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 110 | 110 | 0 | 0 | 1118 | 0 | 6243.93 | 12881.63 | 83.38
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 17 | 17 | 131 | 95 | 0 | 0 | 0 | 35 | 0 | 16 | 450 | 298 | 300 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 24 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 32 | 0 | 100 | 12 | 0 | 40 | 0 | 35 | 157 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 1100 | 0 | 51 | 50 | 185 | 0 | 355 | 0 | 51 | 194 | 36 | 50 | 50 | 60 | 0 | 17 | 80 | 34 | 52.2 | 0 | 0 | 0 | 50 | 301 | 36 | 0 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 0 | 48 | 97 | 33 | 0 | 0 | 12 | 6352.2 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 0 | 1357.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 158 | 0 | 172 | 0 | 325 | 0 | 0 | 0 | 170 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1118 | 0 | 6112.2 | 12464.4 | 83.38
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 131 | 95 | 0 | 0 | 0 | 35 | 0 | 16 | 450 | 276 | 300 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 0 | 100 | 12 | 0 | 40 | 0 | 35 | 157 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 1100 | 0 | 51 | 50 | 185 | 0 | 355 | 0 | 51 | 182 | 36 | 51 | 50 | 120 | 0 | 17 | 80 | 34 | 52.2 | 0 | 0 | 0 | 55 | 293 | 36 | 0 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 17 | 100 | 0 | 48 | 97 | 38 | 0 | 0 | 12 | 6344.2 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1351.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 156 | 0 | 170 | 0 | 310 | 0 | 0 | 0 | 132 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 110 | 0 | 0 | 1118 | 0 | 6046.04 | 12390.24 | 83.37
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 17 | 131 | 95 | 0 | 0 | 0 | 35 | 0 | 0 | 450 | 301 | 300 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 19 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 34 | 157 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 1105 | 0 | 51 | 10 | 185 | 0 | 300 | 0 | 51 | 197 | 33 | 51 | 50 | 120 | 0 | 17 | 52 | 30 | 52.2 | 1 | 0 | 0 | 57 | 293 | 36 | 0 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 48 | 97 | 68 | 0 | 0.56 | 10 | 6138.76 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 1061 | 0 | 1358.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 160 | 0 | 153 | 0 | 159 | 0 | 332 | 0 | 0 | 0 | 131 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 253 | 10 | 112 | 110 | 0 | 0 | 1042 | 0 | 5847.54 | 11986.3 | 83.37
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 17 | 131 | 112 | 0 | 0 | 0 | 35 | 0 | 0 | 450 | 308 | 300 | 0 | 0 | 0 | 330 | 0 | 0 | 5 | 52 | 0 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 1 | 40 | 0 | 34 | 158 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 1103 | 4 | 51 | 10 | 185 | 0 | 300 | 0 | 51 | 205 | 33 | 51 | 70 | 68 | 0 | 17 | 34 | 38 | 52.2 | 10 | 0 | 0 | 56 | 324 | 36 | 0 | 0 | 143 | 16 | 0 | 80 | 30 | 0 | 0 | 101 | 3 | 67 | 126 | 58 | 0 | 8.37 | 9 | 6263.57 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.36 | 1061 | 0 | 1357.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 7.64 | 178 | 0 | 172 | 0 | 164 | 0 | 352 | 0 | 0.65 | 0 | 165 | 55 | 0 | 3 | 31 | 0 | 0 | 0.7 | 23 | 0.1 | 0 | 200 | 10 | 120 | 110 | 0 | 0 | 997 | 0 | 5949.04 | 12212.61 | 83.36
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 17 | 131 | 112 | 0 | 20 | 0 | 35 | 0 | 0 | 450 | 306 | 300 | 0 | 0 | 0 | 329 | 0 | 0 | 12 | 52 | 19 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 1 | 40 | 0 | 8 | 158 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1105 | 5 | 51 | 10 | 185 | 0 | 356 | 0 | 52 | 205 | 33 | 51 | 70 | 68 | 0 | 17 | 34 | 36 | 52.2 | 24 | 0 | 0 | 47 | 318 | 36 | 0 | 0 | 140 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 17 | 68 | 126 | 28 | 1 | 18.73 | 12 | 6334.93 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.89 | 1060 | 0 | 1335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 21 | 173 | 0 | 167 | 0 | 176 | 0 | 357 | 0 | 1.76 | 0 | 167 | 57 | 50 | 9 | 85 | 0 | 0 | 2.3 | 55 | 0.22 | 0 | 250 | 9 | 120 | 110 | 0 | 0 | 995 | 0 | 6128.17 | 12463.1 | 83.36
09:00 | 0 | 34 | 12 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 131 | 112 | 1 | 55 | 0 | 35 | 0 | 8 | 450 | 303 | 300 | 0 | 17 | 0 | 326 | 0 | 0 | 21 | 70 | 18 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 12 | 2 | 40 | 3 | 3 | 156 | 0 | 0 | 0 | 0 | 5 | 147 | 0 | 0 | 0 | 1102 | 11 | 51 | 26 | 185 | 0 | 345 | 0 | 52 | 218 | 31 | 56 | 70 | 68 | 9 | 17 | 34 | 38 | 52.2 | 36 | 0 | 0 | 49 | 387 | 36 | 0 | 0 | 155 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 17 | 67 | 126 | 28 | 1 | 30.65 | 12 | 6626.85 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.07 | 1060 | 0 | 894 | 0 | 0 | 0 | 25 | 0 | 0 | 40 | 0 | 0 | 61 | 0 | 34.55 | 185 | 0 | 183 | 0 | 193 | 0 | 414 | 0 | 3.35 | 0 | 165 | 57 | 70 | 17 | 107 | 0 | 0 | 3.5 | 91 | 0.37 | 0 | 307 | 9 | 120 | 110 | 0 | 0 | 987 | 0 | 6068.84 | 12695.69 | 83.35
10:00 | 8 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 131 | 112 | 108 | 55 | 17 | 72 | 0 | 45 | 450 | 298 | 250 | 0 | 17 | 0 | 324 | 0 | 0 | 28 | 108 | 18 | 22 | 0 | 270 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 48 | 2 | 40 | 17 | 3 | 159 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1180 | 16 | 51 | 88 | 177 | 0 | 356 | 0 | 50 | 185 | 31 | 51 | 50 | 68 | 9 | 11 | 77 | 34 | 52.2 | 40 | 0 | 0 | 50 | 390 | 36 | 0 | 0 | 158 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 17 | 67 | 126 | 26 | 1 | 41.17 | 12 | 7014.37 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.11 | 1108 | 0 | 762 | 0 | 0 | 0 | 109 | 0 | 36 | 90 | 0 | 0 | 83 | 0 | 44.2 | 198 | 0 | 196 | 0 | 201 | 0 | 406 | 0 | 4.41 | 0 | 168 | 56 | 113 | 22 | 107 | 0 | 0 | 4.9 | 117 | 0.53 | 0 | 297 | 8 | 110 | 110 | 0 | 0 | 1005 | 0 | 6351.15 | 13365.52 | 83.35
11:00 | 8 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 131 | 112 | 295 | 55 | 17 | 72 | 0 | 65 | 450 | 295 | 250 | 0 | 17 | 0 | 324 | 0 | 0 | 31 | 160 | 19.5 | 22 | 0 | 330 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 48 | 2 | 40 | 17 | 3 | 158 | 0 | 0 | 0 | 0 | 75 | 147 | 0 | 0 | 0 | 1224 | 10 | 51 | 123 | 177 | 0 | 354 | 0 | 47 | 196 | 30 | 51 | 50 | 68 | 9 | 11 | 80 | 34 | 52.2 | 52 | 4 | 0 | 50 | 360 | 36 | 0 | 0 | 153 | 0 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 67 | 116 | 27 | 2 | 46.17 | 12 | 7421.87 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.19 | 1108 | 0 | 754 | 0 | 0 | 0 | 113 | 0 | 50 | 95 | 7 | 0 | 98 | 0 | 56.92 | 186 | 0 | 185 | 0 | 199 | 0 | 398 | 0 | 4.97 | 0 | 167 | 56 | 98 | 27 | 113 | 0 | 0 | 6 | 130 | 0.62 | 0 | 250 | 7 | 120 | 110 | 0 | 0 | 1052 | 0 | 6394.7 | 13816.57 | 83.34
12:00 | 8 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 131 | 117 | 295 | 55 | 17 | 72 | 0 | 76 | 350 | 297 | 250 | 0 | 17 | 0 | 315 | 0 | 0 | 32 | 160 | 19.5 | 22 | 0 | 450 | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 62 | 3 | 40 | 41 | 5 | 157 | 35 | 0 | 0 | 0 | 105 | 143 | 0 | 0 | 0 | 1224 | 11 | 51 | 127 | 177 | 0 | 341 | 0 | 46 | 208 | 30 | 51 | 50 | 68 | 9 | 17 | 80 | 42 | 43 | 33 | 20 | 0 | 60 | 375 | 36 | 0 | 0 | 154 | 0 | 0 | 82 | 30 | 0 | 0 | 100 | 5 | 67 | 125 | 27 | 2 | 42.87 | 12 | 7610.37 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.93 | 1108 | 0 | 756 | 0 | 0 | 0 | 113 | 0 | 50 | 95 | 27 | 8 | 102 | 0 | 38.22 | 198 | 0 | 200 | 0 | 197 | 0 | 414 | 0 | 5.05 | 0 | 167 | 57 | 98 | 29 | 113 | 0 | 0 | 6.4 | 107 | 0.2 | 0 | 200 | 8 | 120 | 110 | 0 | 0 | 995 | 0 | 6328.8 | 13939.17 | 83.34
13:00 | 8 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 131 | 134 | 295 | 55 | 47 | 72 | 0 | 98 | 350 | 296 | 250 | 0 | 17 | 0 | 316 | 0 | 0 | 31 | 160 | 19.5 | 22 | 0 | 450 | 25 | 32 | 0 | 0 | 0 | 0 | 40 | 4 | 100 | 62 | 3 | 40 | 64 | 9 | 157 | 90 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 1224 | 12 | 51 | 125 | 175 | 0 | 346 | 0 | 46 | 198 | 32 | 51 | 50 | 68 | 9 | 17 | 80 | 40 | 52.2 | 33 | 20 | 0 | 90 | 385 | 36 | 10 | 0 | 153 | 16 | 0 | 82 | 30 | 0 | 0 | 100 | 17 | 66 | 124 | 25 | 1 | 39.1 | 12 | 7765.8 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.39 | 1107 | 0 | 763 | 0 | 0 | 0 | 113 | 4 | 50 | 95 | 28 | 16 | 76 | 0 | 46.53 | 201 | 0 | 198 | 0 | 196 | 0 | 404 | 0 | 4.74 | 0 | 165 | 57 | 115 | 29 | 113 | 0 | 0 | 6.3 | 162 | 0.62 | 0 | 230 | 10 | 120 | 110 | 0 | 0 | 1000 | 0 | 6424.58 | 14190.38 | 83.33
14:00 | 40 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 129 | 133 | 295 | 55 | 55 | 72 | 0 | 85 | 450 | 280 | 250 | 0 | 17 | 0 | 315 | 0 | 0 | 27 | 160 | 17.5 | 22 | 0 | 350 | 72 | 65 | 0 | 0 | 11 | 0 | 57 | 28 | 89 | 74 | 2 | 40 | 81 | 5 | 156 | 90 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 1224 | 12 | 51 | 125 | 175 | 0 | 354 | 0 | 45 | 182 | 32 | 51 | 50 | 68 | 9 | 17 | 80 | 42 | 52.2 | 37 | 21 | 0 | 107 | 352 | 36 | 20 | 0 | 151 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 3 | 66 | 123 | 11 | 1 | 41.49 | 12 | 7856.19 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.02 | 1155 | 0 | 764 | 0 | 36 | 0 | 113 | 0 | 50 | 95 | 28 | 16 | 79 | 0 | 18.11 | 188 | 0 | 177 | 0 | 192 | 0 | 324 | 0 | 0.91 | 0 | 162 | 57 | 115 | 26 | 113 | 0 | 0 | 5.1 | 123 | 0.36 | 0 | 260 | 10 | 110 | 110 | 0 | 0 | 1012 | 0 | 6333.5 | 14189.69 | 83.33
15:00 | 58 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 130 | 123 | 297 | 55 | 55 | 72 | 0 | 83 | 450 | 298 | 250 | 0 | 17 | 0 | 313 | 0 | 0 | 21 | 142 | 17 | 22 | 0 | 350 | 72 | 65 | 10 | 0 | 26 | 0 | 62 | 35 | 89 | 74 | 2 | 40 | 104 | 4 | 157 | 90 | 0 | 0 | 0 | 105 | 145 | 0 | 0 | 0 | 1224 | 10 | 51 | 125 | 175 | 0 | 347 | 0 | 45 | 188 | 29 | 51 | 50 | 68 | 9 | 17 | 80 | 44 | 52.2 | 19 | 25 | 0 | 122 | 350 | 36 | 30 | 0 | 140 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 0 | 65 | 104 | 11 | 1 | 30.63 | 4 | 8005.83 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.1 | 1070 | 0 | 764 | 0 | 50 | 0 | 113 | 4 | 50 | 95 | 28 | 34 | 21 | 0 | 27.43 | 190 | 0 | 192 | 0 | 184 | 0 | 373 | 0 | 2.21 | 0 | 160 | 57 | 115 | 20 | 113 | 0 | 0 | 4.6 | 110 | 0.06 | 0 | 260 | 10 | 108 | 110 | 0 | 0 | 1050 | 0 | 6292.4 | 14298.23 | 83.32
16:00 | 90 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 130 | 127 | 297 | 55 | 55 | 72 | 0 | 85 | 450 | 296 | 320 | 0 | 17 | 0 | 314 | 0 | 0 | 13 | 142 | 16.5 | 22 | 0 | 320 | 35 | 50 | 19 | 0 | 26 | 0 | 78 | 17 | 89 | 74 | 1 | 40 | 68 | 4 | 160 | 90 | 0 | 0 | 0 | 105 | 145 | 0 | 0 | 0 | 1224 | 4 | 51 | 128 | 175 | 0 | 340 | 0 | 45 | 200 | 29 | 51 | 50 | 68 | 9 | 17 | 80 | 46 | 52.2 | 13 | 28 | 0 | 132 | 350 | 36 | 20 | 0 | 152 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 15 | 66 | 114 | 11 | 1 | 18.63 | 12 | 8031.33 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.12 | 1068 | 0 | 762 | 0 | 42 | 0 | 113 | 4 | 50 | 95 | 26 | 34 | 19 | 0 | 23.07 | 182 | 0 | 203 | 0 | 174 | 0 | 340 | 0 | 2.07 | 0 | 160 | 56 | 115 | 12 | 113 | 0 | 0 | 3 | 63 | 0.04 | 0 | 260 | 9 | 116 | 110 | 0 | 0 | 1020 | 0 | 6091.3 | 14122.63 | 83.32
17:00 | 82 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 130 | 139 | 297 | 55 | 55 | 72 | 0 | 83 | 450 | 282 | 320 | 0 | 17 | 0 | 314 | 0 | 0 | 5 | 160 | 17 | 22 | 0 | 320 | 17 | 15 | 34 | 0 | 6 | 0 | 78 | 0 | 48 | 24 | 0 | 40 | 34 | 9 | 156 | 53 | 0 | 0 | 0 | 51 | 147 | 0 | 0 | 0 | 1224 | 5 | 51 | 125 | 175 | 0 | 345 | 0 | 45 | 192 | 29 | 57 | 50 | 70 | 9 | 17 | 62 | 38 | 52.2 | 9 | 34 | 0 | 145 | 350 | 36 | 20 | 0 | 153 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 53 | 66 | 124 | 11 | 0 | 6.97 | 12 | 7768.17 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.78 | 1070 | 0 | 762 | 0 | 42 | 0 | 113 | 8 | 50 | 95 | 26 | 42 | 17 | 20 | 9.31 | 190 | 0 | 203 | 0 | 181 | 0 | 387 | 0 | 0.78 | 0 | 161 | 56 | 115 | 5 | 113 | 0 | 0 | 1.1 | 23 | 0.09 | 0 | 260 | 9 | 108 | 110 | 0 | 0 | 1057 | 0 | 6166.06 | 13934.23 | 83.31
18:00 | 90 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 130 | 142 | 297 | 55 | 55 | 108 | 0 | 83 | 380 | 283 | 300 | 0 | 17 | 0 | 280 | 0 | 0 | 1 | 125 | 15 | 22 | 0 | 300 | 17 | 15 | 45 | 0 | 0 | 0 | 79 | 0 | 48 | 24 | 0 | 40 | 34 | 10 | 156 | 53 | 0 | 0 | 1 | 51 | 147 | 0 | 0 | 0 | 1126 | 0 | 51 | 123 | 145 | 0 | 320 | 0 | 48 | 190 | 30 | 62 | 50 | 122 | 10 | 17 | 62 | 44 | 52.2 | 1 | 36 | 0 | 160 | 370 | 36 | 40 | 0 | 153 | 16 | 0 | 81 | 30 | 0 | 0 | 100 | 53 | 113 | 134 | 11 | 0 | 0.61 | 12 | 7683.81 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.36 | 1061 | 25 | 754 | 0 | 42 | 0 | 70 | 8 | 50 | 70 | 33 | 42 | 0 | 22 | 0.46 | 190 | 0 | 160 | 0 | 164 | 0 | 326 | 0 | 0.05 | 0 | 162 | 56 | 115 | 0 | 113 | 5 | 0 | 0.3 | 2 | 0.01 | 7 | 220 | 8 | 112 | 110 | 0 | 0 | 1054 | 17 | 5912.18 | 13595.99 | 83.31
19:00 | 90 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 21 | 130 | 141 | 297 | 55 | 55 | 108 | 0 | 83 | 450 | 150 | 300 | 0 | 17 | 0 | 322 | 0 | 0 | 0 | 160 | 17 | 22 | 0 | 300 | 22 | 65 | 49 | 0 | 0 | 51 | 79 | 17 | 100 | 86 | 0 | 86 | 57 | 19 | 156 | 160 | 0 | 3 | 8 | 74 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 187 | 0 | 360 | 0 | 47 | 182 | 32 | 71 | 50 | 149 | 30 | 17 | 80 | 40 | 52.2 | 0 | 36 | 0 | 205 | 360 | 36 | 39 | 0 | 152 | 22 | 0 | 79 | 30 | 0 | 0 | 100 | 53 | 113 | 136 | 11 | 0 | 0 | 12 | 8585.2 | 863 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 53 | 753 | 0 | 48 | 0 | 98 | 18 | 98 | 95 | 27 | 52 | 0 | 15 | 0 | 189 | 0 | 205 | 0 | 198 | 0 | 373 | 0 | 0 | 0 | 163 | 56 | 115 | 0 | 113 | 17 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 108 | 110 | 0 | 0 | 1160 | 45 | 6475 | 15060.2 | 83.3
19:30 | 90 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 130 | 144 | 238 | 55 | 55 | 108 | 0 | 83 | 450 | 150 | 300 | 0 | 25 | 0 | 322 | 0 | 0 | 0 | 160 | 17 | 22 | 0 | 300 | 53 | 65 | 51 | 0 | 0 | 68 | 79 | 17 | 100 | 88 | 0 | 46 | 85 | 16 | 156 | 160 | 0 | 12 | 10 | 87 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 187 | 0 | 360 | 0 | 47 | 182 | 32 | 72 | 50 | 155 | 37 | 17 | 80 | 40 | 52.2 | 0 | 36 | 0 | 260 | 350 | 36 | 39 | 0 | 152 | 22 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 113 | 124 | 11 | 0 | 0 | 12 | 8633.2 | 863 | 0 | 0 | 31 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 53 | 750 | 0 | 48 | 0 | 113 | 19 | 98 | 95 | 27 | 42 | 0 | 15 | 0 | 175 | 0 | 205 | 0 | 197 | 0 | 375 | 0 | 0 | 0 | 163 | 56 | 115 | 0 | 113 | 17 | 0 | 0 | 0 | 0 | 18 | 307 | 10 | 108 | 110 | 0 | 0 | 1240 | 72 | 6649 | 15282.2
20:00 | 98 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 54 | 54 | 130 | 146 | 238 | 55 | 55 | 108 | 0 | 83 | 450 | 152 | 250 | 0 | 35 | 0 | 320 | 0 | 0 | 0 | 160 | 17.5 | 22 | 0 | 280 | 35 | 50 | 50 | 0 | 0 | 68 | 79 | 17 | 100 | 88 | 0 | 46 | 68 | 20 | 214 | 160 | 0 | 20 | 24 | 87 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 187 | 0 | 355 | 0 | 48 | 195 | 33 | 73 | 50 | 156 | 37 | 17 | 80 | 40 | 52.2 | 0 | 36 | 0 | 320 | 380 | 36 | 39 | 0 | 152 | 22 | 0 | 82 | 30 | 0 | 0 | 100 | 0 | 113 | 123 | 11 | 0 | 0 | 12 | 8717.7 | 863 | 0 | 0 | 28 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1183 | 53 | 758 | 0 | 49 | 0 | 113 | 19 | 98 | 113 | 27 | 52.2 | 0 | 15 | 0 | 176 | 0 | 206 | 0 | 197 | 0 | 334 | 0 | 0 | 0 | 165 | 56 | 115 | 0 | 113 | 17 | 0 | 0 | 0 | 0 | 32 | 307 | 10 | 112 | 110 | 0 | 0 | 1240 | 72 | 6656.2 | 15373.9 | 83.29
21:00 | 98 | 105 | 42 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 54 | 130 | 145 | 238 | 55 | 55 | 108 | 0 | 84 | 450 | 140 | 250 | 0 | 35 | 0 | 323 | 0 | 0 | 0 | 160 | 16.5 | 22 | 0 | 280 | 17 | 30 | 50 | 0 | 0 | 68 | 72 | 0 | 100 | 60 | 0 | 46 | 34 | 22 | 222 | 160 | 0 | 20 | 25.5 | 68 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 187 | 0 | 360 | 0 | 49 | 182 | 34 | 72 | 70 | 156 | 37 | 17 | 80 | 46 | 52.2 | 0 | 36 | 0 | 320 | 350 | 36 | 39 | 0 | 152 | 22 | 0 | 82 | 30 | 0 | 0 | 100 | 34 | 113 | 134 | 17 | 0 | 0 | 12 | 8617.2 | 910 | 0 | 0 | 30 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234 | 55 | 759.39 | 0 | 49 | 0 | 113 | 20 | 98 | 113 | 27 | 52.2 | 0 | 22 | 0 | 177 | 0 | 207 | 0 | 196 | 0 | 375 | 0 | 0 | 0 | 164 | 56 | 115 | 0 | 113 | 15 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 112 | 110 | 0 | 0 | 1244 | 35 | 6783.59 | 15400.79 | 83.28
22:00 | 82 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 41 | 22 | 130 | 145 | 238 | 55 | 55 | 35 | 0 | 84 | 450 | 302 | 250 | 0 | 35 | 0 | 323 | 0 | 0 | 0 | 160 | 16 | 22 | 0 | 280 | 17 | 30 | 51 | 0 | 0 | 68 | 72 | 0 | 100 | 60 | 0 | 46 | 34 | 21 | 156 | 160 | 0 | 19 | 25.5 | 68 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 187 | 0 | 360 | 0 | 51 | 197 | 35 | 72 | 70 | 156 | 38 | 17 | 80 | 44 | 52.2 | 0 | 36 | 0 | 320 | 319 | 36 | 39 | 0 | 156 | 22 | 0 | 82 | 30 | 0 | 0 | 100 | 53 | 113 | 134 | 16 | 0 | 0 | 12 | 8559.7 | 911 | 0 | 0 | 30 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241 | 53 | 764.63 | 0 | 49 | 0 | 113 | 15 | 98 | 113 | 27 | 52.2 | 0 | 22 | 0 | 188 | 0 | 206 | 0 | 191 | 0 | 341 | 0 | 0 | 0 | 163 | 56 | 115 | 0 | 113 | 15 | 0 | 0 | 0 | 0 | 16 | 307 | 8 | 114 | 110 | 0 | 0 | 1244 | 35 | 6746.83 | 15306.53 | 83.27
23:00 | 82 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 130 | 145 | 238 | 55 | 17 | 35 | 0 | 83 | 450 | 302 | 200 | 0 | 35 | 0 | 323 | 0 | 0 | 0 | 160 | 16 | 22 | 0 | 250 | 17 | 30 | 50 | 0 | 0 | 68 | 72 | 0 | 100 | 60 | 0 | 46 | 34 | 27 | 158 | 160 | 0 | 18 | 25.5 | 68 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 137 | 187 | 0 | 355 | 0 | 51 | 202 | 35 | 57 | 50 | 156 | 39 | 17 | 80 | 44 | 52.2 | 0 | 37 | 0 | 320 | 302 | 36 | 39 | 0 | 153 | 22 | 0 | 82 | 30 | 0 | 0 | 100 | 53 | 113 | 124 | 14 | 0 | 0 | 12 | 8330.7 | 911 | 0 | 0 | 30 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239 | 53 | 763.34 | 0 | 49 | 0 | 113 | 15 | 98 | 113 | 27 | 52.2 | 0 | 22 | 0 | 162 | 0 | 202 | 0 | 193 | 0 | 414 | 0 | 0 | 0 | 161 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 9 | 126 | 110 | 0 | 0 | 1244 | 0 | 6746.54 | 15077.24 | 83.26
Total KWH | 857808 | 894720 | 378720 | 0 | 0 | 0 | 0 | 0 | 9738000 | 0 | 0 | 324000 | 514080 | 3150576 | 3043200 | 4067485 | 938083 | 596895 | 1582560 | 0 | 1339200 | 9941000 | 6668829 | 6794545 | 0 | 364893 | 0 | 7730931 | 0 | 0 | 227290 | 2707200 | 422400 | 525600 | 0 | 7660000 | 460418 | 564545 | 415152 | 0 | 69600 | 493026 | 829549 | 161209 | 2109120 | 1215360 | 18121 | 1037820 | 880687 | 418080 | 3694545.45 | 1272945 | 0 | 110880 | 151380 | 1412618 | 3234048 | 0 | 0 | 0 | 28374543 | 102330 | 1117760 | 2564290 | 4349091 | 0 | 8701000 | 0 | 1171680 | 4763000 | 790488 | 1392000 | 1301890 | 2379840 | 313320 | 386160 | 1735080 | 911040 | 1224101 | 320745 | 507328 | 0 | 2909400 | 8721000 | 854000 | 327120 | 0 | 3530291 | 383928 | 0 | 1977600 | 718272 | 0 | 0 | 2404890 | 532440 | 1807200 | 2810400 | 535680 | 13050 | 318500 | 285840 | 179552415.45 | 21853818 | 0 | 0 | 156480 | 138240 | 0 | 0 | 0 | 0 | 0 | 0 | 658080 | 27192720 | 555360 | 23222381.38 | 0 | 474983 | 0 | 1988448 | 114386 | 1026496 | 1463616 | 308825 | 468437 | 639600 | 133751 | 327752 | 4395091 | 0 | 4627664 | 0 | 4605782 | 0 | 8689812 | 0 | 31260 | 0 | 3942000 | 1324764 | 2004886 | 196656 | 2218608 | 47500 | 0 | 44991.24 | 1025280 | 3318 | 116544 | 6655000 | 230695 | 2774000 | 2663550 | 0 | 0 | 26843636.36 | 230400 | 153394810.98 | 332947226.43

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13939.17 | MW | 12:00 Hr. | Energy Generated |  |  | 332.9472 |  | MKWHr.
| Day Peak Demand |  |  | 14103.17 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.972 |  | MKWHr.
| Evening Peak Generation |  |  | 15400.79 | MW | 21:00 Hr. | Energy Demand |  |  | 335.9192 |  | MKWHr.
| Evening Peak Demand |  |  | 15500.79 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.9 |  | °C
| Minimum Generation of the Day |  |  | 11986.3 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 963.97 |  | MMCFD
| Maximum Generation of the Day |  |  | 15400.79 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.2987 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 49.4813 | 0 | 20.7594 | 0 | 0 | 0.22729 | 0 | 0 | 70.468 | Gas | 126.0633 | Gas | 411738689.28
| Chattogram Zone |  |  | 3.6521 | 32.0691 | 10.0769 | 0 | 1.0378 | 0.12045 | 0 | 0.0696 | 47.026 | Coal | 98.0272 | Coal | 711515813.6378
| Cumilla Zone |  |  | 22.5811 | 0 | 10.116 | 0 | 0 | 0.32075 | 0.91104 | 0 | 33.9288 | HFO | 57.7876 | HFO | 1009859712.45
| Mymensingh Zone |  |  | 0.53568 | 0 | 5.4359 | 0 | 0 | 0.33155 | 0 | 0 | 6.3031 | HSD | 0.0475 | HSD | 2635775
| Sylhet Zone |  |  | 21.8265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.8265 | Hydro | 1.0378 | Hydro | 103782
| Khulna Zone |  |  | 0 | 27.1927 | 0.85008 | 0 | 0 | 0.65808 | 21.8538 | 0 | 50.5547 | Solar | 3.927 | Solar | 64520268.3364
| Barishal Zone |  |  | 5.6682 | 33.4986 | 0.34694 | 0 | 0 | 0.003318 | 0 | 0 | 39.5171 | Import | 45.9872 | Import | 228689139.384
| Rajshahi Zone |  |  | 22.3183 | 0 | 5.9789 | 0 | 0 | 0.99861 | 23.2224 | 0 | 52.5183 | Wind | 0.0696 | Wind | 1018944
| Rangpur Zone |  |  | 0 | 5.2668 | 4.2235 | 0.0475 | 0 | 1.2669 | 0 | 0 | 10.8047
| Total |  |  | 126.0633 | 98.0272 | 57.7876 | 0.0475 | 1.0378 | 3.927 | 45.9872 | 0.0696 | 332.9472
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 411738689.28 |  | Hydro | 103782
|  |  |  | Coal | 711515813.6378 |  | Solar | 64520268.3364
|  |  |  | HFO | 1009859712.45 |  | Import | 228689139.384
|  |  |  | HSD | 2635775 |  | Wind | 1018944
[5 empty] | Total: | 243,00,82,124 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 20072.72 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8538 | Peak Hr Flow | 910.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38703672.83 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.2224 | Peak Hr Flow | 759.39 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 202 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.91104 | Peak Hr Flow | 46.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 694 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.9872 | Peak Hr Flow | 1715.39 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 15 |  | 4937
|  |  |  | Chattogram |  | 0 |  | 1438
|  |  |  | Cumilla |  | 10 |  | 1466
|  |  |  | Mymensingh |  | 66 |  | 1323
|  |  |  | Sylhet |  | 0 |  | 595
|  |  |  | Khulna |  | 0 |  | 1821
|  |  |  | Barishal |  | 0 |  | 465
|  |  |  | Rajshahi |  | 0 |  | 1772
|  |  |  | Rangpur |  | 5 |  | 1067
|  |  |  | Total |  | 96 |  | 14884
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:23 | 17:17 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast Wall Works
| 08:23 | 17:16 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast Wall Works
| 08:29 | 18:10 | Ishwardi-Natore 132kV Ckt-1 Project Work S/D from Ishurdi 132/33kV end Due to Project work
|  | 09:28 | Jhenaidah 132/33kV S/S Transformer T-2 HT is restored.
|  | 09:29 | Jhenaidah 132/33kV S/S Transformer T-2 LT is restored.
| 10:17 | 11:49 | Ashuganj-Brahmanbaria 132kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end Due to
maintenance ashugonj end. and from Ashuganj 230/132/33kV end Due to As per demand of
APSCL substation
| 10:53 | 13:40 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end Due to Project
work Ishwardi 230/132 kv grid substations and from Ishurdi 132/33kVend.
| 11:49 |  | Bibiyana South 400 MW Synchronized with remarks:- st
| 13:42 | 15:30 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end Due to Project
work Ishwardi 230/132 kv grid substations
| 13:43 | 15:41 | Ishwardi-Rooppur 132kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end.
|  | 16:03 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 is restored.
|  | 16:04 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 is restored.
| 16:06 | 16:26 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 LT Scheduled S/D Due to Bird nest cleaning
| 16:06 | 16:26 | Hasnabad 132/33kV S/S 132/33kV 404 T-1 HT Scheduled S/D Due to Bird nest cleaning
| 17:46 |  | Kodda-Rajendrapur 132kV Ckt-1 Forced S/D from Rajendrapur 132/33kV end Due to Order By NLDC
|  | 17:51 | Joydebpur-Kodda B 132 kV Ckt-2 is restored.
|  | 17:56 | Joydebpur-Kodda B 132 kV Ckt-1 is restored.
|  | 18:10 | Ishwardi-Natore 132kV Ckt-1 is restored.
|  | 18:29 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 HT is restored.
|  | 18:35 | Cantonment 132/33kV S/S Transformer-2 (T-2) HT is restored.
|  | 18:37 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 LT is restored.
| 18:56 | 19:13 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing B-Phase
Z1 Loop-3 relays.
| 19:29 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- ST
| 20:48 |  | Sirajgonj 225MW CCPP Unit-2, FGMO is OFF with remarks:- Demand full.
| 03:51 |  | Sylhet CCPP 225 MW ST was sync. at 03:51hrs.
| 04:10 | 04:50 | Khulna (C) S/S Tr-2 415 T LT Tripped showing Inst E/F relays Due to 33 KV BUS Touch by Bagdasha | [7 empty] | 17.0MW load interrup.
| 04:10 | 04:49 | Khulna (C) S/S Tr-2 415 T HT Tripped showing No relays Due to 33 KV BUS touch by Bagdasha | [7 empty] | 17.0MW load interrup.
| 04:10 | 04:49 | Khulna (C) S/S TR-1 425T LT Tripped showing O/C & E/F relays Due to 33 Kv BUS Touch by Bagdasha . | [7 empty] | 36.0MW load interrup.
| 04:39 |  | Bhola Nutan Biddut BD LTD GT-1 Synchronized with remarks:- GT-11 Synchronized to grid at
01:01 hrs. on 9th April 2025
| 06:00 |  | Minimum Generation is 12308 MW
| 06:41 |  | Bashundhara 132/33kV S/S Tr-2 HT Scheduled S/D Due to Energy Meter Change
| 06:48 |  | Bheramara P/S-Faridpur 132 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to Re-
splicins joint box
| 07:08 |  | At Bhola PP,(120/140)MVA (230/33)KV Borhanuddin PBS Transformer is S/D due to LT side
Bushing Red hot.Interruption=40 MW.
| 07:12 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 LT Scheduled S/D Due to 132/33 KV
Tr-2 Painting work
| 07:15 |  | Cantonment 132/33kV S/S Transformer-2 (T-2) HT Scheduled S/D Due to 132/33 KV Tr-2
Painting work
| 07:21 |  | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 HT Scheduled S/D Due to 132/33 KV
Tr-2 Painting work
| 07:49 |  | Bheramara P/S-Faridpur 132 kV Ckt-2 Scheduled S/D from Bheramara 230/132kV end Due to Re-
splicins joint box
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9738000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9941000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 6668829 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 938083 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 323 | 7730931 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 98 | 857808 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 324000 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 3043200 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 596895 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 364893 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16.5 | 422400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 525600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 42 | 378720 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 238 | 4067485 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 130 | 3150576 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 894720 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 84 | 1339200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1582560 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 227290 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 514080 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 280 | 7660000 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 250 | 6794545 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2707200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3245.5 | 70468015
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 151380 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 102330 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 20 | 110880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1037820 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 148 | 3234048 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1412618 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 72 | 829549 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 68 | 493026 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2109120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 22 | 418080 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 415152 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 18121 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 564545 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 161209 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 880687 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 1215360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 460418 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 1272945 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28374543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 69600 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 222 | 3694545.45 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2366.5 | 47025976.45
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4763000 | -
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8701000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 790488 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1171680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 187 | 4349091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1117760 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 135 | 2564290 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 36 | 507328 | -
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1301890 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 156 | 2379840 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 46 | 911040 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1224101 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 386160 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1735080 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 313320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 1392000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 320745 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1564.2 | 33928813
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 17 | 535680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 134 | 2810400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 113 | 1807200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 318500 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 285840 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 34 | 532440 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 310 | 6303110
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 854000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 327120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3530291 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718272 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1977600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 100 | 2404890 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 22 | 383928 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8721000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 2909400 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1131 | 21826501
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 910 | 21853818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 30 | 156480 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 49 | 138240 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 555360 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 658080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234 | 27192720 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2278 | 50554698
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 116544 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 230695 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 112 | 2774000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26843636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 110 | 2663550 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 230400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6655000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3318 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1834 | 39517143.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Low gas pressure
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 49 | 474983 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 20 | 114386 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 27 | 308825 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 177 | 4395091 | -
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 207 | 4627664 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 196 | 4605782 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 375 | 8689812 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 133751 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 468437 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 1026496 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1988448 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1463616 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31260 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 759.39 | 23222381.38 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 327752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 639600 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2208.59 | 52518284.38
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1324764 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 3942000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 47500 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2218608 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44991.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2004886 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 196656 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1025280 | -
Rangpur Area Total |  |  |  |  | 950 | 463 | 10804685.24
Eastern Grid Total |  |  |  |  | 16921.242 | 8617.2 | 179552415.45
Western Grid Total |  |  |  |  | 11614.5 | 6783.59 | 153394810.98
National Grid Total |  |  |  |  | 28535.742 | 15400.79 | 332947226.43
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9668.64 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5120.2 | MW
i) Dhaka area |  |  | 4922.44 |  | MW | i) Khulna area |  |  |  | 1821.2 | MW
ii) Chattogram area |  |  | 1438.2 |  | MW | ii) Barishal area |  |  |  | 465 | MW
iii) Cumilla area |  |  | 1456 |  | MW | iii) Rajshahi area |  |  |  | 1772 | MW
iv) Mymensingh area |  |  | 1257 |  | MW | iv) Rangpur area |  |  |  | 1062 | MW
v) Sylhet area |  |  | 595 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14788.84 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 21:00 | 67 | Jaldhaka | 83 | 20:00 | 133 | Payra | 32 | 00:00
2 | AKSML | 130 | 14:00 | 68 | Jamalpur | 140 | 13:00 | 134 | Postogola | 51 | 18:30
3 | Aftabnagar | 36 | 13:00 | 69 | Jashore | 151 | 13:00 | 135 | Purbachal | 18 | 22:00
4 | Agargaon | 119 | 13:00 | 70 | Jhenaidah | 153 | 19:00 | 136 | Purbasadipur | 144 | 20:00
5 | Agrabad | 92 | 14:00 | 71 | Joydebpur | 138 | 18:30 | 137 | Rahanpur | 36 | 21:00
6 | Amnura | 57 | 19:30 | 72 | Joypurhat | 82 | 20:00 | 138 | Rahim | 30 | 18:00
7 | Ashuganj | 83 | 13:00 | 73 | Juldah | 20 | 17:00 | 139 | Rajbari | 82 | 19:00
8 | BSRM | 173 | 00:00 | 74 | KSRM | 13 | 13:00 | 140 | Rajendrapur | 121 | 20:00
9 | Bagerhat | 83 | 00:00 | 75 | Kabirpur | 240 | 20:00 | 141 | Rajshahi | 125 | 19:30
10 | Bajitpur | 61 | 19:30 | 76 | Kachua | 90 | 18:30 | 142 | Rajshahi-230 | 92 | 13:00
11 | Bakulia | 96 | 15:00 | 77 | Kallyanpur | 108 | 23:00 | 143 | Ramganj | 116 | 18:30
12 | Banani | 69.2 | 13:00 | 78 | Kalurghat | 38 | 10:00 | 144 | Rampur | 41 | 23:00
13 | Bangabhaban | 19 | 12:00 | 79 | Kamrangirchar | 56.01 | 13:00 | 145 | Rangamati | 16 | 18:30
14 | Barapukuria | 81 | 21:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 160 | 18:30
15 | Barguna | 22 | 00:00 | 81 | Kasba | 38 | 00:00 | 147 | Ruppur | 7.4 | 16:00
16 | Barishal | 109 | 12:00 | 82 | Kazla | 98 | 19:30 | 148 | SSM | 3 | 12:00
17 | Barishal-230 | 100 | 00:00 | 83 | Keranigonj | 69 | 19:00 | 149 | Saidpur | 121 | 09:00
18 | Baroaulia | 56 | 20:00 | 84 | Khagrachori | 34 | 18:30 | 150 | Satkhira | 142 | 00:00
19 | Baroirhat | 63 | 20:00 | 85 | Khulna | 80 | 15:00 | 151 | Satmasjid | 100 | 15:00
20 | Bashundhara | 193 | 13:00 | 86 | Khulshi | 178 | 14:00 | 152 | Savar | 196 | 12:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kishoreganj | 148 | 20:00 | 153 | SevenRings | 13.65 | 20:00
22 | Beanibazar | 78 | 19:00 | 88 | Kodda | 306 | 18:30 | 154 | ShahCement | 31 | 22:00
23 | Benapole | 74 | 00:00 | 89 | Kulaura | 48 | 19:00 | 155 | Shahjadpur | 91 | 21:00
24 | Bhaluka | 168 | 18:30 | 90 | Kurigram | 76 | 19:00 | 156 | Shahjibazar | 127 | 19:00
25 | Bhandaria | 55 | 00:00 | 91 | Kushtia | 162 | 19:00 | 157 | Shahmirpur | 58 | 15:00
26 | Bhangura | 48 | 19:00 | 92 | Lalbag | 52 | 13:00 | 158 | Shariatpur | 89 | 22:00
27 | Bheramara(GK) | 67 | 19:00 | 93 | Lalmonirhat | 74 | 19:00 | 159 | Sherpur | 152 | 18:00
28 | Bhulta | 236 | 21:00 | 94 | MI_Cement | 11.6 | 23:00 | 160 | Shikalbaha | 30 | 19:00
29 | Bog-Sherpur | 74 | 20:00 | 95 | Madanganj | 45 | 21:00 | 161 | Shitalakhya | 79.7 | 13:00
30 | Bogura | 196 | 19:30 | 96 | Madaripur | 117 | 22:00 | 162 | Sholosohor | 45 | 18:30
31 | Borhanuddin | 91 | 00:00 | 97 | Madartek | 84.13 | 23:00 | 163 | Shyampur | 120 | 13:00
32 | Brahmanbaria | 136 | 23:00 | 98 | Madunaghat | 50 | 15:00 | 164 | Siddhirganj | 112 | 18:30
33 | Cantonment | 89 | 13:00 | 99 | Magura | 71 | 20:00 | 165 | Sirajganj | 128 | 20:00
34 | Chandpur | 77 | 19:00 | 100 | Mahasthangarh | 92 | 19:00 | 166 | Sonargaon | 95 | 23:00
35 | Chandraghona | 35 | 00:00 | 101 | Manikganj | 142 | 20:00 | 167 | Sreemongol | 76 | 18:30
36 | Chapai | 77 | 21:00 | 102 | Maniknagar | 73 | 13:00 | 168 | Sreepur | 104 | 12:00
37 | Charsaidpur | 36 | 23:00 | 103 | Matarbari | 50 | 19:00 | 169 | Srinagar | 49.32 | 21:00
38 | Chauddagram | 80 | 20:00 | 104 | Matuail | 58 | 16:00 | 170 | Sunamganj | 54 | 19:00
39 | Chhatak | 34 | 22:00 | 105 | Millgate | 89 | 16:00 | 171 | Sylhet | 36 | 22:00
40 | Chowmuhani | 242 | 19:30 | 106 | Mirpur | 145 | 18:30 | 172 | Sylhet-132 | 124 | 21:00
41 | Chuadanga | 117 | 19:00 | 107 | Mirsorai | 9 | 11:00 | 173 | TK | 33.5 | 23:00
42 | Coxsbazar | 136 | 19:00 | 108 | Mirzapur | 50 | 00:00 | 174 | Tangail | 188 | 22:00
43 | Cumilla(N) | 185 | 18:30 | 109 | Mithapukur | 76 | 19:00 | 175 | Thakurgaon | 111 | 20:00
44 | Cumilla(S) | 166 | 18:30 | 110 | Modern | N/A | N/A | 176 | Tongi | 126 | 10:00
45 | Daudkandi | 160 | 22:00 | 111 | Mogbazar | 143.8 | 13:00 | 177 | Ullahpara | 48 | 20:00
46 | Dhaka | 60 | 13:00 | 112 | Mongla | 40 | 23:00 | 178 | Ullon | 45 | 21:00
47 | Dhamrai | 130 | 18:30 | 113 | Motijheel | 40 | 13:00 | 179 | Uttara | 90 | 13:00
48 | Dhanmondi | 132 | 13:00 | 114 | Muktagacha | 42 | 20:00 | 180 | UttaraNew | 46 | 23:00
49 | Dohazari | 132 | 19:30 | 115 | Munshiganj | 111 | 23:00 | 181 | Zigatola | 66 | 18:30
50 | Faridpur | 172 | 19:30 | 116 | Muradnagar | 29 | 18:30
51 | Fatullah | 84 | 15:00 | 117 | Mymensingh | 220 | 21:00
52 | Fenchuganj | 36 | 18:30 | 118 | Naogaon | 157 | 22:00
53 | Feni | 120 | 19:30 | 119 | Narail | 64 | 19:00
54 | GPH | 46 | 00:00 | 120 | Narinda | 63 | 12:00
55 | Ghatail | 88 | 07:00 | 121 | Narshingdi | 175 | 21:00
56 | Ghorashal | 15 | 18:00 | 122 | Natore | 175 | 19:30
57 | Ghorashal-230 | 86 | 23:00 | 123 | Nawabganj | 62.4 | 20:00
58 | Goalpara | 32 | 00:00 | 124 | Netrakona | 140 | 19:00
59 | Gollamari | 86 | 13:00 | 125 | New | 82.1 | 15:00
60 | Gopalganj | 107.4 | 19:00 | 126 | Niamatpur | 127 | 19:00
61 | Gulshan | 128 | 13:00 | 127 | Noapara | 45 | 19:30
62 | Halishahar | 74 | 15:00 | 128 | PHP | 6 | 11:00
63 | HaripurSBU | 126 | 23:00 | 129 | Pabna | 126 | 19:30
64 | Hasnabad | 75 | 21:00 | 130 | Palashbari | 134 | 22:00
65 | Hathazari | 85 | 00:00 | 131 | Panchagarh | 64 | 19:00
66 | Ishurdi | 78 | 19:30 | 132 | Patuakhali | 80.4 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14273.74 | 0 |  | 14273.74
1:00 | 13801.22 | 45 |  | 13848.22
2:00 | 13310.4 | 30 |  | 13341.4
3:00 | 12881.63 | 50 |  | 12933.63
4:00 | 12464.4 | 0 |  | 12464.4
5:00 | 12390.24 | 0 |  | 12390.24
6:00 | 11986.3 | 0 |  | 11986.3
7:00 | 12212.61 | 0 |  | 12212.61
8:00 | 12463.1 | 24 |  | 12488.1
9:00 | 12695.69 | 83 |  | 12782.69
10:00 | 13365.52 | 83 |  | 13452.52
11:00 | 13816.57 | 93 |  | 13913.57
12:00 | 13939.17 | 157 |  | 14103.17
13:00 | 14190.38 | 251 |  | 14452.38
14:00 | 14189.69 | 347 |  | 14552.69
15:00 | 14298.23 | 338 |  | 14651.23
16:00 | 14122.63 | 343 |  | 14480.63
17:00 | 13934.23 | 305 |  | 14253.23
18:00 | 13595.99 | 120 |  | 13720.99
19:00 | 15060.2 | 248 |  | 15319.2
19:30 | 15282.2 | 170 |  | 15460.2
20:00 | 15373.9 | 102 |  | 15480.9
21:00 | 15400.79 | 96 |  | 15500.79
22:00 | 15306.53 | 91 |  | 15401.53
23:00 | 15077.24 | 166 |  | 15250.24
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7483.7 | 6790.04 | 14273.74 | DAILY GENERATION CURVE
00:30 | 7357.45 | 6680.03 | 14037.48
01:00 | 7231.2 | 6570.02 | 13801.22 | 08-04-2025
01:30 | 7067.2 | 6488.61 | 13555.81
02:00 | 6903.2 | 6407.2 | 13310.4
02:30 | 6770.45 | 6325.565 | 13096.015
03:00 | 6637.7 | 6243.93 | 12881.63
03:30 | 6494.95 | 6178.065 | 12673.015
04:00 | 6352.2 | 6112.2 | 12464.4
04:30 | 6348.2 | 6079.12 | 12427.32
05:00 | 6344.2 | 6046.04 | 12390.24
05:30 | 6241.48 | 5946.79 | 12188.27
06:00 | 6138.76 | 5847.54 | 11986.3
06:30 | 6201.165 | 5898.29 | 12099.455
07:00 | 6263.57 | 5949.04 | 12212.61
07:30 | 6299.25 | 6038.605 | 12337.855
08:00 | 6334.93 | 6128.17 | 12463.1
08:30 | 6480.89 | 6098.505 | 12579.395
09:00 | 6626.85 | 6068.84 | 12695.69
09:30 | 6820.61 | 6209.995 | 13030.605
10:00 | 7014.37 | 6351.15 | 13365.52
10:30 | 7218.12 | 6372.925 | 13591.045
11:00 | 7421.87 | 6394.7 | 13816.57
11:30 | 7516.12 | 6361.75 | 13877.87
12:00 | 7610.37 | 6328.8 | 13939.17
12:30 | 7688.085 | 6376.69 | 14064.775
13:00 | 7765.8 | 6424.58 | 14190.38
13:30 | 7810.995 | 6379.04 | 14190.035
14:00 | 7856.19 | 6333.5 | 14189.69
14:30 | 7931.01 | 6312.95 | 14243.96
15:00 | 8005.83 | 6292.4 | 14298.23
15:30 | 8018.58 | 6191.85 | 14210.43
16:00 | 8031.33 | 6091.3 | 14122.63
16:30 | 7899.75 | 6128.68 | 14028.43
17:00 | 7768.17 | 6166.06 | 13934.23
17:30 | 7725.99 | 6039.12 | 13765.11
18:00 | 7683.81 | 5912.18 | 13595.99
18:30 | 8134.505 | 6193.59 | 14328.095
19:00 | 8585.2 | 6475 | 15060.2
19:30 | 8633.2 | 6649 | 15282.2
20:00 | 8717.7 | 6656.2 | 15373.9
20:30 | 8667.45 | 6719.895 | 15387.345 |  | Executive Engineer
21:00 | 8617.2 | 6783.59 | 15400.79 |  | Network Operation Division
21:30 | 8588.45 | 6765.21 | 15353.66
22:00 | 8559.7 | 6746.83 | 15306.53
22:30 | 8445.2 | 6746.685 | 15191.885
23:00 | 8330.7 | 6746.54 | 15077.24

## En-Curve
QF-LDC-12
Date | 08-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3146 | 2081.5 | 910 | 0 | 38 | 1370.04 | 40 | 4192 | 0 | 481 | 2009.2 | 0 | 0 | 6 | 0 | DAILY ENERGY CURVE
00:30 | 3091.5 | 2071.75 | 909.5 | 0 | 37 | 1361.03 | 40 | 4192.5 | 0 | 477 | 1851.2 | 0 | 0 | 6 | 22.5 | 08-04-2025
01:00 | 3037 | 2062 | 909 | 0 | 36 | 1352.02 | 40 | 4193 | 0 | 473 | 1693.2 | 0 | 0 | 6 | 45
01:30 | 3000 | 2061.5 | 909 | 0 | 36 | 1355.61 | 40 | 4175.5 | 0 | 411 | 1564.2 | 0 | 0 | 3 | 37.5 | Energy Generated | 332.9472 |  | MKWHr
02:00 | 2963 | 2061 | 909 | 0 | 36 | 1359.2 | 40 | 4158 | 0 | 349 | 1435.2 | 0 | 0 | 0 | 30 | Energy not Served | 2.972 |  | MKWHr
02:30 | 2977 | 2063.25 | 909 | 0 | 35 | 1358.565 | 40 | 4131 | 0 | 311 | 1271.2 | 0 | 0 | 0 | 40 | Total Energy Requirement | 335.9192 |  | MKWHr
03:00 | 2991 | 2065.5 | 909 | 0 | 34 | 1357.93 | 40 | 4104 | 0 | 273 | 1107.2 | 0 | 0 | 0 | 50
03:30 | 3010.5 | 2074.25 | 909 | 0 | 34 | 1357.565 | 40 | 4059 | 0 | 229.5 | 959.2 | 0 | 0 | 0 | 25
04:00 | 3030 | 2083 | 909 | 0 | 34 | 1357.2 | 40 | 4014 | 0 | 186 | 811.2 | 0 | 0 | 0 | 0
04:30 | 3008.5 | 2069.5 | 909 | 0 | 34 | 1354.12 | 40 | 3997 | 0 | 182 | 833.2 | 0 | 0 | 0 | 0
05:00 | 2987 | 2056 | 909 | 0 | 34 | 1351.04 | 40 | 3980 | 0 | 178 | 855.2 | 0 | 0 | 0 | 0
05:30 | 2959 | 2068 | 909 | 0 | 32 | 1354.63 | 40 | 3892 | 1.94 | 157.5 | 774.2 | 0 | 0 | 0 | 0
06:00 | 2931 | 2080 | 909 | 0 | 30 | 1358.22 | 40 | 3804 | 3.88 | 137 | 693.2 | 0 | 0 | 0 | 0
06:30 | 2997 | 2078.5 | 909 | 0 | 34 | 1357.905 | 40 | 3771.5 | 49.85 | 163 | 698.7 | 0 | 0 | 0 | 0
07:00 | 3063 | 2077 | 909 | 0 | 38 | 1357.59 | 40 | 3739 | 95.82 | 189 | 704.2 | 0 | 0 | 0 | 0
07:30 | 3071.5 | 2071.5 | 886 | 0 | 37 | 1346.295 | 40 | 3765.5 | 155.86 | 189 | 775.2 | 0 | 0 | 0 | 12
08:00 | 3080 | 2066 | 863 | 0 | 36 | 1335 | 40 | 3792 | 215.9 | 189 | 846.2 | 0 | 0 | 0 | 24
08:30 | 3171.5 | 2069 | 863 | 0 | 37 | 1114.5 | 40 | 3813 | 298.695 | 208.5 | 964.2 | 0 | 0 | 0 | 53.5
09:00 | 3263 | 2072 | 863 | 0 | 38 | 894 | 40 | 3834 | 381.49 | 228 | 1082.2 | 0 | 0 | 0 | 83
09:30 | 3249 | 2023 | 887 | 0 | 36 | 828 | 40 | 3903.5 | 434.905 | 267 | 1362.2 | 0 | 0 | 0 | 83
10:00 | 3235 | 1974 | 911 | 0 | 34 | 762 | 40 | 3973 | 488.32 | 306 | 1642.2 | 0 | 0 | 0 | 83
10:30 | 3215 | 1990.75 | 910.5 | 0 | 34 | 758 | 40 | 3994 | 524.095 | 344.5 | 1780.2 | 0 | 0 | 0 | 88
11:00 | 3195 | 2007.5 | 910 | 0 | 34 | 754 | 40 | 4015 | 559.87 | 383 | 1918.2 | 0 | 0 | 0 | 93
11:30 | 3220 | 2023 | 910.5 | 0 | 38 | 755 | 40 | 3961.5 | 533.77 | 403.5 | 1992.6 | 0 | 0 | 0 | 125
12:00 | 3245 | 2038.5 | 911 | 0 | 42 | 756 | 40 | 3908 | 507.67 | 424 | 2067 | 0 | 0 | 0 | 157
12:30 | 3191.5 | 2047.5 | 911 | 0 | 41 | 759.5 | 40 | 3924 | 522.675 | 455 | 2172.6 | 0 | 0 | 0 | 204
13:00 | 3138 | 2056.5 | 911 | 0 | 40 | 763 | 40 | 3940 | 537.68 | 486 | 2278.2 | 0 | 0 | 0 | 251
13:30 | 3059.5 | 2043.5 | 910.5 | 0 | 41 | 763.5 | 40 | 3983 | 497.335 | 502 | 2344.2 | 0 | 0 | 5.5 | 299
14:00 | 2981 | 2030.5 | 910 | 0 | 42 | 764 | 40 | 4026 | 456.99 | 518 | 2410.2 | 0 | 0 | 11 | 347
14:30 | 3090 | 2033.25 | 910 | 0 | 43 | 764 | 40 | 4002 | 396.51 | 513.5 | 2433.2 | 0 | 0 | 18.5 | 342.5
15:00 | 3199 | 2036 | 910 | 0 | 44 | 764 | 40 | 3978 | 336.03 | 509 | 2456.2 | 0 | 0 | 26 | 338
15:30 | 3186.5 | 2060.25 | 910.5 | 0 | 45 | 763 | 40 | 3963 | 257.48 | 515.5 | 2443.2 | 0 | 0 | 26 | 340.5
16:00 | 3174 | 2084.5 | 911 | 0 | 46 | 762 | 40 | 3948 | 178.93 | 522 | 2430.2 | 0 | 0 | 26 | 343
16:30 | 3206.5 | 2080.75 | 911 | 0 | 42 | 762 | 40 | 3966 | 140.98 | 552 | 2311.2 | 0 | 0 | 16 | 324
17:00 | 3239 | 2077 | 911 | 0 | 38 | 762 | 40 | 3984 | 103.03 | 582 | 2192.2 | 0 | 0 | 6 | 305
17:30 | 3178.5 | 2008 | 911 | 0 | 41 | 758 | 40 | 3909.5 | 55.41 | 573.5 | 2284.7 | 2.5 | 0 | 3 | 212.5
18:00 | 3118 | 1939 | 911 | 0 | 44 | 754 | 40 | 3835 | 7.79 | 565 | 2377.2 | 5 | 0 | 0 | 120
18:30 | 3233 | 1936 | 887 | 0 | 42 | 753.5 | 63 | 4015.5 | 3.895 | 712.5 | 2670.7 | 11 | 0 | 0 | 184
19:00 | 3348 | 1933 | 863 | 0 | 40 | 753 | 86 | 4196 | 0 | 860 | 2964.2 | 17 | 0 | 0 | 248
19:30 | 3383 | 1933 | 863 | 0 | 40 | 750 | 46 | 4354 | 0 | 878 | 3018.2 | 17 | 0 | 0 | 170
20:00 | 3445 | 1870.5 | 863 | 0 | 40 | 758 | 46 | 4389 | 0 | 895 | 3050.4 | 17 | 0 | 0 | 102
20:30 | 3461 | 1865.5 | 886.5 | 0 | 43 | 758.695 | 46 | 4420 | 0 | 909 | 2981.65 | 16 | 0 | 0 | 99
21:00 | 3477 | 1860.5 | 910 | 0 | 46 | 759.39 | 46 | 4451 | 0 | 923 | 2912.9 | 15 | 0 | 0 | 96
21:30 | 3456.5 | 1942.75 | 910.5 | 0 | 45 | 762.01 | 46 | 4421 | 0 | 901.5 | 2853.4 | 15 | 0 | 0 | 93.5
22:00 | 3436 | 2025 | 911 | 0 | 44 | 764.63 | 46 | 4391 | 0 | 880 | 2793.9 | 15 | 0 | 0 | 91
22:30 | 3445 | 1987 | 911 | 0 | 44 | 763.985 | 46 | 4390 | 0 | 865.5 | 2731.9 | 7.5 | 0 | 0 | 128.5
23:00 | 3454 | 1949 | 911 | 0 | 44 | 763.34 | 46 | 4389 | 0 | 851 | 2669.9 | 0 | 0 | 0 | 166
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 398 | 18:00 | 390 | 22:00 | Payra | 415 | 06:00 | 410 | 23:00
Ashuganj | 404 | 6:00 | 387 | 12:00 | Rahanpur | 401 | 17:00 | 388 | 07:00
Bhulta | 400 | 05:00 | 389 | 12:00 | Rampal | 404 | 06:00 | 392 | 21:00
Bibiana | 390 | 03:00 | 382 | 14:00
BIPTC | 398 | 08:00 | 387 | 15:00
Bogura | 390 | 14:00 | 375 | 08:00
Gopalganj | 403 | 18:00 | 393 | 22:00
Kaliakoir | 372 | 19:00 | 364 | 08:00
Madunaghat | 406 | 20:00 | 397 | 09:00
Meghnaghat | 400 | 06:00 | 393 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 06:00 | 227 | 12:00 | Keranigonj | 231 | 06:00 | 225 | 12:00
AKSML | 235 | 13:00 | 230 | 00:00 | Khulna(S) | 233 | 18:00 | 219 | 23:00
Aminbazar | 234 | 18:00 | 221 | 07:00 | Madunaghat | 238 | 13:00 | 234 | 21:00
Ashuganj | 232 | 03:00 | 227 | 15:00 | Madunaghat-400 | 238 | 14:00 | 234 | 00:00
Ashuganj-400 | 228 | 6:00 | 218 | 12:00 | Maniknagar | 231 | 06:00 | 222 | 12:00
Baghabari | 234 | 10:00 | 227 | 00:00 | Meghnaghat | 237 | 04:00 | 232 | 11:00
Barapukuria | 226 | 13:00 | 215 | 07:00 | Meghnaghat-400 | 233 | 06:00 | 227 | 12:00
Barapukuria-230 | 225 | 13:00 | 216 | 7:00 | Mirsorai | 236 | 14:00 | 227 | 01:00
Barishal | 235 | 18:00 | 227 | 00:00 | Rajshahi | 232 | 11:00 | 222 | 20:00
Bheramara | 233 | 18:00 | 221 | 22:00 | Rampal | 232 | 18:00 | 220 | 21:00
Bhulta | 230 | 06:00 | 222 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 02:00 | 218 | 23:00 | Rampura | 230 | 06:00 | 220 | 12:00
BIPTC | 236 | 18:00 | 222 | 19:30 | Shikalbaha | 238 | 14:00 | 230 | 05:00
Bogura | 237 | 13:00 | 226 | 07:00 | Shyampur | 231 | 06:00 | 225 | 12:00
Bogura-400 | 237 | 14:00 | 228 | 08:00 | Siddhirganj | 231 | 04:00 | 225 | 14:00
Borhanuddin | 240 | 18:00 | 235 | 00:00 | Sirajgonj | 241 | 18:00 | 236 | 20:00
BSRM | 234 | 14:00 | 227 | 00:00 | Sreepur | 230 | 17:00 | 225 | 08:00
Cumilla(N) | 226 | 05:00 | 221 | 15:00 | Tongi | 229 | 07:00 | 220 | 23:00
Faridpur | 229 | 06:00 | 223 | 00:00
Fenchuganj | 226 | 06:00 | 222 | 21:00
Ghorashal | 240 | 00:00 | 235 | 01:00
Ghorashal-230 | 229 | 18:00 | 222 | 15:00
Gopalganj | 255 | 22:00 | 225 | 00:00
GPH | 236 | 14:00 | 230 | 00:00
Haripur | 230 | 07:00 | 224 | 09:00
Hasnabad | 230 | 05:00 | 226 | 12:00
Hathazari | 237 | 14:00 | 232 | 00:00
Ishurdi | 235 | 09:00 | 225 | 19:30
Jhenaidah | 227 | 18:30 | 211 | 21:00
Kaliakoir | 231 | 18:30 | 226 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 124 | 12:00 | Madartek | 133 | 05:00 | 124 | 12:00
Agargaon | 134 | 04:00 | 129 | 12:00 | Madunaghat | 136 | 13:00 | 132 | 00:00
Agrabad | 135 | 19:30 | 13.4 | 19:00 | Magura | 135 | 18:00 | 124 | 20:00
AKS | 132 | 03:00 | 130 | 08:00 | Mahasthangarh | 134 | 13:00 | 125 | 07:00
Aminbazar | 132 | 01:00 | 129 | 21:00 | Manikganj | 130 | 03:00 | 125 | 15:00
Amnura | 138 | 18:00 | 125 | 07:00 | Maniknagar | 132 | 03:00 | 120 | 14:00
Ashuganj | 136 | 05:00 | 133 | 23:00 | Matarbari | 120 | 11:00 | 114 | 03:00
Bagerhat | 134 | 18:00 | 122 | 22:00 | Matuail | 134 | 06:00 | 131 | 12:00
Bajitpur | 130 | 05:00 | 123 | 19:30 | Millgate | 133 | 03:00 | 126 | 09:00
Bakulia | 136 | 18:30 | 133 | 00:00 | Mirpur | 132 | 04:00 | 127 | 12:00
Banani | 137 | 18:00 | 123 | 13:00 | Mirzapur | 128 | 00:00 | 122 | 18:30
Bangabhaban | 132 | 03:00 | 126 | 12:00 | Mithapukur | 133 | 13:00 | 121 | 07:00
Barapukuria | 139 | 13:00 | 130 | 07:00 | MI_Cement | 136 | 18:00 | 131 | 12:00
Barguna | 136 | 19:00 | 130 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 18:00 | 125 | 00:00 | Mogbazar | 135 | 06:00 | 125 | 12:00
Barishal-230 | 131 | 06:00 | 126 | 00:00 | Mongla | 134 | 18:00 | 123 | 23:00
Baroaulia | 135 | 18:00 | 132 | 01:00 | Motijheel | 132 | 03:00 | 126 | 12:00
Baroirhat | 124 | 10:00 | 120 | 17:00 | Muktagacha | 150 | 22:00 | 117 | 20:00
Bashundhara | 133 | 03:00 | 125 | 09:00 | Munshiganj | 134 | 02:00 | 130 | 12:00
BashundharaCement | 135 | 18:00 | 130 | 11:00 | Muradnagar | 129 | 18:00 | 123 | 15:00
Beanibazar | 130 | 06:00 | 123 | 20:00 | Mymensingh | 132 | 00:00 | 122 | 04:00
Benapole | 132 | 18:00 | 120 | 22:00 | Naogaon | 131 | 14:00 | 122 | 08:00
Bhaluka | 125 | 11:00 | 119 | 18:30 | Narail | 135 | 04:00 | 124 | 19:30
Bhandaria | 127 | 15:00 | 115 | 00:00 | Narinda | 132 | 3:00 | 120 | 14:00
Bhangura | 132 | 05:00 | 126 | 21:00 | Narshingdi | 132 | 06:00 | 122 | 22:00
Bheramara | 136 | 06:00 | 129 | 19:30 | Natore | 134 | 18:00 | 127 | 00:00
Bheramara(GK) | 136 | 18:00 | 129 | 19:30 | Nawabganj | 133 | 04:00 | 127 | 18:30
Bhulta | 130 | 04:00 | 124 | 23:00 | Netrakona | 121 | 04:00 | 106 | 22:00
Bog-Sherpur | 135 | 13:00 | 127 | 07:00 | New | 134 | 19:00 | 127 | 08:00
Bogura | 137 | 14:00 | 131 | 19:30 | Niamatpur | 135 | 17:00 | 129 | 07:00
Bogura-230 | 138 | 14:00 | 129 | 07:00 | Noapara | 135 | 18:00 | 124 | 22:00
Brahmanbaria | 131 | 06:00 | 124 | 22:00 | Pabna | 134 | 09:00 | 127 | 19:30
Cantonment | 134 | 03:00 | 130 | 12:00 | Palashbari | 129 | 04:00 | 118 | 07:00
Chandina | 130 | 18:00 | 125 | 15:00 | Panchagarh | 137 | 13:00 | 119 | 07:00
Chandpur | 128 | 18:00 | 118 | 14:00 | Patuakhali | 135 | 18:00 | 131 | 22:00
Chandraghona | 136 | 18:00 | 133 | 00:00 | Payra | 137 | 18:00 | 134 | 00:00
Chapai | 131 | 09:00 | 127 | 02:00 | PHP | 125 | 08:00 | 118 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 03:00 | 131 | 12:00 | Postogola | 137 | 03:00 | 133 | 11:00
Chauddagram | 125 | 18:00 | 120 | 00:00 | Purbachal | 134 | 05:00 | 124 | 12:00
Chhatak | 129 | 06:00 | 121 | 19:30 | Purbasadipur | 134 | 13:00 | 116 | 06:00
Chowmuhani | 120 | 18:00 | 111 | 01:00 | Rahanpur | 137 | 17:00 | 133 | 00:00
Chuadanga | 134 | 06:00 | 121 | 21:00 | Rahanpur-400 | 137 | 18:00 | 132 | 00:00
Coxsbazar | 121 | 12:00 | 114 | 00:00 | Rahim | 135 | 06:00 | 131 | 12:00
Cumilla(N) | 130 | 18:00 | 126 | 00:00 | Rajbari | 134 | 06:00 | 129 | 00:00
Cumilla(S) | 133 | 20:00 | 123 | 15:00 | Rajendrapur | 132 | 04:00 | 118 | 20:00
Daudkandi | 129 | 18:00 | 122 | 15:00 | Rajshahi | 134 | 18:00 | 128 | 00:00
Dhaka | 133 | 04:00 | 125 | 12:00 | Rajshahi-230 | 136 | 18:00 | 120 | 23:00
Dhamrai | 132 | 19:00 | 127 | 09:00 | Ramganj | 121 | 18:00 | 112 | 00:00
Dhanmondi | 136 | 02:00 | 131 | 14:00 | Rampur | 135 | 18:30 | 130 | 00:00
Dohazari | 130 | 19:30 | 126 | 04:00 | Rampura | 134 | 05:00 | 125 | 12:00
Faridpur | 135 | 06:00 | 132 | 00:00 | Rangamati | 135 | 19:30 | 132 | 10:00
Fatullah | 136 | 04:00 | 131 | 12:00 | Rangpur | 132 | 02:00 | 119 | 07:00
Fenchuganj | 135 | 14:00 | 131 | 12:00 | Ruppur | 138 | 09:00 | 130 | 19:00
Feni | 125 | 18:00 | 117 | 00:00 | Saidpur | 134 | 01:00 | 122 | 19:00
Ghatail | 127 | 00:00 | 116 | 15:00 | Satkhira | 134 | 18:00 | 119 | 22:00
Ghorashal | 138 | 01:00 | 126 | 18:00 | Satmasjid | 134 | 05:00 | 129 | 15:00
Goalpara | 136 | 18:00 | 127 | 00:00 | Savar | 134 | 03:00 | 126 | 08:00
Gollamari | 134 | 17:00 | 128 | 20:00 | SevenRings | 139 | 18:00 | 134 | 09:00
Gopalganj | 135 | 18:00 | 129 | 00:00 | ShahCement | 135 | 03:00 | 131 | 12:00
Gopalganj-400 | 138 | 18:00 | 133 | 22:00 | Shahjadpur | 137 | 18:00 | 131 | 21:00
Gulshan | 133 | 06:00 | 124 | 15:00 | Shahjibazar | 132 | 06:00 | 125 | 21:00
Halishahar | 136 | 18:30 | 132 | 00:00 | Shahmirpur | 137 | 14:00 | 134 | 08:00
Haripur | 135 | 01:00 | 131 | 12:00 | Shariatpur | 135 | 18:00 | 128 | 00:00
HaripurSBU | 135 | 01:00 | 131 | 12:00 | Sherpur | 133 | 00:00 | 115 | 13:00
Hasnabad | 137 | 04:00 | 133 | 12:00 | Shikalbaha | 126 | 18:30 | 122 | 01:00
Hathazari | 137 | 14:00 | 134 | 08:00 | Shikalbaha-230 | 139 | 17:00 | 133 | 03:00
Ishurdi | 137 | 05:00 | 130 | 21:00 | Shitalakhya | 136 | 18:00 | 131 | 12:00
Jaldhaka | 131 | 00:00 | 118 | 07:00 | Sholosohor | 136 | 14:00 | 132 | 00:00
Jamalpur | 136 | 00:00 | 119 | 13:00 | Shyampur | 137 | 07:00 | 131 | 12:00
Jashore | 134 | 18:00 | 122 | 22:00 | Shyampur-230 | 135 | 05:00 | 130 | 12:00
Jhenaidah | 137 | 18:00 | 126 | 22:00 | Siddhirganj | 135 | 06:00 | 131 | 11:00
Jhenaidah-230 | 138 | 18:00 | 127 | 21:00 | Sirajganj | 133 | 11:00 | 125 | 19:30
Joydebpur | 138 | 18:00 | 130 | 12:00 | Sonargaon | 134 | 18:00 | 129 | 08:00
Joypurhat | 129 | 14:00 | 116 | 07:00 | Sreemongol | 132 | 06:00 | 125 | 21:00
Juldah | 138 | 18:30 | 134 | 07:00 | Sreepur | 128 | 17:00 | 123 | 20:00
Kabirpur | 138 | 19:00 | 123 | 09:00 | Srinagar | 133 | 05:00 | 128 | 11:00
Kachua | 127 | 18:00 | 118 | 14:00 | SSM | 138 | 18:00 | 132 | 12:00
Kaliakoir | 135 | 18:30 | 129 | 09:00 | Sunamganj | 128 | 07:00 | 121 | 15:00
Kallyanpur | 133 | 18:30 | 129 | 15:00 | Sylhet | 131 | 07:00 | 125 | 15:00
Kalurghat | 135 | 02:00 | 132 | 10:00 | Sylhet-132 | 131 | 06:00 | 126 | 22:00
Kamrangirchar | 135 | 04:00 | 127 | 11:00 | Tangail | 125 | 00:00 | 120 | 15:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 13:00 | 116 | 07:00
Kasba | 128 | 18:00 | 122 | 21:00 | TK | 137 | 14:00 | 133 | 02:00
Kazla | 132 | 05:00 | 126 | 12:00 | Tongi | 135 | 19:00 | 120 | 09:00
Keranigonj | 133 | 06:00 | 128 | 12:00 | Ullahpara | 133 | 11:00 | 127 | 19:30
Khagrachori | 133 | 18:00 | 131 | 00:00 | Ullon | 133 | 03:00 | 125 | 12:00
Khulna | 135 | 18:00 | 125 | 12:00 | Uttara | 132 | 06:00 | 124 | 09:00
Khulna(S) | 137 | 18:00 | 128 | 19:30 | UttaraNew | 132 | 01:00 | 128 | 12:00
Khulshi | 135 | 19:30 | 131 | 08:00 | Zigatola | 133 | 05:00 | 129 | 12:00
Kishoreganj | 128 | 06:00 | 118 | 20:00
Kodda | 140 | 18:00 | 129 | 08:00
KSRM | 137 | 18:00 | 132 | 03:00
Kulaura | 134 | 05:00 | 130 | 13:00
Kurigram | 131 | 00:00 | 117 | 18:30
Kushtia | 135 | 18:00 | 127 | 19:30
Lalbag | 132 | 04:00 | 128 | 12:00
Lalmonirhat | 132 | 13:00 | 119 | 10:00
Madanganj | 135 | 18:00 | 130 | 11:00
Madaripur | 136 | 18:00 | 131 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division