## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-04-2025 | during | 10-04-2025 | during | 10-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 402 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 263 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 316 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 74 | 8 | 64 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 1 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 144 | 144 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 17 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 25 | 52.19 | 52.19 | 16 | 42 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 278 | 278 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 124 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 52 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 50 | 68 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 36 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 584 | 584 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 400 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2944 | 3121 | 5269.9 | 5293.9 | 4111.13 | 4217.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 8 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 47 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 140 | 149 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 68 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 24 | 78 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 87 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 8 | 20 | 8 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 48 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 2.62 | 0 | 2.62 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 1 | 68 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 62 | 98 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 108 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 19 | 0 | 1 | 3 | 1 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 160 | 160 | 155 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1914 | 2477.5 | 2984.34 | 3000.72 | 2984.34 | 3000.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 206 | 180 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 342 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 187 | 185 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 122 | 132 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 30 | 38 | 47 | 47 | 30 | 30 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 45 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 21 | 180 | 200 | 200 | 34 | 34 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 52 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 17 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 80 | 80 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 37 | 113 | 113 | 9 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 89 | 115 | 115 | 51 | 51 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1385 | 1583.2 | 2125.99 | 2060.99 | 1655.05 | 1618.05
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-04-2025 | during | 10-04-2025 | during | 10-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 8 | 157.5 | 157.5 | 20 | 20 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 116 | 152 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 66 | 114 | 115 | 115 | 66 | 114 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 18.93 | 0 | 45.5 | 0 | 45.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 274.43 | 340.5 | 596.5 | 549 | 400 | 400.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 36 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 38 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 144 | 153 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 28 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 98 | 169 | 160 | 160 | 100 | 100 | Under Maintenance
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 394 | 363 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1175 | 1230 | 1256 | 1256 | 1161 | 1161
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 911 | 902 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 24 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 44 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 102.31 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1060 | 1241 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2073.31 | 2264 | 3614.2 | 3514.2 | 3099.21 | 2999.21
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 98 | 128 | 100 | 100 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 48 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 114 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1098 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.41 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1794.41 | 2088 | 2272.12 | 2271.12 | 2120.12 | 2119.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 52 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 17 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 13 | 35 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 181 | 202 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 205 | 201 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 202 | 220 | 220 | 198 | 198 | Plant is running as per NLDC demand
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 15 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.23 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 760 | 761 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 34.09 | 0 | 62 | 0 | 62 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 103 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2207.52 | 2280.2 | 2510.99 | 2343.99 | 2436.2 | 2269.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 59 | 56 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 157 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 48 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.1 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 42 | 0 | 154.27 | 0 | 154.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 456.1 | 435 | 667.67 | 477 | 667.67 | 477
System Total |  |  |  |  | 27566.2 | 28535.742 | 14223.77 | 15819.4 | 21297.71 | 20766.92 | 18634.72 | 18261.93
Forecast Scenario (10-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14950 |  | 0 |  | 14950
|  |  |  | 1:00 | 14620 |  | 0 |  | 14620
|  |  |  | 2:00 | 14200 |  | 0 |  | 14200
|  |  |  | 3:00 | 13570 |  | 0 |  | 13570
|  |  |  | 4:00 | 13200 |  | 0 |  | 13200
|  |  |  | 5:00 | 12750 |  | 0 |  | 12750
|  |  |  | 6:00 | 12390 |  | 0 |  | 12390
|  |  |  | 7:00 | 12600 |  | 0 |  | 12600
|  |  |  | 8:00 | 12760 |  | 0 |  | 12760
|  |  |  | 9:00 | 13100 |  | 0 |  | 13100
|  |  |  | 10:00 | 13520 |  | 0 |  | 13520
|  |  |  | 11:00 | 13950 |  | 0 |  | 13950
|  |  |  | 12:00 | 14350 |  | 0 |  | 14350
|  |  |  | 13:00 | 14530 |  | 0 |  | 14530
|  |  |  | 14:00 | 14740 |  | 0 |  | 14740
|  |  |  | 15:00 | 14700 |  | 0 |  | 14700
|  |  |  | 16:00 | 14630 |  | 0 |  | 14630
|  |  |  | 17:00 | 14400 |  | 0 |  | 14400
|  |  |  | 18:00 | 14100 |  | 0 |  | 14100
|  |  |  | 18:30 | 14900 |  | 0 |  | 14900
|  |  |  | 19:00 | 15600 |  | 0 |  | 15600
|  |  |  | 19:30 | 15850 |  | 0 |  | 15850
|  |  |  | 20:00 | 15850 |  | 0 |  | 15850
|  |  |  | 21:00 | 15880 |  | 0 |  | 15880
|  |  |  | 22:00 | 15680 |  | 0 |  | 15680
|  |  |  | 23:00 | 15300 |  | 0 |  | 15300
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 14350.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15880.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15880.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 341.37 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:11 hrs on 10-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-04-2025 | [28 empty] | Date: | 09-04-2025 | [28 empty] | Date: | 09-04-2025 | [28 empty] | Date: | 09-04-2025 | [28 empty] | Date: | 09-04-2025 | [16 empty] | Date: | 09-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 82 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 131 | 146 | 0 | 55 | 0 | 35 | 0 | 71 | 320 | 299 | 200 | 0 | 35 | 0 | 325 | 0 | 0 | 0 | 160 | 16.5 | 22 | 0 | 280 | 17 | 30 | 50 | 0 | 0 | 68 | 72 | 0 | 50 | 88 | 0 | 46 | 34 | 29 | 157 | 160 | 0 | 18 | 25.5 | 86 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 187 | 0 | 360 | 0 | 50 | 207 | 35 | 55 | 50 | 75 | 19 | 17 | 80 | 40 | 52.2 | 0 | 37 | 0 | 320 | 400 | 36 | 39 | 0 | 157 | 22 | 0 | 82 | 30 | 0 | 0 | 100 | 53 | 113 | 125 | 9 | 0 | 0 | 12 | 7889.2 | 911 | 0 | 0 | 25 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 54 | 762.9 | 0 | 49 | 0 | 113 | 15 | 98 | 113 | 27 | 52.2 | 0 | 22 | 0 | 186 | 0 | 196 | 0 | 193 | 0 | 414 | 0 | 0 | 0 | 160 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 120 | 110 | 0 | 0 | 1220 | 0 | 6647.1 | 14536.3 | 83.25
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 131 | 147 | 0 | 55 | 0 | 35 | 0 | 80 | 300 | 279 | 200 | 0 | 35 | 0 | 290 | 0 | 0 | 0 | 160 | 16 | 22 | 0 | 280 | 17 | 30 | 51 | 0 | 0 | 68 | 72 | 0 | 50 | 88 | 0 | 46 | 34 | 32 | 157 | 160 | 0 | 18 | 25.5 | 105 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 187 | 0 | 360 | 0 | 51 | 186 | 35 | 56 | 50 | 34 | 9 | 17 | 80 | 38 | 52.2 | 0 | 35 | 0 | 320 | 390 | 36 | 39 | 0 | 156 | 22 | 0 | 82 | 30 | 0 | 17 | 30 | 53 | 47 | 97 | 9 | 0 | 0 | 9 | 7514.7 | 911 | 0 | 0 | 25 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1161 | 54 | 761.87 | 0 | 49 | 0 | 113 | 15 | 98 | 113 | 24 | 52.2 | 0 | 22 | 0 | 195 | 0 | 194 | 0 | 184 | 0 | 383 | 0 | 0 | 0 | 161 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 112 | 110 | 0 | 120 | 1150 | 0 | 6655.07 | 14169.77 | 83.24
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 131 | 147 | 190 | 55 | 0 | 35 | 0 | 84 | 300 | 257 | 200 | 0 | 35 | 0 | 290 | 0 | 0 | 0 | 160 | 16 | 22 | 0 | 280 | 17 | 30 | 50 | 0 | 2 | 68 | 72 | 0 | 50 | 88 | 0 | 46 | 57 | 28 | 156 | 90 | 0 | 18 | 25.5 | 105 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 187 | 0 | 360 | 0 | 50 | 190 | 35 | 56 | 50 | 34 | 9 | 17 | 80 | 32 | 52.2 | 0 | 30 | 0 | 320 | 350 | 36 | 39 | 0 | 152 | 22 | 0 | 82 | 30 | 0 | 16 | 20 | 53 | 48 | 97 | 9 | 0 | 0 | 12 | 7581.7 | 910 | 0 | 0 | 25 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1158 | 54 | 757.45 | 0 | 33 | 0 | 113 | 15 | 0 | 113 | 24 | 52.2 | 0 | 22 | 0 | 191 | 0 | 193 | 0 | 181 | 0 | 380 | 0 | 0 | 0 | 160 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 108 | 120 | 0 | 0 | 1150 | 0 | 6402.65 | 13984.35 | 83.23
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 125 | 147 | 295 | 0 | 0 | 35 | 0 | 72 | 300 | 288 | 220 | 0 | 35 | 0 | 290 | 0 | 0 | 0 | 70 | 17 | 22 | 0 | 280 | 0 | 30 | 29 | 0 | 9 | 68 | 72 | 0 | 50 | 88 | 0 | 46 | 109 | 34 | 157 | 0 | 0 | 0 | 0 | 105 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 187 | 0 | 360 | 0 | 51 | 190 | 35 | 55 | 40 | 34 | 0 | 17 | 80 | 34 | 52.2 | 0 | 31 | 0 | 320 | 361 | 36 | 39 | 0 | 152 | 22 | 0 | 82 | 30 | 0 | 16 | 23 | 53 | 48 | 97 | 9 | 0 | 0 | 12 | 7460.2 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 17 | 761.5 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 193 | 0 | 179 | 0 | 390 | 0 | 0 | 0 | 157 | 56 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 140 | 0 | 0 | 1150 | 0 | 5979.5 | 13439.7 | 83.22
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 112 | 147 | 145 | 0 | 0 | 35 | 0 | 68 | 300 | 285 | 220 | 0 | 35 | 0 | 290 | 0 | 0 | 0 | 70 | 17 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 17 | 68 | 72 | 0 | 50 | 36 | 0 | 46 | 110 | 34 | 157 | 0 | 0 | 0 | 0 | 105 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 187 | 0 | 360 | 0 | 51 | 183 | 35 | 51 | 40 | 35 | 0 | 17 | 52 | 34 | 52.2 | 0 | 32 | 0 | 320 | 348 | 36 | 39 | 0 | 152 | 22 | 0 | 79 | 30 | 0 | 16 | 56 | 53 | 48 | 97 | 9 | 0 | 0 | 12 | 7166.2 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1115 | 17 | 761.12 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 192 | 0 | 175 | 0 | 385 | 0 | 0 | 0 | 158 | 53 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 190 | 0 | 0 | 1150 | 0 | 5941.12 | 13107.32 | 83.21
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 112 | 147 | 145 | 0 | 0 | 35 | 0 | 50 | 300 | 303 | 220 | 0 | 17 | 0 | 290 | 0 | 0 | 0 | 70 | 17 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 34 | 0 | 0 | 50 | 36 | 0 | 46 | 0 | 34 | 157 | 0 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 189 | 0 | 359 | 0 | 52 | 204 | 35 | 51 | 40 | 34 | 0 | 17 | 34 | 32 | 52.2 | 0 | 32 | 0 | 320 | 378 | 36 | 39 | 0 | 154 | 22 | 0 | 82 | 30 | 0 | 16 | 55 | 0 | 48 | 97 | 9 | 0 | 0 | 12 | 6821.2 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 764.51 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 188 | 0 | 175 | 0 | 414 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 0 | 1150 | 0 | 5844.51 | 12665.71 | 83.2
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 112 | 147 | 110 | 0 | 0 | 35 | 0 | 50 | 300 | 308 | 220 | 0 | 17 | 0 | 290 | 0 | 0 | 1 | 52 | 17 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 12 | 12 | 0 | 46 | 0 | 35 | 157 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1155 | 0 | 51 | 80 | 189 | 0 | 360 | 0 | 52 | 211 | 35 | 50 | 40 | 34 | 0 | 17 | 34 | 32 | 34 | 2 | 32 | 0 | 320 | 365 | 36 | 39 | 0 | 155 | 22 | 0 | 82 | 30 | 0 | 16 | 56 | 0 | 48 | 97 | 13 | 0 | 0.84 | 12 | 6551.84 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.21 | 1113 | 0 | 760.24 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 187 | 0 | 175 | 0 | 414 | 0 | 0 | 0 | 157 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 3 | 0 | 0 | 250 | 7 | 120 | 220 | 0 | 0 | 1122 | 0 | 5757.45 | 12309.29 | 83.19
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 112 | 147 | 110 | 0 | 0 | 35 | 0 | 50 | 300 | 275 | 230 | 0 | 17 | 0 | 250 | 0 | 0 | 6 | 52 | 16.5 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 12 | 12 | 1 | 46 | 0 | 32 | 157 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1224 | 1 | 51 | 80 | 189 | 0 | 360 | 0 | 52 | 182 | 32 | 51 | 50 | 34 | 0 | 17 | 34 | 36 | 34 | 15 | 32 | 0 | 320 | 350 | 36 | 39 | 0 | 157 | 22 | 0 | 82 | 30 | 0 | 16 | 56 | 0 | 77 | 116 | 5 | 0 | 9.06 | 12 | 6593.56 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.72 | 1113 | 0 | 760.39 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8.64 | 193 | 0 | 187 | 0 | 176 | 0 | 384 | 0 | 0.7 | 0 | 159 | 55 | 35 | 2 | 70 | 0 | 0 | 0.7 | 34 | 0.09 | 0 | 307 | 6 | 114 | 220 | 0 | 0 | 1124 | 0 | 5939.24 | 12532.8 | 83.18
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 112 | 147 | 110 | 0 | 0 | 35 | 0 | 35 | 300 | 308 | 230 | 0 | 17 | 0 | 250 | 0 | 0 | 15 | 52 | 16 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 11 | 17 | 0 | 0 | 12 | 12 | 2 | 46 | 0 | 5 | 157 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1224 | 3 | 51 | 80 | 189 | 0 | 356 | 0 | 51 | 214 | 33 | 51 | 50 | 34 | 0 | 17 | 34 | 34 | 34 | 32 | 31 | 0 | 320 | 387 | 36 | 39 | 0 | 153 | 0 | 0 | 82 | 30 | 0 | 16 | 68 | 0 | 77 | 116 | 5 | 1 | 14.5 | 12 | 6658.5 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.89 | 1058 | 0 | 759.82 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21.26 | 170 | 0 | 200 | 0 | 176 | 0 | 414 | 0 | 1.97 | 0 | 160 | 57 | 70 | 10 | 107 | 0 | 0 | 0 | 39 | 0.26 | 0 | 307 | 7 | 114 | 220 | 0 | 0 | 1148 | 0 | 6060.2 | 12718.7 | 83.17
09:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 117 | 147 | 160 | 0 | 0 | 35 | 0 | 33 | 300 | 275 | 230 | 0 | 35 | 0 | 250 | 0 | 0 | 22 | 70 | 15 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 48 | 12 | 3 | 46 | 0 | 2 | 157 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1224 | 6 | 43 | 98 | 189 | 0 | 356 | 0 | 52 | 183 | 33 | 52 | 50 | 35 | 8 | 17 | 34 | 38 | 34 | 49 | 31 | 0 | 320 | 350 | 36 | 39 | 0 | 155 | 16 | 0 | 82 | 30 | 0 | 16 | 72 | 0 | 77 | 116 | 5 | 1 | 33.14 | 12 | 6791.14 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72.04 | 1058 | 0 | 767 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 39.07 | 186 | 0 | 210 | 0 | 179 | 0 | 384 | 0 | 1.42 | 0 | 161 | 57 | 72 | 2 | 113 | 0 | 0 | 0.8 | 98 | 0.46 | 0 | 307 | 7 | 114 | 220 | 0 | 0 | 1145 | 0 | 6206.79 | 12997.93 | 83.16
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 128 | 147 | 245 | 0 | 6 | 72 | 0 | 33 | 300 | 294 | 230 | 0 | 35 | 0 | 250 | 0 | 0 | 30 | 70 | 16 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 2 | 17 | 0 | 0 | 50 | 12 | 2 | 46 | 0 | 3 | 159 | 5 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 1224 | 6 | 43 | 120 | 187 | 0 | 347 | 0 | 52 | 213 | 32 | 50 | 50 | 35 | 9 | 17 | 34 | 40 | 34 | 60 | 31 | 0 | 320 | 390 | 36 | 39 | 0 | 154 | 16 | 0 | 81 | 30 | 0 | 16 | 83 | 36 | 67 | 117 | 5 | 1 | 33.91 | 12 | 7100.91 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.34 | 1058 | 0 | 751 | 0 | 0 | 0 | 95 | 0 | 0 | 10 | 0 | 0 | 72 | 0 | 31.43 | 184 | 0 | 209 | 0 | 189 | 0 | 414 | 0 | 4.28 | 0 | 164 | 57 | 80 | 9 | 111 | 0 | 0 | 0.9 | 128 | 0.58 | 0 | 307 | 7 | 114 | 220 | 0 | 0 | 1100 | 0 | 6323.53 | 13424.44 | 83.15
11:00 | 8 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 120 | 144 | 275 | 16 | 25 | 72 | 0 | 50 | 300 | 283 | 230 | 0 | 35 | 0 | 250 | 0 | 0 | 32 | 160 | 16 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 9 | 17 | 2 | 0 | 50 | 48 | 0 | 46 | 0 | 2 | 160 | 53 | 0 | 0 | 0 | 38 | 142 | 0 | 0 | 0 | 1224 | 6 | 43 | 112 | 187 | 0 | 356 | 0 | 49 | 182 | 35 | 51 | 50 | 24 | 9 | 17 | 62 | 34 | 43 | 68 | 30 | 0 | 320 | 350 | 36 | 39 | 0 | 151 | 16 | 0 | 82 | 30 | 0 | 16 | 89 | 54.5 | 66 | 116 | 5 | 2 | 16.64 | 12 | 7379.14 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.94 | 1060 | 0 | 758 | 0 | 0 | 0 | 109 | 0 | 0 | 95 | 0 | 52.2 | 104 | 15 | 19.83 | 181 | 0 | 207 | 0 | 197 | 0 | 329 | 0 | 5.29 | 0 | 160 | 58 | 115 | 14 | 93 | 0 | 0 | 1 | 132 | 0.67 | 0 | 307 | 7 | 108 | 220 | 0 | 6 | 1100 | 0 | 6464.93 | 13844.07 | 83.14
12:00 | 8 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 113 | 144 | 278 | 55 | 35 | 72 | 0 | 50 | 450 | 297 | 350 | 0 | 35 | 0 | 315 | 0 | 0 | 33 | 160 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 17 | 24 | 0 | 50 | 62 | 2 | 46 | 1 | 2 | 160 | 108 | 0 | 0 | 0 | 51 | 140 | 0 | 0 | 0 | 1224 | 8 | 43 | 122 | 187 | 0 | 342 | 0 | 49 | 206 | 34 | 51 | 45 | 21 | 8 | 17 | 80 | 38 | 43 | 69 | 30 | 0 | 320 | 394 | 36 | 39 | 0 | 144 | 16 | 0 | 82 | 30 | 0 | 16 | 98 | 54.5 | 66 | 116 | 5 | 2 | 18.93 | 12 | 7692.43 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.31 | 1060 | 0 | 760 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 13 | 52.2 | 103 | 15 | 34.09 | 181 | 0 | 205 | 0 | 199 | 0 | 414 | 0 | 5.23 | 0 | 158 | 59 | 115 | 31 | 48 | 0 | 0 | 3.1 | 42 | 0.41 | 0 | 250 | 8 | 120 | 220 | 0 | 98 | 1098 | 0 | 6531.34 | 14223.77 | 83.13
13:00 | 8 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 120 | 144 | 278 | 55 | 35 | 72 | 0 | 50 | 450 | 269 | 350 | 0 | 35 | 0 | 318 | 0 | 0 | 34 | 108 | 16 | 22 | 0 | 0 | 0 | 0 | 7 | 0 | 9 | 17 | 40 | 0 | 50 | 62 | 2 | 46 | 39 | 6 | 160 | 160 | 0 | 1 | 14 | 51 | 143 | 0 | 0 | 0 | 1224 | 8 | 43 | 123 | 187 | 0 | 357 | 0 | 48 | 185 | 33 | 51 | 40 | 24 | 9 | 17 | 80 | 44 | 52.2 | 68 | 30 | 0 | 320 | 390 | 36 | 39 | 0 | 153 | 0 | 0 | 81 | 30 | 0 | 16 | 100 | 54.3 | 66 | 116 | 5 | 1 | 42.89 | 12 | 7767.39 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.5 | 1158 | 0 | 757 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 34 | 52.2 | 102 | 15 | 13.18 | 178 | 0 | 201 | 0 | 202 | 0 | 385 | 0 | 2.68 | 0 | 158 | 57 | 115 | 29 | 32 | 0 | 0 | 4.8 | 156 | 0.72 | 0 | 250 | 9 | 108 | 220 | 0 | 120 | 1095 | 0 | 6666.08 | 14433.47 | 83.12
14:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 130 | 143 | 278 | 55 | 50 | 72 | 0 | 50 | 450 | 297 | 400 | 0 | 17 | 0 | 312 | 0 | 0 | 28 | 142 | 16 | 22 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 17 | 71 | 0 | 48 | 62 | 5 | 46 | 51 | 4 | 160 | 160 | 0 | 34 | 24 | 51 | 143 | 0 | 0 | 0 | 1224 | 8 | 43 | 128 | 185 | 0 | 353 | 0 | 48 | 180 | 33 | 53 | 40 | 23 | 11 | 17 | 80 | 46 | 52.2 | 42 | 36 | 0 | 320 | 390 | 37 | 39 | 0 | 152 | 8 | 0 | 81 | 30 | 0 | 16 | 105 | 54.5 | 66 | 115 | 5 | 2 | 43.51 | 12 | 7915.21 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.67 | 1244 | 0 | 757.96 | 0 | 0 | 0 | 113 | 0 | 50 | 113 | 34 | 52.2 | 80 | 15 | 41.85 | 174 | 0 | 201 | 0 | 200 | 0 | 373 | 0 | 3.86 | 0 | 157 | 57 | 115 | 26 | 42 | 0 | 0 | 1.3 | 90 | 0.59 | 0 | 307 | 10 | 108 | 220 | 0 | 134 | 1040 | 0 | 6737.43 | 14652.64 | 83.11
15:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 130 | 142 | 278 | 55 | 55 | 72 | 0 | 50 | 450 | 286 | 430 | 0 | 17 | 0 | 312 | 0 | 0 | 22 | 160 | 16 | 22 | 0 | 0 | 0 | 0 | 43 | 0 | 1 | 14 | 71 | 0 | 48 | 62 | 1 | 46 | 51 | 2 | 160 | 160 | 0 | 44 | 25.5 | 51 | 143 | 0 | 0 | 0 | 1224 | 9 | 43 | 128 | 185 | 0 | 340 | 0 | 47 | 203 | 32 | 51 | 40 | 27 | 17 | 17 | 80 | 46 | 52.2 | 46 | 36 | 0 | 320 | 360 | 36 | 40 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 16 | 105 | 0 | 66 | 105 | 5 | 2 | 30.28 | 12 | 7877.98 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.28 | 1241 | 0 | 766.19 | 0 | 0 | 0 | 113 | 0 | 50 | 113 | 35 | 52.2 | 22 | 15 | 10.61 | 170 | 0 | 198 | 0 | 196 | 0 | 411 | 0 | 1.07 | 0 | 158 | 55 | 115 | 20 | 113 | 0 | 0 | 2.3 | 42 | 0.47 | 0 | 307 | 10 | 110 | 220 | 0 | 142 | 980 | 0 | 6603.12 | 14481.1 | 83.1
16:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 114 | 142 | 261 | 55 | 55 | 72 | 0 | 50 | 450 | 298 | 430 | 0 | 17 | 0 | 314 | 0 | 0 | 14 | 160 | 16 | 21 | 0 | 0 | 0 | 0 | 43 | 0 | 6 | 16 | 80 | 0 | 87 | 60 | 1 | 46 | 51 | 2 | 160 | 160 | 0 | 46 | 25.5 | 51 | 144 | 0 | 0 | 0 | 1224 | 5 | 43 | 125 | 185 | 0 | 348 | 0 | 46 | 187 | 32 | 51 | 40 | 23 | 17 | 17 | 80 | 48 | 52.2 | 29 | 36 | 0 | 320 | 351 | 36 | 38 | 0 | 152 | 16 | 0 | 80 | 30 | 0 | 16 | 169 | 42 | 65 | 124 | 5 | 1 | 19.73 | 12 | 7980.43 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.03 | 1170 | 0 | 759.94 | 0 | 0 | 0 | 113 | 0 | 50 | 113 | 35 | 52.2 | 21 | 15 | 24.31 | 169 | 0 | 197 | 0 | 197 | 0 | 324 | 0 | 0.89 | 0 | 161 | 55 | 115 | 9 | 113 | 0 | 0 | 2.2 | 28 | 0.31 | 0 | 270 | 9 | 110 | 220 | 0 | 138 | 991 | 0 | 6434.88 | 14415.31 | 83.09
17:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 120 | 142 | 278 | 55 | 55 | 72 | 0 | 50 | 450 | 279 | 400 | 0 | 17 | 0 | 317 | 0 | 0 | 5 | 160 | 17 | 21 | 0 | 0 | 0 | 0 | 48 | 0 | 4 | 17 | 78 | 0 | 48 | 36 | 0 | 46 | 34 | 7 | 160 | 160 | 0 | 26 | 25.5 | 34 | 143 | 0 | 0 | 0 | 1224 | 2 | 43 | 125 | 185 | 0 | 340 | 0 | 48 | 185 | 32 | 51 | 40 | 30 | 23 | 17 | 80 | 44 | 43 | 9 | 42 | 0 | 320 | 352 | 36 | 38 | 0 | 151 | 16 | 0 | 80 | 30 | 0 | 16 | 170 | 54.5 | 65 | 124 | 5 | 0 | 7.15 | 12 | 7812.15 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.01 | 1109 | 0 | 762.96 | 0 | 0 | 0 | 113 | 0 | 60 | 113 | 34 | 52.2 | 17 | 20 | 8.96 | 168 | 0 | 202 | 0 | 199 | 0 | 398 | 0 | 0.86 | 0 | 161 | 57 | 115 | 5 | 113 | 0 | 0 | 1.3 | 25 | 0.13 | 0 | 240 | 8 | 110 | 220 | 0 | 140 | 989 | 0 | 6357.42 | 14169.57 | 83.08
18:00 | 8 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 17 | 130 | 142 | 278 | 55 | 55 | 90 | 0 | 51 | 370 | 294 | 400 | 0 | 17 | 0 | 314 | 0 | 0 | 1 | 160 | 16.8 | 21 | 0 | 0 | 3 | 15 | 50 | 0 | 0 | 17 | 78 | 0 | 80 | 50 | 0 | 46 | 34 | 8 | 160 | 108 | 0 | 26 | 25.5 | 50 | 145 | 0 | 0 | 0 | 1100 | 0 | 51 | 125 | 185 | 0 | 300 | 0 | 48 | 190 | 33 | 60 | 40 | 110 | 27 | 17 | 80 | 40 | 52.2 | 1 | 36 | 0 | 320 | 351 | 36 | 38 | 0 | 136 | 16 | 0 | 82 | 30 | 0 | 16 | 169 | 54.5 | 113 | 152 | 5 | 0 | 0.67 | 12 | 7840.67 | 900 | 0 | 0 | 10 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | 1121 | 17 | 768.13 | 0 | 0 | 0 | 70 | 4 | 96 | 70 | 35 | 52.2 | 2 | 22 | 0.71 | 194 | 0 | 170 | 0 | 160 | 0 | 328 | 0 | 0.09 | 0 | 157 | 57 | 115 | 1 | 113 | 0 | 0 | 0.2 | 3 | 0.01 | 8 | 240 | 10 | 110 | 180 | 0 | 138 | 981 | 8 | 6148.85 | 13989.52 | 83.07
19:00 | 68 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 131 | 144 | 278 | 55 | 55 | 144 | 0 | 51 | 450 | 303 | 370 | 0 | 17 | 0 | 316 | 0 | 0 | 0 | 160 | 17 | 21 | 0 | 0 | 27 | 45 | 49 | 0 | 0 | 102 | 78 | 17 | 87 | 94 | 0 | 46 | 58 | 21 | 160 | 160 | 0 | 35 | 25.5 | 90 | 144 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 185 | 0 | 350 | 0 | 49 | 194 | 34 | 81 | 45 | 154 | 37 | 17 | 80 | 46 | 52.2 | 0 | 38 | 0 | 320 | 354 | 36 | 38 | 0 | 146 | 0 | 0 | 82 | 28 | 0 | 16 | 169 | 54.5 | 113 | 153 | 7 | 0 | 0 | 12 | 8608.2 | 852 | 0 | 0 | 37 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1218 | 35 | 767.17 | 0 | 0 | 0 | 100 | 4 | 96 | 113 | 35 | 52.2 | 0 | 22 | 0 | 202 | 0 | 201 | 0 | 196 | 0 | 398 | 0 | 0 | 0 | 158 | 56 | 115 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 24 | 307 | 10 | 110 | 220 | 0 | 142 | 1125 | 35 | 6776.37 | 15384.57 | 83.06
19:30 | 98 | 54 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 131 | 144 | 278 | 55 | 55 | 144 | 0 | 60 | 450 | 304 | 370 | 0 | 17 | 0 | 316 | 0 | 0 | 0 | 160 | 17 | 21 | 0 | 0 | 35 | 65 | 50 | 0 | 0 | 102 | 78 | 17 | 87 | 95 | 0 | 46 | 68 | 13 | 160 | 160 | 0 | 45 | 25.5 | 105 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 185 | 0 | 354 | 0 | 49 | 184 | 34 | 90 | 45 | 180 | 37 | 17 | 80 | 48 | 52.2 | 0 | 38 | 0 | 320 | 340 | 36 | 38 | 0 | 146 | 0 | 0 | 82 | 28 | 0 | 16 | 169 | 54.5 | 113 | 153 | 7 | 0 | 0 | 12 | 8734.2 | 852 | 0 | 0 | 29 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1237 | 35 | 764.05 | 0 | 40 | 0 | 113 | 7 | 96 | 113 | 35 | 52.2 | 0 | 22 | 0 | 202 | 0 | 201 | 0 | 203 | 0 | 377 | 0 | 0 | 0 | 158 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 10 | 110 | 220 | 0 | 148 | 1244 | 45 | 6976.25 | 15710.45 | 83.06
20:00 | 98 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 20 | 131 | 144 | 278 | 55 | 55 | 144 | 0 | 68 | 450 | 303 | 370 | 0 | 17 | 0 | 315 | 0 | 0 | 0 | 160 | 17 | 21 | 0 | 0 | 35 | 45 | 50 | 0 | 0 | 102 | 78 | 17 | 87 | 95 | 0 | 46 | 68 | 16 | 160 | 160 | 0 | 47 | 25.5 | 68 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 185 | 0 | 350 | 0 | 50 | 198 | 34 | 85 | 45 | 177 | 37 | 17 | 80 | 52 | 52.2 | 0 | 38 | 0 | 320 | 361 | 36 | 38 | 0 | 152 | 0 | 0 | 82 | 28 | 0 | 16 | 169 | 54.5 | 114 | 152 | 8 | 0 | 0 | 12 | 8740.2 | 852 | 0 | 0 | 29 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 53 | 759.6 | 0 | 52 | 0 | 113 | 16 | 96 | 113 | 35 | 52.2 | 0 | 22 | 0 | 202 | 0 | 201 | 0 | 202 | 0 | 339 | 0 | 0 | 0 | 158 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 10 | 120 | 220 | 0 | 148 | 1244 | 17 | 6951.8 | 15692 | 83.05
21:00 | 74 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 1 | 36 | 124 | 144 | 278 | 55 | 55 | 144 | 0 | 68 | 450 | 263 | 400 | 0 | 17 | 0 | 316 | 0 | 0 | 0 | 160 | 17 | 22 | 0 | 0 | 35 | 45 | 48 | 0 | 0 | 102 | 78 | 17 | 87 | 98 | 0 | 46 | 68 | 20 | 160 | 160 | 0 | 47 | 25.5 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 185 | 0 | 360 | 0 | 50 | 180 | 35 | 89 | 45 | 180 | 37 | 17 | 80 | 52 | 52.2 | 0 | 38 | 0 | 320 | 363 | 36 | 38 | 0 | 153 | 23 | 0 | 82 | 28 | 0 | 18 | 169 | 54.5 | 114 | 152 | 8 | 0 | 0 | 12 | 8752.2 | 902 | 0 | 0 | 24 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241 | 53 | 761 | 0 | 52 | 0 | 113 | 17 | 96 | 113 | 35 | 52.2 | 0 | 22 | 0 | 202 | 0 | 201 | 0 | 202 | 0 | 414 | 0 | 0 | 0 | 157 | 56 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 10 | 114 | 220 | 0 | 128 | 1244 | 17 | 7067.2 | 15819.4 | 83.04
22:00 | 74 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 36 | 96 | 144 | 262 | 55 | 35 | 90 | 0 | 68 | 450 | 293 | 400 | 0 | 17 | 0 | 318 | 0 | 0 | 0 | 160 | 17 | 22 | 0 | 0 | 17 | 30 | 50 | 0 | 0 | 102 | 78 | 0 | 87 | 100 | 0 | 46 | 51 | 22 | 160 | 160 | 0 | 33 | 25.5 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 185 | 0 | 355 | 0 | 51 | 190 | 35 | 74 | 50 | 180 | 38 | 17 | 80 | 44 | 52.2 | 0 | 38 | 0 | 320 | 350 | 25 | 39 | 0 | 154 | 19 | 0 | 82 | 28 | 0 | 18 | 169 | 54.5 | 114 | 152 | 6 | 0 | 0 | 12 | 8569.2 | 907 | 0 | 0 | 24 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1230 | 54 | 765 | 0 | 52 | 0 | 113 | 17 | 88 | 113 | 33 | 52.2 | 0 | 22 | 0 | 201 | 0 | 201 | 0 | 201 | 0 | 390 | 0 | 0 | 0 | 161 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 10 | 114 | 220 | 0 | 143 | 1244 | 17 | 7056.2 | 15625.4 | 83.03
23:00 | 40 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 36 | 96 | 144 | 262 | 55 | 35 | 35 | 0 | 55 | 450 | 302 | 400 | 0 | 17 | 0 | 320 | 0 | 0 | 0 | 160 | 17 | 22 | 0 | 0 | 17 | 65 | 50 | 0 | 0 | 102 | 78 | 0 | 50 | 100 | 0 | 46 | 51 | 33 | 162 | 160 | 0 | 33 | 25.5 | 68 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 187 | 0 | 350 | 0 | 51 | 210 | 35 | 57 | 50 | 180 | 37 | 17 | 80 | 50 | 52.2 | 0 | 32 | 0 | 320 | 396 | 25 | 39 | 0 | 156 | 15 | 0 | 82 | 30 | 0 | 18 | 168 | 54.5 | 114 | 152 | 5 | 0 | 0 | 12 | 8502.2 | 914 | 0 | 0 | 24 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1154 | 54 | 771 | 0 | 52 | 0 | 113 | 18 | 88 | 113 | 33 | 52.2 | 0 | 22 | 0 | 197 | 0 | 197 | 0 | 197 | 0 | 414 | 0 | 0 | 0 | 162 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 120 | 220 | 0 | 138 | 1150 | 0 | 6864.2 | 15366.4 | 83.02
Total KWH | 464544 | 801600 | 319200 | 0 | 0 | 0 | 0 | 0 | 9792000 | 0 | 0 | 210960 | 508320 | 2865456 | 3476160 | 5233211 | 866188 | 594967 | 1578240 | 0 | 1291200 | 8618500 | 7016756 | 7532273 | 0 | 601037 | 0 | 7121012 | 0 | 0 | 230739 | 2918400 | 391800 | 516600 | 0 | 3304090.91 | 210764 | 398945 | 659520 | 0 | 111840 | 1121326 | 1157040 | 56617 | 1292160 | 1455360 | 18840 | 1073280 | 1089782 | 864960 | 3680000 | 2261527 | 0 | 464160 | 349392.6 | 1404254 | 3481331 | 0 | 0 | 0 | 29089088 | 61965 | 1036236 | 2928945 | 4482909.09 | 0 | 8785700 | 0 | 1195680 | 4742000 | 818640 | 1397760 | 1077770 | 1584480 | 367080 | 395100 | 1588020 | 955200 | 1129992 | 495755 | 812688 | 0 | 7766600 | 9260000 | 827000 | 911760 | 0 | 3656373 | 400656 | 0 | 1947840 | 709152 | 0 | 376000 | 2540570 | 975960 | 1830000 | 2892000 | 139200 | 13450 | 281340 | 294960 | 185172221.6 | 21562909 | 0 | 0 | 184800 | 275200 | 0 | 0 | 0 | 0 | 0 | 0 | 712080 | 27469090 | 474720 | 18010468 | 0 | 345834 | 0 | 2452224 | 108489 | 938016 | 1807392 | 415804 | 792907 | 648550 | 317600 | 259496 | 4539364 | 0 | 4941155 | 0 | 4804327 | 0 | 9432509 | 0 | 26880 | 0 | 3906000 | 1304727 | 2229319 | 153933 | 2194368 | 0 | 0 | 12942.48 | 840240 | 4731 | 246720 | 7069000 | 224242 | 2772000 | 4981900 | 0 | 1686000 | 27195636.36 | 115200 | 155456772.84 | 340628994.44

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14223.77 | MW | 12:00 Hr. | Energy Generated |  |  | 340.629 |  | MKWHr.
| Day Peak Demand |  |  | 14352.77 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.43 |  | MKWHr.
| Evening Peak Generation |  |  | 15819.4 | MW | 21:00 Hr. | Energy Demand |  |  | 344.059 |  | MKWHr.
| Evening Peak Demand |  |  | 15881.4 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.2 |  | °C
| Minimum Generation of the Day |  |  | 12309.29 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 964.53 |  | MMCFD
| Maximum Generation of the Day |  |  | 15819.4 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.2523 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 44.293 | 0 | 21.7295 | 0 | 0 | 0.23074 | 0 | 0 | 66.2533 | Gas | 131.404 | Gas | 422347524.8882
| Chattogram Zone |  |  | 4.3463 | 32.7691 | 11.9208 | 0 | 1.0733 | 0.080805 | 0 | 0.11184 | 50.3022 | Coal | 101.3995 | Coal | 723016580.0268
| Cumilla Zone |  |  | 22.534 | 0 | 9.809 | 0 | 0 | 0.49576 | 0.9552 | 0 | 33.794 | HFO | 62.3508 | HFO | 1074916850.932
| Mymensingh Zone |  |  | 0.1392 | 0 | 5.9929 | 0 | 0 | 0.29479 | 0 | 0 | 6.4269 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.396 | Hydro | 1.0733 | Hydro | 107328
| Khulna Zone |  |  | 0 | 27.4691 | 0.93472 | 0 | 0 | 0.71208 | 21.5629 | 0 | 50.6788 | Solar | 3.7609 | Solar | 60397281.9028
| Barishal Zone |  |  | 7.9781 | 35.9506 | 0.36192 | 0 | 0 | 0.004731 | 0 | 0 | 44.2954 | Import | 40.5286 | Import | 187924409.51
| Rajshahi Zone |  |  | 23.7174 | 0 | 7.1783 | 0 | 0 | 0.93493 | 18.0105 | 0 | 49.841 | Wind | 0.11184 | Wind | 1637337.6
| Rangpur Zone |  |  | 0 | 5.2107 | 4.4237 | 0 | 0 | 1.0071 | 0 | 0 | 10.6415
| Total |  |  | 131.404 | 101.3995 | 62.3508 | 0 | 1.0733 | 3.7609 | 40.5286 | 0.11184 | 340.629
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 422347524.8882 |  | Hydro | 107328
|  |  |  | Coal | 723016580.0268 |  | Solar | 60397281.9028
|  |  |  | HFO | 1074916850.932 |  | Import | 187924409.51
|  |  |  | HSD | 0 |  | Wind | 1637337.6
[5 empty] | Total: | 247,03,47,312 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 1672.73 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5629 | Peak Hr Flow | 902.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 7394872.77 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 18.0105 | Peak Hr Flow | 761.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 322 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9552 | Peak Hr Flow | 52.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 746 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.5286 | Peak Hr Flow | 1715.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 10 |  | 5206
|  |  |  | Chattogram |  | 0 |  | 1404
|  |  |  | Cumilla |  | 10 |  | 1478
|  |  |  | Mymensingh |  | 39 |  | 1335
|  |  |  | Sylhet |  | 0 |  | 604
|  |  |  | Khulna |  | 0 |  | 1868
|  |  |  | Barishal |  | 0 |  | 476
|  |  |  | Rajshahi |  | 0 |  | 1747
|  |  |  | Rangpur |  | 0 |  | 1009
|  |  |  | Total |  | 59 |  | 15127
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:12 | 17:22 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D
| 08:13 | 17:22 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D
| 08:18 | 11:50 | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to CUmillaPBS-2 taken S/D for | [7 empty] | 20.0MW load
|  |  | Red hot maintenance. | [7 empty] | interrup.
| 08:18 | 11:50 | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to CUmillaPBS-2 taken S/D for | [7 empty] | 20.0MW load
|  |  | Red hot maintenance. | [7 empty] | interrup.
| 08:27 | 16:50 | KSRM 132/33kV S/S Transformer-03 LT Scheduled S/D Due to cleaning purpose
| 08:29 | 16:41 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to cleaning purpose
| 08:32 | 16:51 | KSRM 132/33kV S/S Transformer-02 LT Scheduled S/D Due to cleaning purpose
| 08:35 | 16:54 | KSRM 132/33kV S/S Baraulia Main Scheduled S/D Due to Trimming tree
|  | 08:35 | Cantonment 132/33kV S/S Transformer-2 (T-2) LT is restored.
| 08:38 | 15:50 | Baroaulia-KSRM 132 kV Ckt-1 Scheduled S/D from Baroaulia 132/33kV end Due to Maintenance
work at ksrm end
| 08:41 | 17:11 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc changing Work and from Meghnaghat 400/230kV end Due to Requested by NLDC
| 08:59 | 16:26 | Gallamari- Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. and from
Gollamari 132/33kVend.
| 09:13 |  | BIPTC S/S 20DF24 Forced S/D Due to Shutdown is taken for DCRM test of CB
| 09:32 | 11:49 | Ishwardi-Natore 132kV Ckt-1 Forced S/D from Ishurdi 132/33kV end Due to red hot
maintenance and from Natore 132/33kV end Due to Reconductoring Work
| 10:37 |  | Patuakhali 1320 MW (RNPL) unit-1 was sync.
| 11:13 | 13:30 | BIPTC S/S 20DF11 Forced S/D Due to Shutdown is taken for BCU and Relay checking.
| 11:15 | 12:25 | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to CT Connector temperature high.
| 11:15 | 12:25 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to CT Connector temperature high.
| 11:33 |  | Unique Meghnaghat Power Limited (UMPL) ST Shutdown with remarks:- As per NLDC due to Gas
shortage.
| 11:33 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- ST
| 11:36 |  | Unique Meghnaghat Power Limited (UMPL) GT Shutdown with remarks:- As per NLDC due to gas
shortage.
| 11:36 |  | Unique Meghnaghat Power 584 MW CCPP was shutdown due to gas shortage & transformer
overload.
| 11:36 |  | Unique Meghnaghat Power Limited (UMPL) Shutdown with remarks:- GT
| 12:00 |  | Day Peak: 14221 MW.
| 12:00 |  | Day Peak Gen. 14223 MW
|  | 12:06 | Bheramara P/S-Faridpur 132 kV Ckt-1 is restored.
|  | 12:07 | Bheramara P/S-Faridpur 132 kV Ckt-2 is restored.
| 12:10 | 12:16 | Bhaluka 132/33kV S/S Transformer- 02 LT Tripped showing NA relays Due to df/dt | [7 empty] | 70.0MW load
interrup.
| 12:10 | 12:16 | Bhaluka 132/33kV S/S Transformer- 01 LT Tripped showing NA relays Due to BR Powergen 1 & | [7 empty] | 70.0MW load
|  |  | 2 trip from BR Powergen side and load 0 MW from 160 MW. GCB Open by NLDC For TR2 df/dt | [7 empty] | interrup.
| 12:28 | 13:15 | Rajbari 132/33kV S/S Transformer-1 LT Scheduled S/D Due to OLTC Oil Samples
collection...
| 13:19 | 14:10 | Rajbari 132/33kV S/S Transformer-2 LT Forced S/D
| 13:20 | 14:07 | Rajbari 132/33kV S/S Transformer-2 HT Forced S/D
| 15:30 | 15:45 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to For the purpose of removing bird nests
| 15:31 | 15:45 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to For the purpose of removing bird nests.
|  | 18:57 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 HT is restored.
|  | 19:01 | Cantonment 132/33kV S/S Transformer-2 (T-2) HT is restored.
|  | 19:02 | Cantonment 132/33kV S/S Auxiliary Transformer, AT-2 LT is restored.
| 06:05 | 06:55 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Scheduled S/D Due to High
temperature point
| 06:05 | 07:55 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to High
temperature point
| 06:05 | 07:55 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to High
temperature point
| 06:05 | 07:55 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Scheduled S/D Due to High
temperature point
| 06:33 |  | Ghorasal- Ishwardi 230 kV Ckt-2 Project Work S/D from Ghorashal 230kV end Due to Ruppoor
Transmission line project work and from Ishurdi 230/132kV end Due to removal of Cradle
guard in Rooppur Dhaka line.
| 06:33 |  | Ghorasal- Ishwardi 230 kV Ckt-1 Project Work S/D from Ghorashal 230kV end Due to Ruppoor
Transmission line project work and from Ishurdi 230/132kV end Due to removal of Cradle
guard in Rooppur Dhaka line.
| 07:11 |  | Ishurdi-Pabna 132kV ckt Project Work S/D from Pabna 132/33kV end Due to S/D taken by
Ishwardi grid S/S and from Ishurdi 132/33kVend.
| 07:23 |  | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 402 | 9792000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8618500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 263 | 7016756 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 866188 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 316 | 7121012 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 74 | 464544 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 1 | 210960 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 3476160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 594967 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 601037 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 391800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 516600 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 319200 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 5233211 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 124 | 2865456 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 801600 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 68 | 1291200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1578240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 230739 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 508320 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 3304090.91 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 7532273 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2918400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3121 | 66253253.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 349392.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 61965 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 47 | 464160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1073280 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3481331 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1404254 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 1157040 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 1121326 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 87 | 1292160 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 864960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 48 | 659520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 18840 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 45 | 398945 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 56617 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 1089782 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 98 | 1455360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 210764 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 2261527 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 29089088 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 111840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 160 | 3680000 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2477.5 | 50302151.6
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 180 | 4742000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8785700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 818640 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1195680 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 185 | 4482909.09 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1036236 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 132 | 2928945 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 38 | 812688 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1077770 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 1584480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 52 | 955200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1129992 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 395100 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1588020 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 367080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 89 | 1397760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 495755 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1583.2 | 33793955.09
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 8 | 139200 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 152 | 2892000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 114 | 1830000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 281340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294960 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 975960 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 340.5 | 6426910
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 827000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 38 | 911760 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3656373 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 28 | 709152 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1947840 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 169 | 2540570 | Under Maintenance
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 376000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 400656 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 363 | 9260000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7766600 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1230 | 28395951
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 902 | 21562909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 24 | 184800 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 44 | 275200 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 474720 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 712080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1241 | 27469090 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2264 | 50678799
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 128 | 1686000 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 48 | 246720 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 224242 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 114 | 2772000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27195636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4981900 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 115200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7069000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4731 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2088 | 44295429.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 52 | 345834 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 17 | 108489 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 415804 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 202 | 4539364 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 201 | 4941155 | Plant is running as per NLDC demand
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 202 | 4804327 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9432509 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 317600 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 792907 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 938016 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2452224 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1807392 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 761 | 18010468 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 259496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 648550 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2280.2 | 49841015
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1304727 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3906000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 2194368 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 12942.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2229319 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 153933 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 840240 | -
Rangpur Area Total |  |  |  |  | 950 | 435 | 10641529.48
Eastern Grid Total |  |  |  |  | 16921.242 | 8752.2 | 185172221.6
Western Grid Total |  |  |  |  | 11614.5 | 7067.2 | 155456772.84
National Grid Total |  |  |  |  | 28535.742 | 15819.4 | 340628994.44
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9967.84 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5099.4 | MW
i) Dhaka area |  |  | 5195.84 |  | MW | i) Khulna area |  |  |  | 1867.7 | MW
ii) Chattogram area |  |  | 1403.5 |  | MW | ii) Barishal area |  |  |  | 475.9 | MW
iii) Cumilla area |  |  | 1468.5 |  | MW | iii) Rajshahi area |  |  |  | 1746.8 | MW
iv) Mymensingh area |  |  | 1296 |  | MW | iv) Rangpur area |  |  |  | 1009 | MW
v) Sylhet area |  |  | 604 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15067.24 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 11 | 10:00 | 67 | Jaldhaka | 74 | 18:30 | 133 | Payra | 30 | 00:00
2 | AKSML | 129 | 07:00 | 68 | Jamalpur | 138 | 22:00 | 134 | Postogola | 50 | 19:00
3 | Aftabnagar | 36 | 19:00 | 69 | Jashore | 160 | 19:00 | 135 | Purbachal | 18 | 00:00
4 | Agargaon | 122 | 13:00 | 70 | Jhenaidah | 146 | 19:00 | 136 | Purbasadipur | 138 | 20:00
5 | Agrabad | 96 | 13:00 | 71 | Joydebpur | 130 | 21:00 | 137 | Rahanpur | 35 | 00:00
6 | Amnura | 59 | 21:00 | 72 | Joypurhat | 84 | 00:00 | 138 | Rahim | 40 | 17:00
7 | Ashuganj | 90.5 | 23:00 | 73 | Juldah | 21 | 00:00 | 139 | Rajbari | 86 | 20:00
8 | BSRM | 197 | 23:00 | 74 | KSRM | 12 | 00:00 | 140 | Rajendrapur | 125 | 19:30
9 | Bagerhat | 89 | 19:00 | 75 | Kabirpur | 264 | 14:00 | 141 | Rajshahi | 124 | 20:00
10 | Bajitpur | 61 | 19:00 | 76 | Kachua | 90 | 21:00 | 142 | Rajshahi-230 | 90 | 13:00
11 | Bakulia | 95 | 18:30 | 77 | Kallyanpur | 105 | 00:00 | 143 | Ramganj | 116 | 20:00
12 | Banani | 66 | 11:00 | 78 | Kalurghat | 40 | 12:00 | 144 | Rampur | 43 | 23:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kamrangirchar | 61.1 | 12:00 | 145 | Rangamati | 18 | 18:30
14 | Barapukuria | 77 | 19:00 | 80 | Kaptai | N/A | N/A | 146 | Rangpur | 157 | 20:00
15 | Barguna | 20 | 00:00 | 81 | Kasba | 39 | 22:00 | 147 | Ruppur | 7.4 | 16:00
16 | Barishal | 109 | 20:00 | 82 | Kazla | 97 | 13:00 | 148 | SSM | 10 | 01:00
17 | Barishal-230 | 102 | 20:00 | 83 | Keranigonj | 70 | 19:00 | 149 | Saidpur | 122 | 15:00
18 | Baroaulia | 66 | 10:00 | 84 | Khagrachori | 34 | 19:00 | 150 | Satkhira | 140 | 22:00
19 | Baroirhat | 67 | 19:00 | 85 | Khulna | 78 | 19:00 | 151 | Satmasjid | 102 | 13:00
20 | Bashundhara | 181 | 16:00 | 86 | Khulshi | 182 | 22:00 | 152 | Savar | 211 | 14:00
21 | BashundharaCement | 12 | 00:00 | 87 | Kishoreganj | 150 | 19:30 | 153 | SevenRings | 13.44 | 11:00
22 | Beanibazar | 81.3 | 18:30 | 88 | Kodda | 302 | 21:00 | 154 | ShahCement | 33 | 20:00
23 | Benapole | 75 | 21:00 | 89 | Kulaura | 54 | 19:00 | 155 | Shahjadpur | 87 | 22:00
24 | Bhaluka | 172 | 15:00 | 90 | Kurigram | 73 | 18:30 | 156 | Shahjibazar | 127 | 19:00
25 | Bhandaria | 55 | 22:00 | 91 | Kushtia | 145 | 19:00 | 157 | Shahmirpur | 59 | 00:00
26 | Bhangura | 46 | 18:30 | 92 | Lalbag | 58 | 20:00 | 158 | Shariatpur | 90 | 22:00
27 | Bheramara(GK) | 67 | 20:00 | 93 | Lalmonirhat | 72 | 19:00 | 159 | Sherpur | 168 | 21:00
28 | Bhulta | 238 | 22:00 | 94 | MI_Cement | 17.9 | 12:00 | 160 | Shikalbaha | 31 | 00:00
29 | Bog-Sherpur | 74 | 20:00 | 95 | Madanganj | 44 | 18:30 | 161 | Shitalakhya | 80.3 | 12:00
30 | Bogura | 188 | 21:00 | 96 | Madaripur | 117 | 23:00 | 162 | Sholosohor | 42 | 00:00
31 | Borhanuddin | 92 | 22:00 | 97 | Madartek | 83.83 | 23:00 | 163 | Shyampur | 136 | 13:00
32 | Brahmanbaria | 145 | 18:30 | 98 | Madunaghat | 53 | 14:00 | 164 | Siddhirganj | 120 | 11:00
33 | Cantonment | 94 | 22:00 | 99 | Magura | 76 | 19:00 | 165 | Sirajganj | 120 | 19:30
34 | Chandpur | 74 | 21:00 | 100 | Mahasthangarh | 88 | 19:30 | 166 | Sonargaon | 99 | 21:00
35 | Chandraghona | 37 | 20:00 | 101 | Manikganj | 134 | 21:00 | 167 | Sreemongol | 82 | 21:00
36 | Chapai | 75 | 21:00 | 102 | Maniknagar | 75 | 13:00 | 168 | Sreepur | 115 | 15:00
37 | Charsaidpur | 36 | 00:00 | 103 | Matarbari | 51 | 23:00 | 169 | Srinagar | 48.32 | 21:00
38 | Chauddagram | 81 | 18:30 | 104 | Matuail | 64 | 12:00 | 170 | Sunamganj | 55 | 18:30
39 | Chhatak | 36 | 20:00 | 105 | Millgate | 87 | 12:00 | 171 | Sylhet | 50 | 22:00
40 | Chowmuhani | 235 | 21:00 | 106 | Mirpur | 148 | 18:30 | 172 | Sylhet-132 | 129 | 18:30
41 | Chuadanga | 119 | 19:00 | 107 | Mirsorai | 10 | 20:00 | 173 | TK | 32.7 | 00:00
42 | Coxsbazar | 134 | 19:30 | 108 | Mirzapur | 50 | 22:00 | 174 | Tangail | 200 | 22:00
43 | Cumilla(N) | 186 | 18:30 | 109 | Mithapukur | 69 | 07:00 | 175 | Thakurgaon | 105 | 19:30
44 | Cumilla(S) | 164 | 16:00 | 110 | Modern | N/A | N/A | 176 | Tongi | 133 | 10:00
45 | Daudkandi | 155 | 00:00 | 111 | Mogbazar | 153.2 | 12:00 | 177 | Ullahpara | 48 | 20:00
46 | Dhaka | 60 | 12:00 | 112 | Mongla | 40 | 00:00 | 178 | Ullon | 46 | 00:00
47 | Dhamrai | 130 | 19:30 | 113 | Motijheel | 39 | 13:00 | 179 | Uttara | 83 | 13:00
48 | Dhanmondi | 150 | 13:00 | 114 | Muktagacha | 36 | 18:30 | 180 | UttaraNew | 47 | 23:00
49 | Dohazari | 110 | 19:00 | 115 | Munshiganj | 109 | 00:00 | 181 | Zigatola | 67 | 14:00
50 | Faridpur | 165 | 22:00 | 116 | Muradnagar | 29 | 00:00
51 | Fatullah | 88 | 12:00 | 117 | Mymensingh | 213 | 19:00
52 | Fenchuganj | 36 | 19:00 | 118 | Naogaon | 154 | 22:00
53 | Feni | 124 | 23:00 | 119 | Narail | 63 | 20:00
54 | GPH | 92 | 22:00 | 120 | Narinda | 71.5 | 13:00
55 | Ghatail | 80 | 23:00 | 121 | Narshingdi | 178 | 21:00
56 | Ghorashal | 19 | 19:00 | 122 | Natore | 179 | 19:30
57 | Ghorashal-230 | 91 | 21:00 | 123 | Nawabganj | 60.8 | 20:00
58 | Goalpara | 34 | 23:00 | 124 | Netrakona | 135 | 08:00
59 | Gollamari | 90 | 20:00 | 125 | New | 84 | 15:00
60 | Gopalganj | 113 | 19:30 | 126 | Niamatpur | 126 | 21:00
61 | Gulshan | 128 | 13:00 | 127 | Noapara | 47 | 19:30
62 | Halishahar | 70 | 15:00 | 128 | PHP | 6 | 14:00
63 | HaripurSBU | 135 | 12:00 | 129 | Pabna | 130 | 19:30
64 | Hasnabad | 80 | 20:00 | 130 | Palashbari | 140 | 19:30
65 | Hathazari | 86 | 19:00 | 131 | Panchagarh | 48 | 19:00
66 | Ishurdi | 78 | 20:00 | 132 | Patuakhali | 77 | 22:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14536.3 | 397 |  | 14951.17
1:00 | 14169.77 | 432 |  | 14621.21
2:00 | 13984.35 | 207 |  | 14200.35
3:00 | 13439.7 | 125 |  | 13570.7
4:00 | 13107.32 | 98 |  | 13209.32
5:00 | 12665.71 | 81 |  | 12750.71
6:00 | 12309.29 | 78 |  | 12391.29
7:00 | 12532.8 | 68 |  | 12603.8
8:00 | 12718.7 | 48 |  | 12768.7
9:00 | 12997.93 | 99 |  | 13100.93
10:00 | 13424.44 | 95 |  | 13523.44
11:00 | 13844.07 | 105 |  | 13954.07
12:00 | 14223.77 | 123 |  | 14352.77
13:00 | 14433.47 | 96 |  | 14533.47
14:00 | 14652.64 | 89 |  | 14745.64
15:00 | 14481.1 | 212 |  | 14703.1
16:00 | 14415.31 | 209 |  | 14633.31
17:00 | 14169.57 | 224 |  | 14403.57
18:00 | 13989.52 | 110 |  | 14104.52
19:00 | 15384.57 | 207 |  | 15600.57
19:30 | 15710.45 | 135 |  | 15851.45
20:00 | 15692 | 153 |  | 15852
21:00 | 15819.4 | 59 |  | 15881.4
22:00 | 15625.4 | 53 |  | 15680.4
23:00 | 15366.4 | 62 |  | 15431.4
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7889.2 | 6647.1 | 14536.3 | DAILY GENERATION CURVE
00:30 | 7701.95 | 6651.085 | 14353.035
01:00 | 7514.7 | 6655.07 | 14169.77 | 09-04-2025
01:30 | 7548.2 | 6528.86 | 14077.06
02:00 | 7581.7 | 6402.65 | 13984.35
02:30 | 7520.95 | 6191.075 | 13712.025
03:00 | 7460.2 | 5979.5 | 13439.7
03:30 | 7313.2 | 5960.31 | 13273.51
04:00 | 7166.2 | 5941.12 | 13107.32
04:30 | 6993.7 | 5892.815 | 12886.515
05:00 | 6821.2 | 5844.51 | 12665.71
05:30 | 6686.52 | 5800.98 | 12487.5
06:00 | 6551.84 | 5757.45 | 12309.29
06:30 | 6572.7 | 5848.345 | 12421.045
07:00 | 6593.56 | 5939.24 | 12532.8
07:30 | 6626.03 | 5999.72 | 12625.75
08:00 | 6658.5 | 6060.2 | 12718.7
08:30 | 6724.82 | 6133.495 | 12858.315
09:00 | 6791.14 | 6206.79 | 12997.93
09:30 | 6946.025 | 6265.16 | 13211.185
10:00 | 7100.91 | 6323.53 | 13424.44
10:30 | 7240.025 | 6394.23 | 13634.255
11:00 | 7379.14 | 6464.93 | 13844.07
11:30 | 7535.785 | 6498.135 | 14033.92
12:00 | 7692.43 | 6531.34 | 14223.77
12:30 | 7729.91 | 6598.71 | 14328.62
13:00 | 7767.39 | 6666.08 | 14433.47
13:30 | 7841.3 | 6701.755 | 14543.055
14:00 | 7915.21 | 6737.43 | 14652.64
14:30 | 7896.595 | 6670.275 | 14566.87
15:00 | 7877.98 | 6603.12 | 14481.1
15:30 | 7929.205 | 6519 | 14448.205
16:00 | 7980.43 | 6434.88 | 14415.31
16:30 | 7896.29 | 6396.15 | 14292.44
17:00 | 7812.15 | 6357.42 | 14169.57
17:30 | 7826.41 | 6253.135 | 14079.545
18:00 | 7840.67 | 6148.85 | 13989.52
18:30 | 8224.435 | 6462.61 | 14687.045
19:00 | 8608.2 | 6776.37 | 15384.57
19:30 | 8734.2 | 6976.25 | 15710.45
20:00 | 8740.2 | 6951.8 | 15692
20:30 | 8746.2 | 7009.5 | 15755.7 |  | Executive Engineer
21:00 | 8752.2 | 7067.2 | 15819.4 |  | Network Operation Division
21:30 | 8660.7 | 7061.7 | 15722.4
22:00 | 8569.2 | 7056.2 | 15625.4
22:30 | 8535.7 | 6960.2 | 15495.9
23:00 | 8502.2 | 6864.2 | 15366.4

## En-Curve
QF-LDC-12
Date | 09-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3571 | 1852.5 | 911 | 0 | 40 | 762.9 | 46 | 4284 | 0 | 791 | 2277.9 | 0 | 0 | 0 | 397 | DAILY ENERGY CURVE
00:30 | 3491 | 1833.75 | 911 | 0 | 39 | 762.385 | 46 | 4310.5 | 0 | 780 | 2179.4 | 0 | 0 | 0 | 414.5 | 09-04-2025
01:00 | 3411 | 1815 | 911 | 0 | 38 | 761.87 | 46 | 4337 | 0 | 769 | 2080.9 | 0 | 0 | 0 | 432
01:30 | 3381.5 | 1804.5 | 910.5 | 0 | 35 | 759.66 | 46 | 4274 | 0 | 708 | 2156.9 | 0 | 0 | 1 | 319.5 | Energy Generated | 340.629 |  | MKWHr
02:00 | 3352 | 1794 | 910 | 0 | 32 | 757.45 | 46 | 4211 | 0 | 647 | 2232.9 | 0 | 0 | 2 | 207 | Energy not Served | 3.43 |  | MKWHr
02:30 | 3357.5 | 1833.5 | 910 | 0 | 33 | 759.475 | 46 | 4188.5 | 0 | 530 | 2048.55 | 0 | 0 | 5.5 | 166 | Total Energy Requirement | 344.059 |  | MKWHr
03:00 | 3363 | 1873 | 910 | 0 | 34 | 761.5 | 46 | 4166 | 0 | 413 | 1864.2 | 0 | 0 | 9 | 125
03:30 | 3365.5 | 1895 | 910.5 | 0 | 34 | 761.31 | 46 | 4165 | 0 | 413.5 | 1669.7 | 0 | 0 | 13 | 111.5
04:00 | 3368 | 1917 | 911 | 0 | 34 | 761.12 | 46 | 4164 | 0 | 414 | 1475.2 | 0 | 0 | 17 | 98
04:30 | 3411 | 1945 | 911 | 0 | 33 | 762.815 | 46 | 4163 | 0 | 361 | 1238.2 | 0 | 0 | 15.5 | 89.5
05:00 | 3454 | 1973 | 911 | 0 | 32 | 764.51 | 46 | 4162 | 0 | 308 | 1001.2 | 0 | 0 | 14 | 81
05:30 | 3453.5 | 1975 | 911 | 0 | 32 | 762.375 | 46 | 4085.5 | 4.025 | 299 | 912.1 | 0 | 0 | 7 | 79.5
06:00 | 3453 | 1977 | 911 | 0 | 32 | 760.24 | 46 | 4009 | 8.05 | 290 | 823 | 0 | 0 | 0 | 78
06:30 | 3393.5 | 1964.25 | 911 | 0 | 34 | 760.315 | 46 | 4074 | 60.98 | 290 | 887 | 0 | 0 | 0 | 73
07:00 | 3334 | 1951.5 | 911 | 0 | 36 | 760.39 | 46 | 4139 | 113.91 | 290 | 951 | 0 | 0 | 0 | 68
07:30 | 3381.5 | 1941.25 | 887 | 0 | 35 | 760.105 | 46 | 4125 | 170.395 | 281 | 993 | 0 | 0 | 5.5 | 58
08:00 | 3429 | 1931 | 863 | 0 | 34 | 759.82 | 46 | 4111 | 226.88 | 272 | 1035 | 0 | 0 | 11 | 48
08:30 | 3394.5 | 1918 | 863 | 0 | 36 | 763.41 | 46 | 4110 | 306.905 | 289.5 | 1117 | 0 | 0 | 14 | 73.5
09:00 | 3360 | 1905 | 863 | 0 | 38 | 767 | 46 | 4109 | 386.93 | 307 | 1199 | 0 | 0 | 17 | 99
09:30 | 3411.5 | 1913.5 | 886.5 | 0 | 39 | 759 | 46 | 4089 | 431.685 | 311 | 1314.5 | 0 | 0 | 9.5 | 97
10:00 | 3463 | 1922 | 910 | 0 | 40 | 751 | 46 | 4069 | 476.44 | 315 | 1430 | 0 | 0 | 2 | 95
10:30 | 3393 | 1913.5 | 910 | 0 | 37 | 754.5 | 46 | 4072 | 489.405 | 379.5 | 1633.85 | 0 | 0 | 5.5 | 100
11:00 | 3323 | 1905 | 910 | 0 | 34 | 758 | 46 | 4075 | 502.37 | 444 | 1837.7 | 0 | 0 | 9 | 105
11:30 | 3431.5 | 1904 | 910.5 | 0 | 36 | 759 | 46 | 4091 | 478.22 | 461.5 | 1902.2 | 0 | 0 | 14 | 114
12:00 | 3540 | 1903 | 911 | 0 | 38 | 760 | 46 | 4107 | 454.07 | 479 | 1966.7 | 0 | 0 | 19 | 123
12:30 | 3513.5 | 1887 | 911 | 0 | 41 | 758.5 | 46 | 4164.5 | 496.42 | 471.5 | 2025.2 | 0 | 0 | 14 | 109.5
13:00 | 3487 | 1871 | 911 | 0 | 44 | 757 | 46 | 4222 | 538.77 | 464 | 2083.7 | 0 | 0 | 9 | 96
13:30 | 3473.5 | 1912 | 911 | 0 | 45 | 757.48 | 46 | 4272.5 | 488.275 | 498.5 | 2133.8 | 0 | 0 | 5 | 92.5
14:00 | 3460 | 1953 | 911 | 0 | 46 | 757.96 | 46 | 4323 | 437.78 | 533 | 2183.9 | 0 | 0 | 1 | 89
14:30 | 3464 | 1960.5 | 911 | 0 | 46 | 762.075 | 46 | 4295 | 334.895 | 540.5 | 2205.9 | 0 | 0 | 1 | 150.5
15:00 | 3468 | 1968 | 911 | 0 | 46 | 766.19 | 46 | 4267 | 232.01 | 548 | 2227.9 | 0 | 0 | 1 | 212
15:30 | 3448 | 1976.5 | 911 | 0 | 47 | 763.065 | 46 | 4218 | 224.24 | 553.5 | 2257.4 | 0 | 0 | 3.5 | 210.5
16:00 | 3428 | 1985 | 911 | 0 | 48 | 759.94 | 46 | 4169 | 216.47 | 559 | 2286.9 | 0 | 0 | 6 | 209
16:30 | 3465 | 1963.5 | 905.5 | 0 | 46 | 761.45 | 46 | 4124.5 | 156.44 | 568.5 | 2250.55 | 0 | 0 | 5 | 216.5
17:00 | 3502 | 1942 | 900 | 0 | 44 | 762.96 | 46 | 4080 | 96.41 | 578 | 2214.2 | 0 | 0 | 4 | 224
17:30 | 3426.5 | 1888.4 | 900 | 0 | 42 | 765.545 | 46 | 4017 | 53.8 | 613.5 | 2324.8 | 0 | 0 | 2 | 167
18:00 | 3351 | 1834.8 | 900 | 0 | 40 | 768.13 | 46 | 3954 | 11.19 | 649 | 2435.4 | 0 | 0 | 0 | 110
18:30 | 3456 | 1888.4 | 876 | 0 | 43 | 767.65 | 46 | 4172 | 5.595 | 734.5 | 2697.9 | 0 | 0 | 0 | 158.5
19:00 | 3561 | 1942 | 852 | 0 | 46 | 767.17 | 46 | 4390 | 0 | 820 | 2960.4 | 0 | 0 | 0 | 207
19:30 | 3529 | 1935 | 852 | 0 | 48 | 764.05 | 46 | 4534 | 0 | 870 | 3132.4 | 0 | 0 | 0 | 135
20:00 | 3531 | 1944 | 852 | 0 | 52 | 759.6 | 46 | 4501 | 0 | 922 | 3084.4 | 0 | 0 | 0 | 153
20:30 | 3565.5 | 1953.5 | 877 | 0 | 52 | 760.3 | 46 | 4509 | 0 | 914.5 | 3077.9 | 0 | 0 | 0 | 106
21:00 | 3600 | 1963 | 902 | 0 | 52 | 761 | 46 | 4517 | 0 | 907 | 3071.4 | 0 | 0 | 0 | 59
21:30 | 3580.5 | 1978 | 904.5 | 0 | 48 | 763 | 46 | 4521.5 | 0 | 902 | 2978.9 | 0 | 0 | 0 | 56
22:00 | 3561 | 1993 | 907 | 0 | 44 | 765 | 46 | 4526 | 0 | 897 | 2886.4 | 0 | 0 | 0 | 53
22:30 | 3600 | 2003 | 910.5 | 0 | 47 | 768 | 46 | 4440 | 0 | 880.5 | 2800.9 | 0 | 0 | 0 | 57.5
23:00 | 3639 | 2013 | 914 | 0 | 50 | 771 | 46 | 4354 | 0 | 864 | 2715.4 | 0 | 0 | 0 | 62
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 395 | 02:00 | 381 | 15:00 | Payra | 415 | 06:00 | 410 | 13:00
Ashuganj | 401 | 4:00 | 383 | 12:00 | Rahanpur | 403 | 02:00 | 393 | 21:00
Bhulta | 399 | 04:00 | 383 | 12:00 | Rampal | 402 | 02:00 | 388 | 19:00
Bibiana | 389 | 00:00 | 380 | 12:00
BIPTC | 398 | 08:00 | 389 | 15:00
Bogura | 394 | 02:00 | 382 | 21:00
Gopalganj | 401 | 06:00 | 390 | 14:00
Kaliakoir | 370 | 06:00 | 357 | 14:00
Madunaghat | 404 | 02:00 | 394 | 13:00
Meghnaghat | 397 | 02:00 | 383 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 07:00 | 222 | 12:00 | Keranigonj | 229 | 03:00 | 220 | 12:00
AKSML | 236 | 18:00 | 225 | 10:00 | Khulna(S) | 230 | 06:00 | 214 | 19:00
Aminbazar | 257 | 19:30 | 222 | 12:00 | Madunaghat | 239 | 18:00 | 228 | 09:00
Ashuganj | 231 | 03:00 | 225 | 13:00 | Madunaghat-400 | 239 | 20:00 | 228 | 10:00
Ashuganj-400 | 231 | 03:00 | 225 | 13:00 | Maniknagar | 227 | 05:00 | 219 | 12:00
Baghabari | 236 | 08:00 | 227 | 19:00 | Meghnaghat | 235 | 03:00 | 228 | 12:00
Barapukuria | 227 | 10:00 | 219 | 06:00 | Meghnaghat-400 | 231 | 02:00 | 222 | 12:00
Barapukuria-230 | 227 | 10:00 | 219 | 06:00 | Mirsorai | 237 | 02:00 | 221 | 10:00
Barishal | 234 | 06:00 | 228 | 23:00 | Rajshahi | 234 | 02:00 | 223 | 19:00
Bheramara | 234 | 02:00 | 221 | 19:00 | Rampal | 230 | 06:00 | 217 | 19:00
Bhulta | 228 | 03:00 | 219 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 00:00 | 217 | 23:00 | Rampura | 228 | 03:00 | 216 | 12:00
BIPTC | 236 | 02:00 | 222 | 19:00 | Shikalbaha | 238 | 19:00 | 224 | 10:00
Bogura | 240 | 11:00 | 232 | 07:00 | Shyampur | 230 | 03:00 | 221 | 12:00
Bogura-400 | 239 | 02:00 | 231 | 19:30 | Siddhirganj | 228 | 03:00 | 221 | 12:00
Borhanuddin | 239 | 04:00 | 235 | 00:00 | Sirajgonj | 241 | 11:00 | 236 | 19:00
BSRM | 234 | 21:00 | 223 | 10:00 | Sreepur | 230 | 02:00 | 221 | 20:00
Cumilla(N) | 224 | 02:00 | 218 | 15:00 | Tongi | 227 | 04:00 | 218 | 12:00
Faridpur | 228 | 06:00 | 221 | 18:30
Fenchuganj | 225 | 09:00 | 220 | 01:00
Ghorashal | 235 | 00:00 | 235 | 00:00
Ghorashal-230 | 229 | 03:00 | 219 | 15:00
Gopalganj | 229 | 02:00 | 223 | 15:00
GPH | 236 | 21:00 | 224 | 10:00
Haripur | 229 | 03:00 | 220 | 15:00
Hasnabad | 229 | 06:00 | 221 | 12:00
Hathazari | 237 | 17:00 | 228 | 09:00
Ishurdi | 236 | 09:00 | 224 | 19:00
Jhenaidah | 226 | 09:00 | 207 | 19:00
Kaliakoir | 230 | 02:00 | 222 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 02:00 | 123 | 12:00 | Madartek | 132 | 02:00 | 122 | 16:00
Agargaon | 134 | 06:00 | 127 | 12:00 | Madunaghat | 137 | 18:00 | 130 | 11:00
Agrabad | 136 | 18:00 | 128 | 09:00 | Magura | 135 | 08:00 | 121 | 19:00
AKS | 134 | 18:30 | 127 | 09:00 | Mahasthangarh | 135 | 10:00 | 127 | 19:30
Aminbazar | 130 | 01:00 | 125 | 12:00 | Manikganj | 130 | 13:00 | 121 | 21:00
Amnura | 141 | 18:00 | 125 | 22:00 | Maniknagar | 131 | 05:00 | 123 | 15:00
Ashuganj | 135 | 01:00 | 133 | 00:00 | Matarbari | 122 | 17:00 | 115 | 07:00
Bagerhat | 131 | 03:00 | 117 | 19:00 | Matuail | 133 | 02:00 | 128 | 12:00
Bajitpur | 128 | 03:00 | 123 | 20:00 | Millgate | 132 | 06:00 | 124 | 15:00
Bakulia | 139 | 16:00 | 128 | 10:00 | Mirpur | 130 | 04:00 | 123 | 12:00
Banani | 132 | 02:00 | 121 | 13:00 | Mirzapur | 129 | 07:00 | 120 | 22:00
Bangabhaban | 131 | 04:00 | 123 | 15:00 | Mithapukur | 133 | 02:00 | 126 | 07:00
Barapukuria | 139 | 01:00 | 133 | 07:00 | MI_Cement | 134 | 02:00 | 128.3 | 12:00
Barguna | 135 | 18:00 | 131 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 07:00 | 125 | 23:00 | Mogbazar | 133 | 03:00 | 122 | 15:00
Barishal-230 | 131 | 06:00 | 125 | 19:00 | Mongla | 131 | 05:00 | 118 | 19:00
Baroaulia | 136 | 17:00 | 128 | 10:00 | Motijheel | 131 | 04:00 | 123 | 15:00
Baroirhat | 126 | 18:30 | 118 | 10:00 | Muktagacha | 159 | 09:00 | 118 | 02:00
Bashundhara | 132 | 02:00 | 122 | 12:00 | Munshiganj | 132 | 02:00 | 128 | 10:00
BashundharaCement | 133 | 01:00 | 127 | 15:00 | Muradnagar | 127 | 07:00 | 118 | 22:00
Beanibazar | 129 | 04:00 | 124 | 00:00 | Mymensingh | 129 | 09:00 | 108 | 20:00
Benapole | 130 | 05:00 | 115 | 19:00 | Naogaon | 132 | 17:00 | 124 | 07:00
Bhaluka | 126 | 18:00 | 120 | 08:00 | Narail | 136 | 05:00 | 121 | 19:00
Bhandaria | 126 | 06:00 | 117 | 18:30 | Narinda | 131 | 05:00 | 123 | 15:00
Bhangura | 132 | 01:00 | 126 | 19:00 | Narshingdi | 129 | 05:00 | 121 | 19:30
Bheramara | 137 | 11:00 | 128 | 19:00 | Natore | 136 | 11:00 | 129 | 19:00
Bheramara(GK) | 136 | 06:00 | 129 | 19:00 | Nawabganj | 131 | 06:00 | 124 | 12:00
Bhulta | 126 | 02:00 | 122 | 14:00 | Netrakona | 114 | 05:00 | 105 | 19:30
Bog-Sherpur | 135 | 01:00 | 130 | 07:00 | New | 134 | 00:00 | 124 | 14:00
Bogura | 138 | 11:00 | 132 | 06:00 | Niamatpur | 136 | 17:00 | 131 | 07:00
Bogura-230 | 138 | 01:00 | 133 | 06:00 | Noapara | 134 | 04:00 | 120 | 19:00
Brahmanbaria | 128 | 08:00 | 122 | 20:00 | Pabna | 135 | 11:00 | 127 | 19:30
Cantonment | 134 | 03:00 | 127 | 12:00 | Palashbari | 129 | 11:00 | 124 | 19:00
Chandina | 129 | 18:00 | 123 | 15:00 | Panchagarh | 136 | 11:00 | 124 | 07:00
Chandpur | 126 | 18:00 | 113 | 15:00 | Patuakhali | 135 | 18:00 | 131 | 23:00
Chandraghona | 136 | 18:00 | 129 | 10:00 | Payra | 136 | 06:00 | 134 | 00:00
Chapai | 131 | 17:00 | 126 | 22:00 | PHP | 124 | 18:00 | 116 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 01:00 | 128 | 15:00 | Postogola | 135 | 02:00 | 131 | 10:00
Chauddagram | 125 | 18:00 | 117 | 13:00 | Purbachal | 133 | 04:00 | 121 | 12:00
Chhatak | 130 | 07:00 | 122 | 00:00 | Purbasadipur | 134 | 01:00 | 124 | 07:00
Chowmuhani | 119 | 18:00 | 110 | 13:00 | Rahanpur | 137 | 02:00 | 133 | 19:30
Chuadanga | 134 | 09:00 | 119 | 19:00 | Rahanpur-400 | 137 | 01:00 | 133 | 07:00
Coxsbazar | 122 | 16:00 | 114 | 02:00 | Rahim | 134 | 03:00 | 128 | 15:00
Cumilla(N) | 128 | 07:00 | 123 | 12:00 | Rajbari | 134 | 06:00 | 128 | 15:00
Cumilla(S) | 133 | 04:00 | 121 | 10:00 | Rajendrapur | 127 | 18:00 | 119 | 00:00
Daudkandi | 125 | 03:00 | 113 | 23:00 | Rajshahi | 136 | 18:00 | 130 | 18:30
Dhaka | 132 | 02:00 | 122 | 14:00 | Rajshahi-230 | 136 | 02:00 | 120 | 22:00
Dhamrai | 131 | 00:00 | 124 | 15:00 | Ramganj | 121 | 18:00 | 109 | 14:00
Dhanmondi | 133.5 | 03:00 | 128 | 12:00 | Rampur | 136 | 19:00 | 127 | 10:00
Dohazari | 131 | 18:00 | 125 | 06:00 | Rampura | 132 | 02:00 | 122 | 12:00
Faridpur | 135 | 06:00 | 130 | 19:30 | Rangamati | 136 | 18:00 | 127 | 10:00
Fatullah | 134 | 03:00 | 129 | 12:00 | Rangpur | 132 | 11:00 | 123 | 19:00
Fenchuganj | 134 | 06:00 | 130 | 21:00 | Ruppur | 138 | 09:00 | 130 | 18:30
Feni | 124 | 18:00 | 118 | 14:00 | Saidpur | 133 | 01:00 | 125 | 19:00
Ghatail | 126 | 07:00 | 117 | 22:00 | Satkhira | 129 | 05:00 | 116 | 19:00
Ghorashal | 138 | 18:00 | 135 | 00:00 | Satmasjid | 133 | 03:00 | 126 | 13:00
Goalpara | 134 | 06:00 | 123 | 19:00 | Savar | 130 | 18:00 | 124 | 12:00
Gollamari | 134 | 06:00 | 124 | 19:00 | SevenRings | 138 | 02:00 | 134 | 00:00
Gopalganj | 134 | 06:00 | 127 | 19:00 | ShahCement | 133 | 01:00 | 128 | 15:00
Gopalganj-400 | 137 | 06:00 | 132 | 15:00 | Shahjadpur | 135 | 03:00 | 132 | 00:00
Gulshan | 132 | 07:00 | 122 | 12:00 | Shahjibazar | 130 | 05:00 | 124 | 19:00
Halishahar | 136 | 18:30 | 128 | 10:00 | Shahmirpur | 139 | 18:00 | 130 | 10:00
Haripur | 134 | 03:00 | 128 | 12:00 | Shariatpur | 135 | 06:00 | 127 | 23:00
HaripurSBU | 134 | 03:00 | 120 | 15:00 | Sherpur | 131 | 18:00 | 118 | 05:00
Hasnabad | 136 | 05:00 | 130 | 15:00 | Shikalbaha | 124 | 00:00 | 119 | 08:00
Hathazari | 138 | 15:00 | 131 | 10:00 | Shikalbaha-230 | 139 | 19:00 | 131 | 10:00
Ishurdi | 138 | 02:00 | 130 | 19:00 | Shitalakhya | 134 | 02:00 | 128.5 | 12:00
Jaldhaka | 133 | 11:00 | 122 | 19:00 | Sholosohor | 136 | 18:00 | 129 | 10:00
Jamalpur | 135 | 19:30 | 122 | 02:00 | Shyampur | 134 | 01:00 | 129 | 11:00
Jashore | 132 | 03:00 | 118 | 19:00 | Shyampur-230 | 134 | 01:00 | 129 | 10:00
Jhenaidah | 136 | 03:00 | 123 | 18:30 | Siddhirganj | 134 | 02:00 | 127 | 18:30
Jhenaidah-230 | 138 | 09:00 | 125 | 19:00 | Sirajganj | 133 | 11:00 | 126 | 07:00
Joydebpur | 135 | 00:00 | 126 | 12:00 | Sonargaon | 133 | 03:00 | 127 | 18:00
Joypurhat | 127 | 01:00 | 119 | 19:00 | Sreemongol | 131 | 06:00 | 125 | 21:00
Juldah | 139 | 18:00 | 131 | 07:00 | Sreepur | 129 | 13:00 | 124 | 10:00
Kabirpur | 134 | 09:00 | 120 | 12:00 | Srinagar | 136 | 16:00 | 124 | 12:00
Kachua | 125 | 18:00 | 116 | 12:00 | SSM | 140 | 18:00 | 130 | 00:00
Kaliakoir | 133 | 03:00 | 128 | 12:00 | Sunamganj | 127 | 06:00 | 121 | 18:30
Kallyanpur | 132 | 04:00 | 125 | 10:00 | Sylhet | 130 | 07:00 | 125 | 01:00
Kalurghat | 137 | 19:30 | 130 | 09:00 | Sylhet-132 | 131 | 06:00 | 127 | 00:00
Kamrangirchar | 131 | 03:00 | 123 | 13:00 | Tangail | 127 | 18:00 | 116 | 22:00
Kaptai | 133 | 5:00 | 124 | 19:00 | Thakurgaon | 136 | 11:00 | 123 | 07:00
Kasba | 126 | 07:00 | 117 | 23:00 | TK | 137 | 19:00 | 130 | 10:00
Kazla | 131 | 04:00 | 123 | 13:00 | Tongi | 134 | 04:00 | 127 | 12:00
Keranigonj | 131 | 03:00 | 125 | 12:00 | Ullahpara | 134 | 09:00 | 128 | 19:00
Khagrachori | 134 | 18:00 | 127 | 10:00 | Ullon | 132 | 03:00 | 122 | 14:00
Khulna | 133 | 04:00 | 121 | 19:00 | Uttara | 132 | 04:00 | 124 | 15:00
Khulna(S) | 134 | 02:00 | 123 | 19:00 | UttaraNew | 132 | 05:00 | 124 | 10:00
Khulshi | 135 | 19:00 | 126 | 10:00 | Zigatola | 132 | 05:00 | 125 | 12:00
Kishoreganj | 124 | 05:00 | 118 | 20:00
Kodda | 134 | 02:00 | 125 | 16:00
KSRM | 137 | 19:00 | 130 | 06:00
Kulaura | 133 | 06:00 | 129 | 19:00
Kurigram | 132 | 01:00 | 120 | 19:00
Kushtia | 136 | 09:00 | 126 | 19:00
Lalbag | 131 | 03:00 | 124 | 13:00
Lalmonirhat | 130 | 10:00 | 122 | 06:00
Madanganj | 133 | 01:00 | 127 | 16:00
Madaripur | 136 | 06:00 | 130 | 15:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division