## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 12-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-04-2025 | during | 12-04-2025 | during | 12-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 402 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 295 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 314 | 322 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 6 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 30 | 130 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 19.5 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 16 | 52.19 | 52.19 | 8 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 45 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 42 | 69 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 22 | 52 | 105 | 105 | 17 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 102 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 72 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 550 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2166 | 2633.5 | 4610.1 | 4672.1 | 3259.13 | 3364.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 7 | 0 | 5 | 0 | 5 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 145 | 149 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 78 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 36 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 16 | 35 | 8 | 25 | 8 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 2.53 | 0 | 2.53 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 95 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 108 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 88 | 100 | 100 | 88 | 88 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 11 | 1 | 4 | 1 | 4 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 160 | 161 | 155 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1524 | 2327 | 2971.25 | 3006.72 | 2959.25 | 2994.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 204 | 186 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 341 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 173 | 165 | 195 | 195 | 125 | 125 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 11 | 135 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 47 | 47 | 47 | 30 | 46 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 50 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 68 | 181 | 200 | 200 | 190 | 190 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 36 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20.83 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 80 | 114 | 114 | 80 | 80 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 0.01 | 0.01 | Under Maintenance
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1174 | 1496.2 | 2122.32 | 2060.99 | 1735.56 | 1706.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 11-04-2025 | during | 12-04-2025 | during | 12-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 22 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 123 | 164 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 65 | 105 | 115 | 115 | 105 | 105 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 52 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 255 | 291 | 601 | 549 | 423.5 | 371.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 25 | 25 | 25 | 25 | 25 | 25 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 40 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 154 | 149 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 0 | 0 | 30 | 30 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 169 | 170 | 170 | 170 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 15 | 23 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 352 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1206 | 1179 | 1213 | 1213 | 1138 | 1138
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 906 | 899 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 101 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 857 | 1005 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1864 | 1904 | 3614.2 | 3514.2 | 3204.2 | 3104.2
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 129 | 163 | 330 | 330 | 330 | 330 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 912 | 1120 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1696 | 1930 | 2501.12 | 2501.12 | 2449.12 | 2449.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 199 | 196 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 193 | 184 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 180 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 409 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5 | 0 | 5.75 | 0 | 5.75 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 563 | 755.85 | 0 | 0 | 0 | 0 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1722 | 1973.85 | 1760.74 | 1593.99 | 1707.95 | 1541.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 59 | 59 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 171 | 172 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 39 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 169 | 0 | 107.65 | 0 | 107.65 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 495 | 414 | 611.05 | 467 | 611.05 | 467
System Total |  |  |  |  | 27566.2 | 28535.742 | 12102 | 14148.55 | 20004.78 | 19578.12 | 17487.76 | 17136.43
Forecast Scenario (12-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12950 |  | 0 |  | 12950
|  |  |  | 1:00 | 12690 |  | 0 |  | 12690
|  |  |  | 2:00 | 12300 |  | 0 |  | 12300
|  |  |  | 3:00 | 11960 |  | 0 |  | 11960
|  |  |  | 4:00 | 11670 |  | 0 |  | 11670
|  |  |  | 5:00 | 11390 |  | 0 |  | 11390
|  |  |  | 6:00 | 11010 |  | 0 |  | 11010
|  |  |  | 7:00 | 11100 |  | 0 |  | 11100
|  |  |  | 8:00 | 11300 |  | 0 |  | 11300
|  |  |  | 9:00 | 11590 |  | 0 |  | 11590
|  |  |  | 10:00 | 11740 |  | 0 |  | 11740
|  |  |  | 11:00 | 12070 |  | 0 |  | 12070
|  |  |  | 12:00 | 12600 |  | 0 |  | 12600
|  |  |  | 13:00 | 13100 |  | 0 |  | 13100
|  |  |  | 14:00 | 13280 |  | 0 |  | 13280
|  |  |  | 15:00 | 13350 |  | 0 |  | 13350
|  |  |  | 16:00 | 13030 |  | 0 |  | 13030
|  |  |  | 17:00 | 12660 |  | 0 |  | 12660
|  |  |  | 18:00 | 12200 |  | 0 |  | 12200
|  |  |  | 18:30 | 12800 |  | 0 |  | 12800
|  |  |  | 19:00 | 13300 |  | 0 |  | 13300
|  |  |  | 19:30 | 13800 |  | 0 |  | 13800
|  |  |  | 20:00 | 13800 |  | 0 |  | 13800
|  |  |  | 21:00 | 13800 |  | 0 |  | 13800
|  |  |  | 22:00 | 13500 |  | 0 |  | 13500
|  |  |  | 23:00 | 13300 |  | 0 |  | 13300
Probable Maximum Temperature: |  |  | 33.50°C
Probable Maximum Demand at Day Peak: |  |  | 12600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 299.69 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:36 hrs on 12-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 11-04-2025 | [28 empty] | Date: | 11-04-2025 | [28 empty] | Date: | 11-04-2025 | [28 empty] | Date: | 11-04-2025 | [28 empty] | Date: | 11-04-2025 | [16 empty] | Date: | 11-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [16 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 36 | 78 | 32 | 15 | 0 | 0 | 126 | 0 | 31 | 370 | 302 | 350 | 0 | 17 | 0 | 327 | 0 | 0 | 0 | 108 | 17 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 64 | 0 | 60 | 10 | 0 | 46 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1030 | 0 | 51 | 12 | 173 | 0 | 300 | 0 | 50 | 200 | 35 | 0 | 50 | 181 | 21 | 20 | 80 | 44 | 53 | 0 | 40 | 0 | 320 | 318 | 25 | 40 | 0 | 134 | 15 | 0 | 82 | 30 | 0 | 18 | 169 | 0 | 75 | 105 | 0 | 0 | 0 | 11 | 6497 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 918 | 0 | 516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 110 | 0 | 260 | 0 | 0 | 0 | 168 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 180 | 0 | 0 | 950 | 0 | 4659 | 11156 | 82.77
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 17 | 78 | 0 | 15 | 0 | 0 | 54 | 0 | 31 | 420 | 311 | 350 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 70 | 18 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 64 | 0 | 60 | 10 | 0 | 46 | 0 | 25 | 161 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 175 | 0 | 359 | 0 | 51 | 200 | 35 | 0 | 50 | 165 | 18 | 20 | 80 | 44 | 53 | 0 | 32 | 0 | 320 | 380 | 25 | 40 | 0 | 146 | 7 | 0 | 82 | 0 | 0 | 18 | 169 | 0 | 45 | 75 | 0 | 0 | 0 | 12 | 6350 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 110 | 0 | 260 | 0 | 0 | 0 | 170 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 180 | 0 | 0 | 950 | 0 | 4651 | 11001 | 82.76
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 70 | 0 | 15 | 0 | 0 | 17 | 0 | 31 | 420 | 305 | 350 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 52 | 18 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 48 | 0 | 60 | 10 | 0 | 46 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 175 | 0 | 360 | 0 | 52 | 193 | 35 | 0 | 50 | 165 | 18 | 20 | 80 | 36 | 53 | 0 | 32 | 0 | 320 | 350 | 25 | 40 | 0 | 154 | 0 | 0 | 82 | 0 | 0 | 18 | 169 | 0 | 45 | 75 | 0 | 0 | 0 | 12 | 6190 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 913 | 0 | 521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 130 | 0 | 110 | 0 | 280 | 0 | 0 | 0 | 168 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 180 | 0 | 0 | 922 | 0 | 4674 | 10864 | 82.75
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 60 | 0 | 0 | 0 | 0 | 17 | 0 | 31 | 420 | 306 | 350 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 48 | 0 | 60 | 10 | 0 | 46 | 0 | 25 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 175 | 0 | 360 | 0 | 51 | 186 | 35 | 0 | 40 | 169 | 19 | 20 | 80 | 40 | 53 | 0 | 32 | 0 | 320 | 350 | 25 | 40 | 0 | 155 | 0 | 0 | 82 | 0 | 0 | 18 | 169 | 0 | 35 | 75 | 0 | 0 | 0 | 12 | 6106 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 864 | 0 | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 130 | 0 | 110 | 0 | 380 | 0 | 0 | 0 | 162 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 220 | 0 | 0 | 900 | 0 | 4692 | 10798 | 82.74
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 60 | 0 | 0 | 0 | 0 | 17 | 0 | 20 | 340 | 283 | 350 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 48 | 10 | 0 | 46 | 0 | 25 | 161 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1003 | 0 | 51 | 0 | 175 | 0 | 359 | 0 | 52 | 182 | 35 | 0 | 40 | 182 | 18 | 20 | 62 | 38 | 53 | 0 | 44 | 0 | 320 | 348 | 25 | 40 | 0 | 141 | 0 | 0 | 82 | 0 | 0 | 18 | 169 | 0 | 35 | 75 | 0 | 0 | 0 | 12 | 5935 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 862 | 0 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 130 | 0 | 110 | 0 | 380 | 0 | 0 | 0 | 166 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 108 | 220 | 0 | 0 | 852 | 0 | 4667 | 10602 | 82.73
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 308 | 420 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 24 | 10 | 0 | 46 | 0 | 25 | 165 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 952 | 0 | 51 | 0 | 175 | 0 | 320 | 0 | 52 | 210 | 35 | 0 | 40 | 182 | 10 | 20 | 62 | 40 | 53 | 0 | 40 | 0 | 320 | 390 | 25 | 40 | 0 | 141 | 0 | 0 | 82 | 0 | 0 | 18 | 168 | 0 | 35 | 75 | 0 | 0 | 0 | 12 | 5834 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 130 | 0 | 110 | 0 | 350 | 0 | 0 | 0 | 168 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 120 | 220 | 0 | 0 | 800 | 0 | 4507 | 10341 | 82.72
06:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 17 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 286 | 420 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 10 | 0 | 46 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 917 | 0 | 51 | 0 | 128 | 0 | 320 | 0 | 52 | 190 | 35 | 0 | 40 | 136 | 9 | 20 | 34 | 30 | 16 | 1 | 16 | 0 | 320 | 357 | 25 | 40 | 0 | 136 | 0 | 0 | 82 | 0 | 0 | 18 | 168 | 0 | 35 | 65 | 0 | 0 | 1 | 12 | 5421 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 818 | 0 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 197 | 0 | 130 | 0 | 110 | 0 | 300 | 0 | 1 | 0 | 168 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 120 | 220 | 0 | 0 | 800 | 0 | 4465 | 9886 | 82.71
07:00 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 300 | 420 | 0 | 0 | 0 | 280 | 0 | 0 | 6 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 128 | 0 | 320 | 0 | 52 | 201 | 35 | 0 | 40 | 68 | 9 | 20 | 17 | 36 | 8 | 8 | 0 | 0 | 320 | 375 | 25 | 40 | 0 | 137 | 15 | 0 | 82 | 0 | 0 | 18 | 168 | 0 | 55 | 75 | 0 | 0 | 8 | 12 | 5289 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 818 | 0 | 425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 9 | 197 | 0 | 130 | 0 | 110 | 0 | 300 | 0 | 0 | 0 | 169 | 60 | 0 | 3 | 0 | 0 | 0 | 0 | 20 | 1 | 0 | 200 | 3 | 120 | 220 | 0 | 0 | 798 | 0 | 4526 | 9815 | 82.7
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 288 | 450 | 0 | 0 | 0 | 329 | 0 | 0 | 16 | 0 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 128 | 0 | 320 | 0 | 53 | 196 | 35 | 0 | 50 | 68 | 14 | 20 | 17 | 36 | 8 | 26 | 0 | 0 | 320 | 360 | 25 | 40 | 0 | 136 | 15 | 0 | 82 | 0 | 0 | 18 | 168 | 0 | 55 | 75 | 0 | 1 | 13 | 12 | 5432 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 814 | 0 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 29 | 198 | 0 | 130 | 0 | 110 | 0 | 300 | 0 | 0 | 0 | 168 | 60 | 0 | 15 | 0 | 0 | 0 | 2 | 28 | 1 | 0 | 200 | 7 | 120 | 220 | 0 | 0 | 796 | 0 | 4581 | 10013 | 82.69
09:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 294 | 450 | 0 | 0 | 0 | 329 | 0 | 0 | 23 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 10 | 161 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 2 | 51 | 0 | 128 | 0 | 320 | 0 | 52 | 193 | 31 | 0 | 50 | 51 | 9 | 20 | 17 | 36 | 8 | 40 | 0 | 0 | 320 | 380 | 25 | 39 | 0 | 136 | 15 | 0 | 79 | 0 | 0 | 18 | 168 | 0 | 55 | 75 | 0 | 1 | 32 | 12 | 5490 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 810 | 0 | 463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 44 | 198 | 0 | 133 | 0 | 110 | 0 | 300 | 0 | 4 | 0 | 166 | 60 | 0 | 24 | 0 | 0 | 0 | 6 | 132 | 1 | 0 | 200 | 7 | 120 | 220 | 0 | 97 | 795 | 0 | 4903 | 10393 | 82.68
10:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 295 | 450 | 0 | 0 | 0 | 325 | 0 | 0 | 26 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 3 | 46 | 0 | 6 | 161 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 900 | 4 | 51 | 0 | 127 | 0 | 320 | 0 | 49 | 194 | 30 | 0 | 50 | 34 | 9 | 20 | 17 | 32 | 0 | 45 | 0 | 0 | 320 | 359 | 25 | 39 | 0 | 137 | 15 | 0 | 79 | 0 | 0 | 18 | 169 | 0 | 55 | 75 | 0 | 2 | 40 | 12 | 5519 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 807 | 0 | 469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 56 | 198 | 0 | 165 | 0 | 130 | 0 | 341 | 0 | 5 | 0 | 166 | 60 | 0 | 32 | 49 | 0 | 0 | 7 | 182 | 1 | 0 | 200 | 7 | 120 | 220 | 0 | 98 | 800 | 0 | 5209 | 10728 | 82.68
11:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 298 | 500 | 0 | 0 | 0 | 316 | 0 | 0 | 32 | 35 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 46 | 0 | 10 | 162 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1000 | 2 | 51 | 0 | 172 | 0 | 334 | 0 | 52 | 208 | 30 | 0 | 50 | 33 | 9 | 20 | 17 | 34 | 0 | 54 | 0 | 0 | 320 | 395 | 25 | 39 | 0 | 145 | 15 | 0 | 79 | 0 | 0 | 18 | 169 | 0 | 55 | 75 | 0 | 2 | 51 | 12 | 5793 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 808 | 0 | 473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 56 | 197 | 0 | 194 | 0 | 150 | 0 | 399 | 0 | 6 | 0 | 169 | 60 | 0 | 36 | 49 | 0 | 0 | 8 | 159 | 1 | 0 | 257 | 7 | 120 | 220 | 0 | 125 | 820 | 0 | 5414 | 11207 | 82.67
12:00 | 0 | 22 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 6 | 17 | 42 | 30 | 0 | 0 | 35 | 54 | 0 | 0 | 225 | 299 | 550 | 0 | 17 | 0 | 314 | 0 | 0 | 32 | 70 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 36 | 0 | 0 | 46 | 0 | 16 | 160 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1100 | 7 | 51 | 11 | 173 | 0 | 341 | 0 | 49 | 204 | 33 | 0 | 50 | 68 | 9 | 20 | 52 | 38 | 8 | 67 | 0 | 0 | 320 | 385 | 25 | 39 | 0 | 154 | 15 | 0 | 81 | 0 | 0 | 18 | 169 | 0 | 65 | 123 | 0 | 3 | 52 | 12 | 6325 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 857 | 0 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 51 | 199 | 0 | 193 | 0 | 187 | 0 | 409 | 0 | 5 | 0 | 171 | 59 | 0 | 39 | 49 | 0 | 0 | 8 | 169 | 1 | 0 | 307 | 7 | 120 | 220 | 0 | 129 | 912 | 0 | 5777 | 12102 | 82.67
13:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 73 | 30 | 0 | 0 | 43 | 144 | 0 | 0 | 225 | 277 | 583 | 0 | 17 | 0 | 314 | 0 | 0 | 33 | 74 | 19.5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 44 | 10 | 3 | 46 | 0 | 20 | 160 | 0 | 0 | 0 | 0 | 30 | 146 | 0 | 0 | 0 | 1224 | 10 | 51 | 60 | 172 | 0 | 350 | 0 | 47 | 186 | 30 | 0 | 50 | 105 | 8 | 20 | 62 | 42 | 24 | 46 | 0 | 0 | 320 | 352 | 25 | 39 | 0 | 153 | 15 | 0 | 81 | 0 | 0 | 18 | 169 | 0 | 65 | 123 | 0 | 3 | 45.82 | 12 | 6685.32 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 903 | 0 | 756.4 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 43.82 | 203 | 0 | 187 | 0 | 184 | 0 | 384 | 0 | 2.29 | 0 | 174 | 60 | 35 | 36 | 60 | 0 | 0 | 8 | 150 | 1 | 0 | 307 | 9 | 120 | 220 | 0 | 136 | 921 | 0 | 6026.51 | 12711.83 | 82.66
14:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 17 | 10 | 85 | 30 | 0 | 0 | 55 | 132 | 0 | 32 | 225 | 297 | 450 | 0 | 17 | 0 | 310 | 0 | 0 | 0 | 108 | 19.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 44 | 22 | 0 | 46 | 15 | 31 | 160 | 0 | 0 | 0 | 0 | 105 | 146 | 0 | 0 | 0 | 1155 | 19 | 51 | 87 | 172 | 0 | 300 | 0 | 46 | 197 | 31 | 0 | 50 | 155 | 9 | 20 | 70 | 40 | 52.2 | 10 | 0 | 0 | 320 | 385 | 25 | 38 | 0 | 133 | 15 | 0 | 81 | 0 | 0 | 18 | 169 | 0 | 65 | 125 | 0 | 2 | 47.8 | 8 | 6703.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.09 | 805 | 0 | 770.97 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 55.57 | 160 | 0 | 185 | 0 | 140 | 0 | 343 | 0 | 4.93 | 0 | 168 | 60 | 35 | 19 | 70 | 0 | 0 | 5 | 157 | 0.33 | 0 | 200 | 9 | 100 | 180 | 0 | 138 | 850 | 0 | 5532.89 | 12236.39 | 82.66
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 17 | 87 | 30 | 0 | 0 | 55 | 70 | 0 | 32 | 225 | 289 | 500 | 0 | 17 | 0 | 313 | 0 | 0 | 23 | 108 | 19.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 22 | 1 | 42 | 17 | 16 | 160 | 0 | 0 | 0 | 0 | 105 | 144 | 0 | 0 | 0 | 1150 | 15 | 51 | 102 | 170 | 0 | 340 | 0 | 45 | 198 | 31 | 0 | 50 | 155 | 9 | 20 | 70 | 40 | 52.2 | 20 | 0 | 0 | 320 | 363 | 25 | 38 | 0 | 149 | 15 | 0 | 81 | 0 | 0 | 18 | 169 | 0 | 65 | 125 | 0 | 2 | 15.49 | 12 | 6692.19 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.86 | 856 | 0 | 752.86 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 40.58 | 177 | 0 | 185 | 0 | 179 | 0 | 397 | 0 | 3.64 | 0 | 165 | 60 | 35 | 13 | 70 | 0 | 0 | 5 | 138 | 0.34 | 0 | 250 | 9 | 100 | 220 | 0 | 139 | 890 | 0 | 5733.28 | 12425.47 | 82.65
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 72 | 46 | 0 | 0 | 55 | 54 | 0 | 32 | 225 | 298 | 500 | 0 | 17 | 0 | 313 | 0 | 0 | 6 | 46 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 10 | 0 | 43 | 17 | 22 | 160 | 0 | 0 | 0 | 0 | 51 | 144 | 0 | 0 | 0 | 1150 | 11 | 51 | 50 | 163 | 0 | 345 | 0 | 45 | 188 | 32 | 0 | 50 | 100 | 9 | 20 | 52 | 34 | 52.2 | 17 | 0 | 0 | 320 | 369 | 25 | 38 | 0 | 152 | 15 | 0 | 81 | 0 | 0 | 18 | 169 | 0 | 66 | 114 | 0 | 1 | 25.24 | 12 | 6408.44 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.88 | 858 | 0 | 754.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 25.63 | 190 | 0 | 182 | 0 | 177 | 0 | 414 | 0 | 2.33 | 0 | 164 | 60 | 0 | 12 | 34 | 0 | 0 | 3.9 | 80 | 0.28 | 0 | 250 | 9 | 100 | 220 | 0 | 138 | 900 | 0 | 5570.57 | 11979.01 | 82.65
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 69 | 62 | 0 | 0 | 55 | 54 | 0 | 16 | 225 | 285 | 550 | 0 | 17 | 0 | 314 | 0 | 0 | 5 | 35 | 19.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 10 | 1 | 44 | 17 | 15 | 160 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1100 | 4 | 51 | 50 | 163 | 0 | 345 | 0 | 45 | 182 | 32 | 0 | 70 | 68 | 26 | 20 | 52 | 38 | 52.2 | 13 | 0 | 0 | 320 | 349 | 25 | 38 | 0 | 146 | 15 | 0 | 82 | 0 | 0 | 18 | 170 | 0 | 66 | 124 | 0 | 0 | 8.31 | 12 | 6306.01 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.82 | 855 | 0 | 754.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 8.08 | 190 | 0 | 182 | 0 | 176 | 0 | 414 | 0 | 0.72 | 0 | 168 | 60 | 0 | 7 | 34 | 0 | 0 | 1.7 | 24 | 0.13 | 0 | 200 | 8 | 108 | 220 | 0 | 138 | 915 | 0 | 5403.47 | 11709.48 | 82.64
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 10 | 71 | 68 | 15 | 0 | 55 | 54 | 0 | 16 | 225 | 298 | 450 | 0 | 17 | 0 | 280 | 0 | 0 | 1 | 35 | 19.5 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 4 | 0 | 0 | 0 | 48 | 10 | 0 | 46 | 17 | 25 | 160 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 1150 | 0 | 51 | 10 | 107 | 0 | 300 | 0 | 47 | 208 | 34 | 0 | 70 | 68 | 27 | 20 | 52 | 32 | 52.2 | 1 | 0 | 0 | 320 | 354 | 25 | 39 | 0 | 149 | 15 | 0 | 82 | 0 | 0 | 18 | 170 | 0 | 103 | 151 | 0 | 0 | 0.52 | 12 | 6184.22 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 855 | 0 | 752.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64 | 0 | 0.56 | 150 | 0 | 140 | 0 | 154 | 0 | 414 | 0 | 0.08 | 0 | 168 | 60 | 0 | 1 | 34 | 0 | 0 | 0.2 | 8 | 0.02 | 0 | 229 | 8 | 120 | 220 | 0 | 138 | 1030 | 0 | 5391.01 | 11575.23 | 82.64
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 17 | 86 | 144 | 25 | 0 | 55 | 72 | 0 | 50 | 225 | 301 | 583 | 0 | 35 | 0 | 318 | 0 | 0 | 0 | 108 | 19.5 | 15 | 0 | 0 | 1 | 45 | 0 | 0 | 8 | 17 | 46 | 0 | 100 | 50 | 0 | 46 | 19 | 26 | 160 | 0 | 0 | 0 | 0 | 62 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 35 | 165 | 0 | 354 | 0 | 50 | 209 | 34 | 0 | 70 | 120 | 28 | 20 | 80 | 44 | 52.2 | 0 | 36 | 0 | 320 | 362 | 25 | 40 | 0 | 151 | 15 | 0 | 11 | 0 | 0 | 18 | 169 | 0 | 104 | 163 | 0 | 0 | 0 | 12 | 7230.7 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 9 | 757.31 | 0 | 0 | 0 | 46 | 0 | 54 | 25 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 178 | 0 | 175 | 0 | 414 | 0 | 0 | 0 | 164 | 60 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 141 | 1202 | 0 | 6214.31 | 13445.01 | 82.63
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 134 | 145 | 95 | 0 | 55 | 72 | 0 | 90 | 225 | 286 | 500 | 0 | 35 | 0 | 321 | 0 | 0 | 0 | 125 | 19.5 | 15 | 0 | 0 | 35 | 95 | 0 | 0 | 15 | 56 | 64 | 0 | 100 | 88 | 0 | 46 | 51 | 26 | 160 | 0 | 0 | 0 | 0 | 105 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 165 | 0 | 360 | 0 | 50 | 180 | 34 | 0 | 70 | 200 | 28 | 20 | 80 | 38 | 52.2 | 0 | 42 | 0 | 320 | 347 | 25 | 40 | 0 | 137 | 20 | 0 | 79 | 0 | 0 | 18 | 169 | 0 | 104 | 163 | 0 | 0 | 0 | 0 | 7727.7 | 852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 17 | 763.49 | 0 | 0 | 0 | 100 | 0 | 96 | 70 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 182 | 0 | 180 | 0 | 414 | 0 | 0 | 0 | 166 | 60 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 139 | 1180 | 0 | 6349.49 | 14077.19
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 20 | 120 | 130 | 45 | 0 | 55 | 72 | 0 | 96 | 225 | 295 | 500 | 0 | 35 | 0 | 320 | 0 | 0 | 0 | 125 | 19.5 | 15 | 0 | 0 | 17 | 95 | 0 | 0 | 11 | 87 | 78 | 0 | 100 | 88 | 0 | 46 | 70 | 26 | 160 | 0 | 0 | 0 | 1 | 105 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 93 | 165 | 0 | 359 | 0 | 50 | 200 | 34 | 0 | 70 | 190 | 28 | 20 | 80 | 38 | 52.2 | 0 | 48 | 0 | 320 | 384 | 25 | 40 | 0 | 141 | 23 | 0 | 82 | 0 | 0 | 18 | 168 | 0 | 104 | 163 | 0 | 0 | 0 | 0 | 7764.7 | 853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 17 | 767.2 | 0 | 0 | 0 | 110 | 0 | 96 | 35 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 182 | 0 | 179 | 0 | 414 | 0 | 0 | 0 | 162 | 59 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 131 | 1140 | 0 | 6234.2 | 13998.9 | 82.63
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 34 | 69 | 130 | 45 | 0 | 55 | 72 | 0 | 102 | 225 | 295 | 583 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 125 | 19.5 | 15 | 0 | 0 | 17 | 95 | 0 | 0 | 11 | 102 | 78 | 0 | 100 | 88 | 0 | 46 | 108 | 35 | 161 | 0 | 0 | 0 | 8 | 105 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 165 | 0 | 360 | 0 | 50 | 186 | 35 | 0 | 70 | 181 | 28 | 20 | 80 | 36 | 52.2 | 0 | 47 | 0 | 320 | 352 | 25 | 40 | 0 | 149 | 23 | 0 | 82 | 0 | 0 | 18 | 170 | 0 | 105 | 164 | 22 | 0 | 0 | 0 | 7926.7 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 755.85 | 0 | 0 | 0 | 113 | 0 | 96 | 35 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 184 | 0 | 180 | 0 | 414 | 0 | 0 | 0 | 172 | 59 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 163 | 1120 | 0 | 6221.85 | 14148.55 | 82.62
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 17 | 36 | 69 | 130 | 45 | 0 | 55 | 54 | 0 | 102 | 225 | 296 | 583 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 125 | 19 | 15 | 0 | 0 | 17 | 120 | 0 | 0 | 4 | 102 | 78 | 0 | 100 | 76 | 0 | 46 | 105 | 30 | 160 | 0 | 0 | 0 | 8 | 105 | 121 | 0 | 0 | 0 | 1224 | 0 | 51 | 138 | 165 | 0 | 360 | 0 | 51 | 200 | 35 | 0 | 70 | 182 | 29 | 20 | 80 | 42 | 52.2 | 0 | 47 | 0 | 320 | 380 | 25 | 40 | 0 | 157 | 23 | 0 | 82 | 0 | 0 | 18 | 170 | 0 | 105 | 167 | 22 | 0 | 0 | 0 | 7942.2 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 955 | 0 | 754.32 | 0 | 0 | 0 | 113 | 0 | 96 | 35 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 185 | 0 | 179 | 0 | 414 | 0 | 0 | 0 | 172 | 59 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 156 | 1120 | 0 | 6177.32 | 14119.52 | 82.62
23:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 17 | 36 | 69 | 130 | 45 | 0 | 35 | 35 | 0 | 102 | 225 | 305 | 583 | 0 | 55 | 0 | 326 | 0 | 0 | 0 | 125 | 19 | 15 | 0 | 0 | 17 | 135 | 0 | 0 | 9 | 102 | 71 | 0 | 48 | 76 | 0 | 46 | 105 | 30 | 160 | 0 | 0 | 0 | 8 | 105 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 138 | 167 | 0 | 358 | 0 | 52 | 196 | 35 | 0 | 70 | 182 | 28 | 20 | 80 | 38 | 52.2 | 0 | 47 | 0 | 320 | 382 | 25 | 39 | 0 | 154 | 15 | 0 | 82 | 0 | 0 | 18 | 171 | 0 | 105 | 168 | 22 | 0 | 0 | 0 | 7895.2 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 952 | 0 | 754.55 | 0 | 0 | 0 | 113 | 0 | 96 | 35 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 184 | 0 | 179 | 0 | 414 | 0 | 0 | 0 | 174 | 60 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 156 | 1110 | 0 | 6166.55 | 14061.75 | 82.61
Total KWH | 0 | 578880 | 284640 | 0 | 0 | 0 | 0 | 0 | 9550800 | 0 | 0 | 293400 | 481680 | 1545984 | 1098720 | 339229 | 0 | 595315 | 995040 | 0 | 759360 | 6138500 | 7077644 | 11411818 | 0 | 401947 | 0 | 7679076 | 0 | 0 | 218037 | 1410000 | 404400 | 356040 | 0 | 0 | 110400 | 536945 | 0 | 0 | 179040 | 475711 | 531216 | 0 | 1100160 | 581760 | 15160 | 1075320 | 593815 | 506880 | 3730909.09 | 0 | 0 | 0 | 33046.2 | 947599 | 3502407 | 0 | 0 | 0 | 25745452 | 57915 | 1132192 | 1169236 | 3847273 | 0 | 8474500 | 0 | 1198560 | 4781000 | 814752 | 0 | 1285330 | 3170880 | 418320 | 474640 | 1412460 | 881280 | 932582 | 385145 | 462928 | 0 | 7672600 | 9194000 | 597000 | 924960 | 0 | 3519000 | 307752 | 0 | 1823040 | 0 | 0 | 432000 | 4533780 | 0 | 1614000 | 2654400 | 70080 | 14450 | 317160 | 231840 | 156091385.29 | 21895272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 702000 | 21214540 | 40320 | 14577091 | 0 | 0 | 0 | 735456 | 0 | 491296 | 240192 | 0 | 0 | 765521 | 0 | 420744 | 4551909 | 0 | 4111764 | 0 | 3749800 | 0 | 8868800 | 0 | 33540 | 0 | 4090000 | 1364949 | 533378 | 247750 | 1099094 | 11500 | 0 | 54747 | 1261440 | 4192 | 0 | 5869000 | 206407 | 2740000 | 5320940 | 0 | 2105455 | 22981818.18 | 0 | 130288915.18 | 286380300.47

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 11-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12102 | MW | 12:00 Hr. | Energy Generated |  |  | 286.3803 |  | MKWHr.
| Day Peak Demand |  |  | 12102 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.453 |  | MKWHr.
| Evening Peak Generation |  |  | 14148.55 | MW | 21:00 Hr. | Energy Demand |  |  | 286.8333 |  | MKWHr.
| Evening Peak Demand |  |  | 14148.55 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 9815 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 931.77 |  | MMCFD
| Maximum Generation of the Day |  |  | 14148.55 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.1805 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.6183 | 0 | 8.7842 | 0 | 0 | 0.21804 | 0 | 0 | 51.6205 | Gas | 127.2596 | Gas | 404328275.61
| Chattogram Zone |  |  | 4.0093 | 29.4764 | 4.9107 | 0 | 1.0753 | 0.073075 | 0 | 0.17904 | 39.7237 | Coal | 87.1021 | Coal | 617444619.8856
| Cumilla Zone |  |  | 22.0082 | 0 | 7.5664 | 0 | 0 | 0.38515 | 0.88128 | 0 | 30.8411 | HFO | 28.9012 | HFO | 510286168.444
| Mymensingh Zone |  |  | 0.07008 | 0 | 4.5002 | 0 | 0 | 0.33161 | 0 | 0 | 4.9019 | HSD | 0.0115 | HSD | 638135
| Sylhet Zone |  |  | 29.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.0041 | Hydro | 1.0753 | Hydro | 107532
| Khulna Zone |  |  | 0 | 21.2145 | 0.04032 | 0 | 0 | 0.702 | 21.8953 | 0 | 43.8521 | Solar | 4.4978 | Solar | 73499181.94
| Barishal Zone |  |  | 8.2673 | 30.9563 | 0 | 0 | 0 | 0.004192 | 0 | 0 | 39.2278 | Import | 37.3536 | Import | 161054499.48
| Rajshahi Zone |  |  | 21.2823 | 0 | 1.4669 | 0 | 0 | 1.2198 | 14.5771 | 0 | 38.5461 | Wind | 0.17904 | Wind | 2621145.6
| Rangpur Zone |  |  | 0 | 5.4549 | 1.6325 | 0.0115 | 0 | 1.5639 | 0 | 0 | 8.6629
| Total |  |  | 127.2596 | 87.1021 | 28.9012 | 0.0115 | 1.0753 | 4.4978 | 37.3536 | 0.17904 | 286.3803
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 404328275.61 |  | Hydro | 107532
|  |  |  | Coal | 617444619.8856 |  | Solar | 73499181.94
|  |  |  | HFO | 510286168.444 |  | Import | 161054499.48
|  |  |  | HSD | 638135 |  | Wind | 2621145.6
[5 empty] | Total: | 176,99,79,557 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8953 | Peak Hr Flow | 899.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 10611654.62 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 14.5771 | Peak Hr Flow | 755.85 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 448 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.88128 | Peak Hr Flow | 36.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 898 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 37.3536 | Peak Hr Flow | 1690.85 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4636
|  |  |  | Chattogram |  | 0 |  | 1444
|  |  |  | Cumilla |  | 0 |  | 1406
|  |  |  | Mymensingh |  | 0 |  | 1231
|  |  |  | Sylhet |  | 0 |  | 508
|  |  |  | Khulna |  | 0 |  | 1672
|  |  |  | Barishal |  | 0 |  | 440
|  |  |  | Rajshahi |  | 0 |  | 1451
|  |  |  | Rangpur |  | 0 |  | 845
|  |  |  | Total |  | 0 |  | 13633
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:04 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
|  | 08:33 | Coxsbazar 132/33kV S/S T3 HT is restored.
|  | 08:50 | Jashore 132/33kV S/S T-1 HT is restored.
|  | 08:51 | Jashore 132/33kV S/S T-1 LT is restored.
| 09:05 | 15:03 | Barapukuria-Rangpur 132 kV Ckt-1 Project Work S/D from Barapukuria 230/132/33kV end. and
from Rangpur 132/33kV end Due to TEMPARATURE HIGH
| 09:05 | 15:13 | Rangpur 132/33kV S/S 132KV Bus A Forced S/D Due to TEMPARATURE HIGH
|  | 09:10 | Sherpur 132/33kV S/S Transformer- 01 HT is restored.
|  | 09:10 | Sherpur 132/33kV S/S Transformer- 01 LT is restored.
|  | 09:23 | Kushtia 132/33kV S/S T-1 HT is restored.
|  | 09:24 | Kushtia 132/33kV S/S T-1 LT is restored.
| 09:26 | 17:20 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Fire Wall Construction Work.
| 09:26 | 17:20 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Fire Wall Construction Work.
|  | 10:00 | Narail 132/33kV S/S TR2 (413-T) HT is restored.
|  | 10:00 | Narail 132/33kV S/S TR2 (413-T) LT is restored.
|  | 10:32 | Bogura 132/33kV S/S 132KV Bus-B is restored.
| 10:35 |  | Ishwardi-Natore 132kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end Due to
Reconductoring Work and from Natore 132/33kV end Due to Reconductoring work.
| 10:41 | 10:48 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Ins.O/C, Lookout. relays Due to 33 kV | [7 empty] | 29.0MW load
|  |  | Nolcity feeder fault. | [7 empty] | interrup.
|  | 11:28 | Bogura 230/132kV S/S T-03 HT is restored.
|  | 11:29 | Bogura 230/132kV S/S T-03 LT is restored.
| 12:00 |  | Day peak generation 12094 MW
| 12:33 | 12:56 | Sherpur 132/33kV S/S Transformer- 01 LT Tripped showing O/C & E/F. relays Due to SPBS - | [7 empty] | 70.0MW load
|  |  | Bay -03 , 33 Kv feeder Cross arm Brocken. | [7 empty] | interrup.
| 12:33 | 12:55 | Sherpur 132/33kV S/S Transformer- 02 LT Tripped showing O/C & E/F. relays Due to SPBS - | [7 empty] | 70.0MW load
|  |  | Bay -03 , 33 Kv feeder Cross arm Brocken. | [7 empty] | interrup.
| 12:59 | 13:39 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Narshingdi 132/33kV end showing N/A relays | [7 empty] | 55.0MW load
|  |  | Due to Trip from Bhulta side | [7 empty] | interrup.
Narshingdi 132/33kV
end
|  | 15:29 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 is restored.
| 15:55 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Tripped showing Main-01, Main-02
relays Due to Directional Earth Fault IDMT
| 16:07 |  | Cumilla(S) 132/33kV S/S TR-2 HT Scheduled S/D Due to Energypac commissioning work.
|  | 16:08 | Kodda(300MW)-Tongi 230kV Ckt-1 is restored.
| 16:50 | 17:58 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Forced S/D Due to 33kv bus shutdown for | [7 empty] | 6.0MW load
|  |  | Bashkhali Feeder Isolator Problem. | [7 empty] | interrup.
| 16:53 | 17:57 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Forced S/D Due to 33kv bus shutdown for | [7 empty] | 6.0MW load
|  |  | Bashkhali Feeder Isolator Problem. | [7 empty] | interrup.
| 18:22 | 18:52 | Ashuganj-Shahjibazar 132kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing Distance
Relay(Zone-1, Phase-B, Dis-14 km, R-.12) relays Due to Bad weather
| 21:00 |  | Evening Peak Generation: 14147 MW.
| 21:06 |  | Raojan Unit-2 was sync.
| 00:42 |  | Ashuganj CCPP 225 MW ST was tripped.
| 00:42 |  | Ashuganj CCPP 225 MW Tripped with remarks:- ST
| 00:44 |  | Adani Power Jharkhand Ltd. Unit-2 was shutdown due to air pre-heater leakage.
| 05:33 | 05:50 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Distance Relay
relays Due to Showing Z1
| 06:00 |  | Min. Gen. 11364 MW
| 06:28 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT Scheduled S/D Due to Maintenance for | [7 empty] | 50.0MW load
|  |  | temperature rising on B-ph bushing | [7 empty] | interrup.
| 06:29 |  | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT Scheduled S/D Due to Maintenance for | [7 empty] | 50.0MW load
|  |  | temperature rising on B-ph bushing | [7 empty] | interrup.
| 07:21 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Red Hot Repair | [7 empty] | 21.0MW load
interrup.
| 07:21 |  | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Red hot Repair | [7 empty] | 21.0MW load
interrup.
| 07:22 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Red Hot Repair | [7 empty] | 21.0MW load
interrup.
| 07:22 |  | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Red Hot Repair | [7 empty] | 21.0MW load
interrup.
| 07:25 |  | Sholosohor 132/33kV S/S TRAFO-02 LT Scheduled S/D Due to for bird nest removing and to
prevent further nesting.
| 07:25 |  | Sholosohor 132/33kV S/S TRAFO-02 HT Scheduled S/D Due to for bird nest removing and to
prevent further nesting.
| 07:25 |  | Sholosohor 132/33kV S/S TRAFO-01 LT Scheduled S/D Due to for bird nest removing and to
prevent further nesting.
| 07:25 |  | Sholosohor 132/33kV S/S TRAFO-01 HT Scheduled S/D Due to for bird nest removing and to
prevent further nesting.
| 07:39 |  | Jashore-Noapara 132kV Ckt-2 Scheduled S/D from Jashore 132/33kV end Due to Shutdown For
Noapara End and from Noapara 132/33kV end Due to High temperature maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 11-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 402 | 9550800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 6138500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 295 | 7077644 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7679076 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 293400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 130 | 1098720 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 595315 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 401947 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 19.5 | 404400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 356040 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 284640 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 45 | 339229 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 69 | 1545984 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 578880 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 102 | 759360 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 995040 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 218037 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 481680 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 11411818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1410000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2633.5 | 51620510
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 33046.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 57915 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1075320 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3502407 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 947599 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 531216 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 475711 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1100160 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 35 | 506880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 15160 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 95 | 536945 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 108 | 593815 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 581760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 110400 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25745452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 11 | 179040 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 161 | 3730909.09 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2327 | 39723735.29
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 186 | 4781000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8474500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 814752 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1198560 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 165 | 3847273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1132192 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 135 | 1169236 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 47 | 462928 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1285330 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 3170880 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 36 | 881280 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 932582 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 474640 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1412460 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 418320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 385145 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1496.2 | 30841078
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 22 | 70080 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2654400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1614000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 317160 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 231840 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 291 | 4901930
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 25 | 597000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 924960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3519000 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1823040 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 170 | 4533780 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 307752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 352 | 9194000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7672600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1179 | 29004132
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 899 | 21895272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 40320 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 702000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1005 | 21214540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1904 | 43852132
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 163 | 2105455 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 206407 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2740000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 22981818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5320940 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5869000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4192 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1930 | 39227812.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 196 | 4551909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 184 | 4111764 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 180 | 3749800 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8868800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 491296 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 735456 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 240192 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 755.85 | 14577091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 420744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 765521 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1973.85 | 38546113
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 59 | 1364949 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 172 | 4090000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 11500 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1099094 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 54747 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 533378 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 247750 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1261440 | -
Rangpur Area Total |  |  |  |  | 950 | 414 | 8662858
Eastern Grid Total |  |  |  |  | 16921.242 | 7926.7 | 156091385.29
Western Grid Total |  |  |  |  | 11614.5 | 6221.85 | 130288915.18
National Grid Total |  |  |  |  | 28535.742 | 14148.55 | 286380300.47
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 11-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9225.7 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4407.1 | MW
i) Dhaka area |  |  | 4636.5 |  | MW | i) Khulna area |  |  |  | 1671.5 | MW
ii) Chattogram area |  |  | 1444.2 |  | MW | ii) Barishal area |  |  |  | 440 | MW
iii) Cumilla area |  |  | 1406 |  | MW | iii) Rajshahi area |  |  |  | 1450.6 | MW
iv) Mymensingh area |  |  | 1231 |  | MW | iv) Rangpur area |  |  |  | 845 | MW
v) Sylhet area |  |  | 508 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13632.8 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 66 | 13:00 | 133 | Patuakhali | 74.5 | 00:00
2 | AKSML | 121 | 06:00 | 68 | Jaldhaka | 66 | 19:00 | 134 | Payra | 30 | 00:00
3 | Aftabnagar | 34 | 19:00 | 69 | Jamalpur | 136 | 19:30 | 135 | Postogola | 45 | 00:00
4 | Agargaon | 98 | 23:00 | 70 | Jashore | 134 | 21:00 | 136 | Purbachal | 18 | 13:00
5 | Agrabad | 82 | 19:30 | 71 | Jhenaidah | 131 | 19:00 | 137 | Purbasadipur | 121 | 19:00
6 | Amnura | 42 | 21:00 | 72 | Joydebpur | 113 | 00:00 | 138 | Rahanpur | 27 | 22:00
7 | Ashuganj | 89 | 22:00 | 73 | Joypurhat | 68 | 22:00 | 139 | Rahim | 34 | 01:00
8 | BSRM | 194 | 00:00 | 74 | Juldah | 19 | 11:00 | 140 | Rajbari | 76 | 19:00
9 | Bagerhat | 86 | 19:30 | 75 | KSRM | 10 | 06:00 | 141 | Rajendrapur | 110 | 19:30
10 | Bajitpur | 47 | 18:30 | 76 | Kabirpur | 221 | 19:00 | 142 | Rajshahi | 102 | 22:00
11 | Bakulia | 100 | 03:00 | 77 | Kachua | 86 | 23:00 | 143 | Rajshahi-230 | 77 | 23:00
12 | Banani | 30 | 14:00 | 78 | Kallyanpur | 99 | 13:00 | 144 | Ramganj | 112 | 19:00
13 | Bangabhaban | 4 | 12:00 | 79 | Kalurghat | 32 | 00:00 | 145 | Rampur | 41 | 23:00
14 | Barapukuria | 63 | 19:00 | 80 | Kamrangirchar | 54.9 | 00:00 | 146 | Rangamati | 16 | 19:30
15 | Barguna | 20 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 145 | 19:30
16 | Barishal | 106 | 00:00 | 82 | Kasba | 40 | 22:00 | 148 | Ruppur | 6 | 11:00
17 | Barishal-230 | 92 | 20:00 | 83 | Kazla | 96 | 00:00 | 149 | SSM | 11 | 08:00
18 | Baroaulia | 57 | 20:00 | 84 | Keranigonj | 64 | 23:00 | 150 | Saidpur | 99 | 19:30
19 | Baroirhat | 58 | 21:00 | 85 | Khagrachori | 32 | 18:30 | 151 | Satkhira | 123 | 23:00
20 | Bashundhara | 167 | 19:00 | 86 | Khulna | 73 | 20:00 | 152 | Satmasjid | 92 | 20:00
21 | BashundharaCement | 13 | 09:00 | 87 | Khulshi | 166 | 21:00 | 153 | Savar | 163 | 22:00
22 | Beanibazar | 68 | 18:30 | 88 | Kishoreganj | 124 | 13:00 | 154 | SevenRings | 9.39 | 17:00
23 | Benapole | 66 | 19:30 | 89 | Kodda | 263 | 11:00 | 155 | ShahCement | 36 | 00:00
24 | Bhaluka | 145 | 19:00 | 90 | Kulaura | 46 | 18:30 | 156 | Shahjadpur | 83 | 22:00
25 | Bhandaria | 51 | 00:00 | 91 | Kurigram | 58 | 18:00 | 157 | Shahjibazar | 110 | 00:00
26 | Bhangura | 39 | 19:30 | 92 | Kushtia | 134 | 19:00 | 158 | Shahmirpur | 55 | 00:00
27 | Bheramara(GK) | 57 | 19:00 | 93 | Lalbag | 52 | 00:00 | 159 | Shariatpur | 88 | 22:00
28 | Bhulta | 223 | 23:00 | 94 | Lalmonirhat | 56 | 19:30 | 160 | Sherpur | 164 | 21:00
29 | Bog-Sherpur | 68 | 19:00 | 95 | MI_Cement | 17.5 | 07:00 | 161 | Shikalbaha | 28 | 00:00
30 | Bogura | 151 | 19:00 | 96 | Madanganj | 42 | 21:00 | 162 | Shitalakhya | 59.8 | 00:00
31 | Borhanuddin | 92 | 00:00 | 97 | Madaripur | 115 | 22:00 | 163 | Sholosohor | 37 | 00:00
32 | Brahmanbaria | 130 | 00:00 | 98 | Madartek | 81.08 | 23:00 | 164 | Shyampur | 136 | 12:00
33 | Cantonment | 104 | 13:00 | 99 | Madunaghat | 49 | 19:30 | 165 | Siddhirganj | 106 | 00:00
34 | Chandina | 0 | 18:30 | 100 | Magura | 64 | 19:30 | 166 | Sirajganj | 106 | 19:00
35 | Chandpur | 73 | 19:30 | 101 | Mahasthangarh | 74 | 20:00 | 167 | Sonargaon | 82 | 01:00
36 | Chandraghona | 36 | 19:00 | 102 | Manikganj | 121 | 21:00 | 168 | Sreemongol | 63 | 21:00
37 | Chapai | 66 | 21:00 | 103 | Maniknagar | 60 | 13:00 | 169 | Sreepur | 98 | 21:00
38 | Charsaidpur | 40 | 19:30 | 104 | Matarbari | 47 | 19:30 | 170 | Srinagar | 48 | 21:00
39 | Chauddagram | 74 | 19:00 | 105 | Matuail | 56 | 00:00 | 171 | Sunamganj | 51 | 19:00
40 | Chhatak | 33 | 19:30 | 106 | Millgate | 71 | 12:00 | 172 | Sylhet | 40 | 22:00
41 | Chowmuhani | 229 | 21:00 | 107 | Mirpur | 118 | 13:00 | 173 | Sylhet-132 | 106 | 18:30
42 | Chuadanga | 102 | 21:00 | 108 | Mirsorai | 9 | 19:30 | 174 | TK | 33 | 00:00
43 | Coxsbazar | 131 | 20:00 | 109 | Mirzapur | 51 | 08:00 | 175 | Tangail | 190 | 21:00
44 | Cumilla(N) | 188 | 22:00 | 110 | Mithapukur | 66 | 19:00 | 176 | Thakurgaon | 88 | 19:30
45 | Cumilla(S) | 148 | 01:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 130 | 12:00
46 | Daudkandi | 148 | 23:00 | 112 | Mogbazar | 111.1 | 19:00 | 178 | Ullahpara | 46 | 19:30
47 | Dhaka | 24 | 12:00 | 113 | Mongla | 45 | 00:00 | 179 | Ullon | 44 | 23:00
48 | Dhamrai | 130 | 21:00 | 114 | Motijheel | 31 | 20:00 | 180 | Uttara | 86 | 19:00
49 | Dhanmondi | 115 | 18:30 | 115 | Muktagacha | 39 | 19:00 | 181 | UttaraNew | 44 | 23:00
50 | Dohazari | 95 | 19:30 | 116 | Munshiganj | 107 | 23:00 | 182 | Zigatola | 64 | 22:00
51 | Faridpur | 156 | 22:00 | 117 | Muradnagar | 30 | 18:30
52 | Fatullah | 80 | 00:00 | 118 | Mymensingh | 202 | 13:00
53 | Fenchuganj | 34 | 23:00 | 119 | Naogaon | 122 | 20:00
54 | Feni | 112 | 00:00 | 120 | Narail | 62 | 21:00
55 | GPH | 96 | 13:00 | 121 | Narinda | 51 | 13:00
56 | Ghatail | 92 | 20:00 | 122 | Narshingdi | 170 | 21:00
57 | Ghorashal | 12 | 00:00 | 123 | Natore | 140 | 19:30
58 | Ghorashal-230 | 73 | 19:30 | 124 | Nawabganj | 60.4 | 22:00
59 | Goalpara | 28 | 23:00 | 125 | Netrakona | 138 | 19:30
60 | Gollamari | 78 | 13:00 | 126 | New | 64.3 | 00:00
61 | Gopalganj | 111 | 20:00 | 127 | Niamatpur | 102 | 22:00
62 | Gulshan | 86 | 18:30 | 128 | Noapara | 40 | 19:30
63 | Halishahar | 68 | 13:00 | 129 | PHP | 9 | 03:00
64 | HaripurSBU | 145 | 00:00 | 130 | Pabna | 107 | 20:00
65 | Hasnabad | 77 | 23:00 | 131 | Palashbari | 124 | 19:00
66 | Hathazari | 85 | 20:00 | 132 | Panchagarh | 45 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 11-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11156 | 40 |  | 11197.8
1:00 | 11001 | 40 |  | 11042.8
2:00 | 10864 | 40 |  | 10905.8
3:00 | 10798 | 40 |  | 10839.8
4:00 | 10602 | 40 |  | 10643.8
5:00 | 10341 | 40 |  | 10382.8
6:00 | 9886 | 30 |  | 9917.35
7:00 | 9815 | 35 |  | 9851.58
8:00 | 10013 | 30 |  | 10044.35
9:00 | 10393 | 33 |  | 10427.49
10:00 | 10728 | 0 |  | 10728
11:00 | 11207 | 0 |  | 11207
12:00 | 12102 | 0 |  | 12102
13:00 | 12711.83 | 0 |  | 12711.83
14:00 | 12236.39 | 0 |  | 12236.39
15:00 | 12425.47 | 0 |  | 12425.47
16:00 | 11979.01 | 0 |  | 11979.01
17:00 | 11709.48 | 0 |  | 11709.48
18:00 | 11575.23 | 0 |  | 11575.23
19:00 | 13445.01 | 45 |  | 13492.01
19:30 | 14077.19 | 45 |  | 14124.19
20:00 | 13998.9 | 40 |  | 14040.9
21:00 | 14148.55 | 0 |  | 14148.55
22:00 | 14119.52 | 0 |  | 14119.52
23:00 | 14061.75 | 0 |  | 14061.75
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 11-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6497 | 4659 | 11156 | DAILY GENERATION CURVE
00:30 | 6423.5 | 4655 | 11078.5
01:00 | 6350 | 4651 | 11001 | 11-04-2025
01:30 | 6270 | 4662.5 | 10932.5
02:00 | 6190 | 4674 | 10864
02:30 | 6148 | 4683 | 10831
03:00 | 6106 | 4692 | 10798
03:30 | 6020.5 | 4679.5 | 10700
04:00 | 5935 | 4667 | 10602
04:30 | 5884.5 | 4587 | 10471.5
05:00 | 5834 | 4507 | 10341
05:30 | 5627.5 | 4486 | 10113.5
06:00 | 5421 | 4465 | 9886
06:30 | 5355 | 4495.5 | 9850.5
07:00 | 5289 | 4526 | 9815
07:30 | 5360.5 | 4553.5 | 9914
08:00 | 5432 | 4581 | 10013
08:30 | 5461 | 4742 | 10203
09:00 | 5490 | 4903 | 10393
09:30 | 5504.5 | 5056 | 10560.5
10:00 | 5519 | 5209 | 10728
10:30 | 5656 | 5311.5 | 10967.5
11:00 | 5793 | 5414 | 11207
11:30 | 6059 | 5595.5 | 11654.5
12:00 | 6325 | 5777 | 12102
12:30 | 6505.16 | 5901.755 | 12406.915
13:00 | 6685.32 | 6026.51 | 12711.83
13:30 | 6694.41 | 5779.7 | 12474.11
14:00 | 6703.5 | 5532.89 | 12236.39
14:30 | 6697.845 | 5633.085 | 12330.93
15:00 | 6692.19 | 5733.28 | 12425.47
15:30 | 6550.315 | 5651.925 | 12202.24
16:00 | 6408.44 | 5570.57 | 11979.01
16:30 | 6357.225 | 5487.02 | 11844.245
17:00 | 6306.01 | 5403.47 | 11709.48
17:30 | 6245.115 | 5397.24 | 11642.355
18:00 | 6184.22 | 5391.01 | 11575.23
18:30 | 6707.46 | 5802.66 | 12510.12
19:00 | 7230.7 | 6214.31 | 13445.01
19:30 | 7727.7 | 6349.49 | 14077.19
20:00 | 7764.7 | 6234.2 | 13998.9
20:30 | 7845.7 | 6228.025 | 14073.725 |  | Executive Engineer
21:00 | 7926.7 | 6221.85 | 14148.55 |  | Network Operation Division
21:30 | 7934.45 | 6199.585 | 14134.035
22:00 | 7942.2 | 6177.32 | 14119.52
22:30 | 7918.7 | 6171.935 | 14090.635
23:00 | 7895.2 | 6166.55 | 14061.75

## En-Curve
QF-LDC-12
Date | 11-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3136 | 1800 | 907 | 0 | 44 | 516 | 46 | 3486 | 0 | 303 | 911 | 0 | 0 | 7 | 40 | DAILY ENERGY CURVE
00:30 | 3184 | 1833 | 912 | 0 | 44 | 510 | 46 | 3468.5 | 0 | 255.5 | 820.5 | 0 | 0 | 5 | 40 | 11-04-2025
01:00 | 3232 | 1866 | 917 | 0 | 44 | 504 | 46 | 3451 | 0 | 208 | 730 | 0 | 0 | 3 | 40
01:30 | 3231 | 1864 | 917.5 | 0 | 40 | 512.5 | 46 | 3437 | 0 | 174 | 707.5 | 0 | 0 | 3 | 40 | Energy Generated | 286.3803 |  | MKWHr
02:00 | 3230 | 1862 | 918 | 0 | 36 | 521 | 46 | 3423 | 0 | 140 | 685 | 0 | 0 | 3 | 40 | Energy not Served | 0.453 |  | MKWHr
02:30 | 3283.5 | 1880 | 912.5 | 0 | 38 | 492 | 46 | 3384.5 | 0 | 122.5 | 670 | 0 | 0 | 2 | 40 | Total Energy Requirement | 286.8333 |  | MKWHr
03:00 | 3337 | 1898 | 907 | 0 | 40 | 463 | 46 | 3346 | 0 | 105 | 655 | 0 | 0 | 1 | 40
03:30 | 3343 | 1839.5 | 907 | 0 | 39 | 464 | 46 | 3325.5 | 0 | 91 | 640.5 | 0 | 0 | 4.5 | 40
04:00 | 3349 | 1781 | 907 | 0 | 38 | 465 | 46 | 3305 | 0 | 77 | 626 | 0 | 0 | 8 | 40
04:30 | 3331.5 | 1828 | 907 | 0 | 39 | 443 | 46 | 3232.5 | 0 | 62.5 | 575.5 | 0 | 0 | 6.5 | 40
05:00 | 3314 | 1875 | 907 | 0 | 40 | 421 | 46 | 3160 | 0 | 48 | 525 | 0 | 0 | 5 | 40
05:30 | 3233.5 | 1821 | 907.5 | 0 | 35 | 424 | 46 | 3142.5 | 5 | 36 | 460.5 | 0 | 0 | 2.5 | 35
06:00 | 3153 | 1767 | 908 | 0 | 30 | 427 | 46 | 3125 | 10 | 24 | 396 | 0 | 0 | 0 | 30
06:30 | 3171 | 1727 | 907.5 | 0 | 33 | 426 | 46 | 3115.5 | 51 | 28 | 345.5 | 0 | 0 | 0 | 32.5
07:00 | 3189 | 1687 | 907 | 0 | 36 | 425 | 46 | 3106 | 92 | 32 | 295 | 0 | 0 | 0 | 35
07:30 | 3230 | 1695.5 | 882.5 | 0 | 36 | 440 | 46 | 3102 | 147 | 36.5 | 297.5 | 0 | 0 | 1 | 32.5
08:00 | 3271 | 1704 | 858 | 0 | 36 | 455 | 46 | 3098 | 202 | 41 | 300 | 0 | 0 | 2 | 30
08:30 | 3279 | 1710.5 | 857.5 | 0 | 36 | 459 | 46 | 3143.5 | 334.5 | 45.5 | 289 | 0 | 0 | 2.5 | 31.5
09:00 | 3287 | 1717 | 857 | 0 | 36 | 463 | 46 | 3189 | 467 | 50 | 278 | 0 | 0 | 3 | 33
09:30 | 3321 | 1716.5 | 881.5 | 0 | 34 | 466 | 46 | 3190.5 | 530 | 67.5 | 290 | 0 | 0 | 17.5 | 16.5
10:00 | 3355 | 1716 | 906 | 0 | 32 | 469 | 46 | 3192 | 593 | 85 | 302 | 0 | 0 | 32 | 0
10:30 | 3435.5 | 1772.5 | 906 | 0 | 33 | 471 | 46 | 3296.5 | 598 | 85 | 301.5 | 0 | 0 | 22.5 | 0
11:00 | 3516 | 1829 | 906 | 0 | 34 | 473 | 46 | 3401 | 603 | 85 | 301 | 0 | 0 | 13 | 0
11:30 | 3534 | 1862 | 906 | 0 | 36 | 518 | 46 | 3548 | 626.5 | 112 | 452.5 | 0 | 0 | 13.5 | 0
12:00 | 3552 | 1895 | 906 | 0 | 38 | 563 | 46 | 3695 | 650 | 139 | 604 | 0 | 0 | 14 | 0
12:30 | 3515 | 1896.25 | 906 | 0 | 40 | 659.7 | 46 | 3790 | 619.965 | 147 | 774 | 0 | 0 | 13 | 0
13:00 | 3478 | 1897.5 | 906 | 0 | 42 | 756.4 | 46 | 3885 | 589.93 | 155 | 944 | 0 | 0 | 12 | 0
13:30 | 3388 | 1821 | 906 | 0 | 41 | 763.685 | 46 | 3710.5 | 523.325 | 167.5 | 1094.6 | 0 | 0 | 12.5 | 0
14:00 | 3298 | 1744.5 | 906 | 0 | 40 | 770.97 | 46 | 3536 | 456.72 | 180 | 1245.2 | 0 | 0 | 13 | 0
14:30 | 3364 | 1784.5 | 905.5 | 0 | 40 | 761.915 | 44 | 3603 | 420.815 | 171.5 | 1229.2 | 0 | 0 | 6.5 | 0
15:00 | 3430 | 1824.5 | 905 | 0 | 40 | 752.86 | 42 | 3670 | 384.91 | 163 | 1213.2 | 0 | 0 | 0 | 0
15:30 | 3452.5 | 1820.25 | 905.5 | 0 | 37 | 753.705 | 42.5 | 3675 | 329.585 | 140 | 1046.2 | 0 | 0 | 0 | 0
16:00 | 3475 | 1816 | 906 | 0 | 34 | 754.55 | 43 | 3680 | 274.26 | 117 | 879.2 | 0 | 0 | 0 | 0
16:30 | 3477 | 1837.75 | 906 | 0 | 36 | 754.285 | 43.5 | 3638 | 190.51 | 119.5 | 841.7 | 0 | 0 | 0 | 0
17:00 | 3479 | 1859.5 | 906 | 0 | 38 | 754.02 | 44 | 3596 | 106.76 | 122 | 804.2 | 0 | 0 | 0 | 0
17:30 | 3385 | 1795.5 | 906 | 0 | 35 | 753.265 | 45 | 3693 | 60.89 | 129 | 837.7 | 0 | 0 | 2 | 0
18:00 | 3291 | 1731.5 | 906 | 0 | 32 | 752.51 | 46 | 3790 | 15.02 | 136 | 871.2 | 0 | 0 | 4 | 0
18:30 | 3418.5 | 1797 | 892.5 | 0 | 38 | 754.91 | 46 | 4054 | 7.51 | 304.5 | 1191.2 | 0 | 0 | 6 | 22.5
19:00 | 3546 | 1862.5 | 879 | 0 | 44 | 757.31 | 46 | 4318 | 0 | 473 | 1511.2 | 0 | 0 | 8 | 45
19:30 | 3516 | 1823.5 | 852 | 0 | 38 | 763.49 | 46 | 4296 | 0 | 596 | 2131.2 | 0 | 0 | 15 | 45
20:00 | 3580 | 1842.5 | 853 | 0 | 38 | 767.2 | 46 | 4238 | 0 | 632 | 1991.2 | 0 | 0 | 11 | 40
20:30 | 3567.5 | 1892.5 | 876 | 0 | 37 | 761.525 | 46 | 4224.5 | 0 | 639 | 2018.7 | 0 | 0 | 11 | 20
21:00 | 3555 | 1942.5 | 899 | 0 | 36 | 755.85 | 46 | 4211 | 0 | 646 | 2046.2 | 0 | 0 | 11 | 0
21:30 | 3566 | 1944.75 | 899 | 0 | 39 | 755.085 | 46 | 4182 | 0 | 646 | 2048.7 | 0 | 0 | 7.5 | 0
22:00 | 3577 | 1947 | 899 | 0 | 42 | 754.32 | 46 | 4153 | 0 | 646 | 2051.2 | 0 | 0 | 4 | 0
22:30 | 3593.5 | 1947.5 | 899 | 0 | 40 | 754.435 | 46 | 4148 | 0 | 642.5 | 2013.2 | 0 | 0 | 6.5 | 0
23:00 | 3610 | 1948 | 899 | 0 | 38 | 754.55 | 46 | 4143 | 0 | 639 | 1975.2 | 0 | 0 | 9 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 11-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 398 | 06:00 | 379 | 18:00 | Payra | 418 | 00:00 | 411 | 18:30
Ashuganj | 404 | 13:00 | 382 | 12:00 | Rahanpur | 410 | 00:00 | 389 | 08:00
Bhulta | 400 | 04:00 | 387 | 12:00 | Rampal | 409 | 06:00 | 391 | 19:00
Bibiana | 389 | 13:00 | 380 | 23:00
BIPTC | 402 | 01:00 | 392 | 15:00
Bogura | 398 | 00:00 | 379 | 13:00
Gopalganj | 407 | 06:00 | 391 | 19:00
Kaliakoir | 368 | 05:00 | 356 | 11:00
Madunaghat | 404 | 08:00 | 394 | 00:00
Meghnaghat | 400 | 07:00 | 388 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 08:00 | 225 | 11:00 | Keranigonj | 231 | 07:00 | 223 | 11:00
AKSML | 235 | 08:00 | 228 | 00:00 | Khulna(S) | 236 | 00:00 | 216 | 19:00
Aminbazar | 232 | 09:00 | 224 | 06:00 | Madunaghat | 239 | 19:30 | 230 | 00:00
Ashuganj | 233 | 05:00 | 222 | 23:00 | Madunaghat-400 | 239 | 08:00 | 231 | 00:00
Ashuganj-400 | 233 | 05:00 | 222 | 23:00 | Maniknagar | 228 | 03:00 | 221 | 11:00
Baghabari | 237 | 02:00 | 227 | 19:00 | Meghnaghat | 237 | 07:00 | 231 | 00:00
Barapukuria | 226 | 00:00 | 220 | 18:00 | Meghnaghat-400 | 232 | 07:00 | 223 | 12:00
Barapukuria-230 | 226 | 00:00 | 220 | 18:00 | Mirsorai | 232 | 08:00 | 222 | 00:00
Barishal | 238 | 06:00 | 228 | 19:00 | Rajshahi | 235 | 00:00 | 221 | 11:00
Bheramara | 232 | 00:00 | 221 | 11:00 | Rampal | 244 | 20:00 | 217 | 19:00
Bhulta | 229 | 04:00 | 221 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 00:00 | 218 | 11:00 | Rampura | 228 | 04:00 | 219 | 11:00
BIPTC | 237 | 00:00 | 221 | 12:00 | Shikalbaha | 237 | 07:00 | 226 | 00:00
Bogura | 241 | 00:00 | 231 | 19:00 | Shyampur | 230 | 06:00 | 222 | 11:00
Bogura-400 | 242 | 00:00 | 231 | 12:00 | Siddhirganj | 231 | 06:00 | 227 | 00:00
Borhanuddin | 243 | 05:00 | 236 | 20:00 | Sirajgonj | 242 | 00:00 | 236 | 19:00
BSRM | 231 | 08:00 | 222 | 11:00 | Sreepur | 230 | 02:00 | 224 | 11:00
Cumilla(N) | 226 | 06:00 | 217 | 12:00 | Tongi | 229 | 07:00 | 217 | 12:00
Faridpur | 234 | 06:00 | 222 | 19:00
Fenchuganj | 226 | 07:00 | 221 | 01:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 228 | 06:00 | 219 | 11:00
Gopalganj | 233 | 06:00 | 224 | 18:30
GPH | 235 | 07:00 | 226 | 00:00
Haripur | 229 | 04:00 | 222 | 11:00
Hasnabad | 228 | 01:00 | 223 | 12:00
Hathazari | 239 | 06:00 | 229 | 00:00
Ishurdi | 236 | 00:00 | 224 | 12:00
Jhenaidah | 236 | 00:00 | 215 | 19:00
Kaliakoir | 230 | 05:00 | 223 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 126 | 12:00 | Madartek | 133 | 04:00 | 125 | 11:00
Agargaon | 138 | 18:00 | 129 | 11:00 | Madunaghat | 137 | 19:30 | 131 | 00:00
Agrabad | 138 | 07:00 | 130 | 00:00 | Magura | 140 | 00:00 | 119 | 19:00
AKS | 134 | 21:00 | 127 | 00:00 | Mahasthangarh | 137 | 00:00 | 129 | 19:00
Aminbazar | 133 | 06:00 | 129 | 18:30 | Manikganj | 130 | 14:00 | 123 | 17:00
Amnura | 137 | 00:00 | 127 | 19:00 | Maniknagar | 132 | 06:00 | 126 | 12:00
Ashuganj | 138 | 03:00 | 135 | 11:00 | Matarbari | 130 | 07:00 | 114 | 00:00
Bagerhat | 138 | 01:00 | 119 | 19:00 | Matuail | 133 | 06:00 | 123 | 08:00
Bajitpur | 132 | 03:00 | 128 | 12:00 | Millgate | 133 | 03:00 | 124 | 12:00
Bakulia | 139 | 07:00 | 130 | 00:00 | Mirpur | 132 | 04:00 | 125 | 11:00
Banani | 133 | 03:00 | 125 | 11:00 | Mirzapur | 129 | 00:00 | 120 | 11:00
Bangabhaban | 132 | 07:00 | 126 | 11:00 | Mithapukur | 134 | 04:00 | 126 | 12:00
Barapukuria | 139 | 04:00 | 134 | 08:00 | MI_Cement | 134 | 04:00 | 129 | 11:00
Barguna | 136 | 05:00 | 131 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 08:00 | 125 | 23:00 | Mogbazar | 135 | 05:00 | 126 | 12:00
Barishal-230 | 134 | 06:00 | 125 | 23:00 | Mongla | 137 | 06:00 | 120 | 19:00
Baroaulia | 136 | 08:00 | 131 | 00:00 | Motijheel | 132 | 07:00 | 126 | 11:00
Baroirhat | 126 | 07:00 | 119 | 01:00 | Muktagacha | 134 | 00:00 | 119 | 18:30
Bashundhara | 133 | 03:00 | 124 | 11:00 | Munshiganj | 132 | 04:00 | 128 | 11:00
BashundharaCement | 133 | 08:00 | 128 | 13:00 | Muradnagar | 127 | 06:00 | 122 | 11:00
Beanibazar | 132 | 04:00 | 126 | 18:30 | Mymensingh | 130 | 00:00 | 117 | 13:00
Benapole | 141 | 00:00 | 116 | 19:00 | Naogaon | 130 | 00:00 | 123 | 08:00
Bhaluka | 134 | 02:00 | 125 | 13:00 | Narail | 141 | 00:00 | 118 | 19:00
Bhandaria | 128 | 07:00 | 116 | 21:00 | Narinda | 132 | 06:00 | 126 | 12:00
Bhangura | 137 | 00:00 | 127 | 19:00 | Narshingdi | 129 | 04:00 | 119 | 00:00
Bheramara | 138 | 00:00 | 129 | 19:00 | Natore | 138 | 00:00 | 128 | 22:00
Bheramara(GK) | 137 | 00:00 | 128 | 19:00 | Nawabganj | 135 | 04:00 | 129 | 18:30
Bhulta | 130 | 04:00 | 124 | 18:30 | Netrakona | 127 | 01:00 | 114 | 13:00
Bog-Sherpur | 138 | 00:00 | 130 | 19:00 | New | 132 | 03:00 | 125 | 12:00
Bogura | 139 | 00:00 | 132 | 19:00 | Niamatpur | 140 | 00:00 | 131 | 13:00
Bogura-230 | 140 | 00:00 | 133 | 08:00 | Noapara | 140 | 00:00 | 122 | 19:00
Brahmanbaria | 131 | 07:00 | 124 | 00:00 | Pabna | 138 | 00:00 | 128 | 19:00
Cantonment | 134 | 04:00 | 129 | 11:00 | Palashbari | 133 | 00:00 | 125 | 12:00
Chandina | 129 | 07:00 | 124 | 11:00 | Panchagarh | 131 | 23:00 | 120 | 18:00
Chandpur | 126 | 18:30 | 119 | 01:00 | Patuakhali | 136 | 07:00 | 131 | 23:00
Chandraghona | 137 | 07:00 | 131 | 00:00 | Payra | 138 | 07:00 | 135 | 18:30
Chapai | 138 | 00:00 | 129 | 19:00 | PHP | 125 | 07:00 | 117 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 04:00 | 129 | 11:00 | Postogola | 136 | 06:00 | 132 | 11:00
Chauddagram | 136 | 23:00 | 117 | 11:00 | Purbachal | 133 | 03:00 | 125 | 11:00
Chhatak | 132 | 07:00 | 125 | 18:30 | Purbasadipur | 130 | 02:00 | 121 | 15:00
Chowmuhani | 118 | 08:00 | 110 | 06:00 | Rahanpur | 140 | 00:00 | 133 | 13:00
Chuadanga | 139 | 00:00 | 121 | 18:30 | Rahanpur-400 | 140 | 00:00 | 133 | 08:00
Coxsbazar | 132 | 07:00 | 113 | 00:00 | Rahim | 133 | 06:00 | 129 | 12:00
Cumilla(N) | 129 | 07:00 | 123 | 11:00 | Rajbari | 138 | 05:00 | 129 | 22:00
Cumilla(S) | 133 | 22:00 | 121 | 11:00 | Rajendrapur | 135 | 02:00 | 123 | 12:00
Daudkandi | 126 | 04:00 | 122 | 00:00 | Rajshahi | 137 | 00:00 | 128 | 19:00
Dhaka | 133 | 04:00 | 126 | 11:00 | Rajshahi-230 | 136 | 00:00 | 124 | 13:00
Dhamrai | 132 | 00:00 | 125 | 19:00 | Ramganj | 118 | 08:00 | 110 | 00:00
Dhanmondi | 135 | 23:00 | 130 | 11:00 | Rampur | 138 | 08:00 | 129 | 00:00
Dohazari | 133 | 06:00 | 123 | 00:00 | Rampura | 133 | 04:00 | 125 | 12:00
Faridpur | 138 | 04:00 | 131 | 23:00 | Rangamati | 136 | 08:00 | 130 | 00:00
Fatullah | 135 | 06:00 | 130 | 12:00 | Rangpur | 132 | 03:00 | 125 | 08:00
Fenchuganj | 136 | 08:00 | 132 | 18:30 | Ruppur | 138 | 00:00 | 130 | 19:00
Feni | 123 | 04:00 | 118 | 11:00 | Saidpur | 132 | 05:00 | 124 | 12:00
Ghatail | 131 | 00:00 | 117 | 18:30 | Satkhira | 141 | 00:00 | 121 | 19:00
Ghorashal | 138 | 19:00 | 133 | 11:00 | Satmasjid | 134 | 04:00 | 128 | 13:00
Goalpara | 142 | 00:00 | 125 | 19:00 | Savar | 156 | 01:00 | 125 | 11:00
Gollamari | 141 | 00:00 | 126 | 19:00 | SevenRings | 138 | 14:00 | 132 | 11:00
Gopalganj | 140 | 00:00 | 127 | 19:00 | ShahCement | 133 | 04:00 | 129 | 11:00
Gopalganj-400 | 140 | 06:00 | 132 | 18:30 | Shahjadpur | 141 | 00:00 | 133 | 18:30
Gulshan | 133 | 06:00 | 125 | 12:00 | Shahjibazar | 133 | 18:00 | 125 | 18:30
Halishahar | 138 | 07:00 | 130 | 00:00 | Shahmirpur | 139 | 07:00 | 131 | 00:00
Haripur | 134 | 04:00 | 130 | 11:00 | Shariatpur | 138 | 06:00 | 126 | 23:00
HaripurSBU | 134 | 04:00 | 130 | 00:00 | Sherpur | 136 | 02:00 | 120 | 08:00
Hasnabad | 136 | 05:00 | 130 | 13:00 | Shikalbaha | 129 | 07:00 | 120 | 00:00
Hathazari | 138 | 06:00 | 132 | 00:00 | Shikalbaha-230 | 140 | 07:00 | 131 | 00:00
Ishurdi | 140 | 00:00 | 130 | 19:00 | Shitalakhya | 134 | 04:00 | 129 | 11:00
Jaldhaka | 131 | 03:00 | 123 | 12:00 | Sholosohor | 136 | 07:00 | 131 | 00:00
Jamalpur | 136 | 01:00 | 120 | 11:00 | Shyampur | 135 | 05:00 | 130 | 11:00
Jashore | 141 | 00:00 | 118 | 19:00 | Shyampur-230 | 135 | 08:00 | 130 | 11:00
Jhenaidah | 141 | 00:00 | 123 | 18:30 | Siddhirganj | 133 | 02:00 | 129 | 12:00
Jhenaidah-230 | 141 | 00:00 | 123 | 19:00 | Sirajganj | 138 | 00:00 | 126 | 19:00
Joydebpur | 140 | 19:00 | 129 | 11:00 | Sonargaon | 133 | 19:30 | 126 | 00:00
Joypurhat | 131 | 00:00 | 122 | 19:00 | Sreemongol | 131 | 06:00 | 127 | 00:00
Juldah | 139 | 07:00 | 131 | 00:00 | Sreepur | 134 | 01:00 | 129 | 11:00
Kabirpur | 132 | 14:00 | 124 | 11:00 | Srinagar | 135 | 03:00 | 130 | 11:00
Kachua | 123 | 07:00 | 117 | 11:00 | SSM | 140 | 07:00 | 134 | 00:00
Kaliakoir | 134 | 05:00 | 126 | 11:00 | Sunamganj | 130 | 05:00 | 123 | 00:00
Kallyanpur | 132 | 03:00 | 123 | 11:00 | Sylhet | 131 | 02:00 | 127 | 13:00
Kalurghat | 137 | 07:00 | 131 | 00:00 | Sylhet-132 | 131 | 01:00 | 128 | 23:00
Kamrangirchar | 136 | 04:00 | 129 | 12:00 | Tangail | 128 | 00:00 | 117 | 11:00
Kaptai | 134 | 5:00 | 121 | 12:00 | Thakurgaon | 131 | 23:00 | 119 | 18:00
Kasba | 127 | 08:00 | 121 | 00:00 | TK | 139 | 07:00 | 132 | 00:00
Kazla | 131 | 02:00 | 126 | 00:00 | Tongi | 135 | 14:00 | 127 | 12:00
Keranigonj | 136 | 07:00 | 130 | 12:00 | Ullahpara | 137 | 00:00 | 129 | 19:00
Khagrachori | 135 | 07:00 | 129 | 00:00 | Ullon | 133 | 03:00 | 126 | 11:00
Khulna | 141 | 00:00 | 124 | 19:00 | Uttara | 132 | 06:00 | 120 | 18:00
Khulna(S) | 142 | 00:00 | 127 | 19:00 | UttaraNew | 132 | 05:00 | 126 | 11:00
Khulshi | 136 | 07:00 | 129 | 00:00 | Zigatola | 136 | 06:00 | 130 | 11:00
Kishoreganj | 133 | 01:00 | 124 | 13:00
Kodda | 136 | 19:30 | 122 | 15:00
KSRM | 136 | 21:00 | 130 | 00:00
Kulaura | 134 | 05:00 | 130 | 18:30
Kurigram | 131 | 18:30 | 120 | 12:00
Kushtia | 140 | 00:00 | 125 | 19:00
Lalbag | 135 | 04:00 | 129 | 12:00
Lalmonirhat | 130 | 05:00 | 121 | 12:00
Madanganj | 133 | 08:00 | 128 | 13:00
Madaripur | 138 | 06:00 | 129 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division