## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-04-2025 | during | 13-04-2025 | during | 13-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 21 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | Unit-2 shut down for leak repairing
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 296 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 95 | 96 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 322 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 90 | 8 | 8 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 62 | 145 | 149.36 | 149.36 | 62 | 145 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 20 | 30 | 30 | 30 | 30 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 15 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 294 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 141 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 37 | 100 | 104 | 104 | 37 | 100 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 72 | 162 | 162 | 35 | 72 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 36 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 500 | 530 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2681.5 | 3193 | 4784.9 | 4752.9 | 3089.96 | 3240.96
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 45 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 146 | 149 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 85 | 68 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 46 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 44 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 13 | 2 | 30 | 2 | 30 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 24 | 50 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 2.9 | 0 | 2.9 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 10 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 18 | 45 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 4 | 1 | 4 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 161 | 161 | 155 | 155 | 160 | 160 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1789 | 2381.5 | 2983.62 | 3008.72 | 2988.62 | 3013.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 137 | 214 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 347 | 352 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 50 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 165 | 165 | 175 | 175 | 175 | 175 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 112 | 132 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 37 | 45 | 47 | 47 | 37 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 85 | 200 | 200 | 200 | 190 | 190 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 17 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 80 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 0.01 | 0.01 | Under Maintenance
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 64 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1268 | 1521.2 | 2110.99 | 2040.99 | 1747.56 | 1716.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-04-2025 | during | 13-04-2025 | during | 13-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 7 | 11 | 210 | 210 | 23 | 23 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 170 | 200 | 200 | 125 | 170 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 103 | 115 | 115 | 67 | 103 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.9 | 0 | 47 | 0 | 47 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 279.9 | 350.5 | 650.5 | 601.5 | 330.5 | 362.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 25 | 36 | 25 | 25 | 25 | 25 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 151 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 20 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 171 | 170 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 15 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 394 | 383 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1240 | 1246 | 1255 | 1255 | 1220 | 1220
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 905 | 906 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 30 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 37 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.55 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1245 | 1239 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2248.55 | 2265 | 3607.2 | 3512.2 | 3092.01 | 2997.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 239 | 225 | 450 | 450 | 200 | 200 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 126 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 750 | 1180 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.67 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1536.67 | 2068 | 2622.12 | 2621.12 | 2360.12 | 2359.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 27 | 23 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 35 | 35 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 197 | 190 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 196 | 172 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 171 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 22 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 8 | 8 | 52.2 | 52.2 | 8 | 8 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.63 | 0 | 5.8 | 0 | 5.8 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 0 | 314 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 43.95 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1462.58 | 1720 | 2509.79 | 2342.99 | 2412.8 | 2246
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 60 | 57 | 58 | 58 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 166 | 170 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 38 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 134 | 0 | 169 | 0 | 169 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 633.8 | 455 | 675.4 | 470 | 687.4 | 482
System Total |  |  |  |  | 27566.2 | 28535.742 | 13140 | 15200.2 | 21199.52 | 20605.42 | 17928.97 | 17637.87
Forecast Scenario (13-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14650 |  | 0 |  | 14650
|  |  |  | 1:00 | 14320 |  | 0 |  | 14320
|  |  |  | 2:00 | 13900 |  | 0 |  | 13900
|  |  |  | 3:00 | 13270 |  | 0 |  | 13270
|  |  |  | 4:00 | 12900 |  | 0 |  | 12900
|  |  |  | 5:00 | 12450 |  | 0 |  | 12450
|  |  |  | 6:00 | 12090 |  | 0 |  | 12090
|  |  |  | 7:00 | 12300 |  | 0 |  | 12300
|  |  |  | 8:00 | 12460 |  | 0 |  | 12460
|  |  |  | 9:00 | 12800 |  | 0 |  | 12800
|  |  |  | 10:00 | 13220 |  | 0 |  | 13220
|  |  |  | 11:00 | 13650 |  | 0 |  | 13650
|  |  |  | 12:00 | 14050 |  | 0 |  | 14050
|  |  |  | 13:00 | 14230 |  | 0 |  | 14230
|  |  |  | 14:00 | 14440 |  | 0 |  | 14440
|  |  |  | 15:00 | 14400 |  | 0 |  | 14400
|  |  |  | 16:00 | 14330 |  | 0 |  | 14330
|  |  |  | 17:00 | 14100 |  | 0 |  | 14100
|  |  |  | 18:00 | 13800 |  | 0 |  | 13800
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15300 |  | 0 |  | 15300
|  |  |  | 19:30 | 15550 |  | 0 |  | 15550
|  |  |  | 20:00 | 15550 |  | 0 |  | 15550
|  |  |  | 21:00 | 15580 |  | 0 |  | 15580
|  |  |  | 22:00 | 15380 |  | 0 |  | 15380
|  |  |  | 23:00 | 15130 |  | 0 |  | 15130
Probable Maximum Temperature: |  |  | 35.50°C
Probable Maximum Demand at Day Peak: |  |  | 14050.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15580.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15580.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 334.30 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:41 hrs on 13-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-04-2025 | [28 empty] | Date: | 12-04-2025 | [28 empty] | Date: | 12-04-2025 | [28 empty] | Date: | 12-04-2025 | [28 empty] | Date: | 12-04-2025 | [16 empty] | Date: | 12-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 36 | 69 | 147 | 120 | 0 | 0 | 17 | 0 | 102 | 225 | 305 | 583 | 0 | 55 | 0 | 317 | 0 | 0 | 0 | 125 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36 | 71 | 0 | 36 | 76 | 0 | 46 | 34 | 31 | 160 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 140 | 167 | 0 | 360 | 0 | 52 | 209 | 35 | 0 | 70 | 176 | 29 | 20 | 80 | 42 | 52.2 | 0 | 47 | 0 | 320 | 402 | 25 | 40 | 0 | 156 | 15 | 0 | 82 | 0 | 0 | 18 | 170 | 0 | 49 | 140 | 22 | 0 | 0 | 0 | 7435.2 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1058 | 0 | 629.37 | 0 | 0 | 0 | 113 | 0 | 97 | 100 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 184 | 0 | 174 | 0 | 414 | 0 | 0 | 0 | 172 | 60 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 156 | 1160 | 0 | 6262.37 | 13697.57 | 82.61
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 94 | 147 | 295 | 10 | 0 | 17 | 0 | 85 | 225 | 296 | 583 | 0 | 55 | 0 | 325 | 0 | 0 | 0 | 160 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 71 | 0 | 36 | 82 | 0 | 45 | 57 | 30 | 161 | 116 | 0 | 5 | 0 | 52 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 138 | 157 | 0 | 360 | 0 | 52 | 138 | 35 | 0 | 80 | 115 | 10 | 20 | 80 | 40 | 52.2 | 0 | 47 | 0 | 320 | 350 | 25 | 39 | 0 | 156 | 15 | 0 | 82 | 0 | 0 | 18 | 170 | 8 | 49 | 103 | 23 | 0 | 0 | 6 | 7564.2 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 50 | 113 | 0 | 8 | 0 | 0 | 0 | 197 | 0 | 184 | 0 | 167 | 0 | 414 | 0 | 0 | 0 | 171 | 60 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 156 | 1244 | 0 | 5728 | 13292.2 | 82.6
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 17 | 138 | 81 | 295 | 55 | 0 | 17 | 0 | 51 | 225 | 289 | 500 | 0 | 55 | 0 | 327 | 0 | 0 | 0 | 160 | 19 | 15 | 0 | 0 | 0 | 0 | 21 | 0 | 3 | 0 | 71 | 0 | 36 | 48 | 0 | 43 | 34 | 30 | 163 | 90 | 0 | 19 | 0 | 17 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 157 | 0 | 360 | 0 | 52 | 138 | 35 | 0 | 70 | 103 | 9 | 20 | 80 | 38 | 52.2 | 0 | 47 | 0 | 320 | 350 | 25 | 39 | 0 | 150 | 15 | 0 | 82 | 0 | 0 | 18 | 169 | 17 | 49 | 97 | 23 | 0 | 0 | 8 | 7329.2 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0 | 0 | 49 | 0 | 113 | 5 | 0 | 50 | 30 | 16 | 0 | 0 | 0 | 197 | 0 | 183 | 0 | 160 | 0 | 414 | 0 | 0 | 0 | 163 | 59 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 171 | 1200 | 0 | 5667 | 12996.2 | 82.6
03:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 17 | 17 | 115 | 81 | 195 | 55 | 0 | 17 | 0 | 16 | 225 | 301 | 500 | 0 | 55 | 0 | 324 | 0 | 0 | 0 | 90 | 19 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 36 | 10 | 0 | 42 | 17 | 30 | 163 | 90 | 0 | 19 | 0 | 17 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 157 | 0 | 360 | 0 | 52 | 138 | 35 | 0 | 70 | 101 | 9 | 20 | 80 | 34 | 52.2 | 0 | 48 | 0 | 320 | 381 | 25 | 39 | 0 | 152 | 15 | 0 | 82 | 0 | 0 | 18 | 169 | 17 | 49 | 103 | 23 | 0 | 0 | 12 | 7039.2 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 0 | 0 | 0 | 0 | 113 | 5 | 0 | 50 | 28 | 52.2 | 0 | 0 | 0 | 196 | 0 | 181 | 0 | 155 | 0 | 414 | 0 | 0 | 0 | 161 | 60 | 73 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 207 | 1100 | 0 | 5544.2 | 12583.4 | 82.59
04:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 17 | 17 | 83 | 81 | 195 | 0 | 0 | 17 | 0 | 16 | 225 | 300 | 500 | 0 | 55 | 0 | 326 | 0 | 0 | 0 | 70 | 19 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 43 | 5 | 30 | 162 | 90 | 0 | 0 | 0 | 6 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 165 | 0 | 360 | 0 | 52 | 141 | 35 | 0 | 70 | 75 | 9 | 20 | 80 | 36 | 52.2 | 0 | 48 | 0 | 320 | 347 | 25 | 39 | 0 | 152 | 15 | 0 | 82 | 0 | 0 | 18 | 170 | 17 | 49 | 105 | 23 | 0 | 0 | 12 | 6827.2 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 0 | 0 | 0 | 0 | 113 | 21 | 0 | 50 | 28 | 52.2 | 0 | 0 | 0 | 198 | 0 | 181 | 0 | 155 | 0 | 414 | 0 | 0 | 0 | 164 | 60 | 73 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 208 | 1100 | 0 | 5461.2 | 12288.4 | 82.59
05:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 17 | 17 | 83 | 81 | 145 | 0 | 0 | 17 | 0 | 16 | 225 | 308 | 400 | 0 | 55 | 0 | 326 | 0 | 0 | 0 | 70 | 19 | 15 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 45 | 0 | 32 | 162 | 35 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1224 | 0 | 51 | 113 | 167 | 0 | 360 | 0 | 52 | 140 | 35 | 0 | 70 | 69 | 8 | 20 | 80 | 34 | 52.2 | 0 | 48 | 0 | 320 | 372 | 25 | 39 | 0 | 153 | 15 | 0 | 82 | 0 | 0 | 18 | 170 | 17 | 49 | 106 | 23 | 0 | 0 | 12 | 6629.2 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 201 | 0 | 177 | 0 | 151 | 0 | 414 | 0 | 0 | 0 | 164 | 60 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 206 | 1100 | 0 | 5217 | 11846.2 | 82.58
06:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 0 | 17 | 83 | 81 | 15 | 0 | 0 | 17 | 0 | 16 | 225 | 308 | 450 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 70 | 9 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 0 | 46 | 0 | 32 | 162 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 167 | 0 | 350 | 0 | 52 | 138 | 35 | 0 | 70 | 69 | 9 | 20 | 80 | 26 | 8 | 2 | 48 | 0 | 320 | 385 | 25 | 39 | 0 | 155 | 15 | 0 | 82 | 0 | 0 | 18 | 170 | 17 | 49 | 106 | 23 | 0 | 0.91 | 12 | 6280.91 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.42 | 1013 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 28 | 0 | 0 | 0 | 1.01 | 201 | 0 | 177 | 0 | 149 | 0 | 414 | 0 | 0.08 | 0 | 165 | 60 | 35 | 1 | 34 | 0 | 0 | 0 | 1 | 0.01 | 0 | 307 | 10 | 130 | 220 | 0 | 209 | 1000 | 0 | 5083.52 | 11364.43 | 82.58
07:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 0 | 17 | 83 | 115 | 15 | 0 | 0 | 17 | 0 | 16 | 225 | 291 | 500 | 0 | 0 | 0 | 321 | 0 | 0 | 6 | 70 | 22 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 1 | 46 | 0 | 15 | 162 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 1224 | 5 | 51 | 30 | 167 | 0 | 355 | 0 | 51 | 100 | 35 | 0 | 70 | 69 | 9 | 20 | 80 | 30 | 8 | 16 | 48 | 0 | 320 | 400 | 25 | 40 | 0 | 157 | 0 | 0 | 82 | 0 | 0 | 18 | 170 | 17 | 69 | 125 | 23 | 0 | 8.39 | 12 | 6385.39 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8 | 1070 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 10 | 28 | 0 | 16 | 0 | 8.62 | 202 | 0 | 176 | 0 | 139 | 0 | 350 | 0 | 0.88 | 0 | 162 | 59 | 35 | 6 | 38 | 0 | 0 | 0.8 | 31 | 0.1 | 0 | 307 | 8 | 120 | 180 | 0 | 211 | 994 | 0 | 5121.2 | 11506.59 | 82.57
08:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 6 | 89 | 145 | 15 | 0 | 0 | 17 | 0 | 16 | 225 | 303 | 500 | 0 | 0 | 0 | 325 | 0 | 0 | 14 | 70 | 22 | 15 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 10 | 2 | 46 | 0 | 5 | 161 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1224 | 10 | 51 | 30 | 167 | 0 | 359 | 0 | 51 | 29 | 35 | 0 | 70 | 69 | 9 | 20 | 80 | 36 | 8 | 36 | 39 | 0 | 320 | 360 | 25 | 40 | 0 | 152 | 0 | 0 | 82 | 0 | 0 | 18 | 170 | 17 | 69 | 125 | 22 | 1 | 21.3 | 12 | 6354.3 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.37 | 1060 | 0 | 0 | 0 | 0 | 0 | 94 | 22 | 0 | 100 | 28 | 0 | 44 | 14 | 19.62 | 202 | 0 | 177 | 0 | 137 | 0 | 300 | 0 | 2.16 | 0 | 166 | 60 | 115 | 14 | 99 | 0 | 0 | 3.4 | 81 | 0.27 | 0 | 307 | 7 | 110 | 180 | 0 | 209 | 1000 | 0 | 5448.82 | 11803.12 | 82.57
09:00 | 8 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 141 | 145 | 120 | 4 | 0 | 17 | 0 | 16 | 225 | 253 | 500 | 0 | 17 | 0 | 321 | 0 | 0 | 0 | 70 | 19 | 15 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 44 | 10 | 3 | 46 | 3 | 3 | 160 | 0 | 0 | 0 | 0 | 12 | 151 | 0 | 0 | 0 | 1224 | 15 | 51 | 38 | 165 | 0 | 359 | 0 | 51 | 43 | 35 | 0 | 50 | 89 | 9 | 12 | 80 | 38 | 8 | 57 | 39 | 0 | 320 | 347 | 25 | 40 | 0 | 156 | 0 | 0 | 82 | 0 | 0 | 18 | 170 | 17 | 69 | 125 | 16 | 1 | 18.67 | 12 | 6576.67 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.51 | 1061 | 0 | 0 | 0 | 0 | 0 | 113 | 21 | 0 | 113 | 28 | 8 | 70 | 22 | 40.38 | 204 | 0 | 185 | 0 | 153 | 0 | 350 | 0 | 3.59 | 0 | 165 | 60 | 115 | 23 | 99 | 0 | 0 | 5.3 | 133 | 0.31 | 0 | 243 | 7 | 116 | 180 | 0 | 209 | 930 | 0 | 5584.09 | 12160.76 | 82.56
10:00 | 8 | 35 | 16 | 0 | 0 | 0 | 0 | 3 | 401 | 0 | 0 | 0 | 17 | 141 | 93 | 145 | 15 | 17 | 17 | 0 | 18 | 225 | 302 | 450 | 0 | 35 | 0 | 320 | 0 | 0 | 0 | 52 | 19 | 15 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 44 | 10 | 4 | 46 | 17 | 2 | 160 | 0 | 0 | 0 | 0 | 51 | 147 | 0 | 0 | 0 | 1150 | 18 | 43 | 77 | 165 | 0 | 360 | 0 | 51 | 139 | 31 | 0 | 50 | 85 | 9 | 4 | 45 | 38 | 8 | 63 | 37 | 0 | 320 | 360 | 25 | 40 | 0 | 154 | 0 | 0 | 82 | 0 | 0 | 18 | 170 | 17 | 68 | 125 | 10 | 2 | 16.74 | 5 | 6634.74 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.66 | 1056 | 0 | 0 | 0 | 0 | 0 | 113 | 22 | 0 | 113 | 28 | 8 | 93 | 22 | 47.46 | 180 | 0 | 196 | 0 | 178 | 0 | 414 | 0 | 4.82 | 0 | 167 | 60 | 115 | 30 | 99 | 0 | 0 | 6.8 | 159 | 0.58 | 0 | 200 | 7 | 118 | 220 | 0 | 210 | 850 | 0 | 5707.32 | 12342.06 | 82.56
11:00 | 8 | 35 | 16 | 0 | 0 | 0 | 0 | 22 | 401 | 0 | 0 | 0 | 17 | 141 | 80 | 270 | 15 | 17 | 17 | 0 | 31 | 225 | 298 | 500 | 0 | 35 | 0 | 320 | 0 | 0 | 31 | 52 | 19.5 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 44 | 10 | 0 | 46 | 17 | 2 | 160 | 0 | 0 | 0 | 0 | 56 | 146 | 0 | 0 | 0 | 1224 | 15 | 43 | 105 | 165 | 0 | 355 | 0 | 51 | 138 | 34 | 0 | 70 | 85 | 8 | 6 | 34 | 42 | 9 | 48 | 37 | 0 | 320 | 360 | 25 | 40 | 0 | 161 | 15 | 0 | 82 | 0 | 0 | 18 | 171 | 17 | 68 | 125 | 10 | 2 | 43.67 | 12 | 7002.17 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.32 | 1139 | 0 | 0 | 0 | 0 | 0 | 113 | 25 | 0 | 113 | 30 | 8 | 112 | 22 | 55.64 | 192 | 0 | 195 | 0 | 184 | 0 | 414 | 0 | 5.33 | 0 | 165 | 60 | 115 | 34 | 113 | 0 | 0 | 6.7 | 158 | 0.64 | 0 | 200 | 7 | 120 | 220 | 0 | 219 | 850 | 0 | 5879.63 | 12881.8 | 82.55
12:00 | 8 | 35 | 16 | 0 | 0 | 0 | 0 | 21 | 401 | 0 | 0 | 0 | 17 | 141 | 62 | 294 | 15 | 17 | 35 | 0 | 37 | 225 | 299 | 500 | 0 | 35 | 0 | 317 | 95 | 0 | 33 | 52 | 19.5 | 7 | 0 | 0 | 0 | 10 | 24 | 0 | 0 | 0 | 0 | 0 | 44 | 10 | 0 | 46 | 18 | 2 | 161 | 0 | 0 | 0 | 0 | 85 | 146 | 0 | 0 | 0 | 1224 | 19 | 43 | 112 | 165 | 0 | 347 | 0 | 50 | 137 | 34 | 0 | 70 | 85 | 9 | 5 | 34 | 42 | 34 | 64 | 37 | 0 | 320 | 394 | 25 | 40 | 0 | 155 | 15 | 0 | 82 | 20 | 0 | 18 | 171 | 17 | 67 | 125 | 7 | 1 | 50.9 | 12 | 7258.4 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.55 | 1245 | 0 | 0 | 0 | 0 | 0 | 113 | 27 | 0 | 113 | 35 | 8 | 100 | 22 | 43.95 | 197 | 0 | 196 | 0 | 190 | 0 | 414 | 0 | 3.63 | 0 | 166 | 60 | 115 | 38 | 113 | 0 | 0 | 7.8 | 134 | 0.67 | 0 | 200 | 7 | 120 | 220 | 0 | 239 | 750 | 0 | 5881.6 | 13140 | 82.55
13:00 | 8 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 1 | 17 | 146 | 62 | 294 | 15 | 35 | 54 | 0 | 48 | 225 | 298 | 500 | 0 | 35 | 0 | 316 | 95 | 0 | 34 | 54 | 18.5 | 15 | 0 | 0 | 0 | 15 | 25 | 0 | 1 | 0 | 0 | 0 | 44 | 44 | 0 | 46 | 58 | 3 | 157 | 0 | 0 | 0 | 0 | 68 | 144 | 0 | 0 | 0 | 1224 | 19 | 43 | 115 | 165 | 0 | 350 | 0 | 50 | 137 | 34 | 0 | 50 | 103 | 9 | 17 | 52 | 42 | 34 | 69 | 37 | 0 | 320 | 390 | 5 | 40 | 0 | 155 | 15 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 67 | 125 | 7 | 1 | 32.31 | 12 | 7363.81 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.64 | 1255 | 0 | 0 | 0 | 0 | 0 | 113 | 27 | 50 | 113 | 35 | 8 | 64 | 22 | 30.06 | 198 | 0 | 191 | 0 | 192 | 0 | 414 | 0 | 2.65 | 0 | 166 | 60 | 115 | 28 | 113 | 0 | 0 | 7.7 | 101 | 0.64 | 0 | 200 | 8 | 120 | 220 | 0 | 223 | 745 | 0 | 5823.69 | 13187.5 | 82.54
14:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 149 | 62 | 294 | 15 | 55 | 54 | 0 | 50 | 225 | 299 | 500 | 0 | 0 | 0 | 316 | 94 | 0 | 24 | 90 | 18.5 | 15 | 0 | 0 | 0 | 15 | 24 | 0 | 16 | 34 | 44 | 0 | 44 | 76 | 3 | 42 | 68 | 2 | 160 | 0 | 0 | 0 | 0 | 68 | 144 | 0 | 0 | 0 | 1224 | 17 | 43 | 108 | 165 | 0 | 350 | 0 | 49 | 30 | 34 | 0 | 50 | 155 | 8 | 17 | 52 | 46 | 34 | 60 | 38 | 0 | 320 | 385 | 5 | 40 | 0 | 153 | 16 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 67 | 124 | 5 | 1 | 36.73 | 12 | 7448.23 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.06 | 1253 | 0 | 0 | 0 | 49 | 0 | 113 | 26 | 50 | 113 | 35 | 8 | 80 | 22 | 53.35 | 199 | 0 | 180 | 0 | 185 | 0 | 414 | 0 | 4.15 | 0 | 131 | 60 | 115 | 31 | 113 | 0 | 0 | 5.3 | 162 | 0.57 | 0 | 200 | 9 | 120 | 220 | 0 | 223 | 790 | 0 | 5957.43 | 13405.66 | 82.54
15:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 35 | 17 | 149 | 95 | 294 | 15 | 55 | 54 | 0 | 50 | 225 | 296 | 540 | 0 | 0 | 0 | 313 | 94 | 0 | 21 | 108 | 18.5 | 15 | 0 | 0 | 0 | 15 | 25 | 0 | 12 | 32 | 44 | 0 | 44 | 76 | 3 | 41 | 68 | 2 | 160 | 80 | 0 | 0 | 0 | 68 | 143 | 0 | 0 | 0 | 1224 | 13 | 43 | 108 | 164 | 0 | 344 | 0 | 48 | 42 | 34 | 0 | 50 | 155 | 8 | 17 | 80 | 38 | 42 | 48 | 44 | 0 | 320 | 365 | 5 | 39 | 0 | 153 | 16 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 66 | 124 | 7 | 1 | 21.71 | 12 | 7587.21 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.82 | 1252 | 0 | 0 | 0 | 49 | 0 | 113 | 26 | 50 | 113 | 35 | 8 | 67 | 22 | 30.8 | 201 | 0 | 180 | 0 | 180 | 0 | 414 | 0 | 3.99 | 0 | 169 | 57 | 115 | 24 | 113 | 0 | 0 | 5.6 | 133 | 0.42 | 0 | 200 | 10 | 120 | 220 | 0 | 248 | 850 | 0 | 5969.63 | 13556.84 | 82.53
16:00 | 8 | 35 | 18 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 149 | 115 | 294 | 55 | 55 | 54 | 0 | 50 | 225 | 298 | 540 | 0 | 0 | 0 | 309 | 94 | 0 | 13 | 108 | 18.5 | 15 | 0 | 0 | 0 | 15 | 24 | 0 | 8 | 32 | 44 | 0 | 70 | 76 | 2 | 42 | 68 | 2 | 160 | 108 | 0 | 0 | 0 | 68 | 143 | 0 | 0 | 0 | 1224 | 8 | 43 | 115 | 164 | 0 | 344 | 0 | 48 | 55 | 34 | 0 | 50 | 155 | 20 | 17 | 80 | 38 | 52.2 | 30 | 43 | 0 | 320 | 389 | 10 | 39 | 0 | 152 | 22 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 66 | 118 | 8 | 1 | 18.01 | 12 | 7761.71 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.12 | 1244 | 0 | 0 | 0 | 49 | 0 | 113 | 21 | 50 | 113 | 35 | 8 | 47 | 22 | 21.6 | 200 | 0 | 179 | 0 | 179 | 0 | 414 | 0 | 2.32 | 0 | 169 | 57 | 115 | 16 | 109 | 0 | 0 | 4 | 82 | 0.08 | 0 | 200 | 9 | 120 | 180 | 0 | 248 | 850 | 0 | 5809.12 | 13570.83 | 82.53
17:00 | 8 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 35 | 17 | 135 | 128 | 294 | 55 | 55 | 54 | 0 | 52 | 225 | 292 | 540 | 0 | 0 | 0 | 313 | 93 | 0 | 6 | 108 | 18.5 | 15 | 0 | 0 | 0 | 15 | 24 | 0 | 4 | 32 | 44 | 0 | 100 | 76 | 1 | 43 | 68 | 2 | 160 | 124 | 0 | 1 | 1 | 68 | 143 | 0 | 0 | 0 | 1224 | 3 | 51 | 122 | 164 | 0 | 337 | 0 | 48 | 55 | 34 | 0 | 50 | 155 | 42 | 17 | 80 | 40 | 52.2 | 12 | 43 | 0 | 320 | 352 | 10 | 39 | 0 | 154 | 22 | 0 | 81 | 30 | 0 | 18 | 171 | 17 | 66 | 127 | 9 | 0 | 5.56 | 12 | 7771.26 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.48 | 1248 | 0 | 0 | 0 | 49 | 0 | 113 | 21 | 50 | 113 | 33 | 8 | 20 | 22 | 11.29 | 197 | 0 | 174 | 0 | 177 | 0 | 414 | 0 | 0.97 | 0 | 166 | 57 | 115 | 6 | 113 | 0 | 0 | 1.5 | 34 | 0.09 | 0 | 200 | 8 | 120 | 220 | 0 | 248 | 850 | 0 | 5715.33 | 13486.59 | 82.52
18:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 149 | 129 | 294 | 55 | 55 | 108 | 0 | 72 | 225 | 296 | 500 | 0 | 17 | 0 | 319 | 93 | 0 | 1 | 108 | 18.5 | 15 | 0 | 0 | 7 | 15 | 22 | 0 | 2 | 34 | 44 | 0 | 100 | 76 | 0 | 45 | 68 | 2 | 160 | 124 | 0 | 15 | 23 | 68 | 143 | 0 | 0 | 0 | 1150 | 0 | 51 | 122 | 164 | 0 | 347 | 0 | 48 | 55 | 34 | 0 | 50 | 155 | 37 | 17 | 80 | 38 | 52.2 | 1 | 43 | 0 | 320 | 348 | 36 | 39 | 0 | 154 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 17 | 103 | 157 | 8 | 0 | 0.97 | 12 | 7896.67 | 905 | 0 | 0 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 1.18 | 1248 | 17 | 0 | 0 | 50 | 0 | 113 | 15 | 95 | 70 | 35 | 8 | 0 | 22 | 1.12 | 160 | 0 | 173 | 0 | 176 | 0 | 350 | 0 | 0.12 | 0 | 170 | 57 | 115 | 1 | 113 | 0 | 0 | 0.2 | 3 | 0.01 | 13 | 200 | 8 | 120 | 220 | 0 | 248 | 855 | 0 | 5582.63 | 13479.3 | 82.52
19:00 | 40 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 149 | 144 | 294 | 55 | 55 | 108 | 0 | 82 | 225 | 301 | 500 | 0 | 35 | 0 | 321 | 95 | 0 | 0 | 160 | 18.5 | 15 | 0 | 0 | 31 | 60 | 46 | 0 | 0 | 95 | 47 | 17 | 100 | 76 | 0 | 46 | 87 | 15 | 158 | 160 | 0 | 24 | 25.5 | 91 | 145 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 164 | 0 | 350 | 0 | 48 | 205 | 35 | 0 | 50 | 182 | 38 | 17 | 80 | 42 | 52.2 | 0 | 45 | 0 | 320 | 349 | 36 | 39 | 0 | 153 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 20 | 103 | 168 | 11 | 0 | 0 | 12 | 8584.2 | 899 | 0 | 0 | 41 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1248 | 45 | 46 | 0 | 50 | 0 | 113 | 15 | 95 | 113 | 35 | 8 | 0 | 22 | 0 | 177 | 0 | 173 | 0 | 175 | 0 | 414 | 0 | 0 | 0 | 170 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 250 | 10 | 108 | 220 | 0 | 224 | 1040 | 17 | 6061 | 14645.2 | 82.51
19:30 | 77 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 | 35 | 17 | 149 | 144 | 294 | 55 | 55 | 108 | 0 | 90 | 225 | 303 | 440 | 0 | 35 | 0 | 322 | 94 | 0 | 0 | 160 | 20.5 | 15 | 0 | 0 | 17 | 100 | 50 | 0 | 0 | 94 | 46 | 17 | 100 | 76 | 0 | 46 | 110 | 7 | 160 | 160 | 0 | 45 | 25.5 | 105 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 124 | 164 | 0 | 355 | 0 | 50 | 214 | 35 | 0 | 50 | 200 | 38 | 17 | 80 | 36 | 52.2 | 0 | 45 | 0 | 320 | 390 | 36 | 39 | 0 | 153 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 54.5 | 103 | 171 | 11 | 0 | 0 | 12 | 8768.7 | 857 | 0 | 0 | 35 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247 | 53 | 100 | 0 | 50 | 0 | 113 | 15 | 95 | 113 | 35 | 8 | 0 | 22 | 0 | 189 | 0 | 172 | 0 | 176 | 0 | 370 | 0 | 0 | 0 | 169 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 280 | 10 | 124 | 220 | 0 | 223 | 1040 | 17 | 6104 | 14872.7
20:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 17 | 19 | 149 | 147 | 294 | 55 | 55 | 108 | 0 | 94 | 225 | 293 | 440 | 0 | 35 | 0 | 324 | 96 | 0 | 0 | 160 | 20.5 | 15 | 0 | 0 | 17 | 100 | 50 | 0 | 0 | 94 | 46 | 17 | 100 | 88 | 0 | 46 | 110 | 10 | 161 | 160 | 0 | 42 | 25.5 | 105 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 164 | 0 | 352 | 0 | 49 | 215 | 35 | 0 | 50 | 200 | 37 | 17 | 80 | 40 | 52.2 | 0 | 45 | 0 | 320 | 348 | 36 | 39 | 0 | 152 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 54.5 | 103 | 171 | 11 | 0 | 0 | 12 | 8736.7 | 857 | 0 | 0 | 35 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1241 | 53 | 133 | 0 | 50 | 0 | 113 | 15 | 95 | 113 | 35 | 8 | 0 | 22 | 0 | 189 | 0 | 172 | 0 | 175 | 0 | 414 | 0 | 0 | 0 | 170 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 108 | 220 | 0 | 224 | 1130 | 0 | 6237 | 14973.7 | 82.51
21:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 36 | 149 | 145 | 294 | 55 | 55 | 72 | 0 | 100 | 225 | 296 | 530 | 0 | 35 | 0 | 322 | 96 | 0 | 0 | 160 | 20 | 15 | 0 | 0 | 17 | 30 | 50 | 0 | 0 | 102 | 46 | 0 | 100 | 100 | 0 | 46 | 45 | 13 | 161 | 160 | 0 | 45 | 25.5 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 165 | 0 | 352 | 0 | 50 | 214 | 35 | 0 | 50 | 200 | 38 | 17 | 80 | 40 | 52.2 | 0 | 45 | 0 | 320 | 383 | 36 | 40 | 0 | 151 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 54.5 | 103 | 170 | 11 | 0 | 0 | 12 | 8692.2 | 906 | 0 | 0 | 30 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1239 | 53 | 314 | 0 | 50 | 0 | 113 | 23 | 95 | 113 | 35 | 8 | 0 | 22 | 0 | 190 | 0 | 172 | 0 | 171 | 0 | 414 | 0 | 0 | 0 | 170 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 126 | 220 | 0 | 225 | 1180 | 0 | 6508 | 15200.2 | 82.5
22:00 | 8 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 149 | 144 | 294 | 55 | 55 | 72 | 0 | 100 | 225 | 300 | 550 | 0 | 0 | 0 | 325 | 96 | 0 | 0 | 160 | 19 | 15 | 0 | 0 | 17 | 30 | 50 | 0 | 0 | 102 | 47 | 0 | 100 | 86 | 0 | 46 | 51 | 18 | 161 | 160 | 0 | 33 | 25.5 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 133 | 165 | 0 | 350 | 0 | 50 | 214 | 35 | 0 | 50 | 200 | 37 | 17 | 80 | 46 | 52.2 | 0 | 46 | 0 | 320 | 396 | 39 | 40 | 0 | 158 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 22 | 104 | 173 | 11 | 0 | 0 | 0 | 8545.7 | 907 | 0 | 0 | 30 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1247 | 55 | 470 | 0 | 50 | 0 | 113 | 15 | 95 | 113 | 35 | 8 | 0 | 22 | 0 | 190 | 0 | 172 | 0 | 170 | 0 | 414 | 0 | 0 | 0 | 174 | 56 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 116 | 220 | 0 | 196 | 1150 | 0 | 6563 | 15108.7 | 82.5
23:00 | 8 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 149 | 144 | 294 | 55 | 35 | 17 | 0 | 100 | 225 | 305 | 583 | 0 | 0 | 0 | 321 | 96 | 0 | 0 | 142 | 19 | 15 | 0 | 0 | 17 | 30 | 51 | 0 | 0 | 102 | 47 | 0 | 44 | 86 | 0 | 46 | 51 | 22 | 162 | 160 | 0 | 33 | 10 | 69 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 165 | 0 | 355 | 0 | 51 | 215 | 35 | 0 | 70 | 200 | 38 | 17 | 80 | 48 | 52.2 | 0 | 46 | 0 | 320 | 392 | 39 | 40 | 0 | 155 | 16 | 0 | 82 | 30 | 0 | 18 | 171 | 17 | 104 | 154 | 10 | 0 | 0 | 0 | 8423.2 | 906 | 0 | 0 | 29 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 55 | 537 | 0 | 50 | 0 | 113 | 15 | 98 | 113 | 35 | 8 | 0 | 22 | 0 | 190 | 0 | 173 | 0 | 168 | 0 | 414 | 0 | 0 | 0 | 157 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 120 | 220 | 0 | 199 | 1100 | 0 | 6564 | 14987.2 | 82.49
Total KWH | 364320 | 764160 | 338880 | 0 | 0 | 0 | 0 | 48090.91 | 9579600 | 0 | 0 | 348480 | 496440 | 3123360 | 2615520 | 5423400 | 763421 | 594942 | 1005120 | 0 | 1224960 | 5052000 | 7121135 | 12222727 | 0 | 603171 | 0 | 7725285 | 1269000 | 0 | 173907 | 2521200 | 450600 | 334800 | 0 | 0 | 146782 | 408982 | 791040 | 0 | 50400 | 776826 | 605424 | 39886 | 1224000 | 1158720 | 21383 | 1078020 | 1160036 | 332640 | 3730909.09 | 1702836 | 0 | 295200 | 160817.4 | 1390036 | 3494407 | 0 | 0 | 0 | 29296361 | 143775 | 1027176 | 2579345 | 3930909 | 0 | 8798100 | 0 | 1209120 | 3096000 | 830448 | 0 | 1446790 | 3095040 | 442680 | 367430 | 1732800 | 934080 | 934574 | 512900 | 1054944 | 0 | 7687800 | 9260000 | 595000 | 913440 | 0 | 3705300 | 321072 | 0 | 1965120 | 377664 | 0 | 436000 | 3539820 | 498600 | 1698000 | 3060000 | 321600 | 11400 | 296060 | 242400 | 179094611.4 | 21730181 | 0 | 0 | 174240 | 189824 | 0 | 0 | 0 | 0 | 0 | 0 | 696960 | 27810910 | 301440 | 2530909 | 0 | 516201 | 0 | 2491488 | 410179 | 961536 | 2242080 | 626695 | 257760 | 705640 | 346994 | 367504 | 4715000 | 0 | 4527364 | 0 | 4257273 | 0 | 9703490 | 0 | 34680 | 0 | 4051000 | 1344872 | 2415451 | 238399 | 2389104 | 0 | 0 | 55829.76 | 1211760 | 3909 | 81984 | 6218000 | 218211 | 2786000 | 5330010 | 0 | 5191272 | 24637090.91 | 31200 | 141802440.67 | 320897052.07

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13140 | MW | 12:00 Hr. | Energy Generated |  |  | 320.8971 |  | MKWHr.
| Day Peak Demand |  |  | 13345 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.633 |  | MKWHr.
| Evening Peak Generation |  |  | 15200.2 | MW | 21:00 Hr. | Energy Demand |  |  | 324.5301 |  | MKWHr.
| Evening Peak Demand |  |  | 15350.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.1 |  | °C
| Minimum Generation of the Day |  |  | 11364.43 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 954.13 |  | MMCFD
| Maximum Generation of the Day |  |  | 15200.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.1171 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.8032 | 0 | 20.1874 | 0 | 0 | 0.17391 | 0 | 0 | 64.1645 | Gas | 128.9964 | Gas | 411047604.3485
| Chattogram Zone |  |  | 3.827 | 33.0273 | 9.8606 | 0 | 1.078 | 0.16516 | 0 | 0.0504 | 48.0085 | Coal | 102.2804 | Coal | 706864820.6155
| Cumilla Zone |  |  | 20.706 | 0 | 9.8394 | 0 | 0 | 0.5129 | 0.93408 | 0 | 31.9923 | HFO | 58.8225 | HFO | 1025335131.098
| Mymensingh Zone |  |  | 0.3216 | 0 | 5.499 | 0 | 0 | 0.30746 | 0 | 0 | 6.1281 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.8012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.8012 | Hydro | 1.078 | Hydro | 107802
| Khulna Zone |  |  | 0 | 27.8109 | 0.6655 | 0 | 0 | 0.69696 | 21.7302 | 0 | 50.9036 | Solar | 4.4741 | Solar | 72466602.4136
| Barishal Zone |  |  | 8.3342 | 36.0464 | 0.11318 | 0 | 0 | 0.003909 | 0 | 0 | 44.4977 | Import | 25.1952 | Import | 67287694.99
| Rajshahi Zone |  |  | 23.2031 | 0 | 7.8529 | 0 | 0 | 1.1078 | 2.5309 | 0 | 34.6948 | Wind | 0.0504 | Wind | 737856
| Rangpur Zone |  |  | 0 | 5.3959 | 4.8046 | 0 | 0 | 1.506 | 0 | 0 | 11.7064
| Total |  |  | 128.9964 | 102.2804 | 58.8225 | 0 | 1.078 | 4.4741 | 25.1952 | 0.0504 | 320.8971
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 411047604.3485 |  | Hydro | 107802
|  |  |  | Coal | 706864820.6155 |  | Solar | 72466602.4136
|  |  |  | HFO | 1025335131.098 |  | Import | 67287694.99
|  |  |  | HSD | 0 |  | Wind | 737856
[5 empty] | Total: | 228,38,47,511 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 38472.72 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7302 | Peak Hr Flow | 906.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 37655485.84 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 2.5309 | Peak Hr Flow | 314.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 186 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.93408 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 570 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 25.1952 | Peak Hr Flow | 1260.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 106 |  | 5191
|  |  |  | Chattogram |  | 0 |  | 1487
|  |  |  | Cumilla |  | 20 |  | 1450
|  |  |  | Mymensingh |  | 0 |  | 1305
|  |  |  | Sylhet |  | 0 |  | 584
|  |  |  | Khulna |  | 18 |  | 1795
|  |  |  | Barishal |  | 0 |  | 481
|  |  |  | Rajshahi |  | 0 |  | 1591
|  |  |  | Rangpur |  | 0 |  | 975
|  |  |  | Total |  | 144 |  | 14859
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:07 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 LT is restored.
|  | 08:07 | Kaliakoir 400/230/132kV S/S 400/132kV TR1 HT is restored.
| 08:22 | 15:18 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 08:23 | 15:18 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 09:20 | 17:02 | Gallamari- Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end. and from
Gollamari 132/33kV end Due to Control Building Painting Work
| 09:24 | 11:48 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Distance Relay.
relays Due to Showing Z1 Fault.
| 09:43 | 12:43 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Shutdown taken by wzpdcl | [7 empty] | 5.0MW load
interrup.
| 09:43 | 12:43 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Shutdown taken by wzpdcl | [7 empty] | 5.0MW load
interrup.
| 09:44 | 12:11 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end. and from Ishurdi
132/33kVend.
| 09:44 | 12:42 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Shutdown taken by wzpdcl | [7 empty] | 5.0MW load
interrup.
| 09:44 | 12:42 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Shutdown taken by wzpdcl | [7 empty] | 5.0MW load
interrup.
| 09:44 | 12:42 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Shutdown taken by wzpdcl | [7 empty] | 5.0MW load
interrup.
| 09:54 | 17:44 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Project works.
|  | 10:02 | Jashore-Noapara 132kV Ckt-2 is restored.
| 10:14 | 12:18 | Jashore-Noapara 132kV Ckt-1 Scheduled S/D from Jashore 132/33kV end Due to Shutdown For
Noapara End and from Noapara 132/33kVend.
| 10:26 | 12:27 | Khulna (C) S/S Tr-2 415 T LT Project Work S/D Due to 33kv newly installed feeder's Bus
loop( Riser) connection purpose.
| 10:26 | 12:26 | Khulna (C) S/S Tr-2 415 T HT Project Work S/D Due to 33kv newly installed feeder's Bus
loop( Riser) connection purpose.
| 10:28 | 12:04 | Noapara 132/33kV S/S BUS A Scheduled S/D
| 10:35 | 11:30 | Kurigram 132/33kV S/S Capacitor Bank Forced S/D Due to Due to Redhot
|  | 10:49 | Barishal 230/132kV S/S T-4 HT is restored.
|  | 10:52 | Barishal 230/132kV S/S T-4 LT is restored.
| 10:53 |  | BIPTC S/S 20DF11 Forced S/D Due to Corrective Maintenance.
| 10:53 | 11:50 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
Emergency Maintenance work
|  | 12:11 | Sholosohor 132/33kV S/S TRAFO-01 HT is restored.
|  | 12:11 | Sholosohor 132/33kV S/S TRAFO-01 LT is restored.
| 12:12 | 14:48 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end.
| 12:13 | 15:00 | Ishwardi-Rooppur 132kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end.
|  | 12:15 | Sholosohor 132/33kV S/S TRAFO-02 HT is restored.
|  | 12:16 | Sholosohor 132/33kV S/S TRAFO-02 LT is restored.
|  | 13:03 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 13:07 | Barishal 230/132kV S/S T-5 LT is restored.
|  | 15:01 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
| 16:33 | 17:48 | Dohazari 132/33kV S/S Power Transformer -T-1 HT Forced S/D Due to Bashkhali 33kv Isolator | [7 empty] | 2.0MW load
|  |  | pin change | [7 empty] | interrup.
| 16:33 | 17:48 | Dohazari 132/33kV S/S Power Transformer -T-1 LT Forced S/D Due to Bashkhali 33kv Isolator | [7 empty] | 2.0MW load
|  |  | pin change | [7 empty] | interrup.
| 18:42 |  | Rampal 400/230kV S/S Gopalganj Line-2 Reactor Forced S/D Due to Due to low voltage.
| 18:43 |  | Rampal 400/230kV S/S Gopalganj Line-1 Reactor Forced S/D Due to Due to low voltage.
| 21:12 |  | Goalpara- Khulna (C) 132kV Ckt-1 Forced S/D from Goalpara 132/33kV end Due to Order by
ALDC Khulna
| 01:57 |  | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT Tripped showing Alstom MCGG relays.
| 01:57 | 03:32 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Tripped showing Siprotec Siemens | [7 empty] | 30.0MW load
|  |  | relays Due to Thunder and rain | [7 empty] | interrup.
| 02:22 | 03:25 | Thakurgaon 132/33kV S/S T-1(422T) LT Tripped showing Micom P142 relays Due to Thundering | [7 empty] | 28.0MW load
interrup.
| 02:22 | 03:25 | Thakurgaon 132/33kV S/S T-1(422T) HT Tripped showing Mikro relays Due to Thundering | [7 empty] | 28.0MW load
interrup.
| 02:22 | 03:19 | Thakurgaon 132/33kV S/S T-2(412T) LT Tripped showing SIEMENS relays Due to Thundering | [7 empty] | 28.0MW load
interrup.
| 02:22 | 03:19 | Thakurgaon 132/33kV S/S T-2(412T) HT Tripped showing Mikro relays Due to Thundering | [7 empty] | 28.0MW load
interrup.
| 03:55 | 04:23 | Chapai 132/33kV S/S T-2 (415T) LT Tripped showing O/C, Def, Phase R relays Due to 33 kv
feeder trip, strom, thundering.
| 03:55 | 04:16 | Chapai 132/33kV S/S T-2 (415T) HT Tripped showing DIF-Trip-2, Over Currrent, 33KV trip,,
P142 Relay trip. relays Due to 33Kv feeder fault, strom, thundering
| 04:10 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Tripped showing Protection panel: General
trip(87 differential protection) relays Due to Thunder storm
| 04:10 |  | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Tripped showing Protection panel: General
trip relays Due to Thunder storm
| 04:51 | 05:40 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing
SIPROTECH 7SA87 relays Due to Thunderstorm
| 05:01 | 06:21 | Mithapukur-Palashbari 132kV Ckt-2 Tripped from Palashbari 132/33kV end showing Distance
Relay, C Phase relays Due to Bad Weather
| 06:03 | 06:49 | Rahanpur 132/33kV S/S TR-2 (414T) HT Tripped showing Differential Relay (Simens 7UT85)
relays Due to Over Voltage STG-1 OP
| 06:03 | 06:49 | Rahanpur 132/33kV S/S TR-1 404T HT Tripped showing Simens 7UT85 relays Due to Over | [7 empty] | 6.0MW load
|  |  | Voltage STG-1 OP | [7 empty] | interrup.
| 06:03 |  | Chowdhala 132/33 KV T1 & T2 trip.
| 06:04 |  | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to Feni 230kV
LILO and from Cumilla(N) 230/132/33kV end Due to Disk Cleaning & Feni Project Work
|  | 06:08 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 06:13 |  | Bhaluka 132/33kV S/S Transformer- 02 LT Forced S/D Due to 33 kv bushing temperature | [7 empty] | 30.0MW load
|  |  | minimize | [7 empty] | interrup.
| 06:13 |  | Bhaluka 132/33kV S/S Transformer- 02 HT Forced S/D Due to 33 kv bushing temperature | [7 empty] | 30.0MW load
|  |  | minimize | [7 empty] | interrup.
| 06:22 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 Tripped showing Signals
(Main-1) Signals (Main-2): BUS BAR Protection-2 TIE BAY protection TIE BAY
protection -2 Others parameter: relays Due to Directional Earth Fault IDMT (67N) pickup
| 07:00 |  | Minimum generation 10338 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 48090.91 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9579600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5052000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 296 | 7121135 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 763421 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 96 | 1269000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 7725285 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 364320 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 348480 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 2615520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 594942 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 603171 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 450600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 334800 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 338880 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 5423400 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3123360 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 764160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 100 | 1224960 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1005120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 173907 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 496440 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 530 | 12222727 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2521200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3193 | 64164518.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 160817.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 143775 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 295200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1078020 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3494407 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1390036 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 46 | 605424 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 776826 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1224000 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 332640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 791040 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21383 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 408982 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 39886 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 45 | 1160036 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1158720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 146782 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 1702836 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 29296361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 50400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 161 | 3730909.09 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2381.5 | 48008480.49
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 214 | 3096000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 352 | 8798100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 830448 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1209120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 165 | 3930909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1027176 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 132 | 2579345 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 45 | 1054944 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1446790 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3095040 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 934080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 934574 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 17 | 367430 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1732800 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 442680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Under Maintenance
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 512900 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1521.2 | 31992336
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 321600 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 3060000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 1698000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 296060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 242400 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 498600 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 350.5 | 6128060
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 595000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 913440 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3705300 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 377664 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1965120 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 170 | 3539820 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 436000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 321072 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 383 | 9260000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7687800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1246 | 28801216
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 906 | 21730181 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 30 | 174240 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 37 | 189824 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 301440 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 696960 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1239 | 27810910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2265 | 50903555
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 225 | 5191272 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 81984 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 218211 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 126 | 2786000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1180 | 24637090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5330010 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 31200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6218000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3909 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2068 | 44497676.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 516201 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 23 | 410179 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 626695 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 190 | 4715000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 172 | 4527364 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 171 | 4257273 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9703490 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 346994 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 257760 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 961536 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2491488 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2242080 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34680 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 314 | 2530909 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 367504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 705640 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1720 | 34694793
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1344872 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4051000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2389104 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 55829.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2415451 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 238399 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1211760 | -
Rangpur Area Total |  |  |  |  | 950 | 455 | 11706415.76
Eastern Grid Total |  |  |  |  | 16921.242 | 8692.2 | 179094611.4
Western Grid Total |  |  |  |  | 11614.5 | 6508 | 141802440.67
National Grid Total |  |  |  |  | 28535.742 | 15200.2 | 320897052.07
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9891.76 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4824.4 | MW
i) Dhaka area |  |  | 5085.26 |  | MW | i) Khulna area |  |  |  | 1777 | MW
ii) Chattogram area |  |  | 1487 |  | MW | ii) Barishal area |  |  |  | 481 | MW
iii) Cumilla area |  |  | 1430.5 |  | MW | iii) Rajshahi area |  |  |  | 1591.4 | MW
iv) Mymensingh area |  |  | 1305 |  | MW | iv) Rangpur area |  |  |  | 975 | MW
v) Sylhet area |  |  | 584 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14716.16 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 75 | 19:30 | 133 | Patuakhali | 80 | 22:00
2 | AKSML | 114.2 | 10:00 | 68 | Jaldhaka | 71 | 20:00 | 134 | Payra | 32 | 22:00
3 | Aftabnagar | 36 | 18:00 | 69 | Jamalpur | 143 | 21:00 | 135 | Postogola | 53 | 13:00
4 | Agargaon | 107 | 18:30 | 70 | Jashore | 154 | 19:00 | 136 | Purbachal | 20 | 22:00
5 | Agrabad | 96 | 19:00 | 71 | Jhenaidah | 141 | 19:00 | 137 | Purbasadipur | 133 | 12:00
6 | Amnura | 48 | 22:00 | 72 | Joydebpur | 137 | 20:00 | 138 | Rahanpur | 32 | 22:00
7 | Ashuganj | 99 | 23:00 | 73 | Joypurhat | 76 | 21:00 | 139 | Rahim | 39 | 16:00
8 | BSRM | 203 | 23:00 | 74 | Juldah | 17 | 11:00 | 140 | Rajbari | 83 | 19:00
9 | Bagerhat | 92 | 19:00 | 75 | KSRM | 11 | 21:00 | 141 | Rajendrapur | 129 | 20:00
10 | Bajitpur | 53 | 20:00 | 76 | Kabirpur | 248 | 19:30 | 142 | Rajshahi | 116 | 23:00
11 | Bakulia | 100 | 19:00 | 77 | Kachua | 88 | 19:30 | 143 | Rajshahi-230 | 91 | 20:00
12 | Banani | 38 | 13:00 | 78 | Kallyanpur | 108 | 18:30 | 144 | Ramganj | 108 | 00:00
13 | Bangabhaban | 8 | 11:00 | 79 | Kalurghat | 40 | 15:00 | 145 | Rampur | 44 | 23:00
14 | Barapukuria | 72 | 21:00 | 80 | Kamrangirchar | 62.4 | 13:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 22 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 150 | 21:00
16 | Barishal | 117 | 11:00 | 82 | Kasba | 40 | 21:00 | 148 | Ruppur | 5.2 | 11:00
17 | Barishal-230 | 100 | 19:00 | 83 | Kazla | 99 | 19:30 | 149 | SSM | 10 | 02:00
18 | Baroaulia | 72 | 10:00 | 84 | Keranigonj | 79 | 20:00 | 150 | Saidpur | 123 | 19:00
19 | Baroirhat | 73 | 18:30 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 128 | 20:00
20 | Bashundhara | 191 | 19:00 | 86 | Khulna | 88 | 18:30 | 152 | Satmasjid | 104 | 19:30
21 | BashundharaCement | 12 | 01:00 | 87 | Khulshi | 175 | 19:30 | 153 | Savar | 209 | 14:00
22 | Beanibazar | 68 | 18:30 | 88 | Kishoreganj | 140 | 20:00 | 154 | SevenRings | 11.97 | 07:00
23 | Benapole | 70 | 20:00 | 89 | Kodda | 300 | 10:00 | 155 | ShahCement | 36 | 23:00
24 | Bhaluka | 173 | 16:00 | 90 | Kulaura | 44 | 21:00 | 156 | Shahjadpur | 88 | 23:00
25 | Bhandaria | 54 | 22:00 | 91 | Kurigram | 64 | 08:00 | 157 | Shahjibazar | 126 | 22:00
26 | Bhangura | 44 | 23:00 | 92 | Kushtia | 146 | 19:00 | 158 | Shahmirpur | 53 | 08:00
27 | Bheramara(GK) | 65 | 19:00 | 93 | Lalbag | 62 | 13:00 | 159 | Shariatpur | 90 | 22:00
28 | Bhulta | 228 | 10:00 | 94 | Lalmonirhat | 58 | 21:00 | 160 | Sherpur | 158 | 21:00
29 | Bog-Sherpur | 68 | 21:00 | 95 | MI_Cement | 18.2 | 15:00 | 161 | Shikalbaha | 25 | 00:00
30 | Bogura | 178 | 21:00 | 96 | Madanganj | 44 | 20:00 | 162 | Shitalakhya | 79.6 | 12:00
31 | Borhanuddin | 93 | 22:00 | 97 | Madaripur | 120 | 23:00 | 163 | Sholosohor | 43 | 19:00
32 | Brahmanbaria | 136 | 20:00 | 98 | Madartek | 89.08 | 23:00 | 164 | Shyampur | 166 | 11:00
33 | Cantonment | 119 | 13:00 | 99 | Madunaghat | 57 | 22:00 | 165 | Siddhirganj | 128 | 11:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 71 | 19:00 | 166 | Sirajganj | 112 | 19:00
35 | Chandpur | 72 | 19:30 | 101 | Mahasthangarh | 82 | 21:00 | 167 | Sonargaon | 97 | 17:00
36 | Chandraghona | 38 | 19:00 | 102 | Manikganj | 139 | 20:00 | 168 | Sreemongol | 74 | 19:30
37 | Chapai | 73 | 21:00 | 103 | Maniknagar | 65 | 19:30 | 169 | Sreepur | 109 | 12:00
38 | Charsaidpur | 41 | 09:00 | 104 | Matarbari | 51 | 19:30 | 170 | Srinagar | 52.4 | 20:00
39 | Chauddagram | 80 | 23:00 | 105 | Matuail | 62 | 09:00 | 171 | Sunamganj | 52 | 19:30
40 | Chhatak | 36 | 19:30 | 106 | Millgate | 83 | 12:00 | 172 | Sylhet | 42 | 21:00
41 | Chowmuhani | 212 | 16:00 | 107 | Mirpur | 140 | 19:00 | 173 | Sylhet-132 | 117 | 18:30
42 | Chuadanga | 120 | 19:00 | 108 | Mirsorai | 10 | 19:00 | 174 | TK | 36.3 | 23:00
43 | Coxsbazar | 132 | 19:30 | 109 | Mirzapur | 51 | 11:00 | 175 | Tangail | 200 | 21:00
44 | Cumilla(N) | 184 | 20:00 | 110 | Mithapukur | 64 | 21:00 | 176 | Thakurgaon | 102 | 19:30
45 | Cumilla(S) | 179 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 127 | 15:00
46 | Daudkandi | 148 | 01:00 | 112 | Mogbazar | 138.5 | 13:00 | 178 | Ullahpara | 46 | 22:00
47 | Dhaka | 48 | 12:00 | 113 | Mongla | 43 | 00:00 | 179 | Ullon | 48 | 19:30
48 | Dhamrai | 128 | 09:00 | 114 | Motijheel | 38 | 13:00 | 180 | Uttara | 97 | 19:00
49 | Dhanmondi | 139 | 13:00 | 115 | Muktagacha | 41 | 23:00 | 181 | UttaraNew | 52 | 15:00
50 | Dohazari | 116 | 19:30 | 116 | Munshiganj | 105 | 00:00 | 182 | Zigatola | 72 | 19:00
51 | Faridpur | 172 | 19:30 | 117 | Muradnagar | 31 | 20:00
52 | Fatullah | 87 | 15:00 | 118 | Mymensingh | 212 | 20:00
53 | Fenchuganj | 38 | 21:00 | 119 | Naogaon | 137 | 23:00
54 | Feni | 126 | 20:00 | 120 | Narail | 66 | 19:00
55 | GPH | 96 | 09:00 | 121 | Narinda | 72.5 | 13:00
56 | Ghatail | 88 | 12:00 | 122 | Narshingdi | 165 | 23:00
57 | Ghorashal | 18 | 18:30 | 123 | Natore | 160 | 22:00
58 | Ghorashal-230 | 91 | 19:00 | 124 | Nawabganj | 68 | 20:00
59 | Goalpara | 34 | 13:00 | 125 | Netrakona | 130 | 18:30
60 | Gollamari | 88 | 00:00 | 126 | New | 85 | 14:00
61 | Gopalganj | 115 | 21:00 | 127 | Niamatpur | 112 | 23:00
62 | Gulshan | 104 | 13:00 | 128 | Noapara | 47 | 19:30
63 | Halishahar | 82 | 12:00 | 129 | PHP | 8 | 09:00
64 | HaripurSBU | 158 | 09:00 | 130 | Pabna | 124 | 21:00
65 | Hasnabad | 77 | 00:00 | 131 | Palashbari | 128 | 21:00
66 | Hathazari | 92 | 12:00 | 132 | Panchagarh | 48 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13697.57 | 50 |  | 13749.57
1:00 | 13292.2 | 50 |  | 13344.2
2:00 | 12996.2 | 40 |  | 13038
3:00 | 12583.4 | 30 |  | 12614.4
4:00 | 12288.4 | 0 |  | 12288.4
5:00 | 11846.2 | 0 |  | 11846.2
6:00 | 11364.43 | 0 |  | 11364.43
7:00 | 11506.59 | 70 |  | 11579.59
8:00 | 11803.12 | 28 |  | 11832.12
9:00 | 12160.76 | 59 |  | 12222.76
10:00 | 12342.06 | 88 |  | 12434.02
11:00 | 12881.8 | 117 |  | 13003.8
12:00 | 13140 | 196 |  | 13345
13:00 | 13187.5 | 302 |  | 13503.5
14:00 | 13405.66 | 370 |  | 13792.66
15:00 | 13556.84 | 428 |  | 14003.84
16:00 | 13570.83 | 221 |  | 13801.83
17:00 | 13486.59 | 207 |  | 13702.59
18:00 | 13479.3 | 175 |  | 13662.3
19:00 | 14645.2 | 397 |  | 15060.2
19:30 | 14872.7 | 276 |  | 15160.7
20:00 | 14973.7 | 275 |  | 15260.7
21:00 | 15200.2 | 144 |  | 15350.2
22:00 | 15108.7 | 183 |  | 15299.7
23:00 | 14987.2 | 203 |  | 15199.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7435.2 | 6262.37 | 13697.57 | DAILY GENERATION CURVE
00:30 | 7499.7 | 5995.185 | 13494.885
01:00 | 7564.2 | 5728 | 13292.2 | 12-04-2025
01:30 | 7446.7 | 5697.5 | 13144.2
02:00 | 7329.2 | 5667 | 12996.2
02:30 | 7184.2 | 5605.6 | 12789.8
03:00 | 7039.2 | 5544.2 | 12583.4
03:30 | 6933.2 | 5502.7 | 12435.9
04:00 | 6827.2 | 5461.2 | 12288.4
04:30 | 6728.2 | 5339.1 | 12067.3
05:00 | 6629.2 | 5217 | 11846.2
05:30 | 6455.055 | 5150.26 | 11605.315
06:00 | 6280.91 | 5083.52 | 11364.43
06:30 | 6333.15 | 5102.36 | 11435.51
07:00 | 6385.39 | 5121.2 | 11506.59
07:30 | 6369.845 | 5285.01 | 11654.855
08:00 | 6354.3 | 5448.82 | 11803.12
08:30 | 6465.485 | 5516.455 | 11981.94
09:00 | 6576.67 | 5584.09 | 12160.76
09:30 | 6605.705 | 5645.705 | 12251.41
10:00 | 6634.74 | 5707.32 | 12342.06
10:30 | 6818.455 | 5793.475 | 12611.93
11:00 | 7002.17 | 5879.63 | 12881.8
11:30 | 7130.285 | 5880.615 | 13010.9
12:00 | 7258.4 | 5881.6 | 13140
12:30 | 7311.105 | 5852.645 | 13163.75
13:00 | 7363.81 | 5823.69 | 13187.5
13:30 | 7406.02 | 5890.56 | 13296.58
14:00 | 7448.23 | 5957.43 | 13405.66
14:30 | 7517.72 | 5963.53 | 13481.25
15:00 | 7587.21 | 5969.63 | 13556.84
15:30 | 7674.46 | 5889.375 | 13563.835
16:00 | 7761.71 | 5809.12 | 13570.83
16:30 | 7766.485 | 5762.225 | 13528.71
17:00 | 7771.26 | 5715.33 | 13486.59
17:30 | 7833.965 | 5648.98 | 13482.945
18:00 | 7896.67 | 5582.63 | 13479.3
18:30 | 8240.435 | 5821.815 | 14062.25
19:00 | 8584.2 | 6061 | 14645.2
19:30 | 8768.7 | 6104 | 14872.7
20:00 | 8736.7 | 6237 | 14973.7
20:30 | 8714.45 | 6372.5 | 15086.95 |  | Executive Engineer
21:00 | 8692.2 | 6508 | 15200.2 |  | Network Operation Division
21:30 | 8618.95 | 6535.5 | 15154.45
22:00 | 8545.7 | 6563 | 15108.7
22:30 | 8484.45 | 6563.5 | 15047.95
23:00 | 8423.2 | 6564 | 14987.2

## En-Curve
QF-LDC-12
Date | 12-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3630 | 1951 | 905 | 0 | 42 | 629.37 | 46 | 4297 | 0 | 565 | 1627.2 | 0 | 0 | 5 | 50 | DAILY ENERGY CURVE
00:30 | 3573.5 | 1941 | 905.5 | 0 | 41 | 314.685 | 45.5 | 4340 | 0 | 532.5 | 1798.2 | 0 | 0 | 3 | 50 | 12-04-2025
01:00 | 3517 | 1931 | 906 | 0 | 40 | 0 | 45 | 4383 | 0 | 500 | 1969.2 | 0 | 0 | 1 | 50
01:30 | 3497.5 | 1883 | 906 | 0 | 39 | 0 | 44 | 4389 | 0 | 484 | 1899.7 | 0 | 0 | 2 | 45 | Energy Generated | 320.8971 |  | MKWHr
02:00 | 3478 | 1835 | 906 | 0 | 38 | 0 | 43 | 4395 | 0 | 468 | 1830.2 | 0 | 0 | 3 | 40 | Energy not Served | 3.633 |  | MKWHr
02:30 | 3491 | 1842 | 906 | 0 | 36 | 0 | 42.5 | 4363.5 | 0 | 372.5 | 1734.8 | 0 | 0 | 1.5 | 35 | Total Energy Requirement | 324.5301 |  | MKWHr
03:00 | 3504 | 1849 | 906 | 0 | 34 | 0 | 42 | 4332 | 0 | 277 | 1639.4 | 0 | 0 | 0 | 30
03:30 | 3493 | 1852.5 | 906.5 | 0 | 35 | 0 | 42.5 | 4283.5 | 0 | 275 | 1547.9 | 0 | 0 | 0 | 15
04:00 | 3482 | 1856 | 907 | 0 | 36 | 0 | 43 | 4235 | 0 | 273 | 1456.4 | 0 | 0 | 0 | 0
04:30 | 3492 | 1812.5 | 906.5 | 0 | 35 | 0 | 44 | 4235 | 0 | 273 | 1269.3 | 0 | 0 | 0 | 0
05:00 | 3502 | 1769 | 906 | 0 | 34 | 0 | 45 | 4235 | 0 | 273 | 1082.2 | 0 | 0 | 0 | 0
05:30 | 3503 | 1790 | 906 | 0 | 30 | 0 | 45.5 | 4187.5 | 3.715 | 273 | 866.6 | 0 | 0 | 0 | 0
06:00 | 3504 | 1811 | 906 | 0 | 26 | 0 | 46 | 4140 | 7.43 | 273 | 651 | 0 | 0 | 0 | 0
06:30 | 3451.5 | 1797.5 | 906 | 0 | 28 | 0 | 46 | 4164.5 | 63.01 | 290.5 | 688.5 | 0 | 0 | 0 | 35
07:00 | 3399 | 1784 | 906 | 0 | 30 | 0 | 46 | 4189 | 118.59 | 308 | 726 | 0 | 0 | 0 | 70
07:30 | 3319.5 | 1782 | 882 | 0 | 33 | 0 | 46 | 4188 | 203.355 | 325.5 | 875.5 | 0 | 0 | 0 | 49
08:00 | 3240 | 1780 | 858 | 0 | 36 | 0 | 46 | 4187 | 288.12 | 343 | 1025 | 0 | 0 | 0 | 28
08:30 | 3272 | 1749.5 | 857.5 | 0 | 37 | 0 | 46 | 4119.5 | 363.94 | 359.5 | 1177 | 0 | 0 | 0 | 43.5
09:00 | 3304 | 1719 | 857 | 0 | 38 | 0 | 46 | 4052 | 439.76 | 376 | 1329 | 0 | 0 | 0 | 59
09:30 | 3390.5 | 1730.5 | 880.5 | 0 | 38 | 0 | 46 | 3952.5 | 485.41 | 340.5 | 1387.5 | 0 | 0 | 0 | 73.5
10:00 | 3477 | 1742 | 904 | 0 | 38 | 0 | 46 | 3853 | 531.06 | 305 | 1446 | 0 | 0 | 0 | 88
10:30 | 3495 | 1782.75 | 904.5 | 0 | 40 | 0 | 46 | 3935 | 570.68 | 301 | 1537 | 0 | 0 | 0 | 102.5
11:00 | 3513 | 1823.5 | 905 | 0 | 42 | 0 | 46 | 4017 | 610.3 | 297 | 1628 | 0 | 0 | 0 | 117
11:30 | 3586 | 1819.5 | 905 | 0 | 42 | 0 | 46 | 4031 | 602.4 | 291.5 | 1687.5 | 0 | 0 | 0 | 156.5
12:00 | 3659 | 1815.5 | 905 | 0 | 42 | 0 | 46 | 4045 | 594.5 | 286 | 1747 | 0 | 0 | 0 | 196
12:30 | 3641 | 1814.5 | 905 | 0 | 42 | 0 | 46 | 4037.5 | 540.25 | 312 | 1825 | 0 | 0 | 0.5 | 249
13:00 | 3623 | 1813.5 | 905 | 0 | 42 | 0 | 46 | 4030 | 486 | 338 | 1903 | 0 | 0 | 1 | 302
13:30 | 3557 | 1813 | 904.5 | 0 | 44 | 0 | 44 | 4035.5 | 526.58 | 406.5 | 1957 | 0 | 0 | 8.5 | 336
14:00 | 3491 | 1812.5 | 904 | 0 | 46 | 0 | 42 | 4041 | 567.16 | 475 | 2011 | 0 | 0 | 16 | 370
14:30 | 3479.5 | 1830.5 | 904.5 | 0 | 42 | 0 | 41.5 | 4100.5 | 497.25 | 502.5 | 2069 | 0 | 0 | 14 | 399
15:00 | 3468 | 1848.5 | 905 | 0 | 38 | 0 | 41 | 4160 | 427.34 | 530 | 2127 | 0 | 0 | 12 | 428
15:30 | 3488 | 1831.5 | 905 | 0 | 38 | 0 | 41.5 | 4156 | 359.735 | 551 | 2183.1 | 0 | 0 | 10 | 324.5
16:00 | 3508 | 1814.5 | 905 | 0 | 38 | 0 | 42 | 4152 | 292.13 | 572 | 2239.2 | 0 | 0 | 8 | 221
16:30 | 3481.5 | 1836 | 904.5 | 0 | 39 | 0 | 42.5 | 4152.5 | 207.51 | 581 | 2278.2 | 0 | 0 | 6 | 214
17:00 | 3455 | 1857.5 | 904 | 0 | 40 | 0 | 43 | 4153 | 122.89 | 590 | 2317.2 | 0 | 0 | 4 | 207
17:30 | 3423 | 1837 | 904.5 | 0 | 39 | 0 | 44 | 4120.5 | 66.245 | 631 | 2414.7 | 0 | 0 | 3 | 191
18:00 | 3391 | 1816.5 | 905 | 0 | 38 | 0 | 45 | 4088 | 9.6 | 672 | 2512.2 | 0 | 0 | 2 | 175
18:30 | 3507 | 1826 | 902 | 0 | 40 | 23 | 45.5 | 4229.5 | 4.8 | 759 | 2724.45 | 0 | 0 | 1 | 286
19:00 | 3623 | 1835.5 | 899 | 0 | 42 | 46 | 46 | 4371 | 0 | 846 | 2936.7 | 0 | 0 | 0 | 397
19:30 | 3669 | 1773.5 | 857 | 0 | 36 | 100 | 46 | 4400 | 0 | 856 | 3135.2 | 0 | 0 | 0 | 276
20:00 | 3657 | 1764.5 | 857 | 0 | 40 | 133 | 46 | 4514 | 0 | 868 | 3094.2 | 0 | 0 | 0 | 275
20:30 | 3680 | 1812.75 | 881.5 | 0 | 40 | 223.5 | 46 | 4538.5 | 0 | 867.5 | 2997.2 | 0 | 0 | 0 | 209.5
21:00 | 3703 | 1861 | 906 | 0 | 40 | 314 | 46 | 4563 | 0 | 867 | 2900.2 | 0 | 0 | 0 | 144
21:30 | 3704.5 | 1878.5 | 906.5 | 0 | 43 | 392 | 46 | 4520.5 | 0 | 859.5 | 2803.95 | 0 | 0 | 0 | 163.5
22:00 | 3706 | 1896 | 907 | 0 | 46 | 470 | 46 | 4478 | 0 | 852 | 2707.7 | 0 | 0 | 0 | 183
22:30 | 3716.5 | 1916 | 906.5 | 0 | 47 | 503.5 | 46 | 4443.5 | 0 | 844 | 2624.95 | 0 | 0 | 0 | 193
23:00 | 3727 | 1936 | 906 | 0 | 48 | 537 | 46 | 4409 | 0 | 836 | 2542.2 | 0 | 0 | 0 | 203
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 12:00 | 385 | 16:00 | Payra | 414 | 07:00 | 409 | 19:30
Ashuganj | 407 | 4:00 | 390 | 7:00 | Rahanpur | 418 | 19:30 | 370 | 01:00
Bhulta | 402 | 04:00 | 389 | 10:00 | Rampal | 403 | 09:00 | 391 | 18:30
Bibiana | 389 | 07:00 | 381 | 13:00
BIPTC | 400 | 08:00 | 391 | 22:00
Bogura | 415 | 19:30 | 378 | 07:00
Gopalganj | 400 | 09:00 | 391 | 00:00
Kaliakoir | 371 | 04:00 | 360 | 15:00
Madunaghat | 402 | 19:00 | 394 | 13:00
Meghnaghat | 394 | 02:00 | 388 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 02:00 | 225 | 10:00 | Keranigonj | 229 | 04:00 | 223 | 00:00
AKSML | 239 | 19:00 | 226 | 12:00 | Khulna(S) | 231 | 09:00 | 216 | 18:30
Aminbazar | 238 | 4:00 | 226 | 19:30 | Madunaghat | 239 | 19:00 | 228 | 18:00
Ashuganj | 233 | 03:00 | 227 | 22:00 | Madunaghat-400 | 240 | 19:00 | 232 | 11:00
Ashuganj-400 | 233 | 03:00 | 227 | 22:00 | Maniknagar | 228 | 03:00 | 220 | 10:00
Baghabari | 234 | 03:00 | 228 | 16:00 | Meghnaghat | 236 | 02:00 | 230 | 10:00
Barapukuria | 225 | 13:00 | 215 | 07:00 | Meghnaghat-400 | 230 | 02:00 | 225 | 10:00
Barapukuria-230 | 225 | 13:00 | 215 | 07:00 | Mirsorai | 240 | 19:30 | 226 | 00:00
Barishal | 235 | 09:00 | 228 | 00:00 | Rajshahi | 233 | 04:00 | 222 | 21:00
Bheramara | 233 | 04:00 | 222 | 12:00 | Rampal | 231 | 09:00 | 219 | 18:30
Bhulta | 230 | 04:00 | 221 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 09:00 | 217 | 21:00 | Rampura | 228 | 04:00 | 220 | 10:00
BIPTC | 236 | 04:00 | 222 | 12:00 | Shikalbaha | 239 | 18:30 | 228 | 00:00
Bogura | 236 | 00:00 | 220 | 07:00 | Shyampur | 229 | 02:00 | 223 | 10:00
Bogura-400 | 233 | 00:00 | 217 | 07:00 | Siddhirganj | 229 | 01:00 | 223 | 12:00
Borhanuddin | 240 | 06:00 | 234 | 21:00 | Sirajgonj | 240 | 04:00 | 235 | 05:00
BSRM | 235 | 18:30 | 224 | 00:00 | Sreepur | 231 | 04:00 | 224 | 19:30
Cumilla(N) | 226 | 19:00 | 220 | 00:00 | Tongi | 233 | 01:00 | 220 | 10:00
Faridpur | 229 | 09:00 | 221 | 00:00
Fenchuganj | 226 | 08:00 | 222 | 21:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 230 | 04:00 | 222 | 10:00
Gopalganj | 229 | 09:00 | 223 | 21:00
GPH | 237 | 18:30 | 227 | 00:00
Haripur | 229 | 04:00 | 223 | 10:00
Hasnabad | 229 | 04:00 | 222 | 09:00
Hathazari | 238 | 18:00 | 230 | 12:00
Ishurdi | 235 | 04:00 | 225 | 12:00
Jhenaidah | 230 | 05:00 | 216 | 21:00
Kaliakoir | 233 | 04:00 | 225 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 131 | 01:00 | 126 | 12:00 | Madartek | 131 | 02:00 | 126 | 10:00
Agargaon | 133 | 02:00 | 128 | 12:00 | Madunaghat | 138 | 19:00 | 132 | 00:00
Agrabad | 138 | 18:00 | 128 | 10:00 | Magura | 132 | 08:00 | 122 | 17:00
AKS | 134 | 18:00 | 127 | 12:00 | Mahasthangarh | 134 | 13:00 | 125 | 21:00
Aminbazar | 129 | 18:00 | 127 | 08:00 | Manikganj | 131 | 07:00 | 122 | 15:00
Amnura | 138 | 17:00 | 124 | 01:00 | Maniknagar | 131 | 04:00 | 124 | 13:00
Ashuganj | 139 | 03:00 | 135 | 12:00 | Matarbari | 129 | 18:30 | 116 | 00:00
Bagerhat | 134 | 09:00 | 120 | 18:30 | Matuail | 133.5 | 19:00 | 129 | 10:00
Bajitpur | 133 | 03:00 | 126 | 19:30 | Millgate | 135 | 03:00 | 125 | 10:00
Bakulia | 140 | 18:30 | 131 | 11:00 | Mirpur | 130 | 04:00 | 125 | 10:00
Banani | 132 | 04:00 | 125 | 12:00 | Mirzapur | 128 | 19:00 | 121 | 21:00
Bangabhaban | 131 | 03:00 | 124 | 13:00 | Mithapukur | 133 | 01:00 | 122 | 07:00
Barapukuria | 138 | 13:00 | 129 | 07:00 | MI_Cement | 135 | 19:30 | 128 | 12:00
Barguna | 135 | 09:00 | 130 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 06:00 | 125 | 00:00 | Mogbazar | 132 | 05:00 | 125 | 13:00
Barishal-230 | 133 | 09:00 | 124 | 23:00 | Mongla | 135 | 09:00 | 121 | 18:30
Baroaulia | 137 | 18:30 | 132 | 00:00 | Motijheel | 131 | 03:00 | 124 | 13:00
Baroirhat | 127 | 18:30 | 120 | 23:00 | Muktagacha | 130 | 11:00 | 119 | 17:00
Bashundhara | 134 | 02:00 | 125 | 10:00 | Munshiganj | 135 | 19:00 | 128 | 10:00
BashundharaCement | 134 | 19:30 | 130 | 00:00 | Muradnagar | 127 | 09:00 | 119 | 20:00
Beanibazar | 133 | 05:00 | 125 | 18:30 | Mymensingh | 131 | 09:00 | 115 | 21:00
Benapole | 132 | 09:00 | 119 | 18:30 | Naogaon | 133 | 13:00 | 122 | 21:00
Bhaluka | 133 | 14:00 | 124 | 22:00 | Narail | 132 | 05:00 | 121 | 19:00
Bhandaria | 126 | 08:00 | 115 | 21:00 | Narinda | 131 | 04:00 | 124 | 13:00
Bhangura | 134 | 01:00 | 127 | 21:00 | Narshingdi | 129 | 20:00 | 119 | 20:00
Bheramara | 136 | 04:00 | 128 | 21:00 | Natore | 135 | 09:00 | 126 | 21:00
Bheramara(GK) | 136 | 08:00 | 129 | 18:30 | Nawabganj | 133 | 02:00 | 129 | 00:00
Bhulta | 127 | 19:00 | 123 | 10:00 | Netrakona | 124 | 01:00 | 114 | 13:00
Bog-Sherpur | 135 | 09:00 | 124 | 07:00 | New | 134 | 04:00 | 127 | 10:00
Bogura | 137 | 01:00 | 128 | 07:00 | Niamatpur | 142 | 19:00 | 129 | 01:00
Bogura-230 | 137 | 09:00 | 127 | 07:00 | Noapara | 135 | 09:00 | 122 | 18:30
Brahmanbaria | 128 | 07:00 | 122 | 22:00 | Pabna | 134 | 04:00 | 127 | 21:00
Cantonment | 133 | 03:00 | 128 | 12:00 | Palashbari | 131 | 12:00 | 120 | 07:00
Chandina | 129 | 09:00 | 124 | 20:00 | Panchagarh | 136 | 09:00 | 120 | 19:30
Chandpur | 128 | 18:30 | 120 | 00:00 | Patuakhali | 133 | 04:00 | 131 | 00:00
Chandraghona | 137 | 18:30 | 131 | 10:00 | Payra | 137 | 20:00 | 134 | 00:00
Chapai | 138 | 17:00 | 128 | 01:00 | PHP | 127 | 19:00 | 119 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 02:00 | 129 | 10:00 | Postogola | 135 | 05:00 | 131 | 10:00
Chauddagram | 124 | 17:00 | 119 | 23:00 | Purbachal | 131 | 03:00 | 125 | 12:00
Chhatak | 132 | 05:00 | 124 | 00:00 | Purbasadipur | 134 | 01:00 | 122 | 21:00
Chowmuhani | 120 | 18:00 | 111 | 00:00 | Rahanpur | 143 | 19:30 | 132 | 07:00
Chuadanga | 131 | 09:00 | 118 | 21:00 | Rahanpur-400 | 142 | 19:00 | 126 | 01:00
Coxsbazar | 122 | 13:00 | 114 | 00:00 | Rahim | 134 | 19:00 | 123 | 23:00
Cumilla(N) | 128 | 14:00 | 124 | 12:00 | Rajbari | 133 | 04:00 | 128 | 18:30
Cumilla(S) | 133 | 06:00 | 122 | 00:00 | Rajendrapur | 137 | 22:00 | 127 | 22:00
Daudkandi | 127 | 14:00 | 114 | 21:00 | Rajshahi | 135 | 08:00 | 128 | 21:00
Dhaka | 132 | 03:00 | 125 | 13:00 | Rajshahi-230 | 135 | 04:00 | 124 | 23:00
Dhamrai | 130 | 01:00 | 126 | 00:00 | Ramganj | 123 | 18:30 | 113 | 00:00
Dhanmondi | 134 | 03:00 | 129 | 12:00 | Rampur | 138 | 18:30 | 130 | 11:00
Dohazari | 135 | 18:30 | 126 | 13:00 | Rampura | 132 | 04:00 | 126 | 10:00
Faridpur | 135 | 09:00 | 130 | 18:30 | Rangamati | 136 | 18:30 | 130 | 11:00
Fatullah | 135 | 05:00 | 130 | 10:00 | Rangpur | 133 | 13:00 | 123 | 21:00
Fenchuganj | 136 | 08:00 | 131 | 15:00 | Ruppur | 138 | 09:00 | 130 | 21:00
Feni | 124 | 18:30 | 117 | 11:00 | Saidpur | 134 | 02:00 | 124 | 21:00
Ghatail | 127 | 06:00 | 117 | 21:00 | Satkhira | 136 | 09:00 | 120 | 18:30
Ghorashal | 139 | 19:00 | 134 | 13:00 | Satmasjid | 133 | 04:00 | 127 | 13:00
Goalpara | 137 | 09:00 | 124 | 18:30 | Savar | 130 | 03:00 | 125 | 10:00
Gollamari | 138 | 08:00 | 126 | 18:30 | SevenRings | 140 | 02:00 | 134 | 13:00
Gopalganj | 135 | 09:00 | 127 | 18:30 | ShahCement | 136 | 19:30 | 129 | 10:00
Gopalganj-400 | 137 | 09:00 | 132 | 00:00 | Shahjadpur | 136 | 13:00 | 133 | 21:00
Gulshan | 132 | 04:00 | 125 | 12:00 | Shahjibazar | 132 | 04:00 | 125 | 22:00
Halishahar | 138 | 18:30 | 130 | 12:00 | Shahmirpur | 139 | 19:00 | 132 | 08:00
Haripur | 134 | 04:00 | 130 | 10:00 | Shariatpur | 133 | 07:00 | 127 | 00:00
HaripurSBU | 134 | 04:00 | 130 | 10:00 | Sherpur | 132 | 11:00 | 116 | 17:00
Hasnabad | 136 | 03:00 | 131 | 12:00 | Shikalbaha | 127 | 17:00 | 121 | 00:00
Hathazari | 138 | 18:00 | 133 | 00:00 | Shikalbaha-230 | 141 | 18:00 | 132 | 00:00
Ishurdi | 138 | 04:00 | 130 | 21:00 | Shitalakhya | 135 | 19:30 | 128 | 12:00
Jaldhaka | 132 | 02:00 | 120 | 21:00 | Sholosohor | 137 | 19:00 | 131 | 00:00
Jamalpur | 134 | 11:00 | 120 | 17:00 | Shyampur | 134 | 04:00 | 128 | 11:00
Jashore | 133 | 09:00 | 121 | 18:30 | Shyampur-230 | 133 | 02:00 | 129 | 10:00
Jhenaidah | 135 | 09:00 | 123 | 18:30 | Siddhirganj | 134 | 03:00 | 130 | 09:00
Jhenaidah-230 | 135 | 09:00 | 125 | 18:30 | Sirajganj | 133 | 06:00 | 125 | 21:00
Joydebpur | 140 | 04:00 | 133 | 15:00 | Sonargaon | 136 | 19:30 | 127 | 13:00
Joypurhat | 131 | 13:00 | 117 | 21:00 | Sreemongol | 133 | 07:00 | 126 | 20:00
Juldah | 141 | 19:00 | 132 | 12:00 | Sreepur | 135 | 04:00 | 128 | 19:30
Kabirpur | 133 | 04:00 | 122 | 09:00 | Srinagar | 134 | 04:00 | 129 | 13:00
Kachua | 124 | 18:30 | 118 | 03:00 | SSM | 140 | 18:00 | 134 | 11:00
Kaliakoir | 134 | 19:00 | 128 | 15:00 | Sunamganj | 131 | 06:00 | 123 | 00:00
Kallyanpur | 131 | 18:30 | 127 | 00:00 | Sylhet | 132 | 06:00 | 127 | 00:00
Kalurghat | 138 | 18:30 | 132 | 00:00 | Sylhet-132 | 133 | 05:00 | 128 | 00:00
Kamrangirchar | 134 | 04:00 | 129 | 20:00 | Tangail | 128 | 08:00 | 116 | 21:00
Kaptai | 139 | 19:00 | 133 | 12:00 | Thakurgaon | 137 | 09:00 | 120 | 07:00
Kasba | 127 | 14:00 | 118 | 21:00 | TK | 139 | 18:30 | 132 | 12:00
Kazla | 131 | 05:00 | 124 | 13:00 | Tongi | 135 | 04:00 | 129 | 09:00
Keranigonj | 134 | 04:00 | 130 | 00:00 | Ullahpara | 134 | 13:00 | 127 | 21:00
Khagrachori | 134 | 18:00 | 130 | 00:00 | Ullon | 131 | 04:00 | 125 | 10:00
Khulna | 137 | 09:00 | 124 | 18:30 | Uttara | 130 | 04:00 | 125 | 12:00
Khulna(S) | 139 | 09:00 | 127 | 18:30 | UttaraNew | 130 | 02:00 | 125 | 10:00
Khulshi | 136 | 18:30 | 128 | 11:00 | Zigatola | 134 | 04:00 | 129 | 13:00
Kishoreganj | 132 | 14:00 | 123 | 22:00
Kodda | 138 | 02:00 | 124 | 14:00
KSRM | 137 | 19:00 | 130 | 12:00
Kulaura | 136 | 08:00 | 130 | 18:30
Kurigram | 134 | 12:00 | 116 | 07:00
Kushtia | 136 | 09:00 | 126 | 19:30
Lalbag | 134 | 04:00 | 129 | 12:00
Lalmonirhat | 132 | 12:00 | 119 | 07:00
Madanganj | 134 | 19:30 | 130 | 00:00
Madaripur | 134 | 09:00 | 129 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division