## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 13-04-2025 | [28 empty] | Date: | 13-04-2025 | [28 empty] | Date: | 13-04-2025 | [28 empty] | Date: | 13-04-2025 | [28 empty] | Date: | 13-04-2025 | [16 empty] | Date: | 13-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 8 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 149 | 147 | 295 | 55 | 0 | 17 | 0 | 52 | 225 | 277 | 500 | 0 | 0 | 0 | 325 | 99 | 0 | 0 | 160 | 19 | 15 | 0 | 0 | 17 | 100 | 50 | 0 | 0 | 87 | 47 | 0 | 44 | 86 | 0 | 46 | 82 | 25 | 160 | 160 | 0 | 33 | 25.5 | 103 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 165 | 0 | 360 | 0 | 51 | 182 | 35 | 0 | 70 | 200 | 14 | 17 | 80 | 44 | 52.2 | 0 | 46 | 0 | 320 | 349 | 39 | 40 | 0 | 153 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 17 | 104 | 96 | 11 | 0 | 0 | 0 | 8208.7 | 907 | 0 | 0 | 29 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1155 | 55 | 725 | 0 | 50 | 0 | 113 | 11 | 98 | 113 | 35 | 8 | 0 | 22 | 0 | 190 | 0 | 172 | 0 | 167 | 0 | 414 | 0 | 0 | 0 | 150 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 110 | 220 | 0 | 203 | 950 | 0 | 6499 | 14707.7 | 82.48
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 149 | 113 | 294 | 55 | 0 | 17 | 0 | 50 | 225 | 287 | 500 | 0 | 35 | 0 | 327 | 99 | 0 | 0 | 160 | 19 | 15 | 0 | 0 | 17 | 100 | 51 | 0 | 0 | 102 | 47 | 0 | 32 | 76 | 0 | 46 | 110 | 24 | 161 | 160 | 0 | 33 | 25.5 | 105 | 150 | 0 | 0 | 0 | 1172 | 0 | 51 | 130 | 165 | 0 | 360 | 0 | 49 | 182 | 32 | 0 | 70 | 200 | 18 | 17 | 80 | 46 | 52.2 | 0 | 46 | 0 | 320 | 349 | 39 | 40 | 0 | 150 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 17 | 49 | 97 | 11 | 0 | 0 | 0 | 8093.7 | 906 | 0 | 0 | 29 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 55 | 751 | 0 | 50 | 0 | 113 | 11 | 60 | 113 | 35 | 8 | 0 | 22 | 0 | 190 | 0 | 172 | 0 | 167 | 0 | 414 | 0 | 0 | 0 | 151 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 110 | 220 | 0 | 220 | 936 | 0 | 6448 | 14541.7 | 82.48
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 149 | 95 | 294 | 15 | 0 | 17 | 0 | 50 | 225 | 291 | 500 | 0 | 35 | 0 | 326 | 98 | 0 | 0 | 108 | 19 | 15 | 0 | 0 | 17 | 100 | 50 | 0 | 0 | 102 | 47 | 0 | 32 | 76 | 0 | 45 | 110 | 23 | 161 | 108 | 0 | 33 | 25.5 | 105 | 150 | 0 | 0 | 0 | 1081 | 0 | 51 | 128 | 165 | 0 | 355 | 0 | 51 | 187 | 32 | 0 | 70 | 200 | 9 | 17 | 80 | 44 | 52.2 | 0 | 47 | 0 | 320 | 358 | 39 | 40 | 0 | 151 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 17 | 49 | 96 | 17 | 0 | 0 | 1 | 7845.7 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 55 | 753 | 0 | 50 | 0 | 113 | 11 | 0 | 70 | 35 | 8 | 0 | 22 | 0 | 190 | 0 | 172 | 0 | 166 | 0 | 414 | 0 | 0 | 0 | 149 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 110 | 220 | 0 | 258 | 944 | 0 | 6271 | 14116.7 | 82.48
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 134 | 81 | 210 | 0 | 0 | 17 | 0 | 16 | 225 | 288 | 500 | 0 | 35 | 0 | 325 | 98 | 0 | 0 | 108 | 19 | 15 | 0 | 0 | 17 | 100 | 40 | 0 | 0 | 68 | 47 | 0 | 32 | 86 | 0 | 44 | 110 | 24 | 161 | 72 | 0 | 0 | 0 | 105 | 151 | 0 | 0 | 0 | 1080 | 0 | 51 | 133 | 165 | 0 | 355 | 0 | 51 | 196 | 32 | 0 | 70 | 200 | 9 | 17 | 80 | 44 | 52.2 | 0 | 47 | 0 | 320 | 375 | 39 | 40 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 17 | 49 | 96 | 18 | 0 | 0 | 12 | 7567.2 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 55 | 753 | 0 | 0 | 0 | 113 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 172 | 0 | 158 | 0 | 414 | 0 | 0 | 0 | 149 | 57 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 110 | 220 | 0 | 259 | 947 | 0 | 6002 | 13569.2 | 82.47
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 75 | 65 | 210 | 0 | 0 | 17 | 0 | 16 | 225 | 269 | 500 | 0 | 55 | 0 | 328 | 99 | 0 | 0 | 108 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 32 | 86 | 0 | 43 | 34 | 24 | 161 | 0 | 0 | 0 | 0 | 68 | 151 | 0 | 0 | 0 | 1076 | 0 | 51 | 100 | 165 | 0 | 360 | 0 | 52 | 182 | 32 | 0 | 70 | 200 | 9 | 17 | 80 | 44 | 25 | 0 | 0 | 0 | 320 | 300 | 39 | 40 | 0 | 131 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 0 | 49 | 96 | 18 | 0 | 0 | 12 | 6861 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1055 | 55 | 751 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 172 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 149 | 55 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 110 | 180 | 0 | 269 | 946 | 0 | 5757 | 12618 | 82.47
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 75 | 65 | 45 | 0 | 0 | 17 | 0 | 16 | 225 | 270 | 500 | 0 | 55 | 0 | 333 | 99 | 0 | 0 | 108 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 20 | 0 | 44 | 34 | 4 | 161 | 0 | 0 | 0 | 0 | 68 | 153 | 0 | 0 | 0 | 1080 | 0 | 51 | 50 | 165 | 0 | 360 | 0 | 52 | 182 | 32 | 0 | 50 | 200 | 9 | 17 | 80 | 36 | 25 | 0 | 0 | 0 | 320 | 302 | 39 | 40 | 0 | 133 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 0 | 49 | 96 | 18 | 0 | 0 | 12 | 6533 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 902 | 55 | 754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 170 | 0 | 137 | 0 | 350 | 0 | 0 | 0 | 151 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 88 | 180 | 0 | 229 | 900 | 0 | 5312 | 11845 | 82.46
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 17 | 70 | 16 | 15 | 0 | 0 | 17 | 0 | 16 | 225 | 252 | 500 | 0 | 35 | 0 | 335 | 99 | 0 | 1 | 108 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 32 | 20 | 0 | 45 | 34 | 25 | 161 | 0 | 0 | 0 | 0 | 68 | 153 | 0 | 0 | 0 | 1077 | 0 | 51 | 12 | 165 | 0 | 300 | 0 | 51 | 181 | 32 | 0 | 50 | 190 | 9 | 17 | 52 | 32 | 25 | 2 | 0 | 0 | 320 | 303 | 39 | 40 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 0 | 45 | 27 | 18 | 0 | 0.55 | 12 | 6194.55 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.88 | 860 | 55 | 635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 150 | 0 | 169 | 0 | 135 | 0 | 300 | 0 | 0.03 | 0 | 149 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 215 | 9 | 88 | 180 | 0 | 230 | 800 | 0 | 4943.14 | 11137.69 | 82.46
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 77 | 16 | 15 | 0 | 17 | 17 | 0 | 16 | 225 | 254 | 350 | 0 | 0 | 0 | 280 | 36 | 0 | 5 | 8 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 22 | 20 | 0 | 46 | 34 | 22 | 160 | 0 | 0 | 0 | 0 | 34 | 153 | 0 | 0 | 0 | 1080 | 4 | 51 | 12 | 107 | 0 | 300 | 0 | 52 | 181 | 32 | 0 | 50 | 85 | 8 | 17 | 34 | 38 | 25 | 15 | 0 | 0 | 320 | 303 | 39 | 40 | 0 | 132 | 16 | 0 | 82 | 30 | 0 | 18 | 170 | 0 | 8 | 8 | 17 | 0 | 0 | 3 | 5512 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.43 | 860 | 35 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 7.42 | 150 | 0 | 140 | 0 | 136 | 0 | 300 | 0 | 0 | 0 | 150 | 56 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.11 | 0 | 210 | 8 | 88 | 180 | 0 | 226 | 774 | 0 | 4827.16 | 10339.16 | 82.45
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 225 | 290 | 350 | 0 | 0 | 0 | 280 | 39 | 0 | 12 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 100 | 1 | 46 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 865 | 10 | 10 | 0 | 76 | 0 | 300 | 0 | 37 | 204 | 35 | 0 | 50 | 85 | 9 | 17 | 34 | 38 | 25 | 34 | 0 | 0 | 320 | 318 | 39 | 40 | 0 | 133 | 16 | 0 | 41 | 20 | 0 | 18 | 171 | 0 | 0 | 0 | 17 | 0 | 25.03 | 0 | 5135.03 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.89 | 750 | 0 | 567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 25.02 | 150 | 0 | 140 | 0 | 140 | 0 | 250 | 0 | 0 | 0 | 149 | 58 | 0 | 0 | 0 | 0 | 0 | 1.3 | 42 | 0.26 | 0 | 150 | 7 | 98 | 180 | 0 | 228 | 700 | 0 | 4579.47 | 9714.5 | 82.45
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 225 | 308 | 400 | 0 | 0 | 0 | 280 | 39 | 0 | 23 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 100 | 3 | 46 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 800 | 13 | 10 | 0 | 76 | 0 | 300 | 0 | 20 | 216 | 35 | 0 | 50 | 95 | 9 | 17 | 52 | 36 | 25 | 51 | 0 | 0 | 320 | 340 | 39 | 40 | 0 | 137 | 16 | 0 | 41 | 20 | 0 | 17 | 171 | 0 | 0 | 0 | 10 | 0 | 34.68 | 0 | 5138.68 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.6 | 756 | 0 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 41.49 | 150 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 2.39 | 0 | 124 | 58 | 0 | 9 | 0 | 0 | 0 | 0 | 80 | 0.42 | 0 | 150 | 6 | 108 | 180 | 0 | 232 | 700 | 0 | 4744.9 | 9883.58 | 82.44
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 17 | 54 | 0 | 0 | 0 | 14 | 0 | 0 | 16 | 225 | 296 | 480 | 0 | 0 | 0 | 328 | 98 | 0 | 24 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 100 | 3 | 46 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 806 | 17 | 18 | 0 | 110 | 0 | 354 | 0 | 27 | 199 | 35 | 0 | 50 | 100 | 9 | 12 | 52 | 36 | 25 | 64 | 0 | 0 | 320 | 332 | 39 | 40 | 0 | 146 | 16 | 0 | 41 | 20 | 0 | 17 | 170 | 0 | 0 | 0 | 5 | 0 | 47.72 | 0 | 5559.72 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.96 | 760 | 17 | 562.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 52.91 | 150 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 4.72 | 0 | 119 | 60 | 0 | 29 | 0 | 0 | 0 | 4.9 | 194 | 0.48 | 0 | 150 | 7 | 108 | 220 | 0 | 262 | 700 | 0 | 5126.7 | 10686.42 | 82.44
11:00 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 2 | 17 | 70 | 16 | 0 | 0 | 35 | 17 | 0 | 16 | 225 | 303 | 480 | 0 | 0 | 0 | 322 | 95 | 0 | 32 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 100 | 4 | 46 | 0 | 2 | 161 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 853 | 19 | 43 | 0 | 162 | 0 | 342 | 0 | 41 | 211 | 35 | 0 | 50 | 100 | 9 | 19 | 52 | 40 | 25 | 66 | 0 | 0 | 320 | 364 | 36 | 40 | 0 | 148 | 16 | 0 | 77 | 20 | 0 | 17 | 174 | 0 | 8 | 24 | 5 | 0 | 51.71 | 0 | 5917.71 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.92 | 763 | 17 | 519 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 60.58 | 150 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 5.35 | 0 | 130 | 60 | 0 | 17 | 0 | 0 | 0 | 4.1 | 207 | 0.63 | 0 | 200 | 7 | 108 | 220 | 0 | 306 | 720 | 0 | 5302.58 | 11220.29 | 82.43
12:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 86 | 16 | 45 | 0 | 35 | 70 | 0 | 33 | 225 | 305 | 530 | 0 | 30 | 0 | 322 | 95 | 0 | 32 | 17 | 20 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 100 | 5 | 46 | 0 | 2 | 161 | 0 | 0 | 0 | 0 | 3 | 143 | 0 | 0 | 0 | 1078 | 13 | 51 | 4 | 163 | 0 | 340 | 0 | 45 | 210 | 34 | 0 | 45 | 120 | 14 | 17 | 70 | 40 | 26 | 71 | 0 | 0 | 320 | 370 | 36 | 40 | 0 | 156 | 16 | 0 | 80 | 30 | 0 | 17 | 174 | 0 | 11 | 31 | 5 | 0 | 51.9 | 0 | 6536.9 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.09 | 758 | 17 | 604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 0 | 61.96 | 178 | 0 | 195 | 0 | 200 | 0 | 414 | 0 | 5.43 | 0 | 121 | 60 | 0 | 18 | 0 | 0 | 0 | 3.3 | 213 | 0.66 | 0 | 250 | 8 | 120 | 220 | 0 | 311 | 830 | 0 | 5710.44 | 12247.34 | 82.43
13:00 | 8 | 40 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 99 | 47 | 145 | 30 | 35 | 126 | 0 | 51 | 225 | 301 | 540 | 0 | 35 | 0 | 318 | 95 | 0 | 31 | 70 | 19 | 15 | 0 | 0 | 0 | 0 | 2 | 0 | 12 | 34 | 10 | 0 | 45 | 100 | 4 | 46 | 11 | 2 | 160 | 72 | 0 | 0 | 3 | 38 | 143 | 0 | 0 | 0 | 1075 | 19 | 51 | 53 | 163 | 0 | 350 | 0 | 41 | 195 | 34 | 0 | 45 | 153 | 13 | 17 | 80 | 42 | 34 | 67 | 0 | 0 | 320 | 350 | 36 | 38 | 0 | 153 | 16 | 0 | 79 | 30 | 0 | 17 | 174 | 0 | 55 | 85 | 5 | 2 | 50.89 | 3 | 7217.89 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.93 | 760 | 17 | 753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 58.48 | 202 | 0 | 195 | 0 | 198 | 0 | 414 | 0 | 5.03 | 0 | 166 | 60 | 0 | 37 | 0 | 0 | 0 | 1.6 | 162 | 0.45 | 0 | 250 | 7 | 108 | 220 | 0 | 306 | 962 | 0 | 5997.49 | 13215.38 | 82.42
14:00 | 8 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 96 | 46 | 195 | 55 | 35 | 126 | 0 | 51 | 225 | 292 | 480 | 0 | 35 | 0 | 316 | 95 | 0 | 28 | 70 | 18 | 15 | 0 | 0 | 1 | 10 | 24 | 0 | 19 | 33 | 32 | 0 | 45 | 100 | 4 | 43 | 17 | 2 | 160 | 72 | 0 | 0 | 8 | 54 | 142 | 0 | 0 | 0 | 1075 | 17 | 51 | 95 | 163 | 0 | 354 | 0 | 44 | 182 | 34 | 0 | 45 | 155 | 9 | 18 | 80 | 36 | 43 | 58 | 29 | 0 | 320 | 350 | 36 | 38 | 0 | 152 | 16 | 0 | 79 | 30 | 0 | 17 | 174 | 0 | 55 | 87 | 5 | 2 | 16.56 | 12 | 7331.56 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.67 | 860 | 17 | 762 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 50.89 | 190 | 0 | 188 | 0 | 189 | 0 | 360 | 0 | 4.43 | 0 | 168 | 60 | 30 | 32 | 49 | 0 | 0 | 7.2 | 163 | 0.51 | 0 | 250 | 8 | 108 | 220 | 0 | 301 | 1050 | 0 | 6174.7 | 13506.26 | 82.42
15:00 | 8 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 35 | 17 | 94 | 46 | 235 | 55 | 35 | 132 | 0 | 51 | 225 | 295 | 480 | 0 | 35 | 0 | 315 | 91 | 0 | 22 | 70 | 18 | 15 | 0 | 0 | 16 | 45 | 24 | 0 | 15 | 33 | 52 | 0 | 45 | 90 | 3 | 41 | 38 | 2 | 160 | 72 | 0 | 0 | 8 | 70 | 138 | 0 | 0 | 0 | 1082 | 13 | 51 | 100 | 165 | 0 | 333 | 0 | 46 | 203 | 33 | 0 | 45 | 176 | 9 | 19 | 80 | 38 | 52.2 | 45 | 45 | 0 | 320 | 370 | 36 | 38 | 0 | 152 | 16 | 0 | 79 | 30 | 0 | 17 | 173 | 0 | 55 | 120 | 5 | 2 | 35.49 | 12 | 7570.69 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.35 | 819 | 17 | 759.59 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 0 | 0 | 74 | 0 | 40.14 | 187 | 0 | 180 | 0 | 187 | 0 | 414 | 0 | 3.48 | 0 | 112 | 59 | 35 | 9 | 49 | 0 | 0 | 3.4 | 140 | 0.41 | 0 | 250 | 9 | 120 | 220 | 0 | 299 | 1000 | 0 | 6057.37 | 13628.06 | 82.41
16:00 | 50 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 35 | 17 | 98 | 80 | 277 | 55 | 35 | 144 | 0 | 51 | 225 | 289 | 500 | 0 | 55 | 0 | 314 | 95 | 0 | 14 | 108 | 18 | 15 | 0 | 0 | 15 | 65 | 24 | 0 | 0 | 33 | 55 | 0 | 100 | 100 | 2 | 40 | 69 | 2 | 160 | 108 | 0 | 0 | 8 | 85 | 137 | 0 | 0 | 0 | 1064 | 5 | 51 | 100 | 165 | 0 | 354 | 0 | 44 | 182 | 28 | 0 | 50 | 190 | 16 | 19 | 80 | 40 | 52.2 | 28 | 45 | 0 | 320 | 375 | 36 | 37 | 0 | 151 | 16 | 0 | 79 | 30 | 0 | 17 | 173 | 26 | 65 | 113 | 7 | 1 | 22.71 | 12 | 7921.91 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.97 | 811 | 17 | 759.69 | 0 | 0 | 0 | 108 | 0 | 0 | 70 | 0 | 0 | 47 | 0 | 18.62 | 195 | 0 | 174 | 0 | 185 | 0 | 370 | 0 | 2.09 | 0 | 119 | 58 | 94 | 20 | 107 | 0 | 0 | 1.1 | 54 | 0.26 | 0 | 250 | 8 | 110 | 220 | 0 | 298 | 1000 | 0 | 6032.73 | 13954.64 | 82.41
17:00 | 50 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 148 | 94 | 294 | 55 | 35 | 144 | 0 | 66 | 225 | 276 | 500 | 0 | 55 | 0 | 313 | 95 | 0 | 6 | 108 | 17.6 | 7 | 0 | 0 | 17 | 65 | 25 | 0 | 5 | 33 | 69 | 0 | 100 | 70 | 1 | 40 | 34 | 2 | 160 | 54 | 0 | 0 | 8 | 87 | 139 | 0 | 0 | 0 | 1082 | 3 | 51 | 95 | 165 | 0 | 350 | 0 | 46 | 183 | 32 | 0 | 50 | 200 | 36 | 19 | 80 | 40 | 52.2 | 10 | 44 | 0 | 320 | 349 | 35 | 37 | 0 | 152 | 16 | 0 | 79 | 30 | 0 | 17 | 173 | 54.5 | 65 | 124 | 8 | 0 | 9.1 | 12 | 7921.4 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.48 | 810 | 17 | 753.56 | 0 | 0 | 0 | 113 | 5 | 96 | 35 | 0 | 0 | 20 | 22 | 9.8 | 193 | 0 | 172 | 0 | 179 | 0 | 414 | 0 | 0.84 | 0 | 113 | 57 | 115 | 6 | 113 | 0 | 0 | 0.6 | 45 | 0.11 | 0 | 250 | 9 | 108 | 220 | 0 | 292 | 952 | 0 | 6049.39 | 13970.79 | 82.4
18:00 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 149 | 94 | 294 | 55 | 35 | 144 | 0 | 67 | 225 | 290 | 390 | 0 | 55 | 0 | 315 | 38 | 0 | 1 | 108 | 17 | 7 | 0 | 0 | 17 | 65 | 24 | 0 | 0 | 42 | 69 | 0 | 80 | 30 | 0 | 40 | 34 | 5 | 160 | 54 | 0 | 1 | 8 | 89 | 139 | 0 | 0 | 0 | 995 | 0 | 51 | 100 | 165 | 0 | 300 | 0 | 46 | 185 | 32 | 0 | 50 | 200 | 37 | 19 | 80 | 34 | 52.2 | 1 | 44 | 20 | 320 | 301 | 36 | 40 | 0 | 136 | 16 | 0 | 82 | 30 | 0 | 17 | 173 | 54.5 | 103 | 161 | 8 | 0 | 0.93 | 12 | 7661.63 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 911 | 17 | 757.39 | 0 | 50 | 0 | 50 | 20 | 96 | 35 | 32 | 0 | 3 | 22 | 1.14 | 150 | 0 | 172 | 0 | 178 | 0 | 350 | 0 | 0.11 | 0 | 113 | 57 | 115 | 2 | 113 | 0 | 0 | 0.2 | 2 | 0.01 | 0 | 200 | 7 | 120 | 180 | 0 | 286 | 900 | 0 | 5847.85 | 13509.48 | 82.4
19:00 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 149 | 144 | 294 | 55 | 35 | 144 | 0 | 83 | 225 | 289 | 500 | 0 | 55 | 0 | 316 | 96 | 0 | 0 | 160 | 17 | 7 | 0 | 0 | 17 | 100 | 41 | 0 | 4 | 102 | 72 | 4 | 100 | 100 | 0 | 40 | 61 | 3 | 160 | 160 | 0 | 12 | 13 | 105 | 145 | 0 | 0 | 0 | 1112 | 0 | 51 | 122 | 162 | 0 | 354 | 0 | 47 | 182 | 32 | 0 | 50 | 200 | 38 | 19 | 80 | 38 | 52.2 | 0 | 45 | 15 | 320 | 360 | 36 | 38 | 0 | 147 | 16 | 0 | 82 | 30 | 0 | 17 | 173 | 54.5 | 103 | 164 | 9 | 0 | 0 | 12 | 8587.7 | 882 | 0 | 0 | 12 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 906 | 35 | 754.5 | 0 | 50 | 0 | 90 | 24 | 96 | 113 | 30 | 8 | 0 | 22 | 0 | 167 | 0 | 169 | 0 | 178 | 0 | 414 | 0 | 0 | 0 | 110 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 120 | 220 | 0 | 267 | 1010 | 17 | 6322.5 | 14910.2 | 82.39
19:30 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 35 | 17 | 149 | 144 | 294 | 55 | 35 | 144 | 0 | 84 | 225 | 288 | 500 | 0 | 55 | 0 | 316 | 97 | 0 | 0 | 160 | 17 | 7 | 0 | 0 | 17 | 102 | 50 | 0 | 1 | 102 | 72 | 17 | 100 | 100 | 0 | 40 | 68 | 6 | 160 | 160 | 0 | 12 | 25.5 | 105 | 146 | 0 | 0 | 0 | 1175 | 0 | 51 | 128 | 162 | 0 | 358 | 0 | 49 | 182 | 32 | 0 | 50 | 200 | 38 | 19 | 80 | 38 | 52.2 | 0 | 45 | 15 | 320 | 349 | 36 | 38 | 0 | 147 | 16 | 0 | 82 | 30 | 0 | 17 | 173 | 54.5 | 103 | 164 | 9 | 0 | 0 | 12 | 8701.2 | 858 | 0 | 0 | 29 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 980 | 35 | 757.69 | 0 | 41 | 0 | 113 | 25 | 96 | 113 | 35 | 8 | 0 | 22 | 0 | 182 | 0 | 168 | 0 | 173 | 0 | 414 | 0 | 0 | 0 | 106 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 108 | 220 | 0 | 267 | 1090 | 14 | 6497.69 | 15198.89 | 82.39
20:00 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 19 | 149 | 143 | 300 | 55 | 35 | 144 | 0 | 84 | 225 | 281 | 500 | 0 | 55 | 0 | 316 | 97 | 0 | 0 | 160 | 17 | 7 | 0 | 0 | 17 | 65 | 47 | 0 | 0 | 102 | 72 | 17 | 100 | 100 | 0 | 46 | 110 | 10 | 160 | 108 | 0 | 12 | 25.5 | 105 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 162 | 0 | 360 | 0 | 48 | 182 | 33 | 0 | 50 | 200 | 38 | 19 | 80 | 40 | 52.2 | 0 | 46 | 20 | 320 | 349 | 36 | 40 | 0 | 152 | 16 | 0 | 82 | 30 | 0 | 17 | 173 | 54.5 | 103 | 164 | 10 | 0 | 0 | 12 | 8726.2 | 859 | 0 | 0 | 34 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 975 | 35 | 755.73 | 0 | 50 | 0 | 113 | 25 | 96 | 113 | 35 | 8 | 0 | 22 | 0 | 182 | 0 | 168 | 0 | 172 | 0 | 414 | 0 | 0 | 0 | 110 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 10 | 108 | 220 | 0 | 266 | 1115 | 14 | 6559.73 | 15285.93 | 82.39
21:00 | 95 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 35 | 36 | 149 | 144 | 300 | 55 | 35 | 144 | 0 | 84 | 225 | 306 | 500 | 0 | 55 | 0 | 318 | 87 | 0 | 0 | 142 | 17 | 7 | 0 | 0 | 17 | 30 | 12 | 0 | 0 | 102 | 72 | 0 | 100 | 50 | 0 | 46 | 110 | 12 | 160 | 17 | 0 | 0 | 25.5 | 105 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 162 | 0 | 354 | 0 | 50 | 188 | 33 | 0 | 50 | 200 | 38 | 19 | 80 | 34 | 52.2 | 0 | 46 | 15 | 320 | 385 | 36 | 40 | 0 | 152 | 22 | 0 | 82 | 30 | 0 | 17 | 173 | 54.5 | 103 | 164 | 10 | 0 | 0 | 12 | 8544.2 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1033 | 35 | 760.58 | 0 | 50 | 0 | 113 | 25 | 96 | 50 | 35 | 8 | 0 | 22 | 0 | 183 | 0 | 165 | 0 | 169 | 0 | 414 | 0 | 0 | 0 | 110 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 268 | 1115 | 14 | 6513.58 | 15057.78 | 82.38
22:00 | 90 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 36 | 122 | 144 | 262 | 55 | 35 | 144 | 0 | 83 | 225 | 287 | 500 | 0 | 55 | 0 | 325 | 38 | 0 | 0 | 142 | 16 | 7 | 0 | 0 | 17 | 30 | 12 | 0 | 0 | 102 | 72 | 0 | 100 | 50 | 0 | 46 | 110 | 14 | 160 | 17 | 0 | 0 | 25.5 | 105 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 162 | 0 | 359 | 0 | 50 | 182 | 34 | 0 | 50 | 200 | 38 | 19 | 80 | 34 | 52.2 | 0 | 47 | 15 | 320 | 353 | 36 | 40 | 0 | 153 | 22 | 0 | 82 | 30 | 0 | 17 | 172 | 54.5 | 103 | 155 | 6 | 0 | 0 | 12 | 8360.2 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032 | 35 | 756.54 | 0 | 35 | 0 | 113 | 25 | 98 | 50 | 35 | 8 | 0 | 22 | 0 | 183 | 0 | 161 | 0 | 165 | 0 | 414 | 0 | 0 | 0 | 110 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 288 | 1170 | 0 | 6550.54 | 14910.74 | 82.38
23:00 | 50 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 35 | 36 | 122 | 144 | 262 | 55 | 35 | 144 | 0 | 84 | 225 | 306 | 500 | 0 | 55 | 0 | 323 | 40 | 0 | 0 | 142 | 16 | 7 | 0 | 0 | 17 | 30 | 12 | 0 | 0 | 102 | 72 | 0 | 32 | 50 | 0 | 46 | 110 | 20 | 160 | 17 | 0 | 0 | 25.5 | 105 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 162 | 0 | 350 | 0 | 50 | 208 | 31 | 0 | 50 | 200 | 38 | 19 | 80 | 36 | 52.2 | 0 | 47 | 15 | 320 | 392 | 36 | 40 | 0 | 154 | 22 | 0 | 83 | 28 | 0 | 17 | 172 | 54.5 | 103 | 154 | 6 | 0 | 0 | 12 | 8325.2 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1030 | 18 | 755.92 | 0 | 0 | 0 | 113 | 25 | 98 | 50 | 35 | 8 | 0 | 22 | 0 | 180 | 0 | 157 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 110 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 289 | 1170 | 0 | 6484.92 | 14810.12 | 82.38
Total KWH | 628560 | 712320 | 295680 | 0 | 0 | 0 | 0 | 0 | 9496800 | 0 | 0 | 402480 | 507240 | 2559600 | 1753440 | 4216778 | 749382 | 548745 | 1863360 | 0 | 1086720 | 5076000 | 6958545 | 11593636 | 0 | 848343 | 0 | 7644576 | 2055000 | 0 | 214635 | 2162400 | 447000 | 288360 | 0 | 0 | 227073 | 905782 | 413760 | 0 | 55200 | 1155965 | 842928 | 341236 | 1163520 | 1773120 | 30242 | 1045380 | 1461127 | 252480 | 3716363.64 | 1182618 | 0 | 119040 | 248509.8 | 1722073 | 3458400 | 0 | 0 | 0 | 25598179 | 138645 | 1019808 | 1958763 | 3663272 | 0 | 8550200 | 0 | 1089600 | 4726000 | 795744 | 0 | 1279410 | 4120320 | 456120 | 421750 | 1735080 | 918720 | 993086 | 519173 | 621904 | 57030 | 7677400 | 8779000 | 880000 | 927840 | 0 | 3500181 | 382104 | 0 | 1832640 | 674688 | 0 | 428000 | 4566200 | 527400 | 1317600 | 2265600 | 227520 | 8150 | 362440 | 199920 | 175443904.44 | 21950545 | 0 | 0 | 61920 | 95744 | 0 | 0 | 0 | 0 | 0 | 0 | 703440 | 21730910 | 701280 | 16985455 | 0 | 352691 | 0 | 1507296 | 177043 | 817056 | 933312 | 255802 | 68371 | 825300 | 222940 | 427504 | 4305182 | 0 | 4223900 | 0 | 4116624 | 0 | 9283636 | 0 | 34020 | 0 | 3276000 | 1324799 | 1355944 | 174524 | 1512153 | 0 | 0 | 31845.24 | 1226880 | 4557 | 43872 | 5869000 | 214883 | 2609000 | 5178230 | 0 | 6413091 | 22945454.55 | 45600 | 142005803.79 | 317449708.23

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 14-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-04-2025 | during | 14-04-2025 | during | 14-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 404 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | GT-2 shut down for HRSG-2 tube leakage repair
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 281 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 95 | 97 | 208.13 | 208.13 | 100 | 100 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 322 | 316 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 98 | 8 | 102 | 8 | 8 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 143 | 149.36 | 149.36 | 144 | 144 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 17 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 7 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 8 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 86 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 33 | 84 | 104 | 104 | 33 | 84 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 70 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 19 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 530 | 500 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2353 | 3192 | 5044.9 | 5106.9 | 3279.77 | 3306.77
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 13 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 12 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 46 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 146 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 3 | 105 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 72 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 45 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 10 | 8 | 20 | 8 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 47 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 2.92 | 0 | 2.92 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 65 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 110 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 108 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1078 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 1 | 1 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 161 | 160 | 155 | 155 | 160 | 160 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1596 | 2466.5 | 2986.64 | 2998.72 | 2991.64 | 3003.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 210 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 48 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 163 | 162 | 175 | 175 | 175 | 175 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 4 | 128 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 26 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 80 | 114 | 114 | 80 | 80 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 14 | 38 | 113 | 113 | 14 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 0 | 115 | 115 | 0.01 | 0.01 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 71 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1250 | 1489.2 | 2110.99 | 2040.99 | 1738.56 | 1692.56
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 13-04-2025 | during | 14-04-2025 | during | 14-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 5 | 10 | 157.5 | 157.5 | 23 | 23 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 31 | 164 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 11 | 103 | 115 | 115 | 103 | 103 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.9 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 98.9 | 343.5 | 601 | 549 | 444.5 | 392.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 36 | 33 | 33 | 33 | 33 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 152 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 20 | 341 | 341 | 0 | 0 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 349 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1239 | 1235 | 1602 | 1602 | 1226 | 1226
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 910 | 859 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 34 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 51 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 105 | 105 | 35 | 35 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.09 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 758 | 975 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1783.09 | 1954 | 3610.2 | 3512.2 | 3025.01 | 2927.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 311 | 266 | 340 | 340 | 200 | 200 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 108 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 830 | 1115 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 14 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1739.66 | 2056 | 2512.12 | 2511.12 | 2360.12 | 2359.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 25 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 178 | 182 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 168 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 200 | 172 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.43 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 604 | 755.73 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 61.96 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 114 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1772.39 | 2153.73 | 2510.84 | 2343.99 | 2458.05 | 2291.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 60 | 58 | 58 | 58 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 121 | 110 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.3 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 213 | 0 | 171.95 | 0 | 171.95 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 415.3 | 396 | 678.35 | 470 | 690.35 | 482
System Total |  |  |  |  | 27566.2 | 28535.742 | 12247.34 | 15285.93 | 21657.04 | 21134.92 | 18214 | 17680.88
Forecast Scenario (14-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14700 |  | 0 |  | 14700
|  |  |  | 1:00 | 14200 |  | 0 |  | 14200
|  |  |  | 2:00 | 13800 |  | 0 |  | 13800
|  |  |  | 3:00 | 13800 |  | 0 |  | 13800
|  |  |  | 4:00 | 13500 |  | 0 |  | 13500
|  |  |  | 5:00 | 12700 |  | 0 |  | 12700
|  |  |  | 6:00 | 11900 |  | 0 |  | 11900
|  |  |  | 7:00 | 11400 |  | 0 |  | 11400
|  |  |  | 8:00 | 11400 |  | 0 |  | 11400
|  |  |  | 9:00 | 11500 |  | 0 |  | 11500
|  |  |  | 10:00 | 12000 |  | 0 |  | 12000
|  |  |  | 11:00 | 12300 |  | 0 |  | 12300
|  |  |  | 12:00 | 12600 |  | 0 |  | 12600
|  |  |  | 13:00 | 12900 |  | 0 |  | 12900
|  |  |  | 14:00 | 12900 |  | 0 |  | 12900
|  |  |  | 15:00 | 13300 |  | 0 |  | 13300
|  |  |  | 16:00 | 13200 |  | 0 |  | 13200
|  |  |  | 17:00 | 13100 |  | 0 |  | 13100
|  |  |  | 18:00 | 13500 |  | 0 |  | 13500
|  |  |  | 18:30 | 14000 |  | 0 |  | 14000
|  |  |  | 19:00 | 14700 |  | 0 |  | 14700
|  |  |  | 19:30 | 14800 |  | 0 |  | 14800
|  |  |  | 20:00 | 14900 |  | 0 |  | 14900
|  |  |  | 21:00 | 15100 |  | 0 |  | 15100
|  |  |  | 22:00 | 15000 |  | 0 |  | 15000
|  |  |  | 23:00 | 15100 |  | 0 |  | 15100
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 12600.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 319.50 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 10:28 hrs on 14-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 13-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12247.34 | MW | 12:00 Hr. | Energy Generated |  |  | 317.4497 |  | MKWHr.
| Day Peak Demand |  |  | 12247.34 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.708 |  | MKWHr.
| Evening Peak Generation |  |  | 15285.93 | MW | 20:00 Hr. | Energy Demand |  |  | 319.1577 |  | MKWHr.
| Evening Peak Demand |  |  | 15381.93 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35.1 |  | °C
| Minimum Generation of the Day |  |  | 9714.5 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 957.66 |  | MMCFD
| Maximum Generation of the Day |  |  | 15285.93 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.9248 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.5599 | 0 | 18.335 | 0 | 0 | 0.21463 | 0 | 0 | 62.1096 | Gas | 128.6806 | Gas | 414203559.91
| Chattogram Zone |  |  | 3.7109 | 29.3145 | 11.5568 | 0 | 1.0454 | 0.16889 | 0 | 0.0552 | 45.8516 | Coal | 90.8738 | Coal | 611993871.4477
| Cumilla Zone |  |  | 21.5458 | 0 | 9.8853 | 0 | 0 | 0.51917 | 0.91872 | 0 | 32.8689 | HFO | 52.2386 | HFO | 915054658.706
| Mymensingh Zone |  |  | 0.22752 | 0 | 4.3105 | 0 | 0 | 0.37059 | 0 | 0 | 4.9086 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.7051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.7051 | Hydro | 1.0454 | Hydro | 104538
| Khulna Zone |  |  | 0 | 21.7309 | 0.85894 | 0 | 0 | 0.70344 | 21.9505 | 0 | 45.2438 | Solar | 4.7014 | Solar | 75828529.0364
| Barishal Zone |  |  | 8.0021 | 35.2275 | 0.089472 | 0 | 0 | 0.004557 | 0 | 0 | 43.3237 | Import | 39.8547 | Import | 180285371.75
| Rajshahi Zone |  |  | 21.9293 | 0 | 4.3345 | 0 | 0 | 1.2868 | 16.9855 | 0 | 44.5361 | Wind | 0.0552 | Wind | 808128
| Rangpur Zone |  |  | 0 | 4.6008 | 2.8681 | 0 | 0 | 1.4332 | 0 | 0 | 8.9021
| Total |  |  | 128.6806 | 90.8738 | 52.2386 | 0 | 1.0454 | 4.7014 | 39.8547 | 0.0552 | 317.4497
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 414203559.91 |  | Hydro | 104538
|  |  |  | Coal | 611993871.4477 |  | Solar | 75828529.0364
|  |  |  | HFO | 915054658.706 |  | Import | 180285371.75
|  |  |  | HSD | 0 |  | Wind | 808128
[5 empty] | Total: | 219,82,78,656 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9505 | Peak Hr Flow | 859.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 12342036.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 16.9855 | Peak Hr Flow | 755.73 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 186 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.91872 | Peak Hr Flow | 40.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 570 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.8547 | Peak Hr Flow | 1654.73 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 65 |  | 5297
|  |  |  | Chattogram |  | 0 |  | 1546
|  |  |  | Cumilla |  | 27 |  | 1489
|  |  |  | Mymensingh |  | 0 |  | 1171
|  |  |  | Sylhet |  | 0 |  | 598
|  |  |  | Khulna |  | 0 |  | 1874
|  |  |  | Barishal |  | 0 |  | 503
|  |  |  | Rajshahi |  | 0 |  | 1516
|  |  |  | Rangpur |  | 0 |  | 756
|  |  |  | Total |  | 92 |  | 14750
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:03 | Bhaluka 132/33kV S/S Transformer- 02 HT is restored.
|  | 08:06 | Bhaluka 132/33kV S/S Transformer- 02 LT is restored.
| 08:09 | 09:04 | Bhaluka 132/33kV S/S Transformer-03 LT Forced S/D Due to 33 kv bushing clamps temperature | [7 empty] | 5.0MW load
|  |  | minimize | [7 empty] | interrup.
| 08:09 | 09:04 | Bhaluka 132/33kV S/S Transformer-03 HT Forced S/D Due to 33 kv bushing temperature | [7 empty] | 5.0MW load
|  |  | minimize | [7 empty] | interrup.
| 08:48 | 16:31 | Gallamari- Khulna (S) 132kV Ckt-2 Scheduled S/D from Gollamari 132/33kV end Due to
Control Building Painting and from Khulna(S) 230/132kV end Due to Maintenance Work at
Gallamari S/S end.
| 08:49 | 12:27 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by PDB
| 08:49 | 12:25 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by PDB
| 08:59 | 12:26 | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Shutdown Taken by PDB
|  | 09:02 | Goalpara- Khulna (C) 132kV Ckt-1 is restored.
| 09:10 | 16:02 | Khulna (C) S/S TR-1 425T HT Forced S/D Due to Maintenance of 132kv main bus section-2
loop clamp.
| 09:10 | 16:03 | Khulna (C) S/S TR-1 425T LT Forced S/D Due to Maintenance of 132kv main bus section-2
loop clamp
| 09:14 | 16:00 | Khulna (C) S/S North- West Ckt-2 Forced S/D Due to Maintenance of 132kv main bus
section-2 loop clamp
| 09:15 | 15:54 | Khulna(C )-Khulna (S) 132kV Ckt-1 Forced S/D from Khulna (C) end Due to Maintenance of
132kv main bus section-2 loop clamp and from Khulna(S) 230/132kV end Due to Maintenance
Work at Central S/S end.
| 09:18 | 15:59 | Khulna (C) S/S North-WestCkt-1 Forced S/D Due to Maintenance of 132kv main bus section-2
loop clamp
| 09:18 | 17:18 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
due to deadline checking
|  | 09:45 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT is restored.
|  | 10:23 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT is restored.
| 10:27 | 10:36 | Shahjibazar 132/33kV S/S TR-02 LT Tripped showing OC/EF-50 relays Due to PDB 33/0.4 kv | [7 empty] | 6.0MW load
|  |  | Auxilary Transformer loop flashing | [7 empty] | interrup.
|  | 10:42 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) HT is restored.
| 10:42 | 11:02 | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing DIR E/F Trip. relays. | [7 empty] | 60.0MW load
interrup.
|  | 10:45 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT is restored.
| 10:46 | 11:36 | Sherpur 132/33kV S/S Transformer- 04 LT Scheduled S/D Due to Blast Wall Construction
Work.
| 10:46 | 11:36 | Sherpur 132/33kV S/S Transformer- 04 HT Scheduled S/D Due to Blast Wall Construction
Work.
| 10:49 | 14:38 | Haripur 230/132kV S/S 132KV Bhulta-1 (Old Narsingdi) Scheduled S/D Due to From Other End
| 10:50 | 12:41 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast Wall Construction
Work.
| 10:50 | 12:41 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast Wall Construction
Work.
| 11:05 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to Busbar protection works.
| 11:16 | 11:42 | Barishal 230/132kV S/S T-4 LT Tripped showing p142 relays Due to বানারিপাড়া ৩৩কেভি ফিডার | [7 empty] | 31.0MW load
|  |  | ৩ফেজ ফল্ট | [7 empty] | interrup.
| 11:16 | 11:21 | Barishal 230/132kV S/S T-5 LT Tripped showing p142 relays Due to বানারিপাড়া ৩৩কেভি ৩ফেজ | [7 empty] | 31.0MW load
|  |  | ফল্ট | [7 empty] | interrup.
| 11:21 | 15:28 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to CB spring charged problem.
| 11:38 | 12:44 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Blast Wall Construction
Work.
| 11:38 | 12:44 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Blast Wall Construction
Work.
| 11:52 | 12:48 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing
Distance Relay Auto reclose relay relays.
| 12:30 | 13:42 | Tongi 230/132/33kV S/S 132 kV Bus-2 Scheduled S/D Due to Maintenance work
| 16:51 | 18:54 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Barisal PBS_2 take shutdown for DS | [7 empty] | 33.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 16:51 | 18:52 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Barisal PBS 2 take shutdown for | [7 empty] | 33.0MW load
|  |  | maintenance 33kv DS | [7 empty] | interrup.
|  | 19:49 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
|  | 19:49 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
|  | 19:49 | BSRM-Cumilla(N) 230 kV Ckt-2 is restored.
| 05:34 |  | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by NLDC
| 06:09 | 07:32 | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Banaripara 33 kv feeder bus DS | [7 empty] | 41.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 06:10 | 07:30 | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Banaripara 33 kV feeder bus DS | [7 empty] | 41.0MW load
|  |  | maintenance work | [7 empty] | interrup.
| 06:11 | 07:38 | Bhaluka 132/33kV S/S Transformer- 01 LT Forced S/D Due to 33kv bushing R-phase
temperature high
| 06:12 | 07:37 | Bhaluka 132/33kV S/S Transformer- 01 HT Forced S/D
| 07:00 |  | Minimum generation 11914 MW
| 07:46 |  | Ishurdi 132/33kV S/S 132 kV Baghabari Line Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 13-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 404 | 9496800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5076000 | Unit-2 shut down for leak repairing
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 281 | 6958545 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 749382 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 97 | 2055000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 316 | 7644576 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 98 | 628560 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 402480 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 1753440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 548745 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 848343 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 447000 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 288360 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 295680 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 4216778 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2559600 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 712320 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 84 | 1086720 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1863360 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 214635 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 19 | 507240 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 500 | 11593636 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2162400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3192 | 62109600
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 248509.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138645 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 119040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 46 | 1045380 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3458400 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1722073 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 72 | 842928 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 1155965 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1163520 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 252480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 47 | 413760 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 30242 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 65 | 905782 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 341236 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 1461127 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1773120 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 227073 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 108 | 1182618 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 25598179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 55200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 160 | 3716363.64 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2466.5 | 45851641.44
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4726000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8550200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 795744 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1089600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 162 | 3663272 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1019808 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 128 | 1958763 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 46 | 621904 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1279410 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4120320 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 918720 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 993086 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 421750 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1735080 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 456120 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 0 | Under Maintenance
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 519173 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1489.2 | 32868950
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 10 | 227520 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 8150 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 164 | 2265600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 1317600 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 362440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 199920 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 527400 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 343.5 | 4908630
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 880000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 927840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3500181 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 674688 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1832640 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 4566200 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 428000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 382104 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 20 | 57030 | Partial Shutdown due to maintenance
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 349 | 8779000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7677400 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1235 | 29705083
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 859 | 21950545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 34 | 61920 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 51 | 95744 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 701280 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 703440 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 975 | 21730910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1954 | 45243839
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 266 | 6413091 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 43872 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 214883 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 108 | 2609000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1115 | 22945454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5178230 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 14 | 45600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5869000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4557 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2056 | 43323687.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 352691 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 25 | 177043 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 255802 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 182 | 4305182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 168 | 4223900 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 172 | 4116624 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9283636 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 222940 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 8 | 68371 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 817056 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1507296 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 933312 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34020 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 755.73 | 16985455 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 427504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 825300 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2153.73 | 44536132
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1324799 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 110 | 3276000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1512153 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31845.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1355944 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 174524 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1226880 | -
Rangpur Area Total |  |  |  |  | 950 | 396 | 8902145.24
Eastern Grid Total |  |  |  |  | 16921.242 | 8726.2 | 175443904.44
Western Grid Total |  |  |  |  | 11614.5 | 6559.73 | 142005803.79
National Grid Total |  |  |  |  | 28535.742 | 15285.93 | 317449708.23
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 13-04-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10009.13 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4649 | MW
i) Dhaka area |  |  | 5231.73 |  | MW | i) Khulna area |  |  |  | 1874.5 | MW
ii) Chattogram area |  |  | 1545.9 |  | MW | ii) Barishal area |  |  |  | 502.7 | MW
iii) Cumilla area |  |  | 1462.5 |  | MW | iii) Rajshahi area |  |  |  | 1515.8 | MW
iv) Mymensingh area |  |  | 1171 |  | MW | iv) Rangpur area |  |  |  | 756 | MW
v) Sylhet area |  |  | 598 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14658.13 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 75 | 19:00 | 133 | Patuakhali | 81.5 | 22:00
2 | AKSML | 113.7 | 12:00 | 68 | Jaldhaka | 63 | 19:30 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 38 | 00:00 | 69 | Jamalpur | 132 | 19:00 | 135 | Postogola | 54 | 19:00
4 | Agargaon | 117 | 16:00 | 70 | Jashore | 153 | 19:30 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 100 | 14:00 | 71 | Jhenaidah | 139 | 19:00 | 137 | Purbasadipur | 112 | 00:00
6 | Amnura | 43 | 00:00 | 72 | Joydebpur | 149 | 16:00 | 138 | Rahanpur | 32 | 00:00
7 | Ashuganj | 102 | 00:00 | 73 | Joypurhat | 68 | 02:00 | 139 | Rahim | 43 | 15:00
8 | BSRM | 202 | 19:30 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 84 | 19:00
9 | Bagerhat | 95 | 19:00 | 75 | KSRM | 16 | 23:00 | 141 | Rajendrapur | 142 | 16:00
10 | Bajitpur | 59 | 22:00 | 76 | Kabirpur | 247 | 21:00 | 142 | Rajshahi | 113 | 00:00
11 | Bakulia | 102 | 19:30 | 77 | Kachua | 89 | 20:00 | 143 | Rajshahi-230 | 91 | 00:00
12 | Banani | 43.2 | 14:00 | 78 | Kallyanpur | 108 | 00:00 | 144 | Ramganj | 116 | 22:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kalurghat | 42 | 15:00 | 145 | Rampur | 45 | 00:00
14 | Barapukuria | 68 | 02:00 | 80 | Kamrangirchar | 64.8 | 16:00 | 146 | Rangamati | 16 | 18:30
15 | Barguna | 22 | 21:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 138 | 19:00
16 | Barishal | 118 | 20:00 | 82 | Kasba | 40 | 22:00 | 148 | Ruppur | 7 | 16:00
17 | Barishal-230 | 114 | 19:30 | 83 | Kazla | 93 | 21:00 | 149 | SSM | 12 | 04:00
18 | Baroaulia | 64 | 11:00 | 84 | Keranigonj | 77 | 19:00 | 150 | Saidpur | 103 | 00:00
19 | Baroirhat | 71 | 20:00 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 143 | 22:00
20 | Bashundhara | 192 | 19:00 | 86 | Khulna | 73 | 00:00 | 152 | Satmasjid | 104 | 13:00
21 | BashundharaCement | 12 | 00:00 | 87 | Khulshi | 189 | 18:30 | 153 | Savar | 218 | 12:00
22 | Beanibazar | 72 | 19:00 | 88 | Kishoreganj | 138 | 21:00 | 154 | SevenRings | 9.4 | 10:00
23 | Benapole | 72 | 19:00 | 89 | Kodda | 297 | 23:00 | 155 | ShahCement | 33 | 00:00
24 | Bhaluka | 159 | 18:00 | 90 | Kulaura | 48 | 18:30 | 156 | Shahjadpur | 91 | 19:00
25 | Bhandaria | 56 | 22:00 | 91 | Kurigram | 54 | 01:00 | 157 | Shahjibazar | 132 | 21:00
26 | Bhangura | 45 | 19:00 | 92 | Kushtia | 148 | 19:00 | 158 | Shahmirpur | 65 | 00:00
27 | Bheramara(GK) | 65 | 00:00 | 93 | Lalbag | 65 | 13:00 | 159 | Shariatpur | 88 | 21:00
28 | Bhulta | 233 | 22:00 | 94 | Lalmonirhat | 48 | 02:00 | 160 | Sherpur | 126 | 01:00
29 | Bog-Sherpur | 74 | 19:00 | 95 | MI_Cement | 18.1 | 18:30 | 161 | Shikalbaha | 25 | 00:00
30 | Bogura | 166 | 00:00 | 96 | Madanganj | 42 | 17:00 | 162 | Shitalakhya | 85.2 | 16:00
31 | Borhanuddin | 95 | 21:00 | 97 | Madaripur | 124 | 21:00 | 163 | Sholosohor | 44 | 15:00
32 | Brahmanbaria | 139 | 22:00 | 98 | Madartek | 90.08 | 00:00 | 164 | Shyampur | 166 | 13:00
33 | Cantonment | 118 | 13:00 | 99 | Madunaghat | 57 | 19:00 | 165 | Siddhirganj | 120 | 07:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 69 | 19:00 | 166 | Sirajganj | 120 | 19:00
35 | Chandpur | 74 | 19:00 | 101 | Mahasthangarh | 76 | 02:00 | 167 | Sonargaon | 102 | 08:00
36 | Chandraghona | 39 | 18:30 | 102 | Manikganj | 140 | 19:30 | 168 | Sreemongol | 75 | 23:00
37 | Chapai | 68 | 21:00 | 103 | Maniknagar | 75 | 17:00 | 169 | Sreepur | 110 | 19:00
38 | Charsaidpur | 44 | 16:00 | 104 | Matarbari | 48 | 01:00 | 170 | Srinagar | 49.2 | 22:00
39 | Chauddagram | 80 | 18:30 | 105 | Matuail | 66 | 16:00 | 171 | Sunamganj | 52 | 21:00
40 | Chhatak | 36 | 19:00 | 106 | Millgate | 85 | 16:00 | 172 | Sylhet | 50 | 21:00
41 | Chowmuhani | 233 | 19:00 | 107 | Mirpur | 135 | 16:00 | 173 | Sylhet-132 | 126 | 18:30
42 | Chuadanga | 115 | 00:00 | 108 | Mirsorai | 10 | 19:00 | 174 | TK | 37 | 22:00
43 | Coxsbazar | 136 | 20:00 | 109 | Mirzapur | 50 | 14:00 | 175 | Tangail | 212 | 19:00
44 | Cumilla(N) | 178 | 00:00 | 110 | Mithapukur | 58 | 02:00 | 176 | Thakurgaon | 81 | 00:00
45 | Cumilla(S) | 181 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 138 | 11:00
46 | Daudkandi | 161 | 20:00 | 112 | Mogbazar | 155 | 15:00 | 178 | Ullahpara | 48 | 18:30
47 | Dhaka | 60 | 13:00 | 113 | Mongla | 41 | 12:00 | 179 | Ullon | 48 | 00:00
48 | Dhamrai | 132 | 18:30 | 114 | Motijheel | 40 | 13:00 | 180 | Uttara | 87 | 16:00
49 | Dhanmondi | 153 | 13:00 | 115 | Muktagacha | 37 | 20:00 | 181 | UttaraNew | 47 | 00:00
50 | Dohazari | 106 | 20:00 | 116 | Munshiganj | 113 | 23:00 | 182 | Zigatola | 70 | 16:00
51 | Faridpur | 167 | 19:30 | 117 | Muradnagar | 32 | 15:00
52 | Fatullah | 100 | 16:00 | 118 | Mymensingh | 206 | 00:00
53 | Fenchuganj | 39 | 17:00 | 119 | Naogaon | 138 | 01:00
54 | Feni | 126 | 18:30 | 120 | Narail | 64 | 19:00
55 | GPH | 33 | 04:00 | 121 | Narinda | 72 | 13:00
56 | Ghatail | 96 | 19:30 | 122 | Narshingdi | 179 | 23:00
57 | Ghorashal | 21 | 13:00 | 123 | Natore | 157 | 20:00
58 | Ghorashal-230 | 88 | 00:00 | 124 | Nawabganj | 62.6 | 20:00
59 | Goalpara | 34 | 01:00 | 125 | Netrakona | 124 | 22:00
60 | Gollamari | 102 | 19:30 | 126 | New | 84.5 | 16:00
61 | Gopalganj | 116 | 22:00 | 127 | Niamatpur | 106 | 01:00
62 | Gulshan | 124 | 15:00 | 128 | Noapara | 48 | 19:00
63 | Halishahar | 81 | 16:00 | 129 | PHP | 8 | 01:00
64 | HaripurSBU | 162 | 16:00 | 130 | Pabna | 122 | 19:30
65 | Hasnabad | 85 | 18:30 | 131 | Palashbari | 129 | 01:00
66 | Hathazari | 92 | 18:30 | 132 | Panchagarh | 46 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 13-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14707.7 | 280 |  | 15000.3
1:00 | 14541.7 | 200 |  | 14750.7
2:00 | 14116.7 | 128 |  | 14250.7
3:00 | 13569.2 | 106 |  | 13680.2
4:00 | 12618 | 97 |  | 12719
5:00 | 11845 | 76 |  | 11924
6:00 | 11137.69 | 0 |  | 11137.69
7:00 | 10339.16 | 0 |  | 10339.16
8:00 | 9714.5 | 0 |  | 9714.5
9:00 | 9883.58 | 0 |  | 9883.58
10:00 | 10686.42 | 0 |  | 10686.42
11:00 | 11220.29 | 0 |  | 11220.29
12:00 | 12247.34 | 0 |  | 12247.34
13:00 | 13215.38 | 32 |  | 13248.38
14:00 | 13506.26 | 78 |  | 13588.26
15:00 | 13628.06 | 100 |  | 13732.06
16:00 | 13954.64 | 152 |  | 14113.64
17:00 | 13970.79 | 61 |  | 14034.79
18:00 | 13509.48 | 41 |  | 13552.48
19:00 | 14910.2 | 87 |  | 15001.2
19:30 | 15198.89 | 79 |  | 15281.89
20:00 | 15285.93 | 92 |  | 15381.93
21:00 | 15057.78 | 61 |  | 15121.53
22:00 | 14910.74 | 58 |  | 14971.74
23:00 | 14810.12 | 59 |  | 14872.12
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 13-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8208.7 | 6499 | 14707.7 | DAILY GENERATION CURVE
00:30 | 8151.2 | 6473.5 | 14624.7
01:00 | 8093.7 | 6448 | 14541.7 | 13-04-2025
01:30 | 7969.7 | 6359.5 | 14329.2
02:00 | 7845.7 | 6271 | 14116.7
02:30 | 7706.45 | 6136.5 | 13842.95
03:00 | 7567.2 | 6002 | 13569.2
03:30 | 7214.1 | 5879.5 | 13093.6
04:00 | 6861 | 5757 | 12618
04:30 | 6697 | 5534.5 | 12231.5
05:00 | 6533 | 5312 | 11845
05:30 | 6363.775 | 5127.57 | 11491.345
06:00 | 6194.55 | 4943.14 | 11137.69
06:30 | 5853.275 | 4885.15 | 10738.425
07:00 | 5512 | 4827.16 | 10339.16
07:30 | 5323.515 | 4703.315 | 10026.83
08:00 | 5135.03 | 4579.47 | 9714.5
08:30 | 5136.855 | 4662.185 | 9799.04
09:00 | 5138.68 | 4744.9 | 9883.58
09:30 | 5349.2 | 4935.8 | 10285
10:00 | 5559.72 | 5126.7 | 10686.42
10:30 | 5738.715 | 5214.64 | 10953.355
11:00 | 5917.71 | 5302.58 | 11220.29
11:30 | 6227.305 | 5506.51 | 11733.815
12:00 | 6536.9 | 5710.44 | 12247.34
12:30 | 6877.395 | 5853.965 | 12731.36
13:00 | 7217.89 | 5997.49 | 13215.38
13:30 | 7274.725 | 6086.095 | 13360.82
14:00 | 7331.56 | 6174.7 | 13506.26
14:30 | 7451.125 | 6116.035 | 13567.16
15:00 | 7570.69 | 6057.37 | 13628.06
15:30 | 7746.3 | 6045.05 | 13791.35
16:00 | 7921.91 | 6032.73 | 13954.64
16:30 | 7921.655 | 6041.06 | 13962.715
17:00 | 7921.4 | 6049.39 | 13970.79
17:30 | 7791.515 | 5948.62 | 13740.135
18:00 | 7661.63 | 5847.85 | 13509.48
18:30 | 8124.665 | 6085.175 | 14209.84
19:00 | 8587.7 | 6322.5 | 14910.2
19:30 | 8701.2 | 6497.69 | 15198.89
20:00 | 8726.2 | 6559.73 | 15285.93
20:30 | 8635.2 | 6536.655 | 15171.855 |  | Executive Engineer
21:00 | 8544.2 | 6513.58 | 15057.78 |  | Network Operation Division
21:30 | 8452.2 | 6532.06 | 14984.26
22:00 | 8360.2 | 6550.54 | 14910.74
22:30 | 8342.7 | 6517.73 | 14860.43
23:00 | 8325.2 | 6484.92 | 14810.12

## En-Curve
QF-LDC-12
Date | 13-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3652 | 1826 | 907 | 0 | 44 | 725 | 46 | 4169 | 0 | 811 | 2527.7 | 0 | 0 | 0 | 280 | DAILY ENERGY CURVE
00:30 | 3651.5 | 1828 | 906.5 | 0 | 45 | 738 | 46 | 4123.5 | 0 | 775 | 2511.2 | 0 | 0 | 0 | 240 | 13-04-2025
01:00 | 3651 | 1830 | 906 | 0 | 46 | 751 | 46 | 4078 | 0 | 739 | 2494.7 | 0 | 0 | 0 | 200
01:30 | 3657 | 1833 | 906 | 0 | 45 | 752 | 45.5 | 4029 | 0 | 640.5 | 2421.2 | 0 | 0 | 0 | 164 | Energy Generated | 317.4497 |  | MKWHr
02:00 | 3663 | 1836 | 906 | 0 | 44 | 753 | 45 | 3980 | 0 | 542 | 2347.7 | 0 | 0 | 0 | 128 | Energy not Served | 1.708 |  | MKWHr
02:30 | 3672.5 | 1825.5 | 907.5 | 0 | 44 | 753 | 44.5 | 3981.5 | 0 | 463 | 2151.45 | 0 | 0 | 0 | 117 | Total Energy Requirement | 319.1577 |  | MKWHr
03:00 | 3682 | 1815 | 909 | 0 | 44 | 753 | 44 | 3983 | 0 | 384 | 1955.2 | 0 | 0 | 0 | 106
03:30 | 3638 | 1785.5 | 908.5 | 0 | 44 | 752 | 43.5 | 3982 | 0 | 308 | 1632.1 | 0 | 0 | 0 | 101.5
04:00 | 3594 | 1756 | 908 | 0 | 44 | 751 | 43 | 3981 | 0 | 232 | 1309 | 0 | 0 | 0 | 97
04:30 | 3518 | 1748 | 909 | 0 | 40 | 752.5 | 43.5 | 3865 | 0 | 223.5 | 1132 | 0 | 0 | 0 | 86.5
05:00 | 3442 | 1740 | 910 | 0 | 36 | 754 | 44 | 3749 | 0 | 215 | 955 | 0 | 0 | 0 | 76
05:30 | 3373.5 | 1740 | 910 | 0 | 34 | 694.5 | 44.5 | 3648.5 | 2.845 | 190.5 | 853 | 0 | 0 | 0 | 38
06:00 | 3305 | 1740 | 910 | 0 | 32 | 635 | 45 | 3548 | 5.69 | 166 | 751 | 0 | 0 | 0 | 0
06:30 | 3218 | 1635.5 | 909.5 | 0 | 35 | 598.5 | 45.5 | 3532 | 36.425 | 107.5 | 619 | 0 | 0 | 1.5 | 0
07:00 | 3131 | 1531 | 909 | 0 | 38 | 562 | 46 | 3516 | 67.16 | 49 | 487 | 0 | 0 | 3 | 0
07:30 | 3125 | 1475 | 886 | 0 | 38 | 564.5 | 46 | 3288 | 149.33 | 24.5 | 429 | 0 | 0 | 1.5 | 0
08:00 | 3119 | 1419 | 863 | 0 | 38 | 567 | 46 | 3060 | 231.5 | 0 | 371 | 0 | 0 | 0 | 0
08:30 | 3141 | 1446 | 863 | 0 | 37 | 564.5 | 46 | 3020 | 316.04 | 0 | 365.5 | 0 | 0 | 0 | 0
09:00 | 3163 | 1473 | 863 | 0 | 36 | 562 | 46 | 2980 | 400.58 | 0 | 360 | 0 | 0 | 0 | 0
09:30 | 3298.5 | 1554 | 886.5 | 0 | 36 | 562.365 | 46 | 2998.5 | 513.635 | 0 | 388 | 0 | 0 | 1.5 | 0
10:00 | 3434 | 1635 | 910 | 0 | 36 | 562.73 | 46 | 3017 | 626.69 | 0 | 416 | 0 | 0 | 3 | 0
10:30 | 3481 | 1706.5 | 910 | 0 | 38 | 540.865 | 46 | 3105 | 648.99 | 15.5 | 460 | 0 | 0 | 1.5 | 0
11:00 | 3528 | 1778 | 910 | 0 | 40 | 519 | 46 | 3193 | 671.29 | 31 | 504 | 0 | 0 | 0 | 0
11:30 | 3608.5 | 1815.5 | 910 | 0 | 40 | 561.5 | 46 | 3381 | 679.315 | 53 | 639 | 0 | 0 | 0 | 0
12:00 | 3689 | 1853 | 910 | 0 | 40 | 604 | 46 | 3569 | 687.34 | 75 | 774 | 0 | 0 | 0 | 0
12:30 | 3678.5 | 1851 | 910 | 0 | 41 | 678.5 | 46 | 3654 | 665.36 | 150.5 | 1050.5 | 0 | 0 | 6 | 16
13:00 | 3668 | 1849 | 910 | 0 | 42 | 753 | 46 | 3739 | 643.38 | 226 | 1327 | 0 | 0 | 12 | 32
13:30 | 3620.5 | 1816 | 909.5 | 0 | 39 | 757.5 | 44.5 | 3831.5 | 604.82 | 252 | 1470 | 0 | 0 | 15.5 | 55
14:00 | 3573 | 1783 | 909 | 0 | 36 | 762 | 43 | 3924 | 566.26 | 278 | 1613 | 0 | 0 | 19 | 78
14:30 | 3603 | 1787.5 | 909 | 0 | 37 | 760.795 | 42 | 3852.5 | 511.765 | 287.5 | 1759.1 | 0 | 0 | 17 | 89
15:00 | 3633 | 1792 | 909 | 0 | 38 | 759.59 | 41 | 3781 | 457.27 | 297 | 1905.2 | 0 | 0 | 15 | 100
15:30 | 3610.5 | 1797 | 909 | 0 | 39 | 759.64 | 40.5 | 3770.5 | 350.01 | 334.5 | 2173.2 | 0 | 0 | 7.5 | 126
16:00 | 3588 | 1802 | 909 | 0 | 40 | 759.69 | 40 | 3760 | 242.75 | 372 | 2441.2 | 0 | 0 | 0 | 152
16:30 | 3593.5 | 1793.3 | 909.5 | 0 | 40 | 756.625 | 40 | 3738 | 186.34 | 447 | 2455.95 | 0 | 0 | 2.5 | 106.5
17:00 | 3599 | 1784.6 | 910 | 0 | 40 | 753.56 | 40 | 3716 | 129.93 | 522 | 2470.7 | 0 | 0 | 5 | 61
17:30 | 3477 | 1720.3 | 908 | 0 | 37 | 755.475 | 40 | 3669 | 71.66 | 583.5 | 2475.7 | 0 | 0 | 2.5 | 51
18:00 | 3355 | 1656 | 906 | 0 | 34 | 757.39 | 40 | 3622 | 13.39 | 645 | 2480.7 | 0 | 0 | 0 | 41
18:30 | 3481 | 1733 | 894 | 0 | 36 | 755.945 | 40 | 3775.5 | 6.695 | 740 | 2745.7 | 0 | 0 | 2 | 64
19:00 | 3607 | 1810 | 882 | 0 | 38 | 754.5 | 40 | 3929 | 0 | 835 | 3010.7 | 0 | 0 | 4 | 87
19:30 | 3603 | 1814 | 858 | 0 | 38 | 757.69 | 40 | 4142 | 0 | 864 | 3081.2 | 0 | 0 | 1 | 79
20:00 | 3607 | 1820 | 859 | 0 | 40 | 755.73 | 46 | 4215 | 0 | 904 | 3039.2 | 0 | 0 | 0 | 92
20:30 | 3625.5 | 1835 | 882 | 0 | 37 | 758.155 | 46 | 4245 | 0 | 853 | 2890.2 | 0 | 0 | 0 | 76.5
21:00 | 3644 | 1850 | 905 | 0 | 34 | 760.58 | 46 | 4275 | 0 | 802 | 2741.2 | 0 | 0 | 0 | 61
21:30 | 3600 | 1841.5 | 906 | 0 | 34 | 758.56 | 46 | 4312 | 0 | 796 | 2690.2 | 0 | 0 | 0 | 59.5
22:00 | 3556 | 1833 | 907 | 0 | 34 | 756.54 | 46 | 4349 | 0 | 790 | 2639.2 | 0 | 0 | 0 | 58
22:30 | 3577 | 1846.5 | 906.5 | 0 | 35 | 756.23 | 46 | 4348.5 | 0 | 772.5 | 2572.2 | 0 | 0 | 0 | 58.5
23:00 | 3598 | 1860 | 906 | 0 | 36 | 755.92 | 46 | 4348 | 0 | 755 | 2505.2 | 0 | 0 | 0 | 59
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 13-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 02:00 | 383 | 12:00 | Payra | 414 | 06:00 | 408 | 21:00
Ashuganj | 406 | 8:00 | 383 | 11:00 | Rahanpur | 423 | 05:00 | 400 | 21:00
Bhulta | 400 | 00:00 | 383 | 15:00 | Rampal | 406 | 06:00 | 391 | 23:00
Bibiana | 388 | 08:00 | 379 | 15:00
BIPTC | 404 | 09:00 | 392 | 00:00
Bogura | 426 | 06:00 | 397 | 13:00
Gopalganj | 403 | 08:00 | 389 | 23:00
Kaliakoir | 371 | 08:00 | 355 | 10:00
Madunaghat | 403 | 20:00 | 392 | 12:00
Meghnaghat | 394 | 01:00 | 383 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 04:00 | 221 | 12:00 | Keranigonj | 228 | 07:00 | 219 | 12:00
AKSML | 237 | 02:00 | 225 | 12:00 | Khulna(S) | 233 | 06:00 | 218 | 22:00
Aminbazar | 230 | 03:00 | 223 | 10:00 | Madunaghat | 237 | 00:00 | 138 | 02:00
Ashuganj | 232 | 00:00 | 223 | 12:00 | Madunaghat-400 | 239 | 02:00 | 229 | 12:00
Ashuganj-400 | 232 | 00:00 | 223 | 12:00 | Maniknagar | 226 | 02:00 | 217 | 15:00
Baghabari | 236 | 05:00 | 226 | 11:00 | Meghnaghat | 234 | 06:00 | 227 | 15:00
Barapukuria | 235 | 05:00 | 213 | 02:00 | Meghnaghat-400 | 229 | 00:00 | 221 | 12:00
Barapukuria-230 | 235 | 05:00 | 213 | 02:00 | Mirsorai | 238 | 02:00 | 221 | 12:00
Barishal | 235 | 06:00 | 225 | 23:00 | Rajshahi | 235 | 07:00 | 222 | 10:00
Bheramara | 235 | 04:00 | 222 | 15:00 | Rampal | 232 | 06:00 | 219 | 21:00
Bhulta | 227 | 00:00 | 217 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 222 | 07:00 | 217 | 18:30 | Rampura | 226 | 01:00 | 215 | 12:00
BIPTC | 236 | 04:00 | 222 | 23:00 | Shikalbaha | 237 | 23:00 | 226 | 11:00
Bogura | 240 | 06:00 | 224 | 13:00 | Shyampur | 228 | 04:00 | 219 | 12:00
Bogura-400 | 240 | 06:00 | 223 | 13:00 | Siddhirganj | 228 | 00:00 | 220 | 15:00
Borhanuddin | 240 | 05:00 | 233 | 21:00 | Sirajgonj | 243 | 07:00 | 234 | 18:30
BSRM | 235 | 16:00 | 224 | 12:00 | Sreepur | 233 | 07:00 | 222 | 12:00
Cumilla(N) | 223 | 01:00 | 217 | 15:00 | Tongi | 227 | 04:00 | 215 | 11:00
Faridpur | 229 | 08:00 | 220 | 22:00
Fenchuganj | 225 | 06:00 | 220 | 15:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 228 | 01:00 | 217 | 12:00
Gopalganj | 231 | 08:00 | 222 | 22:00
GPH | 236 | 01:00 | 227 | 12:00
Haripur | 227 | 00:00 | 219 | 12:00
Hasnabad | 228 | 03:00 | 218 | 12:00
Hathazari | 236 | 00:00 | 228 | 10:00
Ishurdi | 236 | 04:00 | 225 | 15:00
Jhenaidah | 230 | 06:00 | 213 | 23:00
Kaliakoir | 230 | 08:00 | 221 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 04:00 | 123 | 11:00 | Madartek | 132 | 07:00 | 121 | 12:00
Agargaon | 133 | 07:00 | 126 | 11:00 | Madunaghat | 137 | 02:00 | 131 | 11:00
Agrabad | 135 | 01:00 | 128 | 11:00 | Magura | 135 | 07:00 | 120 | 22:00
AKS | 132 | 00:00 | 127 | 12:00 | Mahasthangarh | 140 | 06:00 | 128 | 13:00
Aminbazar | 131 | 18:00 | 127 | 12:00 | Manikganj | 130 | 08:00 | 119 | 10:00
Amnura | 142 | 05:00 | 127 | 13:00 | Maniknagar | 130 | 06:00 | 123 | 12:00
Ashuganj | 139 | 07:00 | 135 | 11:00 | Matarbari | 124 | 15:00 | 114 | 12:00
Bagerhat | 135 | 06:00 | 117 | 19:00 | Matuail | 133 | 00:00 | 126.6 | 12:00
Bajitpur | 136 | 08:00 | 128 | 00:00 | Millgate | 131 | 01:00 | 121 | 12:00
Bakulia | 137 | 00:00 | 129 | 11:00 | Mirpur | 130 | 07:00 | 124 | 11:00
Banani | 132 | 01:00 | 121 | 15:00 | Mirzapur | 135 | 08:00 | 121 | 10:00
Bangabhaban | 130 | 01:00 | 122 | 12:00 | Mithapukur | 142 | 05:00 | 125 | 13:00
Barapukuria | 140 | 03:00 | 128 | 13:00 | MI_Cement | 133 | 18:30 | 126 | 12:00
Barguna | 135 | 08:00 | 129 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 07:00 | 124 | 22:00 | Mogbazar | 132 | 04:00 | 122 | 12:00
Barishal-230 | 131 | 06:00 | 124 | 19:30 | Mongla | 137 | 06:00 | 120 | 18:30
Baroaulia | 135 | 16:00 | 129 | 12:00 | Motijheel | 130 | 01:00 | 122 | 12:00
Baroirhat | 123 | 18:00 | 119 | 14:00 | Muktagacha | 138 | 07:00 | 117 | 00:00
Bashundhara | 131 | 00:00 | 121 | 11:00 | Munshiganj | 132 | 00:00 | 127 | 11:00
BashundharaCement | 139 | 18:30 | 127 | 15:00 | Muradnagar | 127 | 09:00 | 120 | 00:00
Beanibazar | 131 | 10:00 | 125 | 19:00 | Mymensingh | 139 | 07:00 | 117 | 00:00
Benapole | 133 | 07:00 | 117 | 23:00 | Naogaon | 141 | 06:00 | 126 | 13:00
Bhaluka | 137 | 08:00 | 126 | 15:00 | Narail | 136 | 06:00 | 121 | 19:30
Bhandaria | 125 | 07:00 | 114 | 21:00 | Narinda | 130 | 7:00 | 123 | 12:00
Bhangura | 136 | 05:00 | 127 | 19:30 | Narshingdi | 131 | 08:00 | 118 | 15:00
Bheramara | 137 | 05:00 | 128 | 21:00 | Natore | 135 | 04:00 | 127 | 22:00
Bheramara(GK) | 136 | 04:00 | 128 | 19:00 | Nawabganj | 132 | 05:00 | 126 | 12:00
Bhulta | 126 | 00:00 | 120 | 11:00 | Netrakona | 136 | 08:00 | 116 | 18:30
Bog-Sherpur | 140 | 06:00 | 128 | 13:00 | New | 133 | 08:00 | 124 | 10:00
Bogura | 142 | 06:00 | 130 | 12:00 | Niamatpur | 145 | 05:00 | 131 | 13:00
Bogura-230 | 141 | 06:00 | 130 | 13:00 | Noapara | 137 | 06:00 | 122 | 19:00
Brahmanbaria | 130 | 09:00 | 122 | 14:00 | Pabna | 136 | 07:00 | 127 | 19:00
Cantonment | 132 | 04:00 | 126 | 11:00 | Palashbari | 138 | 05:00 | 126 | 21:00
Chandina | 128 | 01:00 | 123 | 12:00 | Panchagarh | 142 | 05:00 | 124 | 13:00
Chandpur | 125 | 01:00 | 118 | 03:00 | Patuakhali | 135 | 05:00 | 130 | 15:00
Chandraghona | 136 | 01:00 | 130 | 11:00 | Payra | 136 | 05:00 | 133 | 22:00
Chapai | 141 | 04:00 | 128 | 13:00 | PHP | 122 | 01:00 | 116 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 05:00 | 127 | 11:00 | Postogola | 134 | 01:00 | 129 | 12:00
Chauddagram | 123 | 01:00 | 116 | 13:00 | Purbachal | 132 | 03:00 | 121 | 12:00
Chhatak | 134 | 09:00 | 122 | 17:00 | Purbasadipur | 144 | 05:00 | 120 | 13:00
Chowmuhani | 116 | 01:00 | 108 | 18:00 | Rahanpur | 146 | 06:00 | 133 | 13:00
Chuadanga | 132 | 08:00 | 117 | 23:00 | Rahanpur-400 | 145 | 05:00 | 133 | 19:30
Coxsbazar | 120 | 13:00 | 115 | 07:00 | Rahim | 133 | 00:00 | 127 | 12:00
Cumilla(N) | 127 | 01:00 | 124 | 12:00 | Rajbari | 136 | 08:00 | 127 | 23:00
Cumilla(S) | 133 | 04:00 | 114 | 05:00 | Rajendrapur | 159 | 05:00 | 120 | 13:00
Daudkandi | 126 | 09:00 | 120 | 11:00 | Rajshahi | 135 | 06:00 | 128 | 23:00
Dhaka | 132 | 03:00 | 122 | 15:00 | Rajshahi-230 | 138 | 05:00 | 120 | 13:00
Dhamrai | 134 | 08:00 | 124 | 15:00 | Ramganj | 117 | 18:00 | 109 | 18:30
Dhanmondi | 133.5 | 00:00 | 127 | 12:00 | Rampur | 136 | 02:00 | 128 | 12:00
Dohazari | 132 | 19:00 | 125 | 12:00 | Rampura | 132 | 04:00 | 121 | 15:00
Faridpur | 135 | 04:00 | 130 | 22:00 | Rangamati | 134 | 00:00 | 128 | 12:00
Fatullah | 133 | 07:00 | 127 | 12:00 | Rangpur | 141 | 05:00 | 126 | 00:00
Fenchuganj | 134 | 07:00 | 131 | 13:00 | Ruppur | 137 | 04:00 | 130 | 18:30
Feni | 123 | 18:00 | 117 | 02:00 | Saidpur | 140 | 04:00 | 124 | 13:00
Ghatail | 137 | 07:00 | 117 | 00:00 | Satkhira | 135 | 06:00 | 118 | 23:00
Ghorashal | 137 | 20:00 | 131 | 14:00 | Satmasjid | 132 | 04:00 | 125 | 12:00
Goalpara | 139 | 05:00 | 125 | 23:00 | Savar | 131 | 20:00 | 123 | 11:00
Gollamari | 139 | 05:00 | 127 | 23:00 | SevenRings | 139 | 01:00 | 130 | 12:00
Gopalganj | 136 | 06:00 | 127 | 21:00 | ShahCement | 133 | 06:00 | 127 | 11:00
Gopalganj-400 | 137 | 06:00 | 131 | 22:00 | Shahjadpur | 138 | 08:00 | 132 | 21:00
Gulshan | 131 | 04:00 | 121 | 15:00 | Shahjibazar | 134 | 09:00 | 124 | 15:00
Halishahar | 136 | 01:00 | 128 | 12:00 | Shahmirpur | 136 | 00:00 | 131 | 11:00
Haripur | 133 | 00:00 | 127 | 15:00 | Shariatpur | 134 | 06:00 | 125 | 21:00
HaripurSBU | 133 | 00:00 | 131 | 09:00 | Sherpur | 140 | 07:00 | 115 | 01:00
Hasnabad | 134 | 01:00 | 129 | 12:00 | Shikalbaha | 127 | 00:00 | 119 | 11:00
Hathazari | 136 | 00:00 | 132 | 10:00 | Shikalbaha-230 | 139 | 18:30 | 132 | 09:00
Ishurdi | 138 | 05:00 | 130 | 23:00 | Shitalakhya | 133 | 18:30 | 126 | 12:00
Jaldhaka | 139 | 04:00 | 121 | 13:00 | Sholosohor | 136 | 01:00 | 130 | 11:00
Jamalpur | 139 | 07:00 | 118 | 01:00 | Shyampur | 133 | 00:00 | 126 | 12:00
Jashore | 134 | 06:00 | 119 | 19:00 | Shyampur-230 | 132 | 00:00 | 127 | 12:00
Jhenaidah | 135 | 06:00 | 122 | 19:00 | Siddhirganj | 133 | 01:00 | 128 | 11:00
Jhenaidah-230 | 152 | 23:00 | 124 | 19:00 | Sirajganj | 137 | 07:00 | 125 | 19:00
Joydebpur | 133 | 01:00 | 124 | 11:00 | Sonargaon | 134 | 00:00 | 125 | 12:00
Joypurhat | 143 | 06:00 | 124 | 02:00 | Sreemongol | 134 | 09:00 | 125 | 23:00
Juldah | 137 | 17:00 | 132 | 10:00 | Sreepur | 137 | 07:00 | 129 | 15:00
Kabirpur | 135 | 08:00 | 120 | 14:00 | Srinagar | 132 | 01:00 | 126 | 14:00
Kachua | 123 | 01:00 | 116 | 19:00 | SSM | 140 | 02:00 | 132 | 13:00
Kaliakoir | 134 | 07:00 | 126 | 15:00 | Sunamganj | 132 | 08:00 | 122 | 18:30
Kallyanpur | 130 | 04:00 | 125 | 11:00 | Sylhet | 131 | 09:00 | 126 | 19:00
Kalurghat | 137 | 19:00 | 132 | 05:00 | Sylhet-132 | 132 | 09:00 | 127 | 18:30
Kamrangirchar | 136 | 08:00 | 126 | 15:00 | Tangail | 135 | 07:00 | 116 | 01:00
Kaptai | 139 | 19:00 | 133 | 12:00 | Thakurgaon | 144 | 03:00 | 122 | 13:00
Kasba | 127 | 09:00 | 120 | 00:00 | TK | 137 | 00:00 | 132 | 10:00
Kazla | 130 | 07:00 | 122 | 15:00 | Tongi | 135 | 04:00 | 125 | 11:00
Keranigonj | 133 | 04:00 | 126 | 18:30 | Ullahpara | 137 | 06:00 | 127 | 19:00
Khagrachori | 134 | 02:00 | 128 | 12:00 | Ullon | 132 | 04:00 | 122 | 12:00
Khulna | 138 | 06:00 | 124 | 22:00 | Uttara | 130 | 04:00 | 123 | 11:00
Khulna(S) | 139 | 05:00 | 127 | 23:00 | UttaraNew | 132 | 07:00 | 120 | 12:00
Khulshi | 134 | 01:00 | 129 | 07:00 | Zigatola | 133 | 06:00 | 127 | 12:00
Kishoreganj | 138 | 08:00 | 124 | 18:30
Kodda | 136 | 01:00 | 118 | 10:00
KSRM | 135 | 16:00 | 129 | 11:00
Kulaura | 134 | 09:00 | 129 | 18:30
Kurigram | 140 | 05:00 | 122 | 13:00
Kushtia | 135 | 05:00 | 125 | 19:30
Lalbag | 133 | 07:00 | 126 | 12:00
Lalmonirhat | 135 | 05:00 | 120 | 13:00
Madanganj | 132 | 00:00 | 113 | 19:30
Madaripur | 134 | 07:00 | 127 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division