## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 15-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-04-2025 | during | 15-04-2025 | during | 15-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 400 | 403 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 | 225 | GT-2 shut down for HRSG-2 tube leakage repair
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 297 | 280 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 93 | 98 | 208.13 | 208.13 | 100 | 100 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 316 | 320 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 98 | 8 | 102 | 102 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 10 | 35 | 53.97 | 53.97 | 35 | 35 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 31 | 95 | 149.36 | 149.36 | 144 | 144 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 18 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 20 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18.5 | 17 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 8 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 160 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 52 | 68 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 34 | 66 | 104 | 104 | 33 | 84 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 60 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 26 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 36 | 55 | 55 | 17 | 17 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 500 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 60 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2317.5 | 2870 | 5044.9 | 5106.9 | 3354.8 | 3381.8
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 46 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 146 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 12 | 105 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 56 | 64 | 72 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 68 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 33 | 100 | 100 | 100 | 33 | 33 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 39 | 37 | 5 | 21 | 5 | 21 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 25 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 4.52 | 0 | 4.52 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 30 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 8 | 68 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 72 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 9 | 0 | 8 | 1 | 8 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 161 | 161 | 155 | 155 | 160 | 160 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1785 | 2257 | 2992.24 | 2989.72 | 2930.24 | 2937.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 194 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 345 | 357 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 34 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 49 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 162 | 162 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 115 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 144 | 165 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 32 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 30 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 79 | 80 | 114 | 114 | 80 | 80 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 37 | 113 | 113 | 14 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 90 | 115 | 115 | 72 | 72 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 61 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1257 | 1509 | 2105.99 | 2035.99 | 1805.55 | 1759.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 14-04-2025 | during | 15-04-2025 | during | 15-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 11 | 22 | 157.5 | 157.5 | 23 | 23 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 101 | 145 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 85 | 96 | 115 | 115 | 103 | 103 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.77 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 23 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 260.77 | 298 | 601 | 549 | 444.5 | 392.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 39 | 33 | 33 | 33 | 33 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 152 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 25 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 14 | 20 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 75 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 366 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1250 | 1307 | 1602 | 1602 | 1533 | 1533
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 908 | 915 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 105 | 105 | 35 | 35 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 90.47 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 750 | 751 | 1234.2 | 1234.2 | 1234 | 1234 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1748.47 | 1719 | 3274.2 | 3176.2 | 2689.01 | 2591.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 287 | 286 | 530 | 530 | 200 | 200 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 108 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.51 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1982.51 | 2175 | 2701.12 | 2701.12 | 2359.12 | 2359.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 50 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 26 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 35 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 183 | 198 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 161 | 183 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 162 | 140 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 96 | 96 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 25 | 55 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.64 | 0 | 5 | 0 | 5.55 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 757 | 758 | 748 | 748 | 748 | 748 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.89 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 70 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1831.53 | 1979 | 2507.99 | 2341.99 | 2457.75 | 2291.2
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 56 | 58 | 58 | 60 | 60 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 116 | 112 | 110 | 110 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 40 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 90 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 33 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 165 | 0 | 166.94 | 0 | 166.94 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 418 | 366 | 633.34 | 430 | 685.34 | 482
System Total |  |  |  |  | 27566.2 | 28535.742 | 12850.78 | 14480 | 21462.78 | 20932.92 | 18259.31 | 17727.9
Forecast Scenario (15-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13350 |  | 0 |  | 13350
|  |  |  | 1:00 | 13210 |  | 0 |  | 13210
|  |  |  | 2:00 | 12650 |  | 0 |  | 12650
|  |  |  | 3:00 | 12300 |  | 0 |  | 12300
|  |  |  | 4:00 | 12110 |  | 0 |  | 12110
|  |  |  | 5:00 | 11900 |  | 0 |  | 11900
|  |  |  | 6:00 | 11450 |  | 0 |  | 11450
|  |  |  | 7:00 | 11630 |  | 0 |  | 11630
|  |  |  | 8:00 | 11810 |  | 0 |  | 11810
|  |  |  | 9:00 | 12290 |  | 0 |  | 12290
|  |  |  | 10:00 | 12570 |  | 0 |  | 12570
|  |  |  | 11:00 | 12930 |  | 0 |  | 12930
|  |  |  | 12:00 | 13380 |  | 0 |  | 13380
|  |  |  | 13:00 | 13880 |  | 0 |  | 13880
|  |  |  | 14:00 | 14150 |  | 0 |  | 14150
|  |  |  | 15:00 | 14180 |  | 0 |  | 14180
|  |  |  | 16:00 | 14120 |  | 0 |  | 14120
|  |  |  | 17:00 | 13730 |  | 0 |  | 13730
|  |  |  | 18:00 | 13160 |  | 0 |  | 13160
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 15020 |  | 0 |  | 15020
|  |  |  | 19:30 | 15070 |  | 0 |  | 15070
|  |  |  | 20:00 | 15040 |  | 0 |  | 15040
|  |  |  | 21:00 | 14760 |  | 0 |  | 14760
|  |  |  | 22:00 | 14270 |  | 0 |  | 14270
|  |  |  | 23:00 | 13560 |  | 0 |  | 13560
Probable Maximum Temperature: |  |  | 32.80°C
Probable Maximum Demand at Day Peak: |  |  | 13380.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15070.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15070.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 317.45 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:58 hrs on 15-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 14-04-2025 | [28 empty] | Date: | 14-04-2025 | [28 empty] | Date: | 14-04-2025 | [28 empty] | Date: | 14-04-2025 | [28 empty] | Date: | 14-04-2025 | [16 empty] | Date: | 14-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 36 | 122 | 144 | 262 | 40 | 35 | 144 | 0 | 96 | 225 | 267 | 500 | 0 | 55 | 0 | 328 | 38 | 0 | 0 | 142 | 16 | 7 | 0 | 0 | 17 | 30 | 13 | 0 | 0 | 102 | 72 | 0 | 32 | 50 | 0 | 46 | 110 | 20 | 160 | 54 | 0 | 0 | 25.5 | 105 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 162 | 0 | 359 | 0 | 50 | 182 | 31 | 0 | 70 | 200 | 15 | 19 | 80 | 38 | 52.2 | 0 | 46 | 15 | 320 | 348 | 36 | 40 | 0 | 154 | 22 | 0 | 83 | 30 | 0 | 18 | 172 | 54.5 | 104 | 154 | 8 | 0 | 0 | 12 | 8228.2 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 18 | 759.06 | 0 | 0 | 0 | 113 | 20 | 98 | 113 | 35 | 8 | 0 | 22 | 0 | 179 | 0 | 152 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 105 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 278 | 1170 | 0 | 6535.06 | 14763.26 | 82.37
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 18 | 120 | 130 | 262 | 0 | 35 | 144 | 0 | 73 | 225 | 296 | 500 | 0 | 55 | 0 | 330 | 39 | 0 | 0 | 108 | 16.8 | 7 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 102 | 64 | 0 | 32 | 50 | 0 | 46 | 68 | 22 | 160 | 54 | 0 | 0 | 0 | 68 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 162 | 0 | 359 | 0 | 51 | 182 | 32 | 0 | 50 | 200 | 15 | 19 | 80 | 32 | 52.2 | 0 | 46 | 15 | 320 | 348 | 36 | 40 | 0 | 151 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 54.5 | 49 | 98 | 8 | 0 | 0 | 12 | 7782.5 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 18 | 758.93 | 0 | 0 | 0 | 113 | 20 | 0 | 113 | 35 | 8 | 0 | 22 | 0 | 177 | 0 | 152 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 103 | 57 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 271 | 1170 | 0 | 6381.93 | 14164.43 | 82.36
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 18 | 100 | 146 | 195 | 0 | 35 | 144 | 0 | 54 | 225 | 295 | 500 | 0 | 55 | 0 | 330 | 39 | 0 | 0 | 90 | 16.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 40 | 0 | 32 | 50 | 0 | 45 | 68 | 23 | 160 | 17 | 0 | 0 | 0 | 68 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 162 | 0 | 359 | 0 | 51 | 182 | 32 | 0 | 50 | 200 | 9 | 19 | 80 | 32 | 52.2 | 0 | 46 | 15 | 320 | 348 | 36 | 40 | 0 | 151 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 25 | 49 | 96 | 10 | 0 | 0 | 12 | 7533 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 18 | 755.47 | 0 | 0 | 0 | 70 | 0 | 0 | 35 | 0 | 8 | 0 | 0 | 0 | 176 | 0 | 152 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 103 | 57 | 73 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 270 | 1170 | 0 | 6135.47 | 13668.47 | 82.36
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 18 | 87 | 98 | 45 | 0 | 35 | 144 | 0 | 16 | 225 | 282 | 500 | 0 | 55 | 0 | 334 | 39 | 0 | 0 | 90 | 16.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 0 | 32 | 50 | 0 | 43 | 68 | 24 | 160 | 0 | 0 | 0 | 0 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 162 | 0 | 359 | 0 | 52 | 182 | 32 | 0 | 50 | 200 | 9 | 19 | 80 | 32 | 52.2 | 0 | 46 | 15 | 320 | 368 | 36 | 40 | 0 | 153 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 49 | 96 | 10 | 0 | 0 | 12 | 7256 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1015 | 18 | 755.6 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 152 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 108 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 269 | 1170 | 0 | 5978.6 | 13234.6 | 82.35
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 35 | 18 | 87 | 98 | 15 | 0 | 35 | 144 | 0 | 16 | 225 | 290 | 500 | 0 | 55 | 0 | 335 | 40 | 0 | 0 | 90 | 16.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 0 | 22 | 50 | 0 | 41 | 68 | 25 | 160 | 0 | 0 | 0 | 0 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 162 | 0 | 360 | 0 | 52 | 182 | 32 | 0 | 50 | 200 | 9 | 19 | 80 | 30 | 52.2 | 0 | 47 | 15 | 320 | 348 | 36 | 40 | 0 | 151 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 49 | 96 | 10 | 0 | 0 | 12 | 7199 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 18 | 758.06 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 152 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 108 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 269 | 1100 | 0 | 5799.06 | 12998.06 | 82.5
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 17 | 18 | 87 | 98 | 0 | 0 | 35 | 144 | 0 | 16 | 225 | 296 | 500 | 0 | 55 | 0 | 335 | 40 | 0 | 0 | 90 | 16.8 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 0 | 42 | 34 | 27 | 160 | 0 | 0 | 0 | 0 | 34 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 162 | 0 | 360 | 0 | 52 | 182 | 32 | 0 | 50 | 200 | 9 | 19 | 80 | 30 | 52.2 | 0 | 46 | 15 | 320 | 348 | 36 | 40 | 0 | 151 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 49 | 96 | 10 | 0 | 0 | 12 | 6935 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 756.37 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 152 | 0 | 157 | 0 | 414 | 0 | 0 | 0 | 108 | 57 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 293 | 1000 | 0 | 5696.37 | 12631.37 | 82.34
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 18 | 84 | 98 | 0 | 0 | 35 | 35 | 0 | 16 | 225 | 283 | 500 | 0 | 55 | 0 | 335 | 40 | 0 | 1 | 70 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 36 | 0 | 44 | 34 | 29 | 160 | 0 | 0 | 0 | 0 | 34 | 151 | 0 | 0 | 0 | 1185 | 0 | 51 | 50 | 160 | 0 | 359 | 0 | 52 | 182 | 32 | 0 | 50 | 136 | 9 | 20 | 80 | 28 | 16 | 2 | 46 | 15 | 320 | 350 | 36 | 40 | 0 | 149 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 49 | 96 | 10 | 0 | 1.04 | 12 | 6607.04 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.67 | 855 | 0 | 757.71 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.06 | 181 | 0 | 152 | 0 | 162 | 0 | 414 | 0 | 0.08 | 0 | 108 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 3 | 0.02 | 0 | 274 | 10 | 110 | 220 | 0 | 290 | 900 | 0 | 5473.54 | 12080.58 | 82.34
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 18 | 70 | 98 | 0 | 0 | 35 | 35 | 0 | 16 | 225 | 303 | 500 | 0 | 0 | 0 | 333 | 40 | 0 | 5 | 70 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 1 | 46 | 34 | 30 | 160 | 0 | 0 | 0 | 0 | 34 | 150 | 0 | 0 | 0 | 1106 | 5 | 51 | 50 | 162 | 0 | 359 | 0 | 52 | 184 | 32 | 0 | 50 | 136 | 9 | 19 | 80 | 22 | 16 | 14 | 46 | 15 | 320 | 380 | 36 | 40 | 0 | 133 | 14 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 68 | 124 | 10 | 0 | 8.78 | 12 | 6542.78 | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.44 | 858 | 0 | 752.84 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 9.81 | 181 | 0 | 152 | 0 | 167 | 0 | 414 | 0 | 0.71 | 0 | 108 | 58 | 0 | 3 | 34 | 0 | 0 | 1.4 | 30 | 0.08 | 0 | 200 | 10 | 110 | 220 | 0 | 291 | 800 | 0 | 5375.28 | 11918.06 | 82.33
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 17 | 70 | 82 | 0 | 0 | 17 | 35 | 0 | 23 | 225 | 288 | 500 | 0 | 0 | 0 | 330 | 40 | 0 | 9 | 70 | 21 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 12 | 2 | 46 | 34 | 30 | 160 | 0 | 0 | 0 | 0 | 34 | 151 | 0 | 0 | 0 | 1107 | 11 | 51 | 50 | 162 | 0 | 359 | 0 | 52 | 184 | 32 | 0 | 50 | 85 | 9 | 19 | 52 | 26 | 16 | 29 | 46 | 12 | 320 | 340 | 36 | 40 | 0 | 132 | 14 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 81 | 99 | 10 | 1 | 12.58 | 12 | 6404.58 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.78 | 857 | 0 | 753 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 24.06 | 179 | 0 | 152 | 0 | 165 | 0 | 414 | 0 | 1.99 | 0 | 109 | 58 | 0 | 7 | 34 | 0 | 0 | 3.5 | 50 | 0.25 | 0 | 200 | 8 | 108 | 220 | 0 | 290 | 800 | 0 | 5394.58 | 11799.16 | 82.33
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 17 | 65 | 48 | 0 | 0 | 0 | 0 | 0 | 31 | 225 | 302 | 583 | 0 | 0 | 0 | 300 | 40 | 0 | 17 | 52 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 0 | 46 | 0 | 30 | 160 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1101 | 4 | 51 | 0 | 162 | 0 | 354 | 0 | 51 | 192 | 32 | 0 | 50 | 85 | 9 | 19 | 34 | 24 | 16 | 46 | 0 | 0 | 320 | 356 | 36 | 40 | 0 | 140 | 14 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 96 | 58 | 11 | 2 | 36.23 | 12 | 6190.23 | 860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.4 | 901 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 39.48 | 182 | 0 | 153 | 0 | 163 | 0 | 414 | 0 | 3.36 | 0 | 110 | 58 | 0 | 19 | 0 | 0 | 0 | 5.4 | 89 | 0.39 | 0 | 182 | 6 | 108 | 220 | 0 | 290 | 840 | 0 | 5519.03 | 11709.26 | 82.32
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 17 | 52 | 48 | 0 | 0 | 0 | 0 | 0 | 41 | 225 | 302 | 583 | 0 | 0 | 0 | 319 | 39 | 0 | 21 | 52 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 3 | 46 | 0 | 30 | 160 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1105 | 16 | 43 | 0 | 162 | 0 | 347 | 0 | 50 | 201 | 31 | 0 | 50 | 85 | 9 | 19 | 34 | 28 | 16 | 59 | 0 | 0 | 320 | 394 | 36 | 40 | 0 | 152 | 14 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 103 | 0 | 11 | 2 | 44.95 | 12 | 6248.95 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.23 | 904 | 0 | 748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 45.55 | 182 | 0 | 158 | 0 | 163 | 0 | 350 | 0 | 4.3 | 0 | 110 | 58 | 0 | 29 | 0 | 0 | 0 | 8 | 112 | 0.48 | 0 | 200 | 6 | 124 | 220 | 0 | 290 | 1000 | 0 | 5786.56 | 12035.51 | 82.32
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 52 | 62 | 0 | 0 | 0 | 0 | 0 | 32 | 225 | 299 | 500 | 0 | 0 | 0 | 318 | 93 | 0 | 26 | 52 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 4 | 46 | 0 | 39 | 160 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1190 | 10 | 43 | 0 | 162 | 0 | 332 | 0 | 48 | 205 | 33 | 0 | 50 | 104 | 8 | 19 | 62 | 28 | 16 | 51 | 0 | 0 | 320 | 350 | 36 | 40 | 0 | 152 | 14 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 101 | 38 | 11 | 2 | 49.11 | 12 | 6417.11 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.74 | 776 | 0 | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 59.12 | 183 | 0 | 162 | 0 | 164 | 0 | 414 | 0 | 5.01 | 0 | 107 | 57 | 0 | 33 | 0 | 0 | 0 | 5.2 | 148 | 0.57 | 0 | 230 | 6 | 120 | 220 | 0 | 290 | 1025 | 0 | 5847.64 | 12264.75 | 82.31
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 10 | 17 | 52 | 31 | 0 | 0 | 18 | 60 | 0 | 34 | 225 | 297 | 583 | 0 | 20 | 0 | 316 | 93 | 0 | 26 | 60 | 18.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 33 | 88 | 2 | 46 | 8 | 39 | 161 | 0 | 0 | 0 | 0 | 12 | 144 | 0 | 0 | 0 | 1224 | 19 | 43 | 10 | 162 | 0 | 345 | 0 | 48 | 194 | 33 | 0 | 50 | 144 | 9 | 19 | 79 | 30 | 30 | 61 | 0 | 0 | 320 | 386 | 36 | 40 | 0 | 152 | 14 | 0 | 81 | 30 | 0 | 18 | 173 | 0 | 85 | 101 | 11 | 2 | 49.77 | 12 | 6870.27 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.47 | 750 | 0 | 757 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 56.89 | 183 | 0 | 161 | 0 | 162 | 0 | 414 | 0 | 2.64 | 0 | 116 | 56 | 0 | 33 | 40 | 0 | 0 | 8 | 165 | 0.51 | 0 | 250 | 5 | 120 | 220 | 0 | 287 | 1100 | 0 | 5980.51 | 12850.78 | 82.31
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 52 | 31 | 0 | 0 | 35 | 108 | 0 | 35 | 225 | 297 | 583 | 0 | 35 | 0 | 308 | 93 | 0 | 18 | 90 | 18.5 | 7 | 0 | 0 | 13 | 45 | 0 | 0 | 11 | 0 | 0 | 0 | 33 | 100 | 3 | 46 | 40 | 38 | 161 | 0 | 0 | 0 | 0 | 43 | 144 | 0 | 0 | 0 | 1224 | 19 | 43 | 48 | 162 | 0 | 336 | 0 | 47 | 200 | 32 | 0 | 50 | 188 | 14 | 19 | 80 | 30 | 34 | 63 | 0 | 0 | 320 | 386 | 38 | 40 | 0 | 152 | 14 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 76 | 115 | 11 | 2 | 46.93 | 12 | 7200.43 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.14 | 752 | 0 | 756 | 0 | 0 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 54.85 | 183 | 0 | 162 | 0 | 162 | 0 | 414 | 0 | 4.62 | 0 | 117 | 56 | 40 | 20 | 113 | 0 | 0 | 8 | 128 | 0.6 | 0 | 307 | 9 | 120 | 220 | 0 | 289 | 1206 | 0 | 6251.21 | 13451.64 | 82.3
14:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 17 | 17 | 69 | 95 | 0 | 6 | 35 | 108 | 0 | 40 | 225 | 289 | 520 | 0 | 35 | 0 | 313 | 91 | 0 | 22 | 108 | 18 | 7 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 36 | 1 | 46 | 51 | 38 | 160 | 54 | 0 | 0 | 0 | 51 | 145 | 0 | 0 | 0 | 1224 | 17 | 43 | 73 | 162 | 0 | 345 | 0 | 45 | 185 | 31 | 3 | 50 | 197 | 9 | 19 | 80 | 34 | 43 | 53 | 0 | 0 | 320 | 357 | 35 | 40 | 0 | 150 | 8 | 0 | 80 | 30 | 0 | 17 | 173 | 9 | 67 | 123 | 18 | 2 | 42.65 | 12 | 7201.65 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.03 | 748 | 0 | 754.2 | 0 | 0 | 0 | 102 | 0 | 0 | 5 | 0 | 0 | 45 | 0 | 50.29 | 181 | 0 | 158 | 0 | 162 | 0 | 382 | 0 | 4.77 | 0 | 117 | 55 | 108 | 21 | 113 | 0 | 0 | 7.4 | 104 | 0 | 0 | 293 | 8 | 120 | 220 | 0 | 289 | 1150 | 0 | 6179.69 | 13381.34 | 82.3
15:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 128 | 94 | 0 | 55 | 35 | 108 | 0 | 53 | 225 | 299 | 583 | 0 | 35 | 0 | 311 | 37 | 0 | 22 | 108 | 18 | 7 | 0 | 0 | 0 | 15 | 2 | 0 | 2 | 0 | 0 | 0 | 33 | 36 | 1 | 40 | 51 | 38 | 160 | 54 | 0 | 10 | 8 | 51 | 141 | 0 | 0 | 0 | 1224 | 14 | 43 | 76 | 160 | 0 | 349 | 0 | 45 | 182 | 31 | 50 | 50 | 196 | 15 | 19 | 80 | 32 | 52.2 | 41 | 0 | 10 | 320 | 350 | 35 | 40 | 0 | 136 | 8 | 0 | 80 | 30 | 0 | 17 | 173 | 42 | 67 | 124 | 18 | 1 | 31.91 | 12 | 7382.11 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.54 | 748 | 0 | 755.04 | 0 | 0 | 0 | 70 | 0 | 0 | 35 | 0 | 0 | 64 | 0 | 37.62 | 180 | 0 | 158 | 0 | 167 | 0 | 414 | 0 | 3.31 | 0 | 118 | 56 | 70 | 17 | 113 | 0 | 0 | 5.6 | 125 | 0.01 | 0 | 250 | 9 | 96 | 220 | 0 | 287 | 1110 | 0 | 6078.12 | 13460.23 | 82.29
16:00 | 32 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 110 | 80 | 40 | 30 | 35 | 108 | 0 | 64 | 225 | 300 | 583 | 0 | 35 | 0 | 314 | 38 | 0 | 12 | 90 | 18 | 7 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 100 | 10 | 2 | 40 | 17 | 38 | 162 | 17 | 0 | 19 | 8 | 17 | 142 | 0 | 0 | 0 | 1185 | 9 | 43 | 70 | 162 | 0 | 344 | 0 | 45 | 182 | 31 | 70 | 50 | 200 | 24 | 19 | 80 | 34 | 52.2 | 26 | 0 | 15 | 320 | 350 | 35 | 38 | 0 | 133 | 8 | 0 | 80 | 30 | 0 | 17 | 171 | 54.5 | 66 | 106 | 22 | 1 | 21.64 | 12 | 7320.34 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.29 | 745 | 0 | 720.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 17.24 | 180 | 0 | 156 | 0 | 162 | 0 | 350 | 0 | 1.79 | 0 | 118 | 57 | 35 | 19 | 70 | 0 | 0 | 3.8 | 103 | 0.11 | 0 | 250 | 8 | 100 | 180 | 0 | 288 | 1000 | 0 | 5536.15 | 12856.49 | 82.29
17:00 | 49 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 17 | 78 | 80 | 45 | 30 | 17 | 72 | 0 | 64 | 225 | 294 | 500 | 0 | 55 | 0 | 318 | 38 | 0 | 6 | 90 | 17 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 100 | 12 | 1 | 40 | 17 | 30 | 160 | 17 | 0 | 19 | 8 | 17 | 142 | 0 | 0 | 0 | 1107 | 3 | 43 | 70 | 125 | 0 | 345 | 0 | 46 | 183 | 32 | 79 | 70 | 155 | 36 | 19 | 52 | 30 | 25 | 6 | 0 | 35 | 320 | 350 | 35 | 38 | 0 | 132 | 8 | 0 | 81 | 30 | 0 | 17 | 172 | 54.5 | 75 | 114 | 22 | 0 | 12.6 | 12 | 6980.1 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.22 | 751 | 0 | 619.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 4.91 | 180 | 0 | 163 | 0 | 164 | 0 | 350 | 0 | 0.52 | 0 | 119 | 57 | 35 | 3 | 70 | 0 | 0 | 1.8 | 49 | 0.08 | 0 | 248 | 7 | 100 | 180 | 0 | 283 | 950 | 0 | 5272.84 | 12252.94 | 82.28
18:00 | 49 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 78 | 80 | 45 | 30 | 17 | 72 | 0 | 65 | 225 | 300 | 450 | 0 | 55 | 0 | 316 | 38 | 0 | 1 | 90 | 17 | 7 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 4 | 0 | 100 | 12 | 0 | 40 | 17 | 38 | 160 | 17 | 0 | 19 | 8 | 17 | 145 | 0 | 0 | 0 | 1074 | 0 | 43 | 70 | 125 | 0 | 300 | 0 | 46 | 208 | 32 | 80 | 70 | 120 | 37 | 19 | 52 | 28 | 25 | 1 | 0 | 45 | 320 | 378 | 35 | 40 | 0 | 133 | 18 | 0 | 82 | 30 | 0 | 17 | 172 | 54.5 | 103 | 133 | 22 | 0 | 0.71 | 12 | 6970.21 | 908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.19 | 746 | 10 | 619.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 1.15 | 140 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 0.1 | 0 | 117 | 57 | 35 | 1 | 70 | 0 | 0 | 0.2 | 2 | 0.01 | 0 | 200 | 9 | 112 | 180 | 0 | 287 | 950 | 0 | 5039.43 | 12009.64 | 82.28
19:00 | 61 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 17 | 79 | 95 | 190 | 30 | 35 | 118 | 0 | 65 | 225 | 277 | 550 | 0 | 55 | 0 | 316 | 98 | 0 | 0 | 125 | 16 | 7 | 0 | 0 | 11 | 65 | 18 | 0 | 0 | 51 | 39 | 0 | 100 | 60 | 0 | 46 | 50 | 37 | 160 | 72 | 0 | 19 | 9 | 58 | 145 | 0 | 0 | 0 | 1224 | 0 | 43 | 90 | 162 | 0 | 354 | 0 | 47 | 182 | 33 | 85 | 70 | 144 | 37 | 19 | 70 | 32 | 43 | 0 | 37 | 55 | 320 | 350 | 35 | 37 | 0 | 146 | 16 | 0 | 82 | 30 | 0 | 17 | 171 | 54.5 | 104 | 144 | 22 | 0 | 0 | 12 | 8072.5 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 17 | 756.87 | 0 | 15 | 0 | 35 | 5 | 90 | 50 | 30 | 0 | 0 | 22 | 0 | 170 | 0 | 180 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 116 | 57 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 220 | 0 | 287 | 1100 | 0 | 5945.87 | 14018.37 | 82.27
19:30 | 74 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 17 | 68 | 95 | 130 | 55 | 35 | 144 | 0 | 65 | 225 | 303 | 500 | 0 | 55 | 0 | 320 | 96 | 0 | 0 | 125 | 16 | 7 | 0 | 0 | 17 | 65 | 33 | 0 | 0 | 61 | 40 | 0 | 100 | 100 | 0 | 46 | 57 | 37 | 160 | 72 | 0 | 0 | 8 | 105 | 145 | 0 | 0 | 0 | 1150 | 0 | 43 | 107 | 162 | 0 | 345 | 0 | 48 | 191 | 33 | 88 | 70 | 170 | 37 | 19 | 70 | 32 | 34 | 0 | 39 | 55 | 320 | 350 | 39 | 40 | 0 | 146 | 16 | 0 | 82 | 28 | 0 | 17 | 171 | 54.5 | 102 | 144 | 22 | 0 | 0 | 12 | 8119.5 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743 | 53 | 766.8 | 0 | 50 | 0 | 35 | 8 | 95 | 0 | 35 | 0 | 0 | 22 | 0 | 195 | 0 | 182 | 0 | 140 | 0 | 390 | 0 | 0 | 0 | 113 | 56 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 220 | 0 | 287 | 1230 | 0 | 6090.8 | 14210.3
20:00 | 94 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 21 | 78 | 95 | 130 | 55 | 35 | 144 | 0 | 65 | 225 | 307 | 500 | 0 | 55 | 0 | 320 | 96 | 0 | 0 | 125 | 17 | 7 | 0 | 0 | 17 | 30 | 35 | 0 | 0 | 68 | 60 | 0 | 100 | 100 | 0 | 46 | 68 | 37 | 160 | 72 | 0 | 0 | 8 | 105 | 147 | 0 | 0 | 0 | 1150 | 0 | 43 | 103 | 162 | 0 | 343 | 0 | 48 | 204 | 33 | 89 | 70 | 155 | 37 | 19 | 74 | 32 | 34 | 0 | 39 | 55 | 320 | 386 | 39 | 40 | 0 | 151 | 20 | 0 | 82 | 28 | 0 | 17 | 171 | 54.5 | 95 | 144 | 22 | 0 | 0 | 12 | 8200.5 | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 759 | 53 | 752.36 | 0 | 50 | 0 | 35 | 26 | 98 | 0 | 37 | 0 | 0 | 22 | 0 | 196 | 0 | 182 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 114 | 57 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 287 | 1240 | 0 | 6122.36 | 14322.86 | 82.27
21:00 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 36 | 68 | 95 | 160 | 55 | 35 | 144 | 0 | 66 | 225 | 280 | 500 | 0 | 35 | 0 | 320 | 98 | 0 | 0 | 125 | 17 | 7 | 0 | 0 | 17 | 30 | 25 | 0 | 0 | 68 | 56 | 0 | 100 | 100 | 0 | 40 | 68 | 37 | 161 | 72 | 0 | 0 | 8 | 105 | 146 | 0 | 0 | 0 | 1224 | 0 | 43 | 115 | 162 | 0 | 357 | 0 | 49 | 183 | 34 | 90 | 70 | 165 | 37 | 19 | 80 | 32 | 34 | 0 | 39 | 75 | 320 | 366 | 39 | 40 | 0 | 152 | 20 | 0 | 82 | 25 | 0 | 17 | 171 | 23 | 96 | 145 | 22 | 0 | 0 | 12 | 8241 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 53 | 758 | 0 | 50 | 0 | 55 | 26 | 98 | 0 | 35 | 0 | 0 | 22 | 0 | 198 | 0 | 183 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 112 | 56 | 90 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 286 | 1244 | 0 | 6239 | 14480 | 82.26
22:00 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 36 | 68 | 95 | 160 | 55 | 35 | 108 | 0 | 66 | 225 | 305 | 500 | 0 | 35 | 0 | 320 | 98 | 0 | 0 | 125 | 16 | 7 | 0 | 0 | 17 | 30 | 25 | 0 | 0 | 51 | 62 | 0 | 100 | 88 | 0 | 40 | 68 | 37 | 160 | 72 | 0 | 0 | 8 | 105 | 150 | 0 | 0 | 0 | 1224 | 0 | 43 | 115 | 162 | 0 | 359 | 0 | 50 | 183 | 34 | 91 | 70 | 170 | 38 | 19 | 80 | 34 | 34 | 0 | 39 | 80 | 320 | 351 | 39 | 40 | 0 | 151 | 20 | 0 | 82 | 28 | 0 | 17 | 171 | 17 | 95 | 145 | 22 | 0 | 0 | 12 | 8173 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 53 | 751 | 0 | 42 | 0 | 70 | 26 | 89 | 0 | 35 | 0 | 0 | 22 | 0 | 190 | 0 | 188 | 0 | 188 | 0 | 350 | 0 | 0 | 0 | 114 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 11 | 108 | 180 | 0 | 285 | 1244 | 0 | 6184 | 14357 | 82.26
23:00 | 90 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 36 | 68 | 95 | 95 | 15 | 35 | 72 | 0 | 66 | 225 | 303 | 450 | 0 | 35 | 0 | 324 | 98 | 0 | 0 | 125 | 16.5 | 7 | 0 | 0 | 17 | 30 | 24 | 0 | 0 | 34 | 55 | 0 | 33 | 48 | 0 | 40 | 68 | 27 | 160 | 0 | 0 | 0 | 8 | 68 | 151 | 0 | 0 | 0 | 1165 | 0 | 43 | 112 | 162 | 0 | 300 | 0 | 50 | 183 | 33 | 92 | 70 | 170 | 38 | 19 | 80 | 34 | 34 | 0 | 39 | 120 | 320 | 354 | 39 | 39 | 0 | 151 | 20 | 0 | 82 | 28 | 0 | 17 | 170 | 17 | 95 | 145 | 22 | 0 | 0 | 12 | 7641.5 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 757 | 0 | 42 | 0 | 70 | 0 | 90 | 0 | 27 | 0 | 0 | 22 | 0 | 170 | 0 | 195 | 0 | 194 | 0 | 350 | 0 | 0 | 0 | 114 | 57 | 76 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 108 | 180 | 0 | 287 | 1150 | 0 | 5903 | 13544.5 | 82.25
Total KWH | 583488 | 707520 | 277440 | 0 | 0 | 0 | 0 | 0 | 9525600 | 0 | 0 | 518760 | 510120 | 1903680 | 2111040 | 1536065 | 466581 | 727363 | 2161440 | 0 | 1089600 | 5084500 | 7144553 | 12259545 | 0 | 866904 | 0 | 7738249 | 1604000 | 0 | 199605 | 2247600 | 413400 | 164880 | 0 | 0 | 136745 | 361309 | 247680 | 0 | 18240 | 586703 | 526896 | 0 | 1125120 | 1157760 | 23359 | 1041180 | 1226945 | 812640 | 3789090.91 | 538618 | 0 | 98400 | 99464.4 | 1229454 | 3495512 | 0 | 0 | 0 | 28325452 | 130545 | 967096 | 1965454 | 3797091 | 0 | 8659200 | 0 | 1177440 | 4665000 | 785016 | 825600 | 1367710 | 4000320 | 459480 | 455220 | 1732800 | 735360 | 848750 | 468364 | 613232 | 809390 | 7697100 | 9027000 | 861000 | 914880 | 0 | 3517118 | 333216 | 0 | 1974720 | 700032 | 0 | 420000 | 3561360 | 601560 | 1837200 | 2570400 | 340800 | 13800 | 356220 | 293760 | 174165735.31 | 21741091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612000 | 20021814 | 301440 | 17818859 | 0 | 223131 | 0 | 1223328 | 116330 | 500720 | 261120 | 199970 | 19728 | 618865 | 155225 | 384000 | 4363727 | 0 | 4125382 | 0 | 4063720 | 0 | 9606472 | 0 | 32280 | 0 | 2763000 | 1294690 | 1085647 | 198709 | 1620105 | 0 | 0 | 55301.76 | 1110960 | 3273 | 0 | 6415000 | 209617 | 2646000 | 5297300 | 0 | 6857454 | 26391272.73 | 0 | 142337531.49 | 316503266.8

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 14-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12850.78 | MW | 12:00 Hr. | Energy Generated |  |  | 316.5033 |  | MKWHr.
| Day Peak Demand |  |  | 12881.78 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.855 |  | MKWHr.
| Evening Peak Generation |  |  | 14480 | MW | 21:00 Hr. | Energy Demand |  |  | 317.3583 |  | MKWHr.
| Evening Peak Demand |  |  | 14550 | MW | 21:00 Hr. | Maximum Temperature |  |  | 36.1 |  | °C
| Minimum Generation of the Day |  |  | 11709.26 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 962.12 |  | MMCFD
| Maximum Generation of the Day |  |  | 14763.26 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.6052 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.9347 | 0 | 15.7076 | 0 | 0 | 0.19961 | 0 | 0 | 59.8419 | Gas | 130.5855 | Gas | 420584159.08
| Chattogram Zone |  |  | 4.3082 | 32.1145 | 7.3351 | 0 | 1.0412 | 0.1539 | 0 | 0.01824 | 44.9711 | Coal | 95.8578 | Coal | 639187824.2877
| Cumilla Zone |  |  | 21.8738 | 0 | 10.4456 | 0 | 0 | 0.46836 | 0.73536 | 0 | 33.5231 | HFO | 44.498 | HFO | 777343595.428
| Mymensingh Zone |  |  | 0.3408 | 0 | 5.3029 | 0 | 0 | 0.37002 | 0 | 0 | 6.0137 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.8158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.8158 | Hydro | 1.0412 | Hydro | 104118
| Khulna Zone |  |  | 0 | 20.0218 | 0.30144 | 0 | 0 | 0.612 | 21.7411 | 0 | 42.6763 | Solar | 4.2073 | Solar | 68378825.9136
| Barishal Zone |  |  | 8.1529 | 39.6637 | 0 | 0 | 0 | 0.003273 | 0 | 0 | 47.8199 | Import | 40.2953 | Import | 184713086.69
| Rajshahi Zone |  |  | 22.1593 | 0 | 2.6996 | 0 | 0 | 1.0351 | 17.8189 | 0 | 43.7129 | Wind | 0.01824 | Wind | 267033.6
| Rangpur Zone |  |  | 0 | 4.0577 | 2.7058 | 0 | 0 | 1.365 | 0 | 0 | 8.1284
| Total |  |  | 130.5855 | 95.8578 | 44.498 | 0 | 1.0412 | 4.2073 | 40.2953 | 0.01824 | 316.5033
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 420584159.08 |  | Hydro | 104118
|  |  |  | Coal | 639187824.2877 |  | Solar | 68378825.9136
|  |  |  | HFO | 777343595.428 |  | Import | 184713086.69
|  |  |  | HSD | 0 |  | Wind | 267033.6
[5 empty] | Total: | 209,05,78,642 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7411 | Peak Hr Flow | 915.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9034236.42 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 17.8189 | Peak Hr Flow | 758.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 410 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.73536 | Peak Hr Flow | 32.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 946 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 40.2953 | Peak Hr Flow | 1705.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 32 |  | 4812
|  |  |  | Chattogram |  | 0 |  | 1405
|  |  |  | Cumilla |  | 15 |  | 1481
|  |  |  | Mymensingh |  | 20 |  | 1298
|  |  |  | Sylhet |  | 0 |  | 646
|  |  |  | Khulna |  | 0 |  | 1666
|  |  |  | Barishal |  | 0 |  | 381
|  |  |  | Rajshahi |  | 0 |  | 1558
|  |  |  | Rangpur |  | 0 |  | 803
|  |  |  | Total |  | 67 |  | 14050
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:10 |  | Summit Bibiyana-2 CCPP GT tripped.
| 08:17 | 09:35 | BSRM 230/33kV S/S GPH Ispat Ckt. -01 Scheduled S/D Due to Kite remove
| 08:19 | 09:35 | GPH 230/33kV S/S BSRM CKT-1 Forced S/D Due to Emergency Works
| 10:24 | 11:50 | AKSML-Baroaulia 132kV Ckt-1 Forced S/D from AKS 132/33kV end Due to AKSPL to Baraulia 132 | [7 empty] | and 58.0MW load
|  |  | KV Line Shutdown due to forced shutdown. and from Baroaulia 132/33kV end Due to CT OIL | [7 empty] | interrup. Baroaulia
|  |  | LEAKAGE | [7 empty] | 132/33kV end
| 10:50 | 13:29 | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
| 12:00 |  | Day Peak Gen. 12850 MW
|  | 13:19 | Chandpur 132/33kV S/S 115MW CPGL Power Plant Incomer (L5) is restored.
| 15:01 | 16:17 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Distance. D
ST Zone:2 3 relays Due to kalbayashi storms take place in the barisal zone.
|  | 15:08 | Kodda(300MW)-Tongi 230kV Ckt-1 is restored.
| 15:26 | 15:43 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Def. O/c, E/F relays Due to Dopdopia | [7 empty] | 15.0MW load
|  |  | 33kV feeder fault. | [7 empty] | interrup.
| 15:49 | 21:10 | Fatullah-Madanganj 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing 1. 21 Trip 2.
Zone-1 Trip relays.
| 15:51 | 21:11 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Tripped showing General Trip Zone 1
Trip B phase pickup relays Due to Heavy stormy rain
|  | 16:39 | Ishurdi 132/33kV S/S 132 kV Baghabari Line is restored.
| 03:53 | 04:15 | Savar 132/33kV S/S T-3 LT Tripped showing Over current relays Due to dpbs-3 33kv
feeder-L- 45 ( রাজাশন) ফিডার ফল্টের কারনে
| 03:53 | 03:58 | Savar 132/33kV S/S T-4 LT Tripped showing Over current relays Due to dpbs-3 33kv
feeder-L- 45 ( রাজাশন) ফিডার ফল্টের কারনে
| 04:03 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- GT
| 05:49 | 06:19 | Khagrachari-Rangamati 132kV Ckt-2 Tripped from Khagrachori 132/33kV end showing REL670
relays Due to For thundering
| 07:55 |  | Baroirhat-Feni 132 kV Ckt-2 Tripped from Baroirhat 132/33kV end showing K31,K34& K34X
relays Due to Distance trip
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 14-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 403 | 9525600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 5084500 | GT-2 shut down for HRSG-2 tube leakage repair
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 7144553 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 466581 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 98 | 1604000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7738249 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 98 | 583488 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 518760 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 95 | 2111040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 727363 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 866904 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 413400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 164880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 277440 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 160 | 1536065 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 68 | 1903680 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 707520 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 66 | 1089600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2161440 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 199605 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 510120 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 500 | 12259545 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 2247600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2870 | 59841933
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 99464.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 130545 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 98400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 1041180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3495512 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 1229454 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 56 | 526896 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 68 | 586703 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1125120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 37 | 812640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 25 | 247680 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 30 | 361309 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 1226945 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1157760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 136745 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 72 | 538618 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28325452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 18240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 161 | 3789090.91 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2257 | 44971113.31
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4665000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 357 | 8659200 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 0 | 0 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 785016 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1177440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 162 | 3797091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 967096 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 1965454 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 613232 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1367710 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 165 | 4000320 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 32 | 735360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 848750 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 455220 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 1732800 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 459480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 825600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 468364 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1509 | 33523133
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 22 | 340800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 145 | 2570400 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1837200 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 356220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 293760 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 23 | 601560 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 298 | 6013740
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 861000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 914880 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3517118 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 25 | 700032 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1974720 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 171 | 3561360 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 420000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 20 | 333216 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 75 | 809390 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 366 | 9027000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7697100 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1307 | 29815816
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 21741091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 301440 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 612000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 751 | 20021814 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1719 | 42676345
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 286 | 6857454 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 209617 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 108 | 2646000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26391272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5297300 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6415000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3273 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2175 | 47819916.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 50 | 223131 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 26 | 116330 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 35 | 199970 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 198 | 4363727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 183 | 4125382 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 4063720 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9606472 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 155225 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 19728 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 500720 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 55 | 1223328 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 261120 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32280 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 758 | 17818859 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 384000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 618865 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1979 | 43712857
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1294690 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 112 | 2763000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 1620105 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 55301.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 90 | 1085647 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 198709 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1110960 | -
Rangpur Area Total |  |  |  |  | 950 | 366 | 8128412.76
Eastern Grid Total |  |  |  |  | 16921.242 | 8241 | 174165735.31
Western Grid Total |  |  |  |  | 11614.5 | 6239 | 142337531.49
National Grid Total |  |  |  |  | 28535.742 | 14480 | 316503266.8
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 14-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9574.94 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4407.9 | MW
i) Dhaka area |  |  | 4779.94 |  | MW | i) Khulna area |  |  |  | 1665.9 | MW
ii) Chattogram area |  |  | 1405 |  | MW | ii) Barishal area |  |  |  | 381 | MW
iii) Cumilla area |  |  | 1466 |  | MW | iii) Rajshahi area |  |  |  | 1558 | MW
iv) Mymensingh area |  |  | 1278 |  | MW | iv) Rangpur area |  |  |  | 803 | MW
v) Sylhet area |  |  | 646 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13982.84 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 68 | 19:00 | 133 | Patuakhali | 79 | 01:00
2 | AKSML | 129.1 | 03:00 | 68 | Jaldhaka | 70 | 19:00 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 36 | 00:00 | 69 | Jamalpur | 136 | 18:00 | 135 | Postogola | 54 | 00:00
4 | Agargaon | 107 | 23:00 | 70 | Jashore | 142 | 14:00 | 136 | Purbachal | 20 | 22:00
5 | Agrabad | 90 | 00:00 | 71 | Jhenaidah | 140 | 19:00 | 137 | Purbasadipur | 110 | 19:30
6 | Amnura | 46 | 19:00 | 72 | Joydebpur | 127 | 00:00 | 138 | Rahanpur | 27 | 21:00
7 | Ashuganj | 95 | 23:00 | 73 | Joypurhat | 60 | 21:00 | 139 | Rahim | 39 | 00:00
8 | BSRM | 200 | 17:00 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 84 | 19:00
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 16 | 23:00 | 141 | Rajendrapur | 120 | 00:00
10 | Bajitpur | 61 | 20:00 | 76 | Kabirpur | 232 | 00:00 | 142 | Rajshahi | 128 | 21:00
11 | Bakulia | 99 | 00:00 | 77 | Kachua | 87 | 21:00 | 143 | Rajshahi-230 | 83 | 00:00
12 | Banani | 30 | 17:00 | 78 | Kallyanpur | 111 | 22:00 | 144 | Ramganj | 118 | 22:00
13 | Bangabhaban | 4 | 10:00 | 79 | Kalurghat | 34 | 01:00 | 145 | Rampur | 45 | 00:00
14 | Barapukuria | 56 | 22:00 | 80 | Kamrangirchar | 62.2 | 13:00 | 146 | Rangamati | 16 | 13:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 134 | 19:00
16 | Barishal | 109 | 00:00 | 82 | Kasba | 44 | 22:00 | 148 | Ruppur | 7 | 15:00
17 | Barishal-230 | 96 | 00:00 | 83 | Kazla | 97 | 00:00 | 149 | SSM | 1 | 00:00
18 | Baroaulia | 63 | 20:00 | 84 | Keranigonj | 74 | 00:00 | 150 | Saidpur | 94 | 19:00
19 | Baroirhat | 68 | 00:00 | 85 | Khagrachori | 30 | 12:00 | 151 | Satkhira | 142 | 22:00
20 | Bashundhara | 177 | 23:00 | 86 | Khulna | 69 | 23:00 | 152 | Satmasjid | 99 | 14:00
21 | BashundharaCement | 1 | 00:00 | 87 | Khulshi | 173 | 19:00 | 153 | Savar | 188 | 00:00
22 | Beanibazar | 78 | 18:30 | 88 | Kishoreganj | 150 | 20:00 | 154 | SevenRings | 15.37 | 21:00
23 | Benapole | 72 | 22:00 | 89 | Kodda | 262 | 03:00 | 155 | ShahCement | 29 | 00:00
24 | Bhaluka | 143 | 22:00 | 90 | Kulaura | 50 | 18:30 | 156 | Shahjadpur | 92 | 20:00
25 | Bhandaria | 52 | 00:00 | 91 | Kurigram | 56 | 19:00 | 157 | Shahjibazar | 141 | 22:00
26 | Bhangura | 45 | 19:00 | 92 | Kushtia | 144 | 00:00 | 158 | Shahmirpur | 58 | 00:00
27 | Bheramara(GK) | 65 | 19:00 | 93 | Lalbag | 61 | 13:00 | 159 | Shariatpur | 82 | 00:00
28 | Bhulta | 231 | 00:00 | 94 | Lalmonirhat | 51 | 19:00 | 160 | Sherpur | 156 | 21:00
29 | Bog-Sherpur | 76 | 19:00 | 95 | MI_Cement | 17.8 | 00:00 | 161 | Shikalbaha | 24 | 23:00
30 | Bogura | 171 | 19:30 | 96 | Madanganj | 40 | 00:00 | 162 | Shitalakhya | 75.6 | 12:00
31 | Borhanuddin | 92 | 00:00 | 97 | Madaripur | 120 | 00:00 | 163 | Sholosohor | 41 | 00:00
32 | Brahmanbaria | 140 | 19:00 | 98 | Madartek | 88.06 | 23:00 | 164 | Shyampur | 142 | 00:00
33 | Cantonment | 110 | 18:00 | 99 | Madunaghat | 49 | 02:00 | 165 | Siddhirganj | 118 | 00:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 68 | 19:00 | 166 | Sirajganj | 118 | 19:30
35 | Chandpur | 73 | 21:00 | 101 | Mahasthangarh | 76 | 19:00 | 167 | Sonargaon | 95 | 00:00
36 | Chandraghona | 36 | 19:00 | 102 | Manikganj | 127 | 00:00 | 168 | Sreemongol | 82 | 20:00
37 | Chapai | 67 | 00:00 | 103 | Maniknagar | 64 | 13:00 | 169 | Sreepur | 95 | 00:00
38 | Charsaidpur | 46 | 03:00 | 104 | Matarbari | 48 | 19:00 | 170 | Srinagar | 46 | 22:00
39 | Chauddagram | 77 | 18:30 | 105 | Matuail | 60 | 00:00 | 171 | Sunamganj | 57 | 21:00
40 | Chhatak | 40 | 20:00 | 106 | Millgate | 74 | 00:00 | 172 | Sylhet | 49 | 00:00
41 | Chowmuhani | 245 | 19:00 | 107 | Mirpur | 127 | 22:00 | 173 | Sylhet-132 | 125 | 19:00
42 | Chuadanga | 111 | 19:00 | 108 | Mirsorai | 8 | 00:00 | 174 | TK | 34 | 19:00
43 | Coxsbazar | 138 | 18:30 | 109 | Mirzapur | 51 | 07:00 | 175 | Tangail | 212 | 19:30
44 | Cumilla(N) | 175 | 21:00 | 110 | Mithapukur | 60 | 19:00 | 176 | Thakurgaon | 88 | 19:30
45 | Cumilla(S) | 171 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 124 | 23:00
46 | Daudkandi | 153 | 00:00 | 112 | Mogbazar | 120.9 | 16:00 | 178 | Ullahpara | 48 | 18:30
47 | Dhaka | 36 | 13:00 | 113 | Mongla | 34 | 00:00 | 179 | Ullon | 48 | 23:00
48 | Dhamrai | 130 | 00:00 | 114 | Motijheel | 33 | 00:00 | 180 | Uttara | 86 | 19:00
49 | Dhanmondi | 120 | 13:00 | 115 | Muktagacha | 38 | 18:00 | 181 | UttaraNew | 48 | 00:00
50 | Dohazari | 106 | 20:00 | 116 | Munshiganj | 111 | 00:00 | 182 | Zigatola | 70 | 00:00
51 | Faridpur | 160 | 20:00 | 117 | Muradnagar | 32 | 19:00
52 | Fatullah | 90 | 00:00 | 118 | Mymensingh | 206 | 22:00
53 | Fenchuganj | 42 | 19:00 | 119 | Naogaon | 130 | 21:00
54 | Feni | 119 | 19:00 | 120 | Narail | 58.5 | 20:00
55 | GPH | 12 | 23:00 | 121 | Narinda | 68 | 13:00
56 | Ghatail | 98 | 21:00 | 122 | Narshingdi | 179 | 00:00
57 | Ghorashal | 16 | 00:00 | 123 | Natore | 161 | 19:00
58 | Ghorashal-230 | 86 | 01:00 | 124 | Nawabganj | 59 | 21:00
59 | Goalpara | 34 | 00:00 | 125 | Netrakona | 135 | 19:00
60 | Gollamari | 100 | 00:00 | 126 | New | 70.9 | 00:00
61 | Gopalganj | 108.6 | 00:00 | 127 | Niamatpur | 100 | 22:00
62 | Gulshan | 88 | 13:00 | 128 | Noapara | 44 | 19:00
63 | Halishahar | 46 | 16:00 | 129 | PHP | 8 | 01:00
64 | HaripurSBU | 168 | 01:00 | 130 | Pabna | 123 | 21:00
65 | Hasnabad | 85 | 00:00 | 131 | Palashbari | 108 | 19:00
66 | Hathazari | 88 | 00:00 | 132 | Panchagarh | 50 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 14-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14763.26 | 55 |  | 14820.26
1:00 | 14164.43 | 74 |  | 14241.43
2:00 | 13668.47 | 70 |  | 13741.47
3:00 | 13234.6 | 64 |  | 13301.6
4:00 | 12998.06 | 51 |  | 13051.06
5:00 | 12631.37 | 38 |  | 12671.37
6:00 | 12080.58 | 0 |  | 12080.58
7:00 | 11918.06 | 0 |  | 11918.06
8:00 | 11799.16 | 30 |  | 11830.16
9:00 | 11709.26 | 30 |  | 11740.26
10:00 | 12035.51 | 45 |  | 12082.51
11:00 | 12264.75 | 30 |  | 12295.75
12:00 | 12850.78 | 30 |  | 12881.78
13:00 | 13451.64 | 30 |  | 13482.64
14:00 | 13381.34 | 30 |  | 13412.34
15:00 | 13460.23 | 0 |  | 13460.23
16:00 | 12856.49 | 0 |  | 12856.49
17:00 | 12252.94 | 0 |  | 12252.94
18:00 | 12009.64 | 0 |  | 12009.64
19:00 | 14018.37 | 46 |  | 14066.44
19:30 | 14210.3 | 30 |  | 14241.3
20:00 | 14322.86 | 41 |  | 14365.86
21:00 | 14480 | 67 |  | 14550
22:00 | 14357 | 51 |  | 14410
23:00 | 13544.5 | 73 |  | 13620.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 14-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8228.2 | 6535.06 | 14763.26 | DAILY GENERATION CURVE
00:30 | 8005.35 | 6458.495 | 14463.845
01:00 | 7782.5 | 6381.93 | 14164.43 | 14-04-2025
01:30 | 7657.75 | 6258.7 | 13916.45
02:00 | 7533 | 6135.47 | 13668.47
02:30 | 7394.5 | 6057.035 | 13451.535
03:00 | 7256 | 5978.6 | 13234.6
03:30 | 7227.5 | 5888.83 | 13116.33
04:00 | 7199 | 5799.06 | 12998.06
04:30 | 7067 | 5747.715 | 12814.715
05:00 | 6935 | 5696.37 | 12631.37
05:30 | 6771.02 | 5584.955 | 12355.975
06:00 | 6607.04 | 5473.54 | 12080.58
06:30 | 6574.91 | 5424.41 | 11999.32
07:00 | 6542.78 | 5375.28 | 11918.06
07:30 | 6473.68 | 5384.93 | 11858.61
08:00 | 6404.58 | 5394.58 | 11799.16
08:30 | 6297.405 | 5456.805 | 11754.21
09:00 | 6190.23 | 5519.03 | 11709.26
09:30 | 6219.59 | 5652.795 | 11872.385
10:00 | 6248.95 | 5786.56 | 12035.51
10:30 | 6333.03 | 5817.1 | 12150.13
11:00 | 6417.11 | 5847.64 | 12264.75
11:30 | 6643.69 | 5914.075 | 12557.765
12:00 | 6870.27 | 5980.51 | 12850.78
12:30 | 7035.35 | 6115.86 | 13151.21
13:00 | 7200.43 | 6251.21 | 13451.64
13:30 | 7201.04 | 6215.45 | 13416.49
14:00 | 7201.65 | 6179.69 | 13381.34
14:30 | 7291.88 | 6128.905 | 13420.785
15:00 | 7382.11 | 6078.12 | 13460.23
15:30 | 7351.225 | 5807.135 | 13158.36
16:00 | 7320.34 | 5536.15 | 12856.49
16:30 | 7150.22 | 5404.495 | 12554.715
17:00 | 6980.1 | 5272.84 | 12252.94
17:30 | 6975.155 | 5156.135 | 12131.29
18:00 | 6970.21 | 5039.43 | 12009.64
18:30 | 7521.355 | 5492.65 | 13014.005
19:00 | 8072.5 | 5945.87 | 14018.37
19:30 | 8119.5 | 6090.8 | 14210.3
20:00 | 8200.5 | 6122.36 | 14322.86
20:30 | 8220.75 | 6180.68 | 14401.43 |  | Executive Engineer
21:00 | 8241 | 6239 | 14480 |  | Network Operation Division
21:30 | 8207 | 6211.5 | 14418.5
22:00 | 8173 | 6184 | 14357
22:30 | 7907.25 | 6043.5 | 13950.75
23:00 | 7641.5 | 5903 | 13544.5

## En-Curve
QF-LDC-12
Date | 14-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3540 | 1821 | 907 | 0 | 38 | 759.06 | 46 | 4362 | 0 | 723 | 2567.2 | 0 | 0 | 0 | 55 | DAILY ENERGY CURVE
00:30 | 3531 | 1832.4 | 906.5 | 0 | 35 | 758.995 | 46 | 4357 | 0 | 637.5 | 2359.45 | 0 | 0 | 0 | 64.5 | 14-04-2025
01:00 | 3522 | 1843.8 | 906 | 0 | 32 | 758.93 | 46 | 4352 | 0 | 552 | 2151.7 | 0 | 0 | 0 | 74
01:30 | 3522 | 1843.8 | 906 | 0 | 32 | 757.2 | 45.5 | 4351.5 | 0 | 483.5 | 1974.95 | 0 | 0 | 0 | 72 | Energy Generated | 316.5033 |  | MKWHr
02:00 | 3522 | 1843.8 | 906 | 0 | 32 | 755.47 | 45 | 4351 | 0 | 415 | 1798.2 | 0 | 0 | 0 | 70 | Energy not Served | 0.855 |  | MKWHr
02:30 | 3534 | 1839.3 | 906 | 0 | 32 | 755.535 | 44 | 4330.5 | 0 | 382.5 | 1627.7 | 0 | 0 | 0 | 67 | Total Energy Requirement | 317.3583 |  | MKWHr
03:00 | 3546 | 1834.8 | 906 | 0 | 32 | 755.6 | 43 | 4310 | 0 | 350 | 1457.2 | 0 | 0 | 0 | 64
03:30 | 3541.5 | 1838.3 | 906 | 0 | 31 | 756.83 | 42 | 4248 | 0 | 350.5 | 1402.2 | 0 | 0 | 0 | 57.5
04:00 | 3537 | 1841.8 | 906 | 0 | 30 | 758.06 | 41 | 4186 | 0 | 351 | 1347.2 | 0 | 0 | 0 | 51
04:30 | 3525 | 1841.8 | 906 | 0 | 30 | 757.215 | 41.5 | 4147.5 | 0 | 305 | 1260.7 | 0 | 0 | 0 | 44.5
05:00 | 3513 | 1841.8 | 906 | 0 | 30 | 756.37 | 42 | 4109 | 0 | 259 | 1174.2 | 0 | 0 | 0 | 38
05:30 | 3514 | 1835.9 | 906.5 | 0 | 29 | 757.04 | 43 | 3969.5 | 4.935 | 249 | 1047.1 | 0 | 0 | 0 | 19
06:00 | 3515 | 1830 | 907 | 0 | 28 | 757.71 | 44 | 3830 | 9.87 | 239 | 920 | 0 | 0 | 0 | 0
06:30 | 3529 | 1836 | 907 | 0 | 25 | 755.275 | 45 | 3705.5 | 60.545 | 239 | 897 | 0 | 0 | 0 | 0
07:00 | 3543 | 1842 | 907 | 0 | 22 | 752.84 | 46 | 3581 | 111.22 | 239 | 874 | 0 | 0 | 0 | 0
07:30 | 3521 | 1832.5 | 884 | 0 | 24 | 752.92 | 46 | 3581 | 163.69 | 231 | 822.5 | 0 | 0 | 0 | 15
08:00 | 3499 | 1823 | 861 | 0 | 26 | 753 | 46 | 3581 | 216.16 | 223 | 771 | 0 | 0 | 0 | 30
08:30 | 3499 | 1863.5 | 860.5 | 0 | 25 | 751.5 | 46 | 3611.5 | 301.71 | 186.5 | 609 | 0 | 0 | 0 | 30
09:00 | 3499 | 1904 | 860 | 0 | 24 | 750 | 46 | 3642 | 387.26 | 150 | 447 | 0 | 0 | 0 | 30
09:30 | 3504.5 | 1909 | 884.5 | 0 | 26 | 749 | 46 | 3734.5 | 448.885 | 150 | 420 | 0 | 0 | 0 | 37.5
10:00 | 3510 | 1914 | 909 | 0 | 28 | 748 | 46 | 3827 | 510.51 | 150 | 393 | 0 | 0 | 0 | 45
10:30 | 3553 | 1874.5 | 909 | 0 | 28 | 749.5 | 46 | 3831 | 543.13 | 157 | 459 | 0 | 0 | 0 | 37.5
11:00 | 3596 | 1835 | 909 | 0 | 28 | 751 | 46 | 3835 | 575.75 | 164 | 525 | 0 | 0 | 0 | 30
11:30 | 3612.5 | 1874.25 | 908.5 | 0 | 29 | 754 | 46 | 3889.5 | 581.015 | 152.5 | 706 | 0 | 0 | 4.5 | 30
12:00 | 3629 | 1913.5 | 908 | 0 | 30 | 757 | 46 | 3944 | 586.28 | 141 | 887 | 0 | 0 | 9 | 30
12:30 | 3624.5 | 1914.5 | 908.5 | 0 | 30 | 756.5 | 46 | 4028 | 553.71 | 156 | 1123.5 | 0 | 0 | 10 | 30
13:00 | 3620 | 1915.5 | 909 | 0 | 30 | 756 | 46 | 4112 | 521.14 | 171 | 1360 | 0 | 0 | 11 | 30
13:30 | 3585 | 1873.75 | 908.5 | 0 | 32 | 755.1 | 46 | 4074 | 482.64 | 199.5 | 1454.5 | 0 | 0 | 5.5 | 30
14:00 | 3550 | 1832 | 908 | 0 | 34 | 754.2 | 46 | 4036 | 444.14 | 228 | 1549 | 0 | 0 | 0 | 30
14:30 | 3525 | 1866 | 908.5 | 0 | 33 | 754.62 | 43 | 3994.5 | 434.065 | 227.5 | 1633.6 | 0 | 0 | 1 | 15
15:00 | 3500 | 1900 | 909 | 0 | 32 | 755.04 | 40 | 3953 | 423.99 | 227 | 1718.2 | 0 | 0 | 2 | 0
15:30 | 3466.5 | 1882 | 908.5 | 0 | 33 | 737.98 | 40 | 3879 | 351.93 | 211 | 1647.45 | 0 | 0 | 1 | 0
16:00 | 3433 | 1864 | 908 | 0 | 34 | 720.92 | 40 | 3805 | 279.87 | 195 | 1576.7 | 0 | 0 | 0 | 0
16:30 | 3452.5 | 1806.5 | 908.5 | 0 | 32 | 670.115 | 40 | 3740 | 198 | 195 | 1511.6 | 0 | 0 | 0.5 | 0
17:00 | 3472 | 1749 | 909 | 0 | 30 | 619.31 | 40 | 3675 | 116.13 | 195 | 1446.5 | 0 | 0 | 1 | 0
17:30 | 3414 | 1743 | 908.5 | 0 | 29 | 619.545 | 40 | 3633 | 63.745 | 223.5 | 1456.5 | 0 | 0 | 0.5 | 0
18:00 | 3356 | 1737 | 908 | 0 | 28 | 619.78 | 40 | 3591 | 11.36 | 252 | 1466.5 | 0 | 0 | 0 | 0
18:30 | 3475.5 | 1824 | 885.5 | 0 | 30 | 688.325 | 43 | 3796.5 | 5.68 | 414.5 | 1851 | 0 | 0 | 0 | 23
19:00 | 3595 | 1911 | 863 | 0 | 32 | 756.87 | 46 | 4002 | 0 | 577 | 2235.5 | 0 | 0 | 0 | 46
19:30 | 3606 | 1888 | 863 | 0 | 32 | 766.8 | 46 | 4046 | 0 | 638 | 2324.5 | 0 | 0 | 0 | 30
20:00 | 3692 | 1903 | 863 | 0 | 32 | 752.36 | 46 | 4074 | 0 | 688 | 2272.5 | 0 | 0 | 0 | 41
20:30 | 3673 | 1900.5 | 889 | 0 | 32 | 755.18 | 43 | 4107.5 | 0 | 685 | 2316.25 | 0 | 0 | 0 | 54
21:00 | 3654 | 1898 | 915 | 0 | 32 | 758 | 40 | 4141 | 0 | 682 | 2360 | 0 | 0 | 0 | 67
21:30 | 3642.5 | 1893 | 915.5 | 0 | 33 | 754.5 | 40 | 4131 | 0 | 668 | 2341 | 0 | 0 | 0 | 59
22:00 | 3631 | 1888 | 916 | 0 | 34 | 751 | 40 | 4121 | 0 | 654 | 2322 | 0 | 0 | 0 | 51
22:30 | 3598 | 1877.25 | 916.5 | 0 | 34 | 754 | 40 | 4028 | 0 | 625.5 | 2077.5 | 0 | 0 | 0 | 62
23:00 | 3565 | 1866.5 | 917 | 0 | 34 | 757 | 40 | 3935 | 0 | 597 | 1833 | 0 | 0 | 0 | 73
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 14-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 08:00 | 381 | 13:00 | Payra | 414 | 07:00 | 407 | 13:00
Ashuganj | 406 | 7:00 | 385 | 13:00 | Rahanpur | 406 | 06:00 | 395 | 19:30
Bhulta | 401 | 06:00 | 382 | 13:00 | Rampal | 406 | 18:00 | 393 | 00:00
Bibiana | 390 | 19:00 | 378 | 13:00
BIPTC | 401 | 09:00 | 391 | 13:00
Bogura | 402 | 00:00 | 388 | 19:30
Gopalganj | 403 | 18:00 | 385 | 10:00
Kaliakoir | 369 | 18:00 | 353 | 13:00
Madunaghat | 403 | 18:00 | 395 | 11:00
Meghnaghat | 398 | 08:00 | 385 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 08:00 | 220 | 03:00 | Keranigonj | 230 | 08:00 | 219 | 13:00
AKSML | 233 | 21:00 | 223 | 11:00 | Khulna(S) | 233 | 17:00 | 220 | 00:00
Aminbazar | 232 | 07:00 | 224 | 14:00 | Madunaghat | 236 | 19:00 | 226 | 10:00
Ashuganj | 232 | 07:00 | 223 | 12:00 | Madunaghat-400 | 237 | 23:00 | 227 | 11:00
Ashuganj-400 | 232 | 07:00 | 223 | 12:00 | Maniknagar | 228 | 07:00 | 219 | 12:00
Baghabari | 233 | 05:00 | 225 | 12:00 | Meghnaghat | 236 | 07:00 | 227 | 13:00
Barapukuria | 225 | 00:00 | 215 | 20:00 | Meghnaghat-400 | 231 | 08:00 | 222 | 13:00
Barapukuria-230 | 225 | 00:00 | 215 | 20:00 | Mirsorai | 232 | 19:30 | 219 | 11:00
Barishal | 237 | 17:00 | 227 | 01:00 | Rajshahi | 233 | 06:00 | 220 | 12:00
Bheramara | 235 | 08:00 | 222 | 12:00 | Rampal | 232 | 18:00 | 220 | 13:00
Bhulta | 228 | 07:00 | 216 | 13:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 223 | 03:00 | 216 | 13:00 | Rampura | 228 | 07:00 | 216 | 13:00
BIPTC | 236 | 06:00 | 222 | 13:00 | Shikalbaha | 233 | 20:00 | 222 | 10:00
Bogura | 228 | 00:00 | 219 | 19:30 | Shyampur | 230 | 18:00 | 220 | 13:00
Bogura-400 | 227 | 00:00 | 217 | 19:30 | Siddhirganj | 230 | 18:00 | 220 | 13:00
Borhanuddin | 242 | 17:00 | 234 | 00:00 | Sirajgonj | 238 | 04:00 | 233 | 12:00
BSRM | 231 | 19:30 | 219 | 10:00 | Sreepur | 230 | 08:00 | 221 | 12:00
Cumilla(N) | 225 | 07:00 | 215 | 13:00 | Tongi | 225 | 04:00 | 213 | 13:00
Faridpur | 230 | 17:00 | 220 | 13:00
Fenchuganj | 224 | 19:00 | 220 | 01:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 227 | 07:00 | 216 | 13:00
Gopalganj | 231 | 18:00 | 223 | 00:00
GPH | 233 | 19:00 | 222 | 10:00
Haripur | 228 | 18:00 | 222 | 01:00
Hasnabad | 230 | 18:00 | 219 | 13:00
Hathazari | 235 | 22:00 | 220 | 08:00
Ishurdi | 236 | 06:00 | 224 | 13:00
Jhenaidah | 233 | 23:00 | 215 | 13:00
Kaliakoir | 230 | 07:00 | 219 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 04:00 | 123 | 13:00 | Madartek | 132 | 08:00 | 123 | 13:00
Agargaon | 133 | 08:00 | 126 | 13:00 | Madunaghat | 136 | 19:00 | 130 | 08:00
Agrabad | 135 | 19:00 | 126 | 10:00 | Magura | 136 | 23:00 | 122 | 13:00
AKS | 133 | 19:00 | 126 | 10:00 | Mahasthangarh | 132 | 01:00 | 123 | 20:00
Aminbazar | 133 | 07:00 | 127 | 11:00 | Manikganj | 129 | 18:00 | 123 | 00:00
Amnura | 137 | 23:00 | 125 | 20:00 | Maniknagar | 130 | 06:00 | 124 | 12:00
Ashuganj | 139 | 06:00 | 133 | 13:00 | Matarbari | 121 | 12:00 | 112 | 05:00
Bagerhat | 137 | 17:00 | 121 | 00:00 | Matuail | 133 | 02:00 | 127 | 13:00
Bajitpur | 133 | 05:00 | 127 | 12:00 | Millgate | 131 | 06:00 | 122 | 13:00
Bakulia | 136 | 21:00 | 128 | 10:00 | Mirpur | 132 | 05:00 | 125 | 10:00
Banani | 132 | 06:00 | 123 | 13:00 | Mirzapur | 128 | 07:00 | 120 | 10:00
Bangabhaban | 131 | 08:00 | 123 | 13:00 | Mithapukur | 132 | 00:00 | 122 | 20:00
Barapukuria | 137 | 00:00 | 128 | 19:30 | MI_Cement | 135 | 19:00 | 127.2 | 13:00
Barguna | 135 | 18:00 | 130 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 17:00 | 124 | 00:00 | Mogbazar | 133 | 07:00 | 125 | 13:00
Barishal-230 | 133 | 17:00 | 125 | 00:00 | Mongla | 138 | 17:00 | 122 | 00:00
Baroaulia | 134 | 19:00 | 127 | 10:00 | Motijheel | 131 | 08:00 | 123 | 13:00
Baroirhat | 125 | 18:00 | 117 | 10:00 | Muktagacha | 130 | 00:00 | 118 | 10:00
Bashundhara | 133 | 08:00 | 122 | 12:00 | Munshiganj | 133 | 07:00 | 126 | 13:00
BashundharaCement | 133 | 18:00 | 126 | 13:00 | Muradnagar | 128 | 07:00 | 120 | 13:00
Beanibazar | 129 | 05:00 | 125 | 13:00 | Mymensingh | 129 | 18:00 | 115 | 13:00
Benapole | 138 | 23:00 | 116 | 13:00 | Naogaon | 130 | 00:00 | 121 | 19:30
Bhaluka | 133 | 06:00 | 124 | 12:00 | Narail | 137 | 23:00 | 122 | 13:00
Bhandaria | 129 | 18:00 | 115 | 00:00 | Narinda | 130 | 06:00 | 124 | 12:00
Bhangura | 132 | 04:00 | 125 | 12:00 | Narshingdi | 129 | 08:00 | 117 | 12:00
Bheramara | 137 | 08:00 | 129 | 12:00 | Natore | 132 | 07:00 | 125 | 13:00
Bheramara(GK) | 137 | 06:00 | 129 | 12:00 | Nawabganj | 133 | 06:00 | 126 | 12:00
Bhulta | 127 | 18:00 | 121 | 13:00 | Netrakona | 125 | 06:00 | 113 | 20:00
Bog-Sherpur | 130 | 00:00 | 124 | 19:30 | New | 132 | 18:00 | 124 | 13:00
Bogura | 133 | 01:00 | 125 | 20:00 | Niamatpur | 133 | 03:00 | 130 | 20:00
Bogura-230 | 134 | 00:00 | 126 | 19:30 | Noapara | 138 | 23:00 | 124 | 13:00
Brahmanbaria | 129 | 08:00 | 122 | 12:00 | Pabna | 135 | 23:00 | 127 | 12:00
Cantonment | 133 | 06:00 | 126 | 13:00 | Palashbari | 132 | 01:00 | 120 | 19:30
Chandina | 129 | 07:00 | 123 | 13:00 | Panchagarh | 139 | 00:00 | 119 | 12:00
Chandpur | 128 | 18:00 | 116 | 14:00 | Patuakhali | 135 | 16:00 | 131 | 13:00
Chandraghona | 135 | 19:00 | 129 | 09:00 | Payra | 136 | 08:00 | 133 | 00:00
Chapai | 132 | 04:00 | 127 | 18:30 | PHP | 124 | 18:00 | 116 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 08:00 | 127 | 13:00 | Postogola | 136 | 08:00 | 129 | 13:00
Chauddagram | 124 | 07:00 | 116 | 10:00 | Purbachal | 132 | 05:00 | 124 | 12:00
Chhatak | 129 | 06:00 | 123 | 18:30 | Purbasadipur | 134 | 00:00 | 120 | 19:00
Chowmuhani | 120 | 18:00 | 110 | 14:00 | Rahanpur | 136 | 03:00 | 131 | 19:30
Chuadanga | 137 | 23:00 | 120 | 00:00 | Rahanpur-400 | 135 | 00:00 | 131 | 19:30
Coxsbazar | 122 | 21:00 | 113 | 10:00 | Rahim | 134 | 08:00 | 127 | 13:00
Cumilla(N) | 129 | 07:00 | 122 | 13:00 | Rajbari | 134 | 06:00 | 127 | 00:00
Cumilla(S) | 133 | 00:00 | 120 | 13:00 | Rajendrapur | 134 | 06:00 | 123 | 13:00
Daudkandi | 128 | 08:00 | 120 | 13:00 | Rajshahi | 134 | 05:00 | 127 | 12:00
Dhaka | 133 | 06:00 | 124 | 13:00 | Rajshahi-230 | 135 | 06:00 | 121 | 13:00
Dhamrai | 130 | 08:00 | 124 | 10:00 | Ramganj | 121 | 18:00 | 109 | 14:00
Dhanmondi | 134 | 06:00 | 128 | 12:00 | Rampur | 134 | 19:00 | 126 | 10:00
Dohazari | 132 | 21:00 | 122 | 10:00 | Rampura | 132 | 06:00 | 124 | 13:00
Faridpur | 135 | 06:00 | 130 | 00:00 | Rangamati | 134 | 19:30 | 127 | 13:00
Fatullah | 135 | 08:00 | 128 | 12:00 | Rangpur | 133 | 00:00 | 120 | 20:00
Fenchuganj | 134 | 07:00 | 130 | 02:00 | Ruppur | 136 | 05:00 | 130 | 13:00
Feni | 123 | 22:00 | 117 | 15:00 | Saidpur | 134 | 00:00 | 120 | 20:00
Ghatail | 125 | 00:00 | 116 | 10:00 | Satkhira | 135 | 23:00 | 120 | 00:00
Ghorashal | 138 | 19:00 | 131 | 12:00 | Satmasjid | 133 | 06:00 | 126 | 13:00
Goalpara | 138 | 08:00 | 128 | 00:00 | Savar | 134 | 18:30 | 125 | 10:00
Gollamari | 139 | 17:00 | 128 | 01:00 | SevenRings | 137 | 06:00 | 130 | 13:00
Gopalganj | 138 | 16:00 | 128 | 00:00 | ShahCement | 134 | 08:00 | 127 | 13:00
Gopalganj-400 | 138 | 17:00 | 132 | 00:00 | Shahjadpur | 135 | 04:00 | 131 | 10:00
Gulshan | 132 | 07:00 | 124 | 13:00 | Shahjibazar | 131 | 07:00 | 124 | 12:00
Halishahar | 135 | 19:00 | 123 | 18:30 | Shahmirpur | 137 | 21:00 | 130 | 08:00
Haripur | 133 | 07:00 | 131 | 00:00 | Shariatpur | 137 | 17:00 | 125 | 00:00
HaripurSBU | 133 | 18:30 | 129 | 11:00 | Sherpur | 131 | 18:00 | 114 | 10:00
Hasnabad | 136 | 07:00 | 129 | 12:00 | Shikalbaha | 125 | 19:30 | 119 | 05:00
Hathazari | 136 | 18:30 | 130 | 10:00 | Shikalbaha-230 | 137 | 20:00 | 129 | 10:00
Ishurdi | 138 | 06:00 | 131 | 12:00 | Shitalakhya | 135 | 19:00 | 127.2 | 13:00
Jaldhaka | 132 | 00:00 | 118 | 19:30 | Sholosohor | 135 | 19:00 | 128 | 10:00
Jamalpur | 136 | 00:00 | 120 | 10:00 | Shyampur | 135 | 18:00 | 127 | 13:00
Jashore | 138 | 23:00 | 120 | 13:00 | Shyampur-230 | 135 | 18:00 | 127 | 13:00
Jhenaidah | 141 | 23:00 | 123 | 13:00 | Siddhirganj | 134 | 07:00 | 128 | 12:00
Jhenaidah-230 | 139 | 23:00 | 124 | 13:00 | Sirajganj | 130 | 02:00 | 123 | 19:30
Joydebpur | 134 | 15:00 | 125 | 13:00 | Sonargaon | 132 | 06:00 | 125 | 11:00
Joypurhat | 129 | 05:00 | 119 | 19:30 | Sreemongol | 131 | 08:00 | 124 | 23:00
Juldah | 137 | 21:00 | 129 | 09:00 | Sreepur | 135 | 06:00 | 128 | 12:00
Kabirpur | 134 | 18:30 | 122 | 12:00 | Srinagar | 134 | 07:00 | 127 | 12:00
Kachua | 126 | 18:00 | 117 | 10:00 | SSM | 137 | 00:00 | 132 | 03:00
Kaliakoir | 134 | 18:00 | 125 | 13:00 | Sunamganj | 126 | 06:00 | 121 | 21:00
Kallyanpur | 133 | 07:00 | 126 | 10:00 | Sylhet | 130 | 06:00 | 126 | 19:30
Kalurghat | 135 | 19:00 | 128 | 10:00 | Sylhet-132 | 131 | 06:00 | 128 | 13:00
Kamrangirchar | 134 | 18:00 | 124 | 13:00 | Tangail | 125 | 19:00 | 116 | 13:00
Kaptai | 134 | 6:00 | 122 | 12:00 | Thakurgaon | 138 | 00:00 | 117 | 12:00
Kasba | 127 | 07:00 | 119 | 13:00 | TK | 137 | 19:30 | 129 | 10:00
Kazla | 130 | 07:00 | 123 | 13:00 | Tongi | 132 | 04:00 | 126 | 13:00
Keranigonj | 135 | 08:00 | 127 | 13:00 | Ullahpara | 138 | 01:00 | 124 | 20:00
Khagrachori | 133 | 19:00 | 126 | 10:00 | Ullon | 132 | 06:00 | 123 | 13:00
Khulna | 138 | 17:00 | 126 | 00:00 | Uttara | 132 | 04:00 | 125 | 11:00
Khulna(S) | 139 | 17:00 | 128 | 13:00 | UttaraNew | 130 | 18:00 | 122 | 13:00
Khulshi | 133 | 19:00 | 125 | 11:00 | Zigatola | 134 | 07:00 | 127 | 13:00
Kishoreganj | 132 | 05:00 | 123 | 22:00
Kodda | 133 | 15:00 | 123 | 13:00
KSRM | 135 | 19:00 | 127 | 10:00
Kulaura | 133 | 06:00 | 130 | 01:00
Kurigram | 130 | 00:00 | 118 | 20:00
Kushtia | 138 | 23:00 | 126 | 13:00
Lalbag | 134 | 06:00 | 126 | 13:00
Lalmonirhat | 130 | 14:00 | 121 | 20:00
Madanganj | 133 | 16:00 | 126 | 13:00
Madaripur | 137 | 18:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division