## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-04-2025 | during | 16-04-2025 | during | 16-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 404 | 333 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 292 | 286 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 24.4 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 96 | 37 | 208.13 | 208.13 | 100 | 100 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 317 | 265 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 58 | 8 | 102 | 58 | 58 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 29 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 80 | 114 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 29 | 55 | 55 | 35 | 35 | Machine Problem
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 17 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 7 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 110 | 240 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 122 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 57 | 105 | 105 | 34 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 20 | 62 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 144 | 130 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 16 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 400 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2387 | 2916.4 | 5236.9 | 5298.9 | 3639.13 | 3625.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 11 | 47 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 147 | 148 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 53 | 93 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 16 | 75 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 22 | 85 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 33 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 10 | 2 | 15 | 2 | 15 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 10 | 46 | 108 | 108 | 58 | 58 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 3.88 | 0 | 3.88 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 30 | 25 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 17 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 60 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 88 | 100 | 100 | 40 | 40 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 13 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 35 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1101 | 1100 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 4 | 0 | 1 | 3 | 1 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 162 | 159 | 155 | 155 | 160 | 160 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1810 | 2291.5 | 2981.6 | 2995.72 | 2876.6 | 2890.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 180 | 173 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 250 | 240 | 356.56 | 356.56 | 310 | 310 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 31 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 47 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 160 | 170 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 85 | 122 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 38 | 38 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 75 | 70 | 163 | 163 | 85 | 85 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 116 | 166 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 59 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 14 | 38 | 113 | 113 | 9 | 37 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 51 | 76 | 115 | 115 | 84 | 84 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1646 | 1743.2 | 2462.55 | 2392.55 | 2171.55 | 2129.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-04-2025 | during | 16-04-2025 | during | 16-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 6 | 157.5 | 157.5 | 23 | 23 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 105 | 181 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 94 | 115 | 115 | 100 | 100 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.71 | 0 | 49.6 | 0 | 49.6 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 254.71 | 347.5 | 600.6 | 549 | 451.1 | 399.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 36 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 158 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 172 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 379 | 353 | 380 | 380 | 352 | 352 | Fgmo activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 312 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1540 | 1527 | 1609 | 1609 | 1540 | 1540
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 900 | 852 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 12 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 5 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 40 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 350 | 353 | 1234.2 | 1234.2 | 300 | 300 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1379 | 1262 | 3602.2 | 3512.2 | 1817.01 | 1727.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 513 | 731 | 1080 | 1058 | 860 | 860 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 32 | 26 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 1101 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 15 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.68 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 2364.68 | 2521 | 3252.12 | 3229.12 | 3020.12 | 3019.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 34 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 11 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 28 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 210 | 155 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 150 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 140 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 374 | 381 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 15 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 33 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 23 | 94 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 30 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.15 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 736.7 | 1360 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.37 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 107 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1874.22 | 2456 | 3107.53 | 2941.53 | 3054.74 | 2888.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 56 | 0 | 0 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 115 | 166 | 110 | 110 | 115 | 115 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.7 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 91 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 182 | 0 | 177.33 | 0 | 177.33 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 482.7 | 426 | 585.73 | 372 | 645.73 | 432
System Total |  |  |  |  | 27566.2 | 28535.742 | 13738.31 | 15490.6 | 23438.23 | 22900.02 | 19215.98 | 18651.77
Forecast Scenario (16-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14000 |  | 0 |  | 14000
|  |  |  | 1:00 | 13860 |  | 0 |  | 13860
|  |  |  | 2:00 | 13300 |  | 0 |  | 13300
|  |  |  | 3:00 | 12950 |  | 0 |  | 12950
|  |  |  | 4:00 | 12760 |  | 0 |  | 12760
|  |  |  | 5:00 | 12550 |  | 0 |  | 12550
|  |  |  | 6:00 | 12100 |  | 0 |  | 12100
|  |  |  | 7:00 | 12280 |  | 0 |  | 12280
|  |  |  | 8:00 | 12460 |  | 0 |  | 12460
|  |  |  | 9:00 | 12940 |  | 0 |  | 12940
|  |  |  | 10:00 | 13220 |  | 0 |  | 13220
|  |  |  | 11:00 | 13580 |  | 0 |  | 13580
|  |  |  | 12:00 | 14030 |  | 0 |  | 14030
|  |  |  | 13:00 | 14530 |  | 0 |  | 14530
|  |  |  | 14:00 | 14800 |  | 0 |  | 14800
|  |  |  | 15:00 | 14830 |  | 0 |  | 14830
|  |  |  | 16:00 | 14770 |  | 0 |  | 14770
|  |  |  | 17:00 | 14380 |  | 0 |  | 14380
|  |  |  | 18:00 | 13810 |  | 0 |  | 13810
|  |  |  | 18:30 | 14700 |  | 0 |  | 14700
|  |  |  | 19:00 | 15670 |  | 0 |  | 15670
|  |  |  | 19:30 | 15720 |  | 0 |  | 15720
|  |  |  | 20:00 | 15690 |  | 0 |  | 15690
|  |  |  | 21:00 | 15410 |  | 0 |  | 15410
|  |  |  | 22:00 | 14920 |  | 0 |  | 14920
|  |  |  | 23:00 | 14210 |  | 0 |  | 14210
Probable Maximum Temperature: |  |  | 35.40°C
Probable Maximum Demand at Day Peak: |  |  | 14030.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15720.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15220.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 321.05 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:25 hrs on 16-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-04-2025 | [28 empty] | Date: | 15-04-2025 | [28 empty] | Date: | 15-04-2025 | [28 empty] | Date: | 15-04-2025 | [28 empty] | Date: | 15-04-2025 | [16 empty] | Date: | 15-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 36 | 68 | 95 | 95 | 0 | 35 | 54 | 0 | 66 | 225 | 305 | 450 | 0 | 35 | 0 | 325 | 97 | 0 | 0 | 125 | 16 | 7 | 0 | 0 | 0 | 30 | 25 | 0 | 1 | 34 | 55 | 0 | 33 | 48 | 0 | 40 | 68 | 28 | 160 | 0 | 0 | 0 | 8 | 68 | 148 | 0 | 0 | 0 | 1050 | 0 | 43 | 117 | 162 | 0 | 300 | 0 | 50 | 195 | 33 | 92 | 80 | 155 | 14 | 19 | 80 | 36 | 34 | 0 | 39 | 245 | 320 | 363 | 39 | 39 | 0 | 152 | 21 | 0 | 82 | 28 | 0 | 17 | 171 | 0 | 96 | 145 | 22 | 0 | 0 | 9 | 7486 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 743 | 0 | 756 | 0 | 42 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 198 | 0 | 197 | 0 | 414 | 0 | 0 | 0 | 114 | 57 | 52 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 108 | 180 | 0 | 287 | 950 | 0 | 5499 | 12985 | 82.25
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 68 | 16 | 0 | 0 | 35 | 35 | 0 | 0 | 225 | 286 | 420 | 0 | 35 | 0 | 326 | 99 | 0 | 0 | 125 | 16 | 7 | 0 | 0 | 0 | 30 | 25 | 0 | 0 | 34 | 0 | 0 | 33 | 48 | 0 | 40 | 34 | 27 | 160 | 0 | 0 | 0 | 8 | 68 | 148 | 0 | 0 | 0 | 1000 | 0 | 43 | 40 | 155 | 0 | 300 | 0 | 50 | 182 | 34 | 80 | 70 | 155 | 16 | 19 | 80 | 34 | 34 | 0 | 39 | 270 | 320 | 351 | 39 | 40 | 0 | 143 | 21 | 0 | 82 | 25 | 0 | 17 | 171 | 0 | 48 | 65 | 22 | 0 | 0 | 0 | 6744 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741 | 0 | 758 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 196 | 0 | 190 | 0 | 320 | 0 | 0 | 0 | 116 | 57 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 10 | 108 | 180 | 0 | 338 | 900 | 0 | 5254 | 11998 | 82.24
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 25 | 16 | 0 | 0 | 0 | 35 | 0 | 0 | 225 | 299 | 370 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 50 | 16 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 34 | 0 | 0 | 33 | 48 | 0 | 40 | 0 | 27 | 160 | 0 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 85 | 0 | 300 | 0 | 51 | 184 | 34 | 72 | 70 | 136 | 9 | 19 | 80 | 32 | 34 | 0 | 0 | 265 | 320 | 350 | 39 | 40 | 0 | 133 | 21 | 0 | 82 | 25 | 0 | 17 | 171 | 0 | 17 | 45 | 22 | 0 | 0 | 0 | 5906 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 0 | 660 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 151 | 0 | 130 | 0 | 320 | 0 | 0 | 0 | 116 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 10 | 108 | 180 | 0 | 383 | 897 | 0 | 5085 | 10991 | 82.23
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 300 | 370 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 34 | 0 | 0 | 22 | 48 | 0 | 40 | 0 | 33 | 160 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 836 | 0 | 43 | 0 | 85 | 0 | 300 | 0 | 14 | 198 | 5 | 72 | 70 | 100 | 9 | 19 | 80 | 32 | 24 | 0 | 0 | 270 | 320 | 378 | 39 | 40 | 0 | 134 | 16 | 0 | 82 | 25 | 0 | 17 | 173 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 5529 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 741 | 0 | 598 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 147 | 0 | 130 | 0 | 320 | 0 | 0 | 0 | 118 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 1 | 108 | 180 | 0 | 386 | 821 | 0 | 4906 | 10435 | 82.22
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 306 | 370 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 20 | 0 | 0 | 22 | 36 | 0 | 40 | 0 | 37 | 161 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 761 | 0 | 43 | 0 | 85 | 0 | 300 | 0 | 5 | 186 | 5 | 72 | 70 | 100 | 9 | 19 | 80 | 30 | 8 | 0 | 0 | 275 | 320 | 360 | 39 | 40 | 0 | 134 | 16 | 0 | 82 | 25 | 0 | 17 | 173 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 5383 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 0 | 534 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 178 | 0 | 156 | 0 | 320 | 0 | 0 | 0 | 120 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 1 | 108 | 180 | 0 | 389 | 757 | 0 | 4841 | 10224 | 82.21
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 309 | 320 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 25 | 0 | 9 | 0 | 0 | 0 | 22 | 24 | 0 | 40 | 0 | 37 | 159 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 713 | 0 | 5 | 0 | 85 | 0 | 300 | 130 | 5 | 209 | 5 | 68 | 70 | 85 | 9 | 19 | 17 | 30 | 0 | 0 | 0 | 280 | 320 | 320 | 39 | 40 | 0 | 129 | 0 | 0 | 62 | 28 | 0 | 17 | 171 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 5188 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 728 | 0 | 435 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 184 | 0 | 171 | 0 | 320 | 0 | 0 | 0 | 117 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 1 | 120 | 180 | 0 | 391 | 680 | 0 | 4632 | 9820 | 82.2
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 311 | 320 | 0 | 0 | 0 | 280 | 0 | 0 | 1 | 0 | 16 | 7 | 0 | 0 | 0 | 0 | 17 | 0 | 1 | 0 | 0 | 0 | 22 | 0 | 0 | 40 | 0 | 33 | 159 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 658 | 1 | 5 | 0 | 85 | 0 | 300 | 240 | 5 | 216 | 5 | 40 | 70 | 68 | 9 | 19 | 0 | 28 | 0 | 0 | 0 | 275 | 320 | 363 | 39 | 40 | 0 | 135 | 8 | 0 | 62 | 30 | 0 | 17 | 172 | 0 | 0 | 0 | 35 | 0 | 0.09 | 0 | 5203.09 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.54 | 742 | 0 | 412 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 140 | 0 | 320 | 0 | 0 | 0 | 117 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 140 | 0 | 110 | 180 | 0 | 404 | 600 | 0 | 4463.54 | 9666.63 | 82.19
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 312 | 450 | 0 | 0 | 0 | 331 | 0 | 0 | 4 | 0 | 13 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 22 | 0 | 0 | 40 | 0 | 20 | 161 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 655 | 5 | 5 | 0 | 88 | 0 | 358 | 250 | 5 | 206 | 35 | 19 | 70 | 34 | 9 | 19 | 0 | 26 | 0 | 5 | 0 | 275 | 320 | 368 | 36 | 40 | 0 | 154 | 16 | 0 | 62 | 30 | 0 | 17 | 172 | 0 | 9 | 32 | 32 | 0 | 4.11 | 0 | 5560.11 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.03 | 702 | 0 | 417 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 10.03 | 140 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 0.82 | 0 | 116 | 55 | 0 | 2 | 0 | 0 | 0 | 1.3 | 8 | 0.12 | 0 | 200 | 0 | 108 | 220 | 0 | 430 | 600 | 0 | 4698.3 | 10258.41 | 82.18
08:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 0 | 17 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 303 | 450 | 0 | 0 | 0 | 335 | 0 | 0 | 7 | 0 | 14 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 791 | 11 | 26 | 0 | 86 | 0 | 360 | 250 | 5 | 194 | 35 | 16 | 70 | 34 | 9 | 19 | 0 | 34 | 0 | 15 | 0 | 280 | 320 | 390 | 36 | 40 | 0 | 159 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 24 | 32 | 30 | 0 | 13.01 | 0 | 5779.01 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 527 | 0 | 516 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 13.88 | 195 | 0 | 198 | 0 | 186 | 0 | 414 | 0 | 1.31 | 0 | 118 | 55 | 35 | 5 | 34 | 0 | 0 | 4.1 | 19 | 0.2 | 0 | 200 | 3 | 120 | 220 | 0 | 450 | 695 | 0 | 4985.49 | 10764.5 | 82.17
09:00 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0 | 0 | 17 | 54 | 16 | 0 | 0 | 3 | 50 | 0 | 0 | 300 | 290 | 583 | 0 | 10 | 0 | 333 | 0 | 0 | 14 | 17 | 19 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 16 | 0 | 0 | 0 | 12 | 5 | 1 | 40 | 0 | 3 | 160 | 0 | 0 | 0 | 0 | 3 | 152 | 0 | 0 | 0 | 850 | 7 | 43 | 1 | 150 | 0 | 360 | 250 | 13 | 199 | 0 | 16 | 70 | 34 | 9 | 15 | 17 | 34 | 1 | 31 | 0 | 280 | 320 | 350 | 36 | 40 | 0 | 157 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 27 | 45 | 20 | 1 | 19.85 | 0 | 6222.85 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 336 | 0 | 618.05 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 15.05 | 206 | 0 | 199 | 0 | 189 | 0 | 414 | 0 | 1.5 | 0 | 117 | 56 | 35 | 9 | 34 | 0 | 0 | 4 | 63 | 0.43 | 0 | 244 | 4 | 108 | 220 | 0 | 453 | 850 | 0 | 5211.03 | 11433.88 | 82.16
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 17 | 17 | 102 | 48 | 95 | 0 | 35 | 90 | 0 | 6 | 380 | 305 | 500 | 0 | 17 | 0 | 326 | 0 | 0 | 20 | 35 | 19 | 7 | 0 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 0 | 0 | 12 | 12 | 0 | 40 | 17 | 3 | 160 | 0 | 0 | 0 | 0 | 51 | 152 | 0 | 0 | 0 | 852 | 15 | 43 | 30 | 157 | 0 | 357 | 250 | 40 | 188 | 10 | 18 | 85 | 37 | 9 | 19 | 17 | 34 | 8 | 66 | 0 | 275 | 320 | 310 | 38 | 40 | 0 | 136 | 16 | 0 | 79 | 30 | 0 | 17 | 172 | 0 | 45 | 83 | 20 | 2 | 11.66 | 0 | 6773.66 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 338 | 0 | 739.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 46.97 | 214 | 0 | 200 | 0 | 189 | 0 | 414 | 0 | 3.25 | 0 | 115 | 56 | 35 | 15 | 34 | 0 | 0 | 6.1 | 128 | 0.58 | 0 | 250 | 4 | 88 | 220 | 0 | 486 | 890 | 0 | 5474.19 | 12247.85 | 82.15
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 23 | 17 | 113 | 48 | 110 | 7 | 35 | 126 | 0 | 15 | 450 | 306 | 0 | 0 | 35 | 0 | 320 | 0 | 0 | 30 | 40 | 19 | 7 | 0 | 0 | 13 | 30 | 0 | 0 | 2 | 0 | 0 | 12 | 33 | 48 | 5 | 40 | 20 | 3 | 160 | 5 | 0 | 0 | 0 | 51 | 150 | 0 | 0 | 0 | 1000 | 18 | 43 | 50 | 158 | 0 | 340 | 250 | 47 | 202 | 31 | 37 | 85 | 53 | 9 | 19 | 52 | 30 | 17 | 72 | 2 | 295 | 320 | 368 | 38 | 40 | 0 | 143 | 16 | 0 | 81 | 30 | 0 | 17 | 172 | 0 | 50 | 86 | 18 | 2 | 29.77 | 4 | 6975.77 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 342 | 17 | 738.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 51.2 | 214 | 0 | 199 | 0 | 189 | 0 | 414 | 0 | 4.36 | 0 | 118 | 56 | 45 | 35 | 34 | 0 | 0 | 3.4 | 204 | 0.42 | 16 | 307 | 6 | 108 | 220 | 0 | 485 | 930 | 35 | 5798.07 | 12773.84 | 82.14
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 17 | 113 | 80 | 110 | 15 | 35 | 144 | 0 | 20 | 450 | 292 | 0 | 0 | 55 | 0 | 317 | 96 | 0 | 31 | 70 | 19 | 7 | 0 | 0 | 35 | 30 | 10 | 0 | 4 | 22 | 16 | 17 | 33 | 48 | 3 | 40 | 34 | 3 | 162 | 35 | 0 | 11 | 0 | 53 | 147 | 0 | 0 | 0 | 1101 | 6 | 43 | 85 | 160 | 0 | 340 | 250 | 47 | 180 | 31 | 51 | 75 | 116 | 14 | 13 | 70 | 36 | 25 | 72 | 38 | 300 | 320 | 379 | 38 | 39 | 0 | 147 | 16 | 0 | 81 | 30 | 0 | 17 | 173 | 0 | 77 | 105 | 10 | 2 | 48.71 | 12 | 7637.71 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 350 | 35 | 736.7 | 0 | 0 | 0 | 23 | 0 | 0 | 35 | 0 | 0 | 107 | 0 | 51.37 | 210 | 0 | 195 | 0 | 140 | 0 | 374 | 0 | 2.15 | 0 | 115 | 56 | 70 | 23 | 34 | 0 | 0 | 2.7 | 182 | 0.68 | 32 | 307 | 7 | 120 | 220 | 0 | 513 | 1130 | 35 | 6100.6 | 13738.31 | 82.13
13:00 | 0 | 44 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 31 | 17 | 101 | 64 | 118 | 13.41 | 33 | 148 | 0 | 35 | 350 | 301 | 65 | 0 | 55 | 0 | 311 | 96 | 0 | 31 | 90 | 18 | 7 | 0 | 0 | 30 | 40 | 21 | 0 | 12 | 34 | 40 | 17 | 33 | 88 | 5 | 40 | 50 | 5 | 160 | 35 | 0 | 19 | 3 | 74 | 146 | 0 | 0 | 0 | 1100 | 19 | 43 | 115 | 160 | 0 | 338 | 235 | 46 | 180 | 33 | 63 | 50 | 156 | 10 | 13 | 60 | 42 | 25 | 70 | 38 | 310 | 342 | 365 | 38 | 40 | 0 | 152 | 16 | 0 | 78 | 28 | 0 | 17 | 173 | 0 | 76 | 113 | 10 | 2 | 46.79 | 12 | 7785.2 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 351 | 35 | 728.68 | 0 | 0 | 0 | 80 | 0 | 0 | 46 | 0 | 0 | 103 | 0 | 36.2 | 163 | 0 | 175 | 0 | 140 | 0 | 373 | 0 | 4.31 | 0 | 158 | 56 | 65 | 31 | 48 | 0 | 0 | 2.9 | 194 | 0.65 | 28 | 307 | 8 | 120 | 220 | 0 | 540 | 1240 | 33 | 6278.74 | 14063.94 | 82.12
14:00 | 0 | 46 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 31 | 16 | 102 | 66 | 126 | 13.41 | 32 | 142 | 0 | 56 | 350 | 302 | 65 | 0 | 55 | 0 | 311 | 96 | 0 | 15 | 108 | 18 | 7 | 0 | 0 | 30 | 45 | 24 | 0 | 19 | 33 | 40 | 16 | 33 | 88 | 4 | 40 | 68 | 5 | 160 | 35 | 0 | 19 | 8 | 96 | 146 | 0 | 0 | 0 | 1100 | 15 | 43 | 120 | 160 | 0 | 337 | 230 | 46 | 182 | 32 | 71 | 50 | 177 | 9 | 13 | 62 | 40 | 25 | 63 | 38 | 315 | 342 | 389 | 38 | 40 | 0 | 150 | 24 | 0 | 78 | 28 | 0 | 17 | 173 | 0 | 76 | 113 | 10 | 2 | 41.1 | 12 | 7890.51 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 352 | 35 | 731 | 0 | 0 | 0 | 96 | 0 | 0 | 64 | 0 | 0 | 91 | 0 | 42.16 | 163 | 0 | 175 | 0 | 140 | 0 | 349 | 0 | 4.33 | 0 | 161 | 55 | 64 | 20 | 70 | 0 | 0 | 3.9 | 73 | 0.22 | 29 | 250 | 9 | 100 | 220 | 0 | 566 | 1244 | 33 | 6122.61 | 14013.12 | 82.11
15:00 | 0 | 47 | 8 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 33 | 17 | 137 | 72 | 133 | 14.5 | 35 | 152 | 0 | 62 | 350 | 300 | 140 | 0 | 55 | 0 | 285 | 96 | 0 | 19 | 108 | 17.5 | 7 | 0 | 0 | 31 | 45 | 24 | 0 | 14 | 33 | 35 | 16 | 33 | 88 | 1 | 40 | 68 | 3 | 160 | 35 | 0 | 18 | 8 | 102 | 144 | 0 | 0 | 0 | 1100 | 10 | 43 | 117 | 162 | 0 | 335 | 230 | 45 | 185 | 32 | 84 | 50 | 184 | 9 | 19 | 65 | 40 | 25 | 32 | 38 | 315 | 340 | 390 | 38 | 40 | 0 | 156 | 24 | 0 | 81 | 30 | 0 | 17 | 173 | 0 | 75 | 113 | 7 | 1 | 31.64 | 12 | 8000.64 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 352 | 35 | 786 | 0 | 0 | 0 | 104 | 0 | 0 | 70 | 0 | 0 | 69 | 0 | 37.11 | 167 | 0 | 175 | 0 | 140 | 0 | 363 | 0 | 3.3 | 0 | 168 | 55 | 69 | 9 | 70 | 0 | 0 | 3.7 | 93 | 0.06 | 29 | 250 | 9 | 100 | 220 | 0 | 593 | 1244 | 33 | 6212.17 | 14212.81 | 82.1
16:00 | 0 | 46 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 32 | 17 | 133 | 94 | 127 | 14.02 | 32 | 144 | 0 | 60 | 350 | 296 | 270 | 0 | 55 | 0 | 270 | 96 | 0 | 11 | 108 | 17.5 | 7 | 0 | 0 | 30 | 45 | 24 | 0 | 18 | 34 | 70 | 16 | 98 | 88 | 2 | 40 | 68 | 3 | 160 | 35 | 0 | 19 | 8 | 95 | 144 | 0 | 0 | 0 | 1080 | 10 | 43 | 113 | 160 | 0 | 341 | 235 | 44 | 173 | 32 | 84 | 50 | 179 | 26 | 19 | 62 | 32 | 25 | 31 | 38 | 305 | 318 | 361 | 38 | 40 | 0 | 155 | 24 | 0 | 82 | 30 | 0 | 17 | 173 | 0 | 76 | 113 | 6 | 1 | 18.01 | 12 | 8084.53 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 352 | 35 | 896 | 0 | 0 | 0 | 98 | 0 | 0 | 60 | 0 | 0 | 46 | 0 | 21.87 | 162 | 0 | 175 | 0 | 140 | 0 | 330 | 0 | 1.99 | 0 | 166 | 55 | 65 | 9 | 70 | 0 | 0 | 2.7 | 98 | 0.16 | 44 | 250 | 8 | 100 | 220 | 0 | 610 | 1143 | 30 | 6131.72 | 14216.25 | 82.09
17:00 | 0 | 46 | 10 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 30 | 16 | 124 | 107 | 120 | 13.3 | 30 | 135 | 0 | 57 | 400 | 290 | 350 | 0 | 55 | 0 | 263 | 96 | 0 | 7 | 108 | 17 | 7 | 0 | 0 | 14 | 15 | 24 | 0 | 8 | 34 | 31 | 15 | 100 | 30 | 0 | 40 | 30 | 5 | 160 | 17 | 0 | 19 | 8 | 51 | 147 | 0 | 0 | 0 | 1040 | 4 | 43 | 60 | 160 | 0 | 342 | 235 | 44 | 170 | 31 | 77 | 70 | 168 | 36 | 19 | 58 | 38 | 8 | 12 | 38 | 300 | 312 | 348 | 37 | 40 | 0 | 150 | 0 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 75 | 113 | 6 | 0 | 8.02 | 12 | 7724.32 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 354 | 17 | 1078 | 0 | 0 | 0 | 94 | 0 | 0 | 60 | 0 | 0 | 19 | 0 | 8.8 | 155 | 0 | 177 | 0 | 190 | 0 | 376 | 0 | 0.79 | 0 | 168 | 55 | 61 | 7 | 38 | 0 | 0 | 0 | 32 | 0.14 | 26 | 200 | 8 | 100 | 220 | 0 | 617 | 1101 | 14 | 6097.73 | 13822.05 | 82.08
18:00 | 0 | 48 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 29 | 16 | 124 | 124 | 118 | 13.1 | 30 | 135 | 0 | 57 | 350 | 300 | 350 | 0 | 55 | 0 | 282 | 96 | 0 | 1 | 108 | 17 | 7 | 0 | 0 | 12 | 14 | 24 | 0 | 0 | 34 | 31 | 15 | 100 | 30 | 0 | 40 | 31 | 7 | 160 | 17 | 0 | 19 | 8 | 47 | 147 | 0 | 0 | 0 | 1040 | 0 | 43 | 60 | 160 | 0 | 300 | 180 | 46 | 185 | 31 | 77 | 70 | 165 | 37 | 19 | 65 | 32 | 8 | 1 | 39 | 305 | 336 | 333 | 37 | 40 | 0 | 150 | 0 | 0 | 82 | 30 | 0 | 18 | 171 | 0 | 94 | 150 | 7 | 0 | 1.02 | 12 | 7702.12 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 354 | 17 | 969 | 0 | 0 | 0 | 44 | 4 | 0 | 32 | 0 | 0 | 2 | 0 | 1.09 | 151 | 0 | 177 | 0 | 195 | 0 | 348 | 0 | 0.11 | 0 | 168 | 55 | 65 | 1 | 38 | 0 | 0 | 0.2 | 3 | 0.01 | 29 | 200 | 8 | 100 | 180 | 0 | 615 | 952 | 16 | 5627.41 | 13329.53 | 82.07
19:00 | 25 | 67 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 33 | 17 | 140 | 120 | 176 | 15 | 34 | 149 | 0 | 62 | 420 | 291 | 400 | 0 | 55 | 0 | 276 | 86 | 0 | 0 | 160 | 17 | 7 | 0 | 0 | 20 | 30 | 28 | 0 | 0 | 74 | 75 | 17 | 100 | 100 | 0 | 40 | 34 | 5 | 159 | 90 | 0 | 21 | 10 | 71 | 147 | 0 | 0 | 0 | 1100 | 0 | 43 | 98 | 170 | 0 | 355 | 220 | 46 | 180 | 33 | 86 | 70 | 183 | 38 | 19 | 64 | 44 | 52.2 | 0 | 38 | 305 | 320 | 366 | 36 | 40 | 0 | 158 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 21 | 94 | 179 | 6 | 0 | 0 | 12 | 8638.2 | 859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 17 | 1375 | 0 | 32 | 0 | 70 | 4 | 33 | 80 | 22 | 8 | 0 | 15 | 0 | 165 | 0 | 180 | 0 | 140 | 0 | 398 | 0 | 0 | 0 | 167 | 55 | 87 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 28 | 307 | 10 | 116 | 220 | 0 | 690 | 1042 | 15 | 6600 | 15238.2 | 82.06
19:30 | 58 | 57 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 29 | 16 | 122 | 114 | 240 | 24.4 | 29 | 130 | 0 | 62 | 450 | 286 | 400 | 0 | 55 | 0 | 265 | 37 | 0 | 0 | 160 | 17 | 7 | 0 | 0 | 13 | 25 | 46 | 0 | 0 | 85 | 75 | 17 | 100 | 88 | 0 | 40 | 60 | 10 | 159 | 160 | 0 | 47 | 25.5 | 93 | 148 | 0 | 0 | 0 | 1100 | 0 | 43 | 122 | 170 | 0 | 355 | 240 | 47 | 173 | 33 | 76 | 70 | 166 | 38 | 19 | 59 | 42 | 52.2 | 0 | 38 | 310 | 312 | 353 | 36 | 40 | 0 | 158 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 54.5 | 94 | 181 | 6 | 0 | 0 | 12 | 8825.6 | 852 | 0 | 0 | 12 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 40 | 1360 | 0 | 34 | 0 | 94 | 11 | 33 | 30 | 28 | 25 | 0 | 15 | 0 | 155 | 0 | 150 | 0 | 140 | 0 | 381 | 0 | 0 | 0 | 166 | 56 | 91 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 26 | 307 | 11 | 110 | 220 | 0 | 731 | 1101 | 15 | 6665 | 15490.6
20:00 | 92 | 57 | 25 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 29 | 17 | 125 | 117 | 234 | 47 | 30 | 133 | 0 | 62 | 450 | 289 | 400 | 0 | 55 | 0 | 267 | 37 | 0 | 0 | 125 | 17.5 | 7 | 0 | 0 | 15 | 26 | 45 | 0 | 0 | 85 | 76 | 15 | 50 | 40 | 0 | 40 | 55 | 10 | 159 | 72 | 0 | 45 | 8 | 90 | 148 | 0 | 0 | 0 | 1070 | 0 | 43 | 70 | 173 | 0 | 355 | 250 | 50 | 180 | 35 | 77 | 70 | 166 | 38 | 19 | 61 | 42 | 52.2 | 0 | 38 | 310 | 320 | 359 | 37 | 40 | 0 | 148 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 54.5 | 94 | 181 | 6 | 0 | 0 | 12 | 8595.2 | 852 | 0 | 0 | 36 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 51 | 1370 | 0 | 34 | 0 | 92 | 25 | 41 | 30 | 30 | 43 | 0 | 15 | 0 | 153 | 0 | 150 | 0 | 140 | 0 | 334 | 0 | 0 | 0 | 167 | 56 | 92 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 13 | 307 | 11 | 116 | 220 | 0 | 732 | 1102 | 14 | 6709 | 15304.2 | 82.05
21:00 | 49 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 36 | 143 | 115 | 198 | 0 | 35 | 162 | 0 | 86 | 450 | 283 | 450 | 0 | 55 | 0 | 260 | 37 | 0 | 0 | 125 | 17 | 7 | 0 | 0 | 0 | 12 | 47 | 0 | 4 | 85 | 68 | 17 | 50 | 40 | 0 | 40 | 34 | 20 | 158 | 72 | 0 | 3 | 8 | 51 | 148 | 0 | 0 | 0 | 1040 | 0 | 43 | 70 | 173 | 0 | 355 | 250 | 51 | 178 | 35 | 77 | 70 | 166 | 38 | 19 | 58 | 32 | 52.2 | 0 | 39 | 300 | 320 | 351 | 37 | 40 | 0 | 149 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 54.5 | 94 | 181 | 8 | 0 | 0 | 12 | 8436.7 | 898 | 0 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 51 | 1363.88 | 0 | 34 | 0 | 105 | 26 | 41 | 29 | 30 | 0 | 0 | 15 | 0 | 152 | 0 | 150 | 0 | 140 | 0 | 376 | 0 | 0 | 0 | 168 | 56 | 93 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 108 | 220 | 0 | 733 | 1105 | 0 | 6716.88 | 15153.58 | 82.04
22:00 | 49 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 30 | 149 | 147 | 195 | 0 | 35 | 162 | 0 | 69 | 450 | 282 | 450 | 0 | 55 | 0 | 260 | 37 | 0 | 0 | 125 | 17 | 7 | 0 | 0 | 0 | 0 | 50 | 0 | 2 | 85 | 68 | 17 | 50 | 40 | 0 | 40 | 0 | 16 | 160 | 72 | 0 | 0 | 0 | 48 | 149 | 0 | 0 | 0 | 1040 | 0 | 43 | 70 | 173 | 0 | 355 | 250 | 51 | 180 | 35 | 84 | 70 | 161 | 38 | 19 | 58 | 38 | 52.2 | 0 | 39 | 300 | 320 | 349 | 37 | 40 | 0 | 147 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 54.5 | 100 | 162 | 6 | 0 | 0 | 12 | 8354.7 | 898 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 51 | 1362.54 | 0 | 34 | 0 | 113 | 25 | 41 | 35 | 30 | 0 | 0 | 15 | 0 | 149 | 0 | 150 | 0 | 140 | 0 | 375 | 0 | 0 | 0 | 169 | 56 | 91 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 108 | 220 | 0 | 731 | 1106 | 0 | 6667.54 | 15022.24 | 82.03
23:00 | 16 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 35 | 36 | 149 | 147 | 195 | 0 | 35 | 144 | 0 | 67 | 450 | 289 | 450 | 0 | 55 | 0 | 270 | 37 | 0 | 0 | 125 | 17 | 7 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 85 | 68 | 17 | 50 | 40 | 0 | 40 | 0 | 25 | 160 | 17 | 0 | 0 | 0 | 45 | 150 | 0 | 0 | 0 | 1080 | 0 | 43 | 70 | 173 | 0 | 358 | 250 | 51 | 190 | 35 | 90 | 70 | 163 | 38 | 19 | 68 | 36 | 52.2 | 0 | 40 | 305 | 320 | 358 | 40 | 40 | 0 | 148 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 54.5 | 103 | 162 | 5 | 0 | 0 | 12 | 8341.7 | 898 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 53 | 1358.78 | 0 | 34 | 0 | 113 | 25 | 41 | 35 | 30 | 0 | 0 | 15 | 0 | 147 | 0 | 140 | 0 | 140 | 0 | 335 | 0 | 0 | 0 | 171 | 56 | 92 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 114 | 220 | 0 | 731 | 1110 | 0 | 6620.78 | 14962.48 | 82.02
Total KWH | 243936 | 734400 | 297120 | 0 | 0 | 0 | 0 | 0 | 8881200 | 0 | 0 | 483840 | 494280 | 2158848 | 578400 | 2307862 | 204140 | 558556 | 2139840 | 0 | 838080 | 7808500 | 7101731 | 7979473 | 0 | 781263 | 0 | 7169939 | 1128000 | 0 | 204307 | 1770000 | 393600 | 166680 | 0 | 0 | 265964 | 401455 | 572160 | 0 | 129120 | 824303 | 679440 | 234855 | 981120 | 1034880 | 23762 | 961800 | 686700 | 371520 | 3832727.27 | 540290 | 0 | 224640 | 100425.6 | 1125745 | 3525345 | 0 | 0 | 0 | 23007270 | 109080 | 842072 | 1415127 | 3362182 | 0 | 8388100 | 4574000 | 861600 | 4573000 | 642744 | 1542720 | 1623660 | 3096480 | 465360 | 432000 | 1231200 | 821760 | 572760 | 485927 | 538640 | 7108500 | 7756800 | 8949000 | 879000 | 906240 | 0 | 3528409 | 321648 | 0 | 1905600 | 686496 | 0 | 417000 | 4572630 | 295560 | 1382400 | 2232000 | 366720 | 12500 | 282030 | 174240 | 171302701.87 | 21732363 | 0 | 0 | 111840 | 20160 | 0 | 0 | 0 | 0 | 0 | 0 | 575280 | 11636363 | 413280 | 20084130.72 | 0 | 556620 | 0 | 1205472 | 102649 | 214704 | 619776 | 133608 | 55829 | 759010 | 74705 | 357744 | 4125364 | 0 | 4373309 | 0 | 3999684 | 0 | 8887200 | 0 | 28860 | 0 | 3457000 | 1344872 | 1172374 | 175173 | 1143456 | 0 | 0 | 34773.36 | 1084320 | 3763 | 277728 | 5803000 | 171609 | 2596000 | 5240850 | 0 | 12735999 | 24072727.27 | 266400 | 139647995.35 | 310950697.22

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13738.31 | MW | 12:00 Hr. | Energy Generated |  |  | 310.9507 |  | MKWHr.
| Day Peak Demand |  |  | 13783.31 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.271 |  | MKWHr.
| Evening Peak Generation |  |  | 15490.6 | MW | 19:30 Hr. | Energy Demand |  |  | 312.2217 |  | MKWHr.
| Evening Peak Demand |  |  | 15642.6 | MW | 19:30 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 9666.63 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1036.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 15490.6 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.2748 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.6291 | 0 | 13.5906 | 0 | 0 | 0.20431 | 0 | 0 | 54.424 | Gas | 136.6174 | Gas | 443114825.55
| Chattogram Zone |  |  | 3.8969 | 26.84 | 7.672 | 0 | 0.9618 | 0.13284 | 0 | 0.12912 | 39.6326 | Coal | 85.89 | Coal | 524053873.2067
| Cumilla Zone |  |  | 25.2994 | 0 | 8.8623 | 0 | 0 | 0.48593 | 0.82176 | 0 | 35.4693 | HFO | 40.5776 | HFO | 712344537.442
| Mymensingh Zone |  |  | 0.36672 | 0 | 4.0842 | 0 | 0 | 0.29453 | 0 | 0 | 4.7454 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 37.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.0313 | Hydro | 0.9618 | Hydro | 96180
| Khulna Zone |  |  | 0 | 11.6364 | 0.54528 | 0 | 0 | 0.57528 | 21.7324 | 0 | 34.4893 | Solar | 4.1365 | Solar | 66493609.9596
| Barishal Zone |  |  | 8.0085 | 42.6117 | 0.54413 | 0 | 0 | 0.003763 | 0 | 0 | 51.1681 | Import | 42.6383 | Import | 203166646.986
| Rajshahi Zone |  |  | 21.3856 | 0 | 2.9634 | 0 | 0 | 1.1456 | 20.0841 | 0 | 45.5787 | Wind | 0.12912 | Wind | 1890316.8
| Rangpur Zone |  |  | 0 | 4.8019 | 2.3158 | 0 | 0 | 1.2943 | 0 | 0 | 8.412
| Total |  |  | 136.6174 | 85.89 | 40.5776 | 0 | 0.9618 | 4.1365 | 42.6383 | 0.12912 | 310.9507
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 443114825.55 |  | Hydro | 96180
|  |  |  | Coal | 524053873.2067 |  | Solar | 66493609.9596
|  |  |  | HFO | 712344537.442 |  | Import | 203166646.986
|  |  |  | HSD | 0 |  | Wind | 1890316.8
[5 empty] | Total: | 195,11,59,989 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7324 | Peak Hr Flow | 852.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 42523618.25 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 20.0841 | Peak Hr Flow | 1360.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 628 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.82176 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 870 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.6383 | Peak Hr Flow | 2254.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 110 |  | 5567
|  |  |  | Chattogram |  | 0 |  | 1519
|  |  |  | Cumilla |  | 0 |  | 1478
|  |  |  | Mymensingh |  | 35 |  | 1262
|  |  |  | Sylhet |  | 0 |  | 501
|  |  |  | Khulna |  | 0 |  | 1807
|  |  |  | Barishal |  | 0 |  | 440
|  |  |  | Rajshahi |  | 0 |  | 1574
|  |  |  | Rangpur |  | 0 |  | 933
|  |  |  | Total |  | 145 |  | 15081
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:16 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U2
| 08:27 |  | BSRM-Cumilla(N) 230 kV Ckt-2 Project Work S/D from BSRM 230/33kV end Due to CONDUCTOR
REPLACE and from Cumilla(N) 230/132/33kV end Due to Project work
| 08:35 | 11:00 | Dhaka University - Rampura 132kV ckt-1 Scheduled S/D from Rampura 230/132kV end Due to
GIS bay Maintenance Taken by DPDC
| 08:41 | 19:29 | Rangpur-Saidpur 132kV Ckt-1 Project Work S/D from Saidpur 132/33kV end Due to QF- GMD-
39 and as the instruction of ALDC, Bogura (499264)
| 08:43 | 19:38 | Jaldhaka-Saidpur 132kV Ckt-1 Project Work S/D from Jaldhaka 132/33kV end Due to Saidpur
150MW SCPP Project ,BPDB has requested for a shutdown of Jaldhaka-Saidpur 132KV Ckt-01 at
Saidpur Grid S/S due to power evacuation from plant side to Grid side. and from Saidpur
132/33kV end Due to QF- GMD- 39 and as the instruction of ALDC, Bogura (499264)
| 08:46 | 09:33 | Khulshi 132/33kV S/S 405T (T1) LT Tripped showing MVAJM25 relays Due to O/C DMT
| 08:54 | 19:38 | Saidpur 132/33kV S/S TR-01 HT Project Work S/D Due to QF- GMD- 39 and as the
instruction of ALDC, Bogura (499264)
| 08:59 | 16:53 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline checking.
| 09:00 |  | Rampal 1320 MW (BIFPCL) Synchronized
|  | 09:10 | Feni 132/33kV S/S T-1(405T) LT is restored.
|  | 09:10 | Feni 132/33kV S/S T-1(405T) HT is restored.
| 09:20 | 19:02 | Saidpur 132/33kV S/S BUS A Project Work S/D Due to QF- GMD- 39 and as the instruction
of ALDC, Bogura (499264)
|  | 09:28 | Baroirhat-Feni 132 kV Ckt-2 is restored.
| 10:28 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 10:38 | 19:14 | Rangpur-Saidpur 132kV Ckt-2 Forced S/D from Saidpur 132/33kV end Due to As the
instruction of NLDC, Dhaka (299727)
| 11:07 |  | Bheramara P/S-Ishurdi 132 kV Ckt-1 Project Work S/D from Bheramara 230/132kV end Due to
Reconducting and from Ishurdi 132/33kV end Due to reconductoring work
| 11:07 |  | Bheramara P/S-Ishurdi 132 kV Ckt-2 Project Work S/D from Bheramara 230/132kV end Due to
Reconducting and from Ishurdi 132/33kV end Due to reconductoring work
| 12:33 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 13:46 | 14:03 | Ullahpara 132/33kV S/S Power Transformer -1 LT Scheduled S/D Due to Energy Meter Changing
work of 33kV Incomer-1 by Energy Audit Unit, Bogura.
| 13:48 | 13:56 | Ullahpara 132/33kV S/S Power Transformer -1 HT Scheduled S/D Due to Energy Meter Changing
work of 33kV Incomer-1 by Energy Audit Unit, Bogura.
| 14:05 | 14:15 | Ullahpara 132/33kV S/S Power Transformer-2 LT Scheduled S/D Due to Energy Meter Changing
work of 33kV Incomer-2 by Energy Audit Unit, Bogura.
| 14:06 | 14:14 | Ullahpara 132/33kV S/S Power Transformer-2 HT Scheduled S/D Due to Energy Meter Changing
work of 33kV Incomer-2 by Energy Audit Unit, Bogura.
| 14:32 |  | Adani Power Jharkhand Ltd. Unit-2 was sync.
| 14:43 |  | Summit meghnaghat-2 589 MW CCPP ST was sync.
| 14:43 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 19:30 |  | Evening Peak Gen. 15490 MW
|  | 23:24 | Ghorasal-Joydeb-B 132kV Ckt-1 is restored.
| 06:10 |  | BSRM-Cumilla(N) 230 kV Ckt-1 Scheduled S/D from BSRM 230/33kV end Due to Annual
Maintenance
| 07:03 |  | Naogaon 132/33kV S/S T-1 LT Scheduled S/D Due to 33KV Bus PT Y-phase oil leakage | [7 empty] | 35.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 07:05 |  | Naogaon 132/33kV S/S T-1 HT Scheduled S/D Due to 33 KV T-1 Bus PT Y-Phase Oil leakage | [7 empty] | 35.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 07:08 |  | Bakulia 132/33kV S/S Aux Tr-1 HT Scheduled S/D Due to New Aux Tr-2 loop connection and
turn on. It is done from the edge of the bakalia S&D BPDB.
| 07:19 |  | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to TR-3 Development work
| 07:20 |  | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to TR-3 Development work
| 07:38 |  | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT Scheduled S/D Due to Equipment loop
connection tightening.
| 07:38 |  | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Scheduled S/D Due to Equipment loop
connection tightening.
| 07:47 |  | Bakulia 132/33kV S/S T-1 (402T) LT Scheduled S/D Due to New Aux Tr-2 loop connection and | [7 empty] | 14.0MW load
|  |  | turn on. It is done from the edge of the bakalia S&D BPDB. | [7 empty] | interrup.
| 07:47 |  | Bakulia 132/33kV S/S T-2 (412T) LT Scheduled S/D Due to New Aux Tr-2 loop connection and | [7 empty] | 14.0MW load
|  |  | turn on. It is done from the edge of the bakalia S&D BPDB. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 333 | 8881200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 7808500 | GT-2 shut down for HRSG-2 tube leakage repair
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 286 | 7101731 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 24.4 | 204140 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 37 | 1128000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 265 | 7169939 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 243936 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 29 | 483840 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 114 | 578400 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 29 | 558556 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 781263 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 393600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 7 | 166680 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 297120 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 240 | 2307862 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 122 | 2158848 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 57 | 734400 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 62 | 838080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 130 | 2139840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 204307 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 16 | 494280 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 7979473 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1770000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2916.4 | 54423995
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 100425.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109080 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 47 | 224640 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 961800 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 148 | 3525345 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 93 | 1125745 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 75 | 679440 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 824303 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 981120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 371520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 46 | 572160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 25 | 401455 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 234855 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 60 | 686700 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1034880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 13 | 265964 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 540290 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1100 | 23007270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 129120 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 159 | 3832727.27 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2291.5 | 39632601.87
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 173 | 4573000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8388100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 240 | 4574000 | Under Maintenance
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 642744 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 861600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 170 | 3362182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 842072 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 122 | 1415127 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 38 | 538640 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1623660 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 166 | 3096480 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 42 | 821760 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 572760 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 432000 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 59 | 1231200 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 465360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 76 | 1542720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 485927 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1743.2 | 35469332
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 6 | 366720 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 181 | 2232000 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 1382400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 282030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 174240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 295560 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 347.5 | 4745450
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 879000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 906240 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 158 | 3528409 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 686496 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1905600 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 172 | 4572630 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 417000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 321648 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7108500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 353 | 8949000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 312 | 7756800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1527 | 37031323
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 852 | 21732363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 12 | 111840 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 5 | 20160 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 40 | 413280 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 575280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 353 | 11636363 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1262 | 34489286
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 731 | 12735999 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 26 | 277728 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 171609 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 2596000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1101 | 24072727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5240850 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 15 | 266400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5803000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3763 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2521 | 51168076.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 34 | 556620 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 11 | 102649 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 28 | 133608 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 155 | 4125364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 150 | 4373309 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 140 | 3999684 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 381 | 8887200 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 15 | 74705 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 55829 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 33 | 214704 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 94 | 1205472 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 30 | 619776 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1360 | 20084130.72 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 357744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 759010 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2456 | 45578664.72
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1344872 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 166 | 3457000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1143456 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34773.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 91 | 1172374 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 175173 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1084320 | -
Rangpur Area Total |  |  |  |  | 950 | 426 | 8411968.36
Eastern Grid Total |  |  |  |  | 16921.242 | 8825.6 | 171302701.87
Western Grid Total |  |  |  |  | 11614.5 | 6665 | 139647995.35
National Grid Total |  |  |  |  | 28535.742 | 15490.6 | 310950697.22
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10182.62 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4753.7 | MW
i) Dhaka area |  |  | 5457.12 |  | MW | i) Khulna area |  |  |  | 1807 | MW
ii) Chattogram area |  |  | 1519 |  | MW | ii) Barishal area |  |  |  | 439.7 | MW
iii) Cumilla area |  |  | 1478.5 |  | MW | iii) Rajshahi area |  |  |  | 1574 | MW
iv) Mymensingh area |  |  | 1227 |  | MW | iv) Rangpur area |  |  |  | 933 | MW
v) Sylhet area |  |  | 501 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14936.32 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 76 | 21:00 | 133 | Patuakhali | 73.9 | 21:00
2 | AKSML | 117 | 04:00 | 68 | Jaldhaka | 70 | 19:00 | 134 | Payra | 30 | 00:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jamalpur | 140 | 19:30 | 135 | Postogola | 55 | 18:30
4 | Agargaon | 123 | 13:00 | 70 | Jashore | 151 | 19:00 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 92 | 13:00 | 71 | Jhenaidah | 140 | 19:30 | 137 | Purbasadipur | 118 | 19:30
6 | Amnura | 46 | 21:00 | 72 | Joydebpur | 139 | 11:00 | 138 | Rahanpur | 26 | 21:00
7 | Ashuganj | 100 | 00:00 | 73 | Joypurhat | 61 | 22:00 | 139 | Rahim | 43 | 16:00
8 | BSRM | 197 | 05:00 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 80 | 19:00
9 | Bagerhat | 83 | 19:30 | 75 | KSRM | 16 | 07:00 | 141 | Rajendrapur | 117 | 13:00
10 | Bajitpur | 57 | 00:00 | 76 | Kabirpur | 274 | 19:30 | 142 | Rajshahi | 118 | 21:00
11 | Bakulia | 100 | 18:30 | 77 | Kachua | 93 | 21:00 | 143 | Rajshahi-230 | 78 | 21:00
12 | Banani | 46 | 12:00 | 78 | Kallyanpur | 111 | 00:00 | 144 | Ramganj | 112 | 22:00
13 | Bangabhaban | 20 | 17:00 | 79 | Kalurghat | 38 | 09:00 | 145 | Rampur | 44 | 00:00
14 | Barapukuria | 63 | 21:00 | 80 | Kamrangirchar | 68.6 | 19:00 | 146 | Rangamati | 16 | 19:30
15 | Barguna | 20 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 160 | 19:00
16 | Barishal | 106 | 20:00 | 82 | Kasba | 40 | 18:30 | 148 | Ruppur | 7 | 15:00
17 | Barishal-230 | 88 | 19:00 | 83 | Kazla | 102 | 19:30 | 149 | SSM | 8 | 00:00
18 | Baroaulia | 70 | 12:00 | 84 | Keranigonj | 76 | 19:00 | 150 | Saidpur | 111 | 12:00
19 | Baroirhat | 62 | 19:30 | 85 | Khagrachori | 34 | 20:00 | 151 | Satkhira | 144 | 22:00
20 | Bashundhara | 199 | 14:00 | 86 | Khulna | 76 | 12:00 | 152 | Satmasjid | 104 | 19:30
21 | BashundharaCement | 12 | 12:00 | 87 | Khulshi | 177 | 19:00 | 153 | Savar | 224 | 16:00
22 | Beanibazar | 70 | 21:00 | 88 | Kishoreganj | 138 | 00:00 | 154 | SevenRings | 20.38 | 15:00
23 | Benapole | 71 | 21:00 | 89 | Kodda | 302 | 21:00 | 155 | ShahCement | 37 | 22:00
24 | Bhaluka | 167 | 15:00 | 90 | Kulaura | 48 | 00:00 | 156 | Shahjadpur | 92 | 19:30
25 | Bhandaria | 50 | 00:00 | 91 | Kurigram | 64 | 19:00 | 157 | Shahjibazar | 134 | 00:00
26 | Bhangura | 44 | 19:00 | 92 | Kushtia | 145 | 19:30 | 158 | Shahmirpur | 54 | 17:00
27 | Bheramara(GK) | 63 | 20:00 | 93 | Lalbag | 66 | 13:00 | 159 | Shariatpur | 85 | 21:00
28 | Bhulta | 237 | 23:00 | 94 | Lalmonirhat | 58 | 19:00 | 160 | Sherpur | 166 | 19:00
29 | Bog-Sherpur | 74 | 19:00 | 95 | MI_Cement | 18.1 | 19:30 | 161 | Shikalbaha | 29 | 19:30
30 | Bogura | 180 | 19:00 | 96 | Madanganj | 42 | 15:00 | 162 | Shitalakhya | 81.3 | 16:00
31 | Borhanuddin | 90 | 23:00 | 97 | Madaripur | 113 | 21:00 | 163 | Sholosohor | 44 | 15:00
32 | Brahmanbaria | 135 | 19:30 | 98 | Madartek | 89.62 | 00:00 | 164 | Shyampur | 164 | 11:00
33 | Cantonment | 130 | 13:00 | 99 | Madunaghat | 50 | 15:00 | 165 | Siddhirganj | 124 | 23:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 67 | 19:00 | 166 | Sirajganj | 114 | 19:00
35 | Chandpur | 71 | 19:00 | 101 | Mahasthangarh | 80 | 19:30 | 167 | Sonargaon | 100 | 23:00
36 | Chandraghona | 35 | 19:00 | 102 | Manikganj | 143 | 21:00 | 168 | Sreemongol | 76 | 00:00
37 | Chapai | 68 | 19:30 | 103 | Maniknagar | 74 | 13:00 | 169 | Sreepur | 106 | 16:00
38 | Charsaidpur | 48 | 15:00 | 104 | Matarbari | 49 | 22:00 | 170 | Srinagar | 47.52 | 22:00
39 | Chauddagram | 78 | 19:00 | 105 | Matuail | 62 | 16:00 | 171 | Sunamganj | 58 | 01:00
40 | Chhatak | 34 | 00:00 | 106 | Millgate | 95 | 14:00 | 172 | Sylhet | 46 | 00:00
41 | Chowmuhani | 233 | 18:30 | 107 | Mirpur | 142 | 19:00 | 173 | Sylhet-132 | 122 | 14:00
42 | Chuadanga | 115 | 20:00 | 108 | Mirsorai | 8 | 00:00 | 174 | TK | 35 | 19:30
43 | Coxsbazar | 130 | 19:00 | 109 | Mirzapur | 48 | 15:00 | 175 | Tangail | 186 | 19:00
44 | Cumilla(N) | 187 | 18:30 | 110 | Mithapukur | 59 | 19:00 | 176 | Thakurgaon | 92 | 19:30
45 | Cumilla(S) | 184 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 132 | 11:00
46 | Daudkandi | 152 | 21:00 | 112 | Mogbazar | 153.4 | 16:00 | 178 | Ullahpara | 45 | 19:30
47 | Dhaka | 64 | 13:00 | 113 | Mongla | 29 | 12:00 | 179 | Ullon | 49 | 00:00
48 | Dhamrai | 130 | 13:00 | 114 | Motijheel | 42 | 13:00 | 180 | Uttara | 98 | 17:00
49 | Dhanmondi | 139 | 13:00 | 115 | Muktagacha | 37 | 00:00 | 181 | UttaraNew | 49 | 13:00
50 | Dohazari | 104 | 20:00 | 116 | Munshiganj | 107 | 22:00 | 182 | Zigatola | 74 | 19:00
51 | Faridpur | 165 | 20:00 | 117 | Muradnagar | 30 | 19:30
52 | Fatullah | 98 | 12:00 | 118 | Mymensingh | 206 | 19:00
53 | Fenchuganj | 40 | 00:00 | 119 | Naogaon | 133 | 20:00
54 | Feni | 124 | 20:00 | 120 | Narail | 62 | 19:30
55 | GPH | 69 | 21:00 | 121 | Narinda | 75 | 13:00
56 | Ghatail | 90 | 00:00 | 122 | Narshingdi | 176 | 22:00
57 | Ghorashal | 18 | 15:00 | 123 | Natore | 159 | 21:00
58 | Ghorashal-230 | 83 | 19:00 | 124 | Nawabganj | 61.6 | 20:00
59 | Goalpara | 34 | 13:00 | 125 | Netrakona | 124 | 18:30
60 | Gollamari | 88 | 19:00 | 126 | New | 86 | 15:00
61 | Gopalganj | 108 | 20:00 | 127 | Niamatpur | 100 | 21:00
62 | Gulshan | 134 | 13:00 | 128 | Noapara | 46 | 19:00
63 | Halishahar | 80 | 15:00 | 129 | PHP | 9 | 02:00
64 | HaripurSBU | 180 | 20:00 | 130 | Pabna | 125 | 20:00
65 | Hasnabad | 82 | 23:00 | 131 | Palashbari | 124 | 19:30
66 | Hathazari | 83 | 23:00 | 132 | Panchagarh | 43 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12985 | 50 |  | 13037
1:00 | 11998 | 21 |  | 12020
2:00 | 10991 | 0 |  | 10991
3:00 | 10435 | 0 |  | 10435
4:00 | 10224 | 0 |  | 10224
5:00 | 9820 | 0 |  | 9820
6:00 | 9666.63 | 0 |  | 9666.63
7:00 | 10258.41 | 0 |  | 10258.41
8:00 | 10764.5 | 0 |  | 10764.5
9:00 | 11433.88 | 0 |  | 11433.88
10:00 | 12247.85 | 0 |  | 12247.85
11:00 | 12773.84 | 28 |  | 12802.84
12:00 | 13738.31 | 43 |  | 13783.31
13:00 | 14063.94 | 38 |  | 14103.94
14:00 | 14013.12 | 90 |  | 14107.12
15:00 | 14212.81 | 86 |  | 14302.81
16:00 | 14216.25 | 115 |  | 14336.25
17:00 | 13822.05 | 120 |  | 13947.05
18:00 | 13329.53 | 80 |  | 13413.53
19:00 | 15238.2 | 200 |  | 15447.2
19:30 | 15490.6 | 145 |  | 15642.6
20:00 | 15304.2 | 120 |  | 15429.2
21:00 | 15153.58 | 150 |  | 15310.58
22:00 | 15022.24 | 70 |  | 15095.24
23:00 | 14962.48 | 60 |  | 15025.48
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7486 | 5499 | 12985 | DAILY GENERATION CURVE
00:30 | 7115 | 5376.5 | 12491.5
01:00 | 6744 | 5254 | 11998 | 15-04-2025
01:30 | 6325 | 5169.5 | 11494.5
02:00 | 5906 | 5085 | 10991
02:30 | 5717.5 | 4995.5 | 10713
03:00 | 5529 | 4906 | 10435
03:30 | 5456 | 4873.5 | 10329.5
04:00 | 5383 | 4841 | 10224
04:30 | 5285.5 | 4736.5 | 10022
05:00 | 5188 | 4632 | 9820
05:30 | 5195.545 | 4547.77 | 9743.315
06:00 | 5203.09 | 4463.54 | 9666.63
06:30 | 5381.6 | 4580.92 | 9962.52
07:00 | 5560.11 | 4698.3 | 10258.41
07:30 | 5669.56 | 4841.895 | 10511.455
08:00 | 5779.01 | 4985.49 | 10764.5
08:30 | 6000.93 | 5098.26 | 11099.19
09:00 | 6222.85 | 5211.03 | 11433.88
09:30 | 6498.255 | 5342.61 | 11840.865
10:00 | 6773.66 | 5474.19 | 12247.85
10:30 | 6874.715 | 5636.13 | 12510.845
11:00 | 6975.77 | 5798.07 | 12773.84
11:30 | 7306.74 | 5949.335 | 13256.075
12:00 | 7637.71 | 6100.6 | 13738.31
12:30 | 7711.455 | 6189.67 | 13901.125
13:00 | 7785.2 | 6278.74 | 14063.94
13:30 | 7837.855 | 6200.675 | 14038.53
14:00 | 7890.51 | 6122.61 | 14013.12
14:30 | 7945.575 | 6167.39 | 14112.965
15:00 | 8000.64 | 6212.17 | 14212.81
15:30 | 8042.585 | 6171.945 | 14214.53
16:00 | 8084.53 | 6131.72 | 14216.25
16:30 | 7904.425 | 6114.725 | 14019.15
17:00 | 7724.32 | 6097.73 | 13822.05
17:30 | 7713.22 | 5862.57 | 13575.79
18:00 | 7702.12 | 5627.41 | 13329.53
18:30 | 8170.16 | 6113.705 | 14283.865
19:00 | 8638.2 | 6600 | 15238.2
19:30 | 8825.6 | 6665 | 15490.6
20:00 | 8595.2 | 6709 | 15304.2
20:30 | 8515.95 | 6712.94 | 15228.89 |  | Executive Engineer
21:00 | 8436.7 | 6716.88 | 15153.58 |  | Network Operation Division
21:30 | 8395.7 | 6692.21 | 15087.91
22:00 | 8354.7 | 6667.54 | 15022.24
22:30 | 8348.2 | 6644.16 | 14992.36
23:00 | 8341.7 | 6620.78 | 14962.48

## En-Curve
QF-LDC-12
Date | 15-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3665 | 1995 | 916 | 0 | 36 | 756 | 40 | 3561 | 0 | 415 | 1600 | 0 | 0 | 1 | 50 | DAILY ENERGY CURVE
00:30 | 3597 | 1974.5 | 916 | 0 | 35 | 757 | 40 | 3525.5 | 0 | 348 | 1298 | 0 | 0 | 0.5 | 35.5 | 15-04-2025
01:00 | 3529 | 1954 | 916 | 0 | 34 | 758 | 40 | 3490 | 0 | 281 | 996 | 0 | 0 | 0 | 21
01:30 | 3428 | 1893.5 | 916 | 0 | 33 | 709 | 40 | 3457 | 0 | 211.5 | 806.5 | 0 | 0 | 0 | 10.5 | Energy Generated | 310.9507 |  | MKWHr
02:00 | 3327 | 1833 | 916 | 0 | 32 | 660 | 40 | 3424 | 0 | 142 | 617 | 0 | 0 | 0 | 0 | Energy not Served | 1.271 |  | MKWHr
02:30 | 3309 | 1814 | 916 | 0 | 32 | 629 | 40 | 3357 | 0 | 109 | 507 | 0 | 0 | 0 | 0 | Total Energy Requirement | 312.2217 |  | MKWHr
03:00 | 3291 | 1795 | 916 | 0 | 32 | 598 | 40 | 3290 | 0 | 76 | 397 | 0 | 0 | 0 | 0
03:30 | 3311 | 1790 | 916 | 0 | 31 | 566 | 40 | 3224 | 0 | 69 | 382.5 | 0 | 0 | 0 | 0
04:00 | 3331 | 1785 | 916 | 0 | 30 | 534 | 40 | 3158 | 0 | 62 | 368 | 0 | 0 | 0 | 0
04:30 | 3373.5 | 1732.5 | 916 | 0 | 30 | 484.5 | 40 | 3071.5 | 0 | 52 | 317.5 | 0 | 0 | 4.5 | 0
05:00 | 3416 | 1680 | 916 | 0 | 30 | 435 | 40 | 2985 | 0 | 42 | 267 | 0 | 0 | 9 | 0
05:30 | 3448 | 1683 | 916 | 0 | 29 | 423.5 | 40 | 2931 | 2.815 | 42 | 223 | 0 | 0 | 5 | 0
06:00 | 3480 | 1686 | 916 | 0 | 28 | 412 | 40 | 2877 | 5.63 | 42 | 179 | 0 | 0 | 1 | 0
06:30 | 3611.5 | 1791 | 916 | 0 | 27 | 414.5 | 40 | 2898 | 41.02 | 42 | 177.5 | 0 | 0 | 4 | 0
07:00 | 3743 | 1896 | 916 | 0 | 26 | 417 | 40 | 2919 | 76.41 | 42 | 176 | 0 | 0 | 7 | 0
07:30 | 3834 | 1912 | 890 | 0 | 30 | 466.5 | 40 | 2957.5 | 117.955 | 46 | 207 | 0 | 0 | 10.5 | 0
08:00 | 3925 | 1928 | 864 | 0 | 34 | 516 | 40 | 2996 | 159.5 | 50 | 238 | 0 | 0 | 14 | 0
08:30 | 3887 | 2051.5 | 864 | 0 | 34 | 567.025 | 40 | 3031 | 227.665 | 69 | 313 | 0 | 0 | 15 | 0
09:00 | 3849 | 2175 | 864 | 0 | 34 | 618.05 | 40 | 3066 | 295.83 | 88 | 388 | 0 | 0 | 16 | 0
09:30 | 3826 | 2189 | 888 | 0 | 34 | 678.67 | 40 | 3106.5 | 350.195 | 124 | 595 | 0 | 0 | 9.5 | 0
10:00 | 3803 | 2203 | 912 | 0 | 34 | 739.29 | 40 | 3147 | 404.56 | 160 | 802 | 0 | 0 | 3 | 0
10:30 | 3854.5 | 2008 | 906 | 0 | 32 | 738.99 | 40 | 3272.5 | 492.855 | 163.5 | 1000 | 0 | 0 | 2.5 | 14
11:00 | 3906 | 1813 | 900 | 0 | 30 | 738.69 | 40 | 3398 | 581.15 | 167 | 1198 | 0 | 0 | 2 | 28
11:30 | 3895.5 | 1809 | 900 | 0 | 33 | 737.695 | 40 | 3566 | 603.38 | 235 | 1433.5 | 0 | 0 | 3 | 35.5
12:00 | 3885 | 1805 | 900 | 0 | 36 | 736.7 | 40 | 3734 | 625.61 | 303 | 1669 | 0 | 0 | 4 | 43
12:30 | 3811.5 | 1798.5 | 900.5 | 0 | 39 | 732.69 | 40 | 3823 | 631.23 | 319 | 1797.705 | 0 | 0 | 8 | 40.5
13:00 | 3738 | 1792 | 901 | 0 | 42 | 728.68 | 40 | 3912 | 636.85 | 335 | 1926.41 | 0 | 0 | 12 | 38
13:30 | 3720.5 | 1798.5 | 900.5 | 0 | 41 | 729.84 | 40 | 3900 | 546.78 | 337 | 2008.91 | 0 | 0 | 15.5 | 64
14:00 | 3703 | 1805 | 900 | 0 | 40 | 731 | 40 | 3888 | 456.71 | 339 | 2091.41 | 0 | 0 | 19 | 90
14:30 | 3703 | 1848.25 | 900 | 0 | 40 | 758.5 | 40 | 3905 | 415.76 | 340 | 2145.955 | 0 | 0 | 16.5 | 88
15:00 | 3703 | 1891.5 | 900 | 0 | 40 | 786 | 40 | 3922 | 374.81 | 341 | 2200.5 | 0 | 0 | 14 | 86
15:30 | 3644 | 1947.5 | 900 | 0 | 36 | 841 | 40 | 3869 | 335.27 | 369.5 | 2216.26 | 0 | 0 | 16 | 100.5
16:00 | 3585 | 2003.5 | 900 | 0 | 32 | 896 | 40 | 3816 | 295.73 | 398 | 2232.02 | 0 | 0 | 18 | 115
16:30 | 3619.5 | 2049.25 | 900.5 | 0 | 35 | 987 | 40 | 3755.5 | 207.24 | 386 | 2026.16 | 0 | 0 | 13 | 117.5
17:00 | 3654 | 2095 | 901 | 0 | 38 | 1078 | 40 | 3695 | 118.75 | 374 | 1820.3 | 0 | 0 | 8 | 120
17:30 | 3622.5 | 2059.5 | 900.5 | 0 | 35 | 1023.5 | 40 | 3619.5 | 66.09 | 393.5 | 1811.7 | 0 | 0 | 4 | 100
18:00 | 3591 | 2024 | 900 | 0 | 32 | 969 | 40 | 3544 | 13.43 | 413 | 1803.1 | 0 | 0 | 0 | 80
18:30 | 3646.5 | 2116.5 | 879.5 | 0 | 38 | 1172 | 40 | 3708 | 6.715 | 539 | 2137.65 | 0 | 0 | 0 | 140
19:00 | 3702 | 2209 | 859 | 0 | 44 | 1375 | 40 | 3872 | 0 | 665 | 2472.2 | 0 | 0 | 0 | 200
19:30 | 3557 | 2246 | 852 | 0 | 42 | 1360 | 40 | 3973 | 0 | 692 | 2728.6 | 0 | 0 | 0 | 145
20:00 | 3549 | 2245.5 | 852 | 0 | 42 | 1370 | 40 | 3948 | 0 | 719 | 2538.7 | 0 | 0 | 0 | 120
20:30 | 3557.5 | 2268.25 | 875 | 0 | 37 | 1366.94 | 40 | 3934.5 | 0 | 725.5 | 2422.2 | 0 | 0 | 2 | 135
21:00 | 3566 | 2291 | 898 | 0 | 32 | 1363.88 | 40 | 3921 | 0 | 732 | 2305.7 | 0 | 0 | 4 | 150
21:30 | 3560.5 | 2287.5 | 898 | 0 | 35 | 1363.21 | 40 | 3922.5 | 0 | 721.5 | 2256.7 | 0 | 0 | 3 | 110
22:00 | 3555 | 2284 | 898 | 0 | 38 | 1362.54 | 40 | 3924 | 0 | 711 | 2207.7 | 0 | 0 | 2 | 70
22:30 | 3551.5 | 2294.5 | 898 | 0 | 37 | 1360.66 | 40 | 3947 | 0 | 696 | 2166.7 | 0 | 0 | 1 | 65
23:00 | 3548 | 2305 | 898 | 0 | 36 | 1358.78 | 40 | 3970 | 0 | 681 | 2125.7 | 0 | 0 | 0 | 60
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 397 | 07:00 | 372 | 12:00 | Payra | 416 | 06:00 | 407 | 13:00
Ashuganj | 389 | 02:00 | 381 | 11:00 | Rahanpur | 408 | 15:00 | 393 | 19:00
Bhulta | 400 | 04:00 | 377 | 12:00 | Rampal | 406 | 02:00 | 385 | 13:00
Bibiana | 389 | 02:00 | 381 | 11:00
BIPTC | 403 | 09:00 | 393 | 20:00
Bogura | 402 | 05:00 | 386 | 19:00
Gopalganj | 405 | 06:00 | 383 | 12:00
Kaliakoir | 373 | 01:00 | 351 | 11:00
Madunaghat | 406 | 06:00 | 325 | 15:00
Meghnaghat | 398 | 07:00 | 372 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 02:00 | 215 | 12:00 | Keranigonj | 229 | 06:00 | 213 | 12:00
AKSML | 232 | 22:00 | 224 | 11:00 | Khulna(S) | 235 | 05:00 | 217 | 19:00
Aminbazar | 231 | 01:00 | 216 | 12:00 | Madunaghat | 235 | 08:00 | 128 | 12:00
Ashuganj | 233 | 13:00 | 223 | 11:00 | Madunaghat-400 | 239 | 17:00 | 228 | 12:00
Ashuganj-400 | 234 | 13:01 | 224 | 11:01 | Maniknagar | 227 | 04:00 | 212 | 12:00
Baghabari | 233 | 00:00 | 225 | 12:00 | Meghnaghat | 235 | 00:00 | 221 | 12:00
Barapukuria | 221 | 15:00 | 214 | 19:00 | Meghnaghat-400 | 230 | 06:00 | 216 | 12:00
Barapukuria-230 | 222 | 15:01 | 215 | 19:01 | Mirsorai | 233 | 19:30 | 222 | 11:00
Barishal | 238 | 06:00 | 227 | 13:00 | Rajshahi | 231 | 21:00 | 221 | 10:00
Bheramara | 232 | 21:00 | 221 | 12:00 | Rampal | 232 | 05:00 | 216 | 19:00
Bhulta | 227 | 02:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 01:00 | 217 | 11:00 | Rampura | 227 | 06:00 | 210 | 12:00
BIPTC | 233 | 00:00 | 222 | 12:00 | Shikalbaha | 231 | 05:00 | 225 | 03:00
Bogura | 226 | 02:00 | 218 | 19:00 | Shyampur | 229 | 06:00 | 214 | 12:00
Bogura-400 | 225 | 05:00 | 219 | 19:00 | Siddhirganj | 228 | 07:00 | 215 | 11:00
Borhanuddin | 243 | 04:00 | 232 | 19:30 | Sirajgonj | 238 | 02:00 | 233 | 18:30
BSRM | 230 | 19:30 | 221 | 11:00 | Sreepur | 233 | 17:00 | 221 | 11:00
Cumilla(N) | 224 | 05:00 | 213 | 11:00 | Tongi | 227 | 03:00 | 212 | 15:00
Faridpur | 231 | 04:00 | 218 | 12:00
Fenchuganj | 226 | 05:00 | 220 | 12:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 227 | 02:00 | 214 | 11:00
Gopalganj | 232 | 06:00 | 220 | 12:00
GPH | 232 | 07:00 | 224 | 11:00
Haripur | 228 | 07:00 | 214 | 11:00
Hasnabad | 225 | 00:00 | 213 | 12:00
Hathazari | 234 | 06:00 | 227 | 11:00
Ishurdi | 233 | 20:00 | 225 | 10:00
Jhenaidah | 230 | 00:00 | 214 | 19:00
Kaliakoir | 232 | 01:00 | 217 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 22:00 | 119 | 11:00 | Madartek | 132 | 22:00 | 123 | 11:00
Agargaon | 133 | 04:00 | 122 | 12:00 | Madunaghat | 134 | 08:00 | 130 | 12:00
Agrabad | 136 | 05:00 | 128 | 11:00 | Magura | 135 | 00:00 | 120 | 19:00
AKS | 132 | 04:00 | 126 | 16:00 | Mahasthangarh | 130 | 05:00 | 123 | 19:00
Aminbazar | 132 | 01:00 | 122 | 12:00 | Manikganj | 136 | 01:00 | 119 | 09:00
Amnura | 135 | 21:00 | 124 | 19:00 | Maniknagar | 131 | 05:00 | 120 | 11:00
Ashuganj | 137 | 04:00 | 133 | 13:00 | Matarbari | 131 | 09:00 | 113 | 01:00
Bagerhat | 136 | 02:00 | 119 | 18:30 | Matuail | 132 | 04:00 | 124 | 11:00
Bajitpur | 134 | 04:00 | 125 | 12:00 | Millgate | 134 | 01:00 | 120 | 11:00
Bakulia | 136 | 19:00 | 130 | 11:00 | Mirpur | 131 | 01:00 | 121 | 11:00
Banani | 132 | 04:00 | 119 | 11:00 | Mirzapur | 138 | 02:00 | 119 | 16:00
Bangabhaban | 130 | 03:00 | 119 | 11:00 | Mithapukur | 128 | 05:00 | 122 | 19:00
Barapukuria | 133 | 15:00 | 128 | 07:00 | MI_Cement | 134 | 12:00 | 124 | 11:00
Barguna | 137 | 14:00 | 131 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 05:00 | 124 | 22:00 | Mogbazar | 133 | 05:00 | 13.2 | 03:00
Barishal-230 | 134 | 04:00 | 125 | 19:00 | Mongla | 138 | 02:00 | 121 | 19:00
Baroaulia | 135 | 05:00 | 129 | 11:00 | Motijheel | 130 | 03:00 | 119 | 11:00
Baroirhat | 125 | 09:00 | 119 | 12:00 | Muktagacha | 130 | 01:00 | 117 | 18:30
Bashundhara | 133 | 01:00 | 119 | 11:00 | Munshiganj | 131 | 03:00 | 122 | 12:00
BashundharaCement | 132 | 05:00 | 123 | 11:00 | Muradnagar | 126 | 06:00 | 119 | 11:00
Beanibazar | 130 | 05:00 | 125 | 00:00 | Mymensingh | 140 | 02:00 | 117 | 16:00
Benapole | 136 | 00:00 | 117 | 19:00 | Naogaon | 128 | 05:00 | 122 | 19:00
Bhaluka | 134 | 03:00 | 124 | 11:00 | Narail | 136 | 00:00 | 119 | 19:00
Bhandaria | 129 | 07:00 | 115 | 21:00 | Narinda | 131 | 05:00 | 120 | 11:00
Bhangura | 135 | 01:00 | 126 | 19:00 | Narshingdi | 128 | 04:00 | 117 | 13:00
Bheramara | 135 | 00:00 | 127 | 12:00 | Natore | 133 | 01:00 | 126 | 19:00
Bheramara(GK) | 136 | 00:00 | 127 | 12:00 | Nawabganj | 133 | 01:00 | 122 | 12:00
Bhulta | 128 | 05:00 | 119 | 11:00 | Netrakona | 135 | 03:00 | 115 | 00:00
Bog-Sherpur | 131 | 01:00 | 124 | 19:00 | New | 135 | 07:00 | 121 | 11:00
Bogura | 132 | 02:00 | 127 | 07:00 | Niamatpur | 134 | 01:00 | 128 | 19:00
Bogura-230 | 132 | 14:00 | 127 | 19:00 | Noapara | 138 | 00:00 | 122 | 19:00
Brahmanbaria | 133 | 13:00 | 122 | 12:00 | Pabna | 137 | 00:00 | 128 | 18:30
Cantonment | 133 | 04:00 | 122 | 11:00 | Palashbari | 126 | 03:00 | 119 | 19:30
Chandina | 128 | 05:00 | 122 | 11:00 | Panchagarh | 136 | 23:00 | 123 | 07:00
Chandpur | 126 | 18:00 | 119 | 11:00 | Patuakhali | 136 | 03:00 | 131 | 22:00
Chandraghona | 136 | 06:00 | 130 | 11:00 | Payra | 137 | 04:00 | 134 | 16:00
Chapai | 132 | 02:00 | 125 | 19:00 | PHP | 125 | 07:00 | 117 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 04:00 | 24 | 15:00 | Postogola | 135 | 01:00 | 27 | 15:00
Chauddagram | 123 | 05:00 | 117 | 11:00 | Purbachal | 133 | 04:00 | 119 | 11:00
Chhatak | 132 | 04:00 | 123 | 01:00 | Purbasadipur | 132 | 23:00 | 120 | 19:00
Chowmuhani | 119 | 05:00 | 111 | 13:00 | Rahanpur | 136 | 03:00 | 130 | 19:00
Chuadanga | 135 | 00:00 | 120 | 19:00 | Rahanpur-400 | 136 | 05:00 | 130 | 19:00
Coxsbazar | 128 | 09:00 | 114 | 00:00 | Rahim | 133 | 07:00 | 124 | 12:00
Cumilla(N) | 128 | 05:00 | 122 | 11:00 | Rajbari | 136 | 04:00 | 127 | 12:00
Cumilla(S) | 133 | 04:00 | 120 | 10:00 | Rajendrapur | 138 | 03:00 | 122 | 09:00
Daudkandi | 125 | 04:00 | 118 | 11:00 | Rajshahi | 132 | 00:00 | 127 | 12:00
Dhaka | 133 | 21:00 | 120 | 11:00 | Rajshahi-230 | 134 | 01:00 | 119 | 19:00
Dhamrai | 133 | 04:00 | 120 | 11:00 | Ramganj | 121 | 18:00 | 113 | 11:00
Dhanmondi | 133.5 | 04:00 | 124 | 12:00 | Rampur | 134 | 06:00 | 129 | 11:00
Dohazari | 134 | 09:00 | 124 | 18:30 | Rampura | 133 | 22:00 | 120 | 11:00
Faridpur | 137 | 03:00 | 129 | 19:00 | Rangamati | 135 | 07:00 | 129 | 15:00
Fatullah | 134 | 04:00 | 124 | 12:00 | Rangpur | 131 | 02:00 | 119 | 07:00
Fenchuganj | 135 | 07:00 | 131 | 00:00 | Ruppur | 137 | 00:00 | 132 | 09:00
Feni | 124 | 05:00 | 114 | 15:00 | Saidpur | 129 | 05:00 | 122 | 19:00
Ghatail | 140 | 02:00 | 113 | 18:30 | Satkhira | 137 | 00:00 | 118 | 19:00
Ghorashal | 136 | 08:00 | 132 | 12:00 | Satmasjid | 140 | 14:00 | 122 | 11:00
Goalpara | 139 | 05:00 | 125 | 19:00 | Savar | 131 | 02:00 | 122 | 11:00
Gollamari | 138 | 00:00 | 127 | 19:00 | SevenRings | 137 | 02:00 | 129 | 11:00
Gopalganj | 137 | 04:00 | 126 | 19:00 | ShahCement | 133 | 04:00 | 12 | 13:00
Gopalganj-400 | 138 | 04:00 | 130 | 12:00 | Shahjadpur | 138 | 06:00 | 130 | 12:00
Gulshan | 132 | 04:00 | 120 | 11:00 | Shahjibazar | 129 | 16:00 | 123 | 00:00
Halishahar | 135 | 06:00 | 129 | 12:00 | Shahmirpur | 136 | 09:00 | 131 | 11:00
Haripur | 132 | 04:00 | 124 | 11:00 | Shariatpur | 137 | 04:00 | 126 | 19:00
HaripurSBU | 132 | 03:00 | 124 | 12:00 | Sherpur | 136 | 02:00 | 118 | 16:00
Hasnabad | 135 | 05:00 | 125 | 11:00 | Shikalbaha | 127 | 06:00 | 119 | 11:00
Hathazari | 136 | 05:00 | 131 | 11:00 | Shikalbaha-230 | 137 | 05:00 | 132 | 01:00
Ishurdi | 137 | 00:00 | 132 | 10:00 | Shitalakhya | 132.6 | 06:00 | 124 | 11:00
Jaldhaka | 128 | 23:00 | 116 | 18:00 | Sholosohor | 135 | 07:00 | 129 | 11:00
Jamalpur | 140 | 02:00 | 122 | 06:00 | Shyampur | 133 | 05:00 | 128 | 10:00
Jashore | 138 | 00:00 | 119 | 19:00 | Shyampur-230 | 133 | 02:00 | 121 | 12:00
Jhenaidah | 138 | 00:00 | 12 | 15:00 | Siddhirganj | 133 | 01:00 | 124 | 11:00
Jhenaidah-230 | 139 | 00:00 | 123 | 19:00 | Sirajganj | 133 | 01:00 | 124 | 17:00
Joydebpur | 135 | 02:00 | 124 | 11:00 | Sonargaon | 130 | 00:00 | 125 | 07:00
Joypurhat | 127 | 04:00 | 119 | 19:00 | Sreemongol | 130 | 08:00 | 125 | 00:00
Juldah | 134 | 03:00 | 132 | 00:00 | Sreepur | 136 | 03:00 | 127 | 11:00
Kabirpur | 132 | 02:00 | 116 | 11:00 | Srinagar | 134 | 05:00 | 123 | 12:00
Kachua | 124 | 05:00 | 118 | 11:00 | SSM | 138 | 19:00 | 132 | 10:00
Kaliakoir | 138 | 01:00 | 123 | 11:00 | Sunamganj | 130 | 05:00 | 121 | 00:00
Kallyanpur | 131 | 01:00 | 121 | 12:00 | Sylhet | 131 | 06:00 | 126 | 00:00
Kalurghat | 134 | 07:00 | 130 | 11:00 | Sylhet-132 | 131 | 03:00 | 128 | 00:00
Kamrangirchar | 135 | 04:00 | 122 | 13:00 | Tangail | 139 | 02:00 | 114 | 18:30
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 135 | 23:00 | 120 | 07:00
Kasba | 125 | 05:00 | 119 | 11:00 | TK | 136 | 06:00 | 132 | 00:00
Kazla | 130 | 05:00 | 120 | 12:00 | Tongi | 133 | 05:00 | 124 | 15:00
Keranigonj | 134 | 02:00 | 123 | 12:00 | Ullahpara | 135 | 01:00 | 126 | 19:00
Khagrachori | 135 | 06:00 | 127 | 15:00 | Ullon | 132 | 04:00 | 120 | 11:00
Khulna | 138 | 00:00 | 124 | 19:00 | Uttara | 131 | 04:00 | 120 | 11:00
Khulna(S) | 139 | 05:00 | 127 | 19:00 | UttaraNew | 134 | 01:00 | 120 | 12:00
Khulshi | 133 | 06:00 | 127 | 11:00 | Zigatola | 135 | 06:00 | 123 | 12:00
Kishoreganj | 130 | 03:00 | 122 | 12:00
Kodda | 136 | 01:00 | 117 | 09:00
KSRM | 135 | 05:00 | 128 | 11:00
Kulaura | 134 | 07:00 | 129 | 13:00
Kurigram | 129 | 00:00 | 118 | 18:30
Kushtia | 138 | 00:00 | 29 | 17:00
Lalbag | 134 | 06:00 | 122 | 12:00
Lalmonirhat | 128 | 23:00 | 120 | 19:00
Madanganj | 132 | 05:00 | 123 | 11:00
Madaripur | 136 | 06:00 | 128 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division