## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-04-2025 | during | 17-04-2025 | during | 17-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 354 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 306 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 96 | 103 | 208.13 | 208.13 | 100 | 100 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 302 | 285 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 0 | 53.97 | 53.97 | 0.01 | 0.01 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 111 | 32 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 0 | 55 | 55 | 50 | 50 | FGMO
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 0 | 30 | 30 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 13 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 8 | 52.19 | 52.19 | 16 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 293 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 104 | 34 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 35 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 14 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 17 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 23 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 0 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 400 | 400 | 583 | 583 | 583 | 583 | Allocation limit by Titas Gas
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 17 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2851 | 2071 | 5269.9 | 5331.9 | 3582.42 | 3644.42
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 146 | 150 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 72 | 64 | 72 | -
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 32 | 68 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 0 | 15 | 2 | 35 | 2 | 35 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.88 | 0 | 4.88 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1183 | 850 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 1 | 4 | 0 | 4 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 160 | 160 | 155 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1677 | 1411 | 2985.6 | 3002.72 | 2985.6 | 3002.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 205 | 213 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 85 | 285 | 356.56 | 356.56 | 250 | 250 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 37 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 5 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 173 | 8 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 78 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 39 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 45 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 112 | 59 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 28 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 18 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 66 | 16 | 105.3 | 105.3 | 72 | 72 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 38 | 113 | 113 | 8 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 70 | 74 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 66 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1477 | 1232 | 2453.85 | 2383.85 | 2064.55 | 2024.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-04-2025 | during | 17-04-2025 | during | 17-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 23 | 23 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2 | 0 | 2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 120 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 66 | 55 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 9.88 | 0 | 48.2 | 0 | 48.2 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 14 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 228.88 | 187 | 599.2 | 549 | 454.7 | 404.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 39 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 155 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 82 | 82 | 82 | 82 | 82 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 172 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 371 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1561 | 1532 | 1607 | 1607 | 1538 | 1538
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 897 | 900 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 96.95 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 356 | 556 | 617.1 | 617.1 | 617.1 | 617.1 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1349.95 | 1456 | 2985.1 | 2895.1 | 2470.11 | 2380.11
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 684 | 494 | 990 | 1110 | 990 | 1110 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 124 | 114 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 780 | 1120 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 280 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 2045 | 2238 | 3162.12 | 3281.12 | 3110.12 | 3229.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 2 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 160 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 148 | 132 | 220 | 220 | 220 | 220 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 145 | 131 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 113 | 113 | 103 | 103 | FGMO
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.16 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1347.1 | 1212 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 16.58 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 74 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2358.84 | 2051 | 3107.63 | 2941.53 | 3044.84 | 2878.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 57 | 56 | 56 | 56 | 56 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 114 | 162 | 110 | 110 | 110 | 110 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 50 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.6 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 55 | 115 | 115 | 115 | 103.5 | 103.5 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 185 | 0 | 177.33 | 0 | 177.33 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 503.6 | 447 | 629.73 | 428 | 618.23 | 416.5
System Total |  |  |  |  | 27566.2 | 28535.742 | 14052.27 | 12625 | 22800.13 | 22420.22 | 19868.57 | 19518.66
Forecast Scenario (17-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12200 |  | 0 |  | 12200
|  |  |  | 1:00 | 11180 |  | 0 |  | 11180
|  |  |  | 2:00 | 10150 |  | 0 |  | 10150
|  |  |  | 3:00 | 9580 |  | 0 |  | 9580
|  |  |  | 4:00 | 9370 |  | 0 |  | 9370
|  |  |  | 5:00 | 8960 |  | 0 |  | 8960
|  |  |  | 6:00 | 8800 |  | 0 |  | 8800
|  |  |  | 7:00 | 9390 |  | 0 |  | 9390
|  |  |  | 8:00 | 9890 |  | 0 |  | 9890
|  |  |  | 9:00 | 10560 |  | 0 |  | 10560
|  |  |  | 10:00 | 11370 |  | 0 |  | 11370
|  |  |  | 11:00 | 11920 |  | 0 |  | 11920
|  |  |  | 12:00 | 12900 |  | 0 |  | 12900
|  |  |  | 13:00 | 13200 |  | 0 |  | 13200
|  |  |  | 14:00 | 13180 |  | 0 |  | 13180
|  |  |  | 15:00 | 13360 |  | 0 |  | 13360
|  |  |  | 16:00 | 13370 |  | 0 |  | 13370
|  |  |  | 17:00 | 12960 |  | 0 |  | 12960
|  |  |  | 18:00 | 12400 |  | 0 |  | 12400
|  |  |  | 18:30 | 13400 |  | 0 |  | 13400
|  |  |  | 19:00 | 14410 |  | 0 |  | 14410
|  |  |  | 19:30 | 14580 |  | 0 |  | 14580
|  |  |  | 20:00 | 14350 |  | 0 |  | 14350
|  |  |  | 21:00 | 14200 |  | 0 |  | 14200
|  |  |  | 22:00 | 13990 |  | 0 |  | 13990
|  |  |  | 23:00 | 13920 |  | 0 |  | 13920
Probable Maximum Temperature: |  |  | 32.40°C
Probable Maximum Demand at Day Peak: |  |  | 12900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14580.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14580.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 285.61 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:27 hrs on 17-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-04-2025 | [28 empty] | Date: | 16-04-2025 | [28 empty] | Date: | 16-04-2025 | [28 empty] | Date: | 16-04-2025 | [28 empty] | Date: | 16-04-2025 | [16 empty] | Date: | 16-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 16 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 35 | 36 | 149 | 147 | 200 | 0 | 35 | 144 | 0 | 80 | 450 | 284 | 450 | 0 | 55 | 0 | 270 | 37 | 0 | 0 | 108 | 16.5 | 7 | 0 | 0 | 0 | 0 | 50 | 0 | 2 | 85 | 68 | 17 | 50 | 40 | 0 | 40 | 0 | 25 | 160 | 17 | 0 | 0 | 0 | 45 | 150 | 0 | 0 | 0 | 1070 | 0 | 43 | 70 | 175 | 0 | 359 | 100 | 52 | 192 | 36 | 90 | 70 | 167 | 18 | 19 | 68 | 38 | 52.2 | 0 | 40 | 305 | 320 | 357 | 40 | 40 | 0 | 149 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 54.5 | 103 | 163 | 8 | 0 | 0 | 12 | 8160.2 | 899 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 51 | 1369.16 | 0 | 34 | 0 | 70 | 21 | 41 | 35 | 0 | 0 | 0 | 15 | 0 | 147 | 0 | 140 | 0 | 140 | 0 | 333 | 0 | 0 | 0 | 172 | 56 | 93 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 180 | 0 | 730 | 1100 | 0 | 6500.16 | 14660.36 | 82.01
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 35 | 20 | 102 | 147 | 195 | 0 | 35 | 54 | 0 | 63 | 450 | 291 | 450 | 0 | 35 | 0 | 275 | 37 | 0 | 0 | 90 | 16.5 | 7 | 0 | 0 | 0 | 0 | 30 | 0 | 2 | 85 | 68 | 17 | 50 | 40 | 0 | 40 | 0 | 30 | 159 | 0 | 0 | 0 | 0 | 47 | 150 | 0 | 0 | 0 | 1100 | 0 | 43 | 70 | 175 | 0 | 360 | 33 | 52 | 194 | 36 | 89 | 70 | 173 | 18 | 19 | 72 | 38 | 52.2 | 0 | 40 | 300 | 320 | 370 | 40 | 40 | 0 | 154 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 33 | 47 | 96 | 8 | 0 | 0 | 12 | 7765.7 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 51 | 1361.69 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 156 | 0 | 140 | 0 | 140 | 0 | 337 | 0 | 0 | 0 | 172 | 56 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 220 | 0 | 731 | 1120 | 0 | 6355.69 | 14121.39 | 82
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 35 | 17 | 70 | 147 | 145 | 0 | 35 | 54 | 0 | 50 | 450 | 278 | 450 | 0 | 35 | 0 | 260 | 37 | 0 | 0 | 90 | 16.5 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 68 | 0 | 50 | 40 | 0 | 40 | 0 | 30 | 160 | 0 | 0 | 0 | 0 | 45 | 150 | 0 | 0 | 0 | 1000 | 0 | 43 | 70 | 175 | 0 | 360 | 55 | 52 | 179 | 36 | 58 | 70 | 165 | 9 | 19 | 66 | 36 | 52.2 | 0 | 40 | 300 | 320 | 292 | 40 | 40 | 0 | 149 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 17 | 47 | 96 | 10 | 0 | 0 | 12 | 7327.7 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 51 | 1363.77 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 140 | 0 | 140 | 0 | 318 | 0 | 0 | 0 | 172 | 56 | 60 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 114 | 220 | 0 | 732 | 1110 | 0 | 6329.77 | 13657.47 | 81.99
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 17 | 17 | 60 | 147 | 0 | 0 | 35 | 54 | 0 | 16 | 400 | 286 | 450 | 0 | 35 | 0 | 266 | 37 | 0 | 0 | 90 | 16.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 51 | 68 | 0 | 50 | 12 | 0 | 40 | 0 | 33 | 160 | 0 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 1065 | 0 | 43 | 50 | 175 | 0 | 360 | 70 | 52 | 187 | 33 | 55 | 70 | 164 | 9 | 19 | 66 | 30 | 52.2 | 0 | 40 | 305 | 320 | 292 | 40 | 40 | 0 | 148 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 48 | 96 | 10 | 0 | 0 | 12 | 7046.4 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 1369.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 140 | 0 | 140 | 0 | 327 | 0 | 0 | 0 | 171 | 56 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 732 | 1112 | 0 | 6193.3 | 13239.7 | 81.98
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 17 | 17 | 50 | 147 | 0 | 0 | 35 | 54 | 0 | 0 | 400 | 284 | 450 | 0 | 35 | 0 | 265 | 37 | 0 | 0 | 52 | 16.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 34 | 48 | 0 | 24 | 0 | 0 | 40 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1060 | 0 | 43 | 30 | 175 | 0 | 360 | 80 | 52 | 186 | 33 | 54 | 70 | 149 | 9 | 19 | 70 | 30 | 52.2 | 0 | 40 | 300 | 320 | 292 | 40 | 40 | 0 | 148 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 48 | 97 | 10 | 0 | 0 | 12 | 6821.4 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 1375.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 140 | 0 | 140 | 0 | 327 | 0 | 0 | 0 | 129 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 110 | 220 | 0 | 723 | 1109 | 0 | 6109.2 | 12930.6 | 81.97
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 17 | 17 | 50 | 131 | 0 | 0 | 35 | 54 | 0 | 0 | 400 | 291 | 450 | 0 | 35 | 0 | 273 | 38 | 0 | 0 | 52 | 16.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 34 | 48 | 0 | 24 | 0 | 0 | 40 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1090 | 0 | 43 | 30 | 175 | 0 | 320 | 60 | 52 | 193 | 32 | 51 | 70 | 132 | 9 | 19 | 70 | 34 | 52.2 | 0 | 40 | 305 | 320 | 296 | 40 | 40 | 0 | 149 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 48 | 97 | 10 | 0 | 0 | 12 | 6797.4 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 1271.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 140 | 0 | 140 | 0 | 337 | 0 | 0 | 0 | 117 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 114 | 220 | 0 | 641 | 1100 | 0 | 5916.71 | 12714.11 | 81.96
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 17 | 50 | 147 | 0 | 0 | 17 | 17 | 0 | 0 | 350 | 296 | 450 | 0 | 0 | 0 | 278 | 38 | 0 | 1 | 52 | 16.2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 3 | 162 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1100 | 1 | 43 | 12 | 127 | 0 | 320 | 60 | 53 | 199 | 32 | 51 | 70 | 136 | 9 | 19 | 73 | 32 | 25 | 2 | 16 | 300 | 320 | 321 | 40 | 40 | 0 | 156 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 48 | 97 | 10 | 0 | 1.23 | 12 | 6577.43 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 357 | 0 | 1217.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 | 179 | 0 | 140 | 0 | 140 | 0 | 348 | 0 | 0.1 | 0 | 112 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 3.6 | 0.02 | 0 | 200 | 7 | 120 | 180 | 0 | 562 | 1060 | 0 | 5583.56 | 12160.99 | 81.95
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 17 | 50 | 114 | 0 | 0 | 17 | 17 | 0 | 0 | 350 | 305 | 450 | 0 | 0 | 0 | 288 | 38 | 0 | 5 | 52 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 10 | 163 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1101 | 4 | 43 | 12 | 127 | 0 | 354 | 60 | 53 | 203 | 32 | 50 | 70 | 117 | 9 | 19 | 67 | 30 | 25 | 15 | 16 | 300 | 320 | 321 | 40 | 40 | 0 | 160 | 22 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 67 | 125 | 5 | 0 | 5.55 | 12 | 6648.55 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.96 | 358 | 0 | 1219.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 6.99 | 182 | 0 | 140 | 0 | 140 | 0 | 362 | 0 | 0.75 | 0 | 109 | 55 | 0 | 6 | 0 | 0 | 0 | 1.4 | 38 | 0.87 | 0 | 250 | 7 | 122 | 180 | 0 | 494 | 1100 | 0 | 5697.79 | 12346.34 | 81.94
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 17 | 57 | 115 | 0 | 0 | 17 | 17 | 0 | 0 | 350 | 289 | 450 | 0 | 0 | 0 | 295 | 38 | 0 | 6 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 24 | 0 | 1 | 40 | 0 | 5 | 162 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1106 | 11 | 43 | 12 | 127 | 0 | 357 | 60 | 52 | 200 | 32 | 54 | 50 | 115 | 9 | 19 | 49 | 26 | 25 | 34 | 16 | 300 | 320 | 319 | 40 | 40 | 0 | 157 | 16 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 67 | 127 | 5 | 1 | 17.45 | 12 | 6636.45 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.87 | 358 | 0 | 1256.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 11.4 | 184 | 0 | 140 | 0 | 140 | 0 | 342 | 0 | 1.79 | 0 | 111 | 57 | 0 | 14 | 20 | 0 | 0 | 3.4 | 70 | 0.18 | 0 | 250 | 7 | 120 | 180 | 0 | 514 | 1102 | 0 | 5819.97 | 12456.42 | 81.93
09:00 | 0 | 25 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 17 | 70 | 114 | 47 | 0 | 23 | 54 | 0 | 0 | 380 | 286 | 450 | 0 | 25 | 0 | 275 | 38 | 0 | 22 | 70 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 24 | 0 | 2 | 40 | 3 | 4 | 160 | 0 | 0 | 0 | 0 | 9 | 153 | 0 | 0 | 0 | 1045 | 5 | 43 | 16 | 173 | 0 | 355 | 80 | 51 | 217 | 29 | 69 | 50 | 116 | 9 | 19 | 44 | 28 | 25 | 56 | 16 | 310 | 320 | 307 | 39 | 40 | 0 | 155 | 16 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 67 | 126 | 5 | 1 | 30.77 | 12 | 6883.77 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.42 | 358 | 0 | 1359.72 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 35 | 184 | 0 | 140 | 0 | 140 | 0 | 329 | 0 | 3.02 | 0 | 113 | 57 | 35 | 22 | 44 | 0 | 0 | 5.2 | 121 | 0.46 | 0 | 250 | 6 | 108 | 180 | 0 | 567 | 1100 | 0 | 6119.82 | 13003.59 | 81.92
10:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 17 | 17 | 94 | 113 | 144 | 0 | 35 | 90 | 0 | 0 | 380 | 300 | 450 | 0 | 34 | 0 | 279 | 38 | 0 | 27 | 85 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 50 | 0 | 2 | 40 | 14 | 0 | 160 | 0 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 | 1074 | 0 | 43 | 50 | 173 | 0 | 352 | 70 | 49 | 183 | 31 | 68 | 50 | 103 | 9 | 4 | 44 | 28 | 25 | 65 | 16 | 300 | 320 | 350 | 39 | 40 | 0 | 147 | 16 | 0 | 80 | 30 | 0 | 18 | 173 | 0 | 67 | 126 | 0 | 0 | 41.36 | 12 | 7191.36 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55.64 | 357 | 0 | 1361.89 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 45.77 | 175 | 0 | 165 | 0 | 157 | 0 | 414 | 0 | 4.18 | 0 | 115 | 56 | 41 | 28 | 51 | 0 | 0 | 6.5 | 147 | 0.24 | 0 | 250 | 7 | 110 | 180 | 0 | 584 | 1000 | 0 | 6325.22 | 13516.58 | 81.92
11:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 20 | 94 | 113 | 145 | 0 | 35 | 108 | 0 | 0 | 380 | 300 | 450 | 0 | 51 | 0 | 285 | 37 | 0 | 30 | 108 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 62 | 5 | 5 | 40 | 15 | 0 | 160 | 0 | 0 | 0 | 0 | 15 | 148 | 0 | 0 | 0 | 1140 | 0 | 43 | 63 | 173 | 0 | 345 | 75 | 44 | 194 | 28 | 69 | 50 | 107 | 10 | 11 | 45 | 32 | 25 | 70 | 16 | 305 | 320 | 375 | 39 | 39 | 0 | 152 | 16 | 0 | 80 | 28 | 0 | 17 | 173 | 0 | 68 | 126 | 0 | 1 | 46.37 | 12 | 7452.37 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.16 | 357 | 0 | 1363.52 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 39.22 | 167 | 0 | 160 | 0 | 154 | 0 | 414 | 0 | 4.88 | 0 | 114 | 57 | 45 | 31 | 50 | 0 | 0 | 7.1 | 173 | 0 | 0 | 250 | 7 | 120 | 220 | 0 | 682 | 800 | 0 | 6285.88 | 13738.25 | 81.91
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 35 | 104 | 111 | 293 | 0 | 35 | 108 | 0 | 14 | 380 | 296 | 400 | 0 | 55 | 0 | 302 | 96 | 0 | 23 | 108 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 62 | 50 | 4 | 40 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1183 | 0 | 43 | 78 | 173 | 0 | 340 | 85 | 44 | 205 | 30 | 70 | 50 | 112 | 8 | 11 | 66 | 32 | 25 | 66 | 39 | 305 | 320 | 390 | 39 | 39 | 0 | 152 | 16 | 0 | 80 | 30 | 0 | 17 | 173 | 14 | 66 | 125 | 0 | 2 | 9.88 | 12 | 7794.88 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.95 | 356 | 0 | 1347.1 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 16.58 | 176 | 0 | 148 | 0 | 145 | 0 | 414 | 0 | 3.16 | 0 | 114 | 58 | 55 | 34 | 50 | 0 | 0 | 7.6 | 185 | 0 | 0 | 230 | 7 | 124 | 220 | 0 | 684 | 780 | 0 | 6257.39 | 14052.27 | 81.91
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 17 | 20 | 124 | 111 | 295 | 0 | 35 | 108 | 0 | 41 | 330 | 255 | 400 | 0 | 55 | 0 | 256 | 41 | 0 | 20 | 108 | 15 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 33 | 60 | 2 | 40 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1224 | 0 | 43 | 108 | 173 | 0 | 360 | 120 | 47 | 180 | 31 | 74 | 50 | 133 | 9 | 19 | 63 | 36 | 25 | 25 | 39 | 295 | 320 | 350 | 36 | 40 | 0 | 150 | 24 | 0 | 82 | 30 | 0 | 17 | 173 | 33 | 67 | 125 | 0 | 0 | 3.37 | 12 | 7738.37 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.21 | 356 | 0 | 1351.99 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 0.35 | 173 | 0 | 141 | 0 | 138 | 0 | 414 | 0 | 0.04 | 0 | 114 | 57 | 62 | 32 | 50 | 0 | 0 | 7.5 | 169 | 0 | 0 | 219 | 7 | 80 | 180 | 0 | 719 | 790 | 0 | 6157.09 | 13895.46 | 81.9
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 18 | 102 | 79 | 195 | 0 | 35 | 108 | 0 | 50 | 330 | 288 | 300 | 0 | 55 | 0 | 260 | 36 | 0 | 26 | 17 | 15 | 7 | 0 | 0 | 0 | 0 | 1 | 0 | 25 | 100 | 0 | 0 | 33 | 88 | 4 | 40 | 0 | 3 | 160 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1110 | 0 | 43 | 90 | 137 | 0 | 300 | 165 | 48 | 182 | 33 | 69 | 50 | 131 | 8 | 19 | 63 | 38 | 25 | 3 | 39 | 280 | 320 | 300 | 36 | 40 | 0 | 147 | 16 | 0 | 82 | 20 | 0 | 17 | 173 | 17 | 45 | 125 | 0 | 0 | 2.54 | 12 | 7084.54 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.77 | 358 | 0 | 1269 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 1.75 | 166 | 0 | 138 | 0 | 133 | 0 | 360 | 0 | 0.13 | 0 | 112 | 57 | 59 | 30 | 49 | 0 | 0 | 6.8 | 98 | 0 | 0 | 150 | 0 | 80 | 180 | 0 | 650 | 680 | 0 | 5580.45 | 12664.99 | 81.9
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 17 | 34 | 65 | 0 | 45 | 0 | 0 | 54 | 0 | 30 | 330 | 235 | 300 | 0 | 0 | 0 | 257 | 36 | 0 | 7 | 17 | 0 | 7 | 0 | 0 | 0 | 0 | 13 | 0 | 30 | 100 | 0 | 0 | 33 | 40 | 4 | 40 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 900 | 14 | 10 | 40 | 86 | 0 | 300 | 195 | 43 | 179 | 33 | 50 | 50 | 103 | 9 | 19 | 6 | 28 | 8 | 16 | 0 | 270 | 320 | 303 | 40 | 40 | 0 | 147 | 16 | 0 | 30 | 20 | 0 | 17 | 172 | 17 | 45 | 75 | 0 | 1 | 6.37 | 3 | 5971.37 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.9 | 360 | 0 | 1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 21.08 | 164 | 0 | 134 | 0 | 126 | 0 | 300 | 0 | 1.78 | 0 | 110 | 57 | 62 | 15 | 49 | 0 | 0 | 5.5 | 118 | 0 | 0 | 150 | 0 | 80 | 180 | 0 | 574 | 631 | 0 | 5304.26 | 11275.63 | 81.89
16:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 215 | 300 | 0 | 0 | 0 | 170 | 35 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 90 | 0 | 0 | 12 | 10 | 2 | 40 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 659 | 0 | 5 | 0 | 16 | 0 | 280 | 205 | 8 | 144 | 0 | 16 | 50 | 25 | 9 | 0 | 0 | 28 | 0 | 14 | 0 | 255 | 320 | 302 | 40 | 40 | 0 | 120 | 16 | 0 | 5 | 20 | 0 | 17 | 172 | 0 | 24 | 45 | 0 | 1 | 14.94 | 0 | 4644.94 | 796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.9 | 361 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 26.52 | 130 | 0 | 140 | 0 | 126 | 0 | 250 | 0 | 2.49 | 0 | 112 | 57 | 70 | 14 | 0 | 0 | 0 | 3.7 | 91 | 0 | 0 | 150 | 3 | 80 | 180 | 0 | 400 | 540 | 0 | 4418.61 | 9063.55 | 81.89
17:00 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 17 | 0 | 0 | 420 | 260 | 0 | 0 | 0 | 0 | 265 | 98 | 0 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 84 | 0 | 0 | 12 | 10 | 0 | 40 | 0 | 5 | 162 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 609 | 0 | 14 | 0 | 81 | 0 | 300 | 285 | 12 | 180 | 0 | 23 | 50 | 16 | 18 | 0 | 0 | 24 | 1 | 10 | 0 | 300 | 320 | 311 | 40 | 40 | 0 | 141 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 40 | 110 | 0 | 0 | 5.71 | 2 | 5135.71 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.01 | 360 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9.31 | 146 | 0 | 144 | 0 | 133 | 0 | 350 | 0 | 0.93 | 0 | 111 | 57 | 35 | 6 | 0 | 0 | 0 | 1.7 | 37 | 0 | 0 | 200 | 4 | 108 | 220 | 0 | 399 | 590 | 0 | 4665.95 | 9801.66 | 81.88
18:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 40 | 64 | 15 | 0 | 0 | 54 | 0 | 0 | 350 | 267 | 0 | 0 | 0 | 0 | 265 | 38 | 0 | 2 | 24 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 68 | 0 | 0 | 60 | 50 | 0 | 40 | 0 | 7 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 81 | 0 | 300 | 325 | 50 | 179 | 37 | 50 | 50 | 46 | 37 | 0 | 0 | 28 | 8 | 1 | 0 | 290 | 320 | 310 | 40 | 40 | 0 | 136 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 73 | 140 | 0 | 0 | 0.79 | 12 | 5687.79 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.07 | 359 | 0 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.38 | 170 | 0 | 144 | 0 | 136 | 0 | 350 | 0 | 0.13 | 0 | 155 | 57 | 35 | 1 | 34 | 0 | 0 | 0.3 | 6 | 0 | 0 | 200 | 6 | 100 | 220 | 0 | 391 | 762 | 0 | 4957.88 | 10645.67 | 81.88
19:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 73 | 64 | 15 | 0 | 4 | 126 | 0 | 0 | 450 | 292 | 64 | 0 | 0 | 0 | 265 | 104 | 0 | 0 | 52 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 68 | 0 | 0 | 100 | 50 | 0 | 40 | 0 | 7 | 160 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 809 | 0 | 51 | 1 | 63 | 0 | 355 | 260 | 25 | 194 | 36 | 54 | 45 | 50 | 38 | 0 | 22 | 24 | 8 | 0 | 0 | 300 | 320 | 346 | 39 | 40 | 0 | 146 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 75 | 150 | 0 | 0 | 0 | 12 | 6272 | 897 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 1103 | 0 | 0 | 0 | 3 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 140 | 0 | 134 | 0 | 414 | 0 | 0 | 0 | 161 | 57 | 50 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 220 | 0 | 447 | 940 | 0 | 5652 | 11924 | 81.87
19:30 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 17 | 0 | 73 | 64 | 15 | 0 | 17 | 108 | 0 | 0 | 450 | 275 | 146 | 0 | 0 | 0 | 265 | 105 | 0 | 0 | 35 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 68 | 0 | 0 | 100 | 22 | 0 | 40 | 0 | 10 | 160 | 0 | 0 | 0 | 2 | 0 | 149 | 0 | 0 | 0 | 830 | 0 | 51 | 25 | 35 | 0 | 355 | 285 | 5 | 173 | 36 | 75 | 45 | 73 | 38 | 11 | 28 | 24 | 8 | 0 | 0 | 265 | 320 | 350 | 40 | 40 | 0 | 146 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 75 | 150 | 0 | 0 | 0 | 12 | 6336 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 465 | 0 | 1190 | 0 | 0 | 0 | 40 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 135 | 0 | 131 | 0 | 414 | 0 | 0 | 0 | 159 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 220 | 0 | 464 | 1170 | 0 | 6114 | 12450 | 81.87
20:00 | 0 | 50 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 70 | 32 | 15 | 0 | 17 | 54 | 0 | 0 | 450 | 283 | 150 | 0 | 0 | 0 | 265 | 106 | 0 | 0 | 34 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 68 | 0 | 0 | 60 | 22 | 0 | 40 | 0 | 15 | 160 | 0 | 0 | 0 | 5 | 0 | 150 | 0 | 0 | 0 | 900 | 0 | 51 | 15 | 35 | 0 | 355 | 285 | 5 | 179 | 37 | 75 | 45 | 89 | 39 | 14 | 27 | 26 | 8 | 0 | 0 | 275 | 320 | 350 | 39 | 40 | 0 | 147 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 55 | 120 | 0 | 0 | 0 | 12 | 6257 | 849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 0 | 1214 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 134 | 0 | 131 | 0 | 414 | 0 | 0 | 0 | 160 | 56 | 115 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 108 | 220 | 0 | 492 | 1200 | 0 | 6211 | 12468 | 81.87
21:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 34 | 32 | 0 | 0 | 17 | 17 | 0 | 0 | 450 | 306 | 400 | 0 | 0 | 0 | 285 | 103 | 0 | 0 | 17 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 68 | 0 | 0 | 60 | 50 | 0 | 40 | 0 | 15 | 160 | 0 | 0 | 0 | 17 | 0 | 150 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 355 | 285 | 5 | 213 | 37 | 74 | 45 | 59 | 38 | 18 | 16 | 28 | 0 | 0 | 0 | 290 | 320 | 371 | 39 | 40 | 0 | 155 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 55 | 120 | 0 | 0 | 0 | 12 | 6433 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 1212 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 132 | 0 | 131 | 0 | 414 | 0 | 0 | 0 | 162 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 10 | 114 | 220 | 0 | 494 | 1120 | 0 | 6192 | 12625 | 81.86
22:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 32 | 40 | 32 | 0 | 0 | 0 | 17 | 0 | 0 | 450 | 280 | 400 | 0 | 0 | 0 | 267 | 104 | 0 | 0 | 17 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 60 | 50 | 0 | 40 | 0 | 0 | 160 | 0 | 0 | 0 | 17 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 355 | 285 | 5 | 223 | 37 | 74 | 50 | 64 | 39 | 20 | 14 | 28 | 18 | 0 | 0 | 305 | 320 | 338 | 39 | 40 | 0 | 153 | 16 | 0 | 82 | 30 | 0 | 17 | 172 | 0 | 55 | 120 | 0 | 0 | 0 | 12 | 6437 | 899 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 130 | 0 | 128 | 0 | 414 | 0 | 0 | 0 | 164 | 58 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 108 | 220 | 0 | 495 | 1109 | 0 | 6203 | 12640 | 81.86
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 36 | 43 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 303 | 400 | 0 | 0 | 0 | 287 | 104 | 0 | 0 | 17 | 16 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 68 | 0 | 0 | 60 | 10 | 0 | 40 | 0 | 25 | 160 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 354 | 285 | 5 | 221 | 37 | 68 | 50 | 75 | 38 | 20 | 15 | 28 | 25 | 0 | 0 | 310 | 320 | 335 | 39 | 39 | 0 | 141 | 16 | 0 | 82 | 30 | 0 | 17 | 171 | 0 | 55 | 120 | 0 | 0 | 0 | 12 | 6473 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 130 | 0 | 137 | 0 | 414 | 0 | 0 | 0 | 163 | 58 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 494 | 1111 | 0 | 6059 | 12532 | 81.85
Total KWH | 4032 | 642240 | 224160 | 0 | 0 | 0 | 0 | 0 | 8496000 | 0 | 0 | 344880 | 413640 | 1524816 | 2095680 | 1677076 | 0 | 535325 | 1254240 | 0 | 291840 | 9327000 | 6949178 | 8649545 | 0 | 498887 | 0 | 6620657 | 1524000 | 0 | 160383 | 1288800 | 264000 | 171360 | 0 | 0 | 0 | 0 | 61440 | 0 | 208320 | 1309987 | 378336 | 0 | 1029120 | 587520 | 27598 | 957600 | 42700 | 287520 | 3825454.55 | 3345 | 0 | 0 | 60865.2 | 202399 | 3379360 | 0 | 0 | 0 | 23443634 | 56700 | 945960 | 930036 | 2776727 | 0 | 8544800 | 3692000 | 869760 | 4703000 | 741240 | 1474560 | 1308670 | 2469600 | 425040 | 345710 | 979260 | 715200 | 604450 | 366745 | 433904 | 7236500 | 7692000 | 8361000 | 931000 | 932040 | 0 | 3558518 | 413712 | 0 | 1832640 | 686208 | 0 | 422000 | 3572700 | 15120 | 1388400 | 2731200 | 6624 | 7250 | 201560 | 265680 | 161400451.75 | 21493818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 492480 | 9752727 | 122880 | 29369731.64 | 0 | 0 | 0 | 420672 | 27776 | 28769 | 7296 | 0 | 0 | 657252 | 21439 | 213752 | 4079364 | 0 | 3602518 | 0 | 3542752 | 0 | 8825309 | 0 | 22260 | 0 | 3283000 | 1264582 | 1171431 | 237361 | 1184102 | 0 | 0 | 55337.88 | 1136160 | 810 | 0 | 5957000 | 174601 | 2619000 | 5204710 | 0 | 13852364 | 23780363.64 | 0 | 142601618.16 | 304002069.91

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14052.27 | MW | 12:00 Hr. | Energy Generated |  |  | 304.0021 |  | MKWHr.
| Day Peak Demand |  |  | 14103.48 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.866 |  | MKWHr.
| Evening Peak Generation |  |  | 12625 | MW | 21:00 Hr. | Energy Demand |  |  | 304.8681 |  | MKWHr.
| Evening Peak Demand |  |  | 12625 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.4 |  | °C
| Minimum Generation of the Day |  |  | 9063.55 | MW | 16:00 Hr. | Total Gas Supplied |  |  | 986.79 |  | MMCFD
| Maximum Generation of the Day |  |  | 14660.36 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.9184 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.0017 | 0 | 10.7956 | 0 | 0 | 0.16038 | 0 | 0 | 52.9577 | Gas | 133.2897 | Gas | 432519525.64
| Chattogram Zone |  |  | 3.6669 | 27.2691 | 3.6757 | 0 | 0.9576 | 0.084298 | 0 | 0.20832 | 35.8619 | Coal | 85.1591 | Coal | 508607251.8822
| Cumilla Zone |  |  | 23.9279 | 0 | 7.3168 | 0 | 0 | 0.36674 | 0.7152 | 0 | 32.3267 | HFO | 29.1729 | HFO | 521189054.174
| Mymensingh Zone |  |  | 0.006624 | 0 | 4.4004 | 0 | 0 | 0.20881 | 0 | 0 | 4.6158 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.6383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6383 | Hydro | 0.9576 | Hydro | 95760
| Khulna Zone |  |  | 0 | 9.7527 | 0.12288 | 0 | 0 | 0.49248 | 21.4938 | 0 | 31.8619 | Solar | 3.6356 | Solar | 59552428.3568
| Barishal Zone |  |  | 7.9983 | 43.5897 | 0 | 0 | 0 | 0.00081 | 0 | 0 | 51.5888 | Import | 51.5787 | Import | 274180593.012
| Rajshahi Zone |  |  | 20.0499 | 0 | 0.50595 | 0 | 0 | 0.89326 | 29.3697 | 0 | 50.8189 | Wind | 0.20832 | Wind | 3049804.8
| Rangpur Zone |  |  | 0 | 4.5476 | 2.3555 | 0 | 0 | 1.4289 | 0 | 0 | 8.332
| Total |  |  | 133.2897 | 85.1591 | 29.1729 | 0 | 0.9576 | 3.6356 | 51.5787 | 0.20832 | 304.0021
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 432519525.64 |  | Hydro | 95760
|  |  |  | Coal | 508607251.8822 |  | Solar | 59552428.3568
|  |  |  | HFO | 521189054.174 |  | Import | 274180593.012
|  |  |  | HSD | 0 |  | Wind | 3049804.8
[5 empty] | Total: | 179,91,94,417 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.4938 | Peak Hr Flow | 900.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36160000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 29.3697 | Peak Hr Flow | 1212.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 628 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.7152 | Peak Hr Flow | 28.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 870 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.5787 | Peak Hr Flow | 2140.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4355
|  |  |  | Chattogram |  | 0 |  | 1261
|  |  |  | Cumilla |  | 0 |  | 1072
|  |  |  | Mymensingh |  | 0 |  | 875
|  |  |  | Sylhet |  | 0 |  | 435
|  |  |  | Khulna |  | 0 |  | 1580
|  |  |  | Barishal |  | 0 |  | 382
|  |  |  | Rajshahi |  | 0 |  | 1282
|  |  |  | Rangpur |  | 0 |  | 870
|  |  |  | Total |  | 0 |  | 12112
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:09 | Bakulia 132/33kV S/S Aux Tr-1 HT is restored.
|  | 08:09 | Bakulia 132/33kV S/S T-1 (402T) LT is restored.
|  | 08:10 | Bakulia 132/33kV S/S T-2 (412T) LT is restored.
|  | 08:25 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT is restored.
| 08:36 | 19:45 | Cox'sbazar-Dohazari 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to For disk
change. 27 MW interruption matarbari around 3Hour.
| 08:40 | 18:05 | Rangpur-Saidpur 132kV Ckt-1 Project Work S/D from Saidpur 132/33kV end Due to QF- GMD-
39 and as the instruction of ALDC, Bogura (499264) and from Rangpur 132/33kV end Due to
Work of OPGW
| 08:40 | 18:07 | Jaldhaka-Saidpur 132kV Ckt-1 Project Work S/D from Jaldhaka 132/33kV end Due to Saidpur
150MW SCPP Project ,BPDB has requested for a shutdown of Jaldhaka-Saidpur 132KV Ckt-01 at
Saidpur Grid S/S due to power evacuation from plant side to Grid side. and from Saidpur
132/33kV end Due to QF- GMD- 39 and as the instruction of ALDC, Bogura (499264)
|  | 08:40 | Naogaon 132/33kV S/S T-1 HT is restored.
| 08:41 | 15:54 | Rangpur-Saidpur 132kV Ckt-2 Project Work S/D from Saidpur 132/33kV end Due to QF- GMD-
39 and as the instruction of ALDC, Bogura (499264) and from Rangpur 132/33kV end Due to
Work of OPGW
|  | 08:42 | Naogaon 132/33kV S/S T-1 LT is restored.
| 08:46 | 13:21 | Saidpur 132/33kV S/S TR-01 HT Project Work S/D Due to QF- GMD- 39 and as the instruction
of ALDC, Bogura (499264)
| 08:52 | 18:42 | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline checking.
| 08:52 | 11:13 | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Emergency Maintenance for | [7 empty] | 4.0MW load
|  |  | BREB-2(Betagi) Feeder | [7 empty] | interrup.
| 09:15 | 12:25 | Saidpur 132/33kV S/S BUS A Project Work S/D Due to QF- GMD- 39 and as the instruction of
ALDC, Bogura (499264)
|  | 09:25 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) LT is restored.
| 09:27 | 11:16 | Bibiana 400/230kV S/S ICT-02 LT Scheduled S/D Due to EM
| 09:27 | 11:16 | Bibiana 400/230kV S/S ICT-02 HT Scheduled S/D Due to EM
| 09:28 | 12:42 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to Tree
trimming at Mymensingh end. and from Jamalpur 132/33kVend.
| 09:53 | 11:12 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Emergency Maintenance for | [7 empty] | 4.0MW load
|  |  | BREB-2(Betagi) Feeder | [7 empty] | interrup.
| 10:10 | 14:00 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Maintenance of 33 kV jack | [7 empty] | 50.0MW load
|  |  | bus | [7 empty] | interrup.
| 10:10 | 14:00 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Maintenance of 33 kV Jack | [7 empty] | 50.0MW load
|  |  | Bus | [7 empty] | interrup.
| 10:23 |  | Barishal-Barishal(N) 132 kV Ckt-2 Scheduled S/D from Barishal 132/33kV end Due to For new
Relay install work. and from Barishal 230/132kV end Due to S/d taken by Barishal 132/33kv
s.stn.
| 10:54 | 15:47 | Amnura 132/33kV S/S T-1 (406T) HT Tripped showing OC/EF, 87T1/87T2 relays Due to Oil
temperature trip(OTH Trip)
| 10:54 | 14:51 | Amnura 132/33kV S/S T-1 (406T) LT Tripped showing 33kv side NONE relays.
|  | 11:16 | Bibiana 400/230kV S/S ICT-02 HT is restored.
| 11:25 | 12:50 | Joydebpur 132/33kV S/S GT-3 HT Scheduled S/D Due to Installation Of Multifunctional
Meter.
| 11:46 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 12:00 |  | Day peak Generation is 14049 MW
| 12:03 | 13:30 | Ghorasal-Tongi 230kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance relay
relays.
| 12:50 | 17:55 | Saidpur 132/33kV S/S BUS B Project Work S/D Due to QF- GMD- 39 and as the instruction
of ALDC, Bogura (499264)
| 12:54 |  | At Bhola PP,Borhanuddin WZPDCL(230/33)kv Transformer 33 kv CB trip Due to Bad
weather.Interruption=20MW
| 12:54 |  | At Bhola PP,Borhanuddin PBS (230/33)kv Transformer 33 kv CB trip Due to Bad
weather.Interruption=40MW
| 13:13 | 14:26 | Kodda 132/33kV S/S Tr-3 (426T) HT Scheduled S/D Due to Red hot maintenance
| 13:13 | 14:28 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 50.0MW load
interrup.
| 13:20 | 14:10 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Tripped from Brahmanbaria 132/33kV end showing
Distance Relay Trip relays Due to Distance Relay Trip
| 13:20 | 13:50 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing
Distance Relay Trip relays Due to Distance Relay Trip
| 13:48 |  | At Bhola PP,Borhanuddin PBS (230/33)kv Transformer 33 kv CB is restored.
| 14:14 |  | At Bhola PP,Borhanuddin wzpdcl(230/33)kv Transformer 33 kv CB is restored.
| 15:12 | 15:47 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Tripped showing Over current relay operated | [7 empty] | 25.0MW load
|  |  | relays Due to 33kv Zinzira-2 relay operated but CB not tripped. | [7 empty] | interrup.
| 15:26 | 16:00 | Bashundhara-Tongi 132 kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance
B,C-Phase Main prot. Trip relays.
| 15:34 | 18:08 | Sonargaon 132/33kV S/S Tr-1 LT Tripped showing Dir O/C & E/F Relay relays Due to Due to | [7 empty] | 3.0MW load
|  |  | Bad Weather. | [7 empty] | interrup.
| 15:35 | 18:05 | Sonargaon 132/33kV S/S Tr-1 HT Tripped showing TRAFO.DIFF.RALAY relays Due to Due to bad | [7 empty] | 3.0MW load
|  |  | weather. | [7 empty] | interrup.
| 15:45 | 17:25 | Siddhirganj 132/33kV S/S T-1 LT Forced S/D Due to Due to the fire at DPDC 33kv | [7 empty] | 66.0MW load
|  |  | Sub-station | [7 empty] | interrup.
| 15:45 | 17:25 | Siddhirganj 132/33kV S/S T-2 LT Forced S/D Due to Due to the fier at DPDC 33kv | [7 empty] | 66.0MW load
|  |  | Sub-station | [7 empty] | interrup.
| 15:58 | 16:13 | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing Micom-127 relays Due to Trip | [7 empty] | 40.0MW load
interrup.
| 16:18 | 16:51 | Rampura-Ullon-2 132kV Ckt-2 Tripped from Rampura 230/132kV end showing Distance trip
21.Z1 PI 1(Dist./DEF) Send relays Due to At Moghbazar substation and GT 3 LA brust. (
Moghbazar 2 overhead line shutdown Because of xlpe cable commissioning & relay setting.
Now Moghbazar 2 connected via Ullon substation)
| 16:46 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- GT
| 17:04 | 17:22 | Rajbari 132/33kV S/S Faridpur - 2 Tripped showing 86.1&86.2 lock out relay operated.
relays Due to Thundering faridpur grid end
|  | 17:53 | Kulaura 132/33kV S/S TR-1 HT is restored.
|  | 17:54 | Kulaura 132/33kV S/S TR-1 LT is restored.
| 18:41 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 18:56 | 20:56 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Back up relay relays Due to Earth fault in | [7 empty] | 3.0MW load
|  |  | 33kv side | [7 empty] | interrup.
| 18:56 | 19:58 | Madanganj 132/33kV S/S GT-2 LT Tripped showing Earth fault relay relays Due to Earth | [7 empty] | 3.0MW load
|  |  | fault | [7 empty] | interrup.
| 21:00 |  | Peak generation 12625 MW
| 23:09 |  | 132/11kV T-2 transformer tripped at Bangabhaban substation showing Buchholz Relay.
| 23:16 |  | Bibiyana-III 400 MW CCPP, FGMO is ON with remarks:-
| 03:40 |  | Haripur-Meghnaghat 230kV Ckt-2 Tripped from Haripur 230/132kV end showing Z2, Z3, DEF,
BN. relays Due to Unknown. and from Meghnaghat 230/132kV end showing Micromoho relays Due
to Y-Phase LA BLust
| 04:02 | 04:32 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Tripped showing Overcurrent Protection | [7 empty] | 34.0MW load
|  |  | P132 relays Due to over voltage>> | [7 empty] | interrup.
| 04:02 | 04:42 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Tripped showing RET-521 relays Due | [7 empty] | 60.0MW load
|  |  | to Earth Fault | [7 empty] | interrup.
| 04:02 | 04:39 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Tripped showing RET-521 relays Due | [7 empty] | 60.0MW load
|  |  | to Earth Fault | [7 empty] | interrup.
| 04:02 | 04:32 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Tripped showing overcurrent protection | [7 empty] | 34.0MW load
|  |  | P132 relays Due to over voltage>> | [7 empty] | interrup.
| 04:03 |  | Rangpur-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing Zone 02, Zone 03
and Aurore close. relays Due to Rain and Thanderstron
| 04:03 |  | Rangpur-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing Zone 02 and Zone | [7 empty] | and 20.0MW load
|  |  | 03 ,Autoreclose relays Due to Rain and thanderstrom. and from Rangpur 132/33kV end | [7 empty] | interrup. Rangpur
|  |  | showing Saidpur Ckt 2 Distance Relay relays Due to Grid power Field | [7 empty] | 132/33kV end
| 04:03 |  | About 54 MW interruption occurred under Rangpur, Kurigram & Lalmonirhat S/S from 4:03 hr | [7 empty] | 54MW load interrup.
to 4:26 hr as Baropukuria 230/132 kv T-1 (Relay E/F), Saidpur - Rangpur line-1 tripped
(Dist. Z-1,2, 3) from Saidpur & line-2 from both ends (Dist Z-1,2,3) Rangpur Confidence -
Rangpur S/S line - 1 & 2 tripped from PP end (Dist. Z-3, 3-phase). Again the same
tripping occurred at the time (5:18 hrs) of giving a trial of Saidpur - Rangpur line-2 &
restored at 5:38 hrs.
| 05:16 | 05:48 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Tripped showing Overcurrent Protection | [7 empty] | 30.0MW load
|  |  | P132 relays Due to Overvoltage>> | [7 empty] | interrup.
| 05:16 | 05:48 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Tripped showing Overcurrent Protection | [7 empty] | 30.0MW load
|  |  | P132 relays Due to Over voltage>> | [7 empty] | interrup.
| 05:17 | 05:32 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Tripped showing RET 521 relays Due | [7 empty] | 58.0MW load
|  |  | to Earth Fault | [7 empty] | interrup.
| 05:17 | 05:31 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Tripped showing RET 521 relays Due | [7 empty] | 58.0MW load
|  |  | to Earth Fault | [7 empty] | interrup.
| 05:56 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- STG
| 06:00 |  | Min. Gen. 9881 MW
| 06:10 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 06:19 | 06:25 | Sylhet 132/33kV S/S Sylhet-90MW P/S Tripped showing 21 relays Due to Distance Protection
| 07:09 |  | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by NLDC
| 07:09 |  | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 354 | 8496000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9327000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 306 | 6949178 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 103 | 1524000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 285 | 6620657 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 4032 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 344880 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 32 | 2095680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 535325 | Machine Problem
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 498887 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 264000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 13 | 171360 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 8 | 224160 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 1677076 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 34 | 1524816 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 35 | 642240 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 291840 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 1254240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 160383 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 413640 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 8649545 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 17 | 1288800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2071 | 52957739
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 60865.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 56700 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 957600 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3379360 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 202399 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 378336 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 68 | 1309987 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 1029120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 287520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 61440 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 27598 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 42700 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 587520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 3345 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 850 | 23443634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 208320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 160 | 3825454.55 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1411 | 35861898.75
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 213 | 4703000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8544800 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 285 | 3692000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 37 | 741240 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 869760 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 2776727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 945960 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 930036 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 433904 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1308670 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 59 | 2469600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 28 | 715200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 604450 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 18 | 345710 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 16 | 979260 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 425040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 74 | 1474560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 366745 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1232 | 32326662
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 6624 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 120 | 2731200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 55 | 1388400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 201560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 265680 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 15120 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 187 | 4615834
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 931000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 932040 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3558518 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 686208 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1832640 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 172 | 3572700 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 422000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 413712 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7236500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 371 | 8361000 | Fgmo activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7692000 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1532 | 35638318
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 900 | 21493818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 122880 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 492480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 556 | 9752727 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1456 | 31861905
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 494 | 13852364 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 174601 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 114 | 2619000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1120 | 23780363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5204710 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 280 | 5957000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 810 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2238 | 51588848.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 2 | 27776 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 160 | 4079364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 132 | 3602518 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 131 | 3542752 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8825309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 21439 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 28769 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 420672 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 7296 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22260 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1212 | 29369731.64 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 213752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 657252 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2051 | 50818890.64
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1264582 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 162 | 3283000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1184102 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 55337.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1171431 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 237361 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1136160 | -
Rangpur Area Total |  |  |  |  | 950 | 447 | 8331973.88
Eastern Grid Total |  |  |  |  | 16921.242 | 6433 | 161400451.75
Western Grid Total |  |  |  |  | 11614.5 | 6192 | 142601618.16
National Grid Total |  |  |  |  | 28535.742 | 12625 | 304002069.91
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7997.69 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4113.2 | MW
i) Dhaka area |  |  | 4355.09 |  | MW | i) Khulna area |  |  |  | 1579.5 | MW
ii) Chattogram area |  |  | 1260.6 |  | MW | ii) Barishal area |  |  |  | 381.9 | MW
iii) Cumilla area |  |  | 1072 |  | MW | iii) Rajshahi area |  |  |  | 1281.8 | MW
iv) Mymensingh area |  |  | 875 |  | MW | iv) Rangpur area |  |  |  | 870 | MW
v) Sylhet area |  |  | 435 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12110.89 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 75 | 19:00 | 133 | Patuakhali | 68.5 | 00:00
2 | AKSML | 138 | 01:00 | 68 | Jaldhaka | 81 | 19:00 | 134 | Payra | 30 | 00:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jamalpur | 128 | 00:00 | 135 | Postogola | 58 | 13:00
4 | Agargaon | 129 | 13:00 | 70 | Jashore | 144 | 19:30 | 136 | Purbachal | 18 | 00:00
5 | Agrabad | 98 | 18:30 | 71 | Jhenaidah | 133 | 19:00 | 137 | Purbasadipur | 129 | 19:30
6 | Amnura | 43 | 00:00 | 72 | Joydebpur | 135 | 10:00 | 138 | Rahanpur | 24 | 00:00
7 | Ashuganj | 111 | 01:00 | 73 | Joypurhat | 62 | 13:00 | 139 | Rahim | 55 | 09:00
8 | BSRM | 196 | 00:00 | 74 | Juldah | 16 | 13:00 | 140 | Rajbari | 74 | 00:00
9 | Bagerhat | 80 | 00:00 | 75 | KSRM | 16 | 23:00 | 141 | Rajendrapur | 117 | 12:00
10 | Bajitpur | 51 | 00:00 | 76 | Kabirpur | 271 | 14:00 | 142 | Rajshahi | 120 | 19:30
11 | Bakulia | 97 | 15:00 | 77 | Kachua | 91 | 00:00 | 143 | Rajshahi-230 | 86 | 13:00
12 | Banani | 48 | 13:00 | 78 | Kallyanpur | 105 | 00:00 | 144 | Ramganj | 116 | 18:30
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 40 | 15:00 | 145 | Rampur | 41 | 00:00
14 | Barapukuria | 62 | 19:00 | 80 | Kamrangirchar | 70 | 12:00 | 146 | Rangamati | 17 | 19:00
15 | Barguna | 18 | 20:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 152 | 18:30
16 | Barishal | 101 | 12:00 | 82 | Kasba | 35 | 00:00 | 148 | Ruppur | 8 | 11:00
17 | Barishal-230 | 82 | 00:00 | 83 | Kazla | 100 | 13:00 | 149 | SSM | 8 | 23:00
18 | Baroaulia | 64 | 10:00 | 84 | Keranigonj | 73 | 13:00 | 150 | Saidpur | 113 | 15:00
19 | Baroirhat | 58 | 00:00 | 85 | Khagrachori | 28 | 11:00 | 151 | Satkhira | 138 | 00:00
20 | Bashundhara | 191 | 13:00 | 86 | Khulna | 72 | 13:00 | 152 | Satmasjid | 109 | 14:00
21 | BashundharaCement | 12 | 09:00 | 87 | Khulshi | 174 | 16:00 | 153 | Savar | 222 | 10:00
22 | Beanibazar | 64 | 00:00 | 88 | Kishoreganj | 120 | 00:00 | 154 | SevenRings | 19.31 | 15:00
23 | Benapole | 67 | 00:00 | 89 | Kodda | 296 | 19:00 | 155 | ShahCement | 37 | 02:00
24 | Bhaluka | 144 | 12:00 | 90 | Kulaura | 38 | 00:00 | 156 | Shahjadpur | 76 | 00:00
25 | Bhandaria | 42 | 19:00 | 91 | Kurigram | 68 | 19:00 | 157 | Shahjibazar | 109 | 00:00
26 | Bhangura | 39 | 00:00 | 92 | Kushtia | 134 | 19:30 | 158 | Shahmirpur | 58 | 15:00
27 | Bheramara(GK) | 60 | 19:00 | 93 | Lalbag | 70 | 13:00 | 159 | Shariatpur | 81 | 00:00
28 | Bhulta | 234 | 12:00 | 94 | Lalmonirhat | 58 | 19:30 | 160 | Sherpur | 158 | 00:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | MI_Cement | 18.4 | 00:00 | 161 | Shikalbaha | 28 | 19:00
30 | Bogura | 169 | 00:00 | 96 | Madanganj | 46 | 15:00 | 162 | Shitalakhya | 88.9 | 15:00
31 | Borhanuddin | 88 | 00:00 | 97 | Madaripur | 105 | 00:00 | 163 | Sholosohor | 47 | 15:00
32 | Brahmanbaria | 128 | 00:00 | 98 | Madartek | 87.34 | 00:00 | 164 | Shyampur | 172 | 12:00
33 | Cantonment | 130 | 13:00 | 99 | Madunaghat | 56 | 18:30 | 165 | Siddhirganj | 140 | 12:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 61 | 19:00 | 166 | Sirajganj | 104 | 00:00
35 | Chandpur | 69 | 00:00 | 101 | Mahasthangarh | 76 | 00:00 | 167 | Sonargaon | 102 | 01:00
36 | Chandraghona | 35 | 18:30 | 102 | Manikganj | 131 | 00:00 | 168 | Sreemongol | 58 | 00:00
37 | Chapai | 68 | 23:00 | 103 | Maniknagar | 77 | 13:00 | 169 | Sreepur | 94 | 10:00
38 | Charsaidpur | 46 | 07:00 | 104 | Matarbari | 58 | 20:00 | 170 | Srinagar | 43.98 | 00:00
39 | Chauddagram | 74 | 00:00 | 105 | Matuail | 66 | 15:00 | 171 | Sunamganj | 47 | 19:30
40 | Chhatak | 28 | 01:00 | 106 | Millgate | 98 | 11:00 | 172 | Sylhet | 38 | 00:00
41 | Chowmuhani | 218 | 00:00 | 107 | Mirpur | 137.5 | 12:00 | 173 | Sylhet-132 | 114 | 13:00
42 | Chuadanga | 110 | 19:30 | 108 | Mirsorai | 9 | 19:30 | 174 | TK | 35.7 | 19:00
43 | Coxsbazar | 134 | 20:00 | 109 | Mirzapur | 52 | 14:00 | 175 | Tangail | 182 | 00:00
44 | Cumilla(N) | 174 | 01:00 | 110 | Mithapukur | 56 | 19:30 | 176 | Thakurgaon | 106 | 19:30
45 | Cumilla(S) | 172 | 14:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 135 | 09:00
46 | Daudkandi | 141 | 00:00 | 112 | Mogbazar | 163.1 | 13:00 | 178 | Ullahpara | 40 | 08:00
47 | Dhaka | 64 | 13:00 | 113 | Mongla | 41 | 11:00 | 179 | Ullon | 48 | 00:00
48 | Dhamrai | 132 | 00:00 | 114 | Motijheel | 42 | 13:00 | 180 | Uttara | 97 | 13:00
49 | Dhanmondi | 163.4 | 13:00 | 115 | Muktagacha | 33 | 19:00 | 181 | UttaraNew | 48 | 13:00
50 | Dohazari | 101 | 19:30 | 116 | Munshiganj | 103 | 00:00 | 182 | Zigatola | 74 | 13:00
51 | Faridpur | 153 | 00:00 | 117 | Muradnagar | 27 | 00:00
52 | Fatullah | 104 | 12:00 | 118 | Mymensingh | 184 | 00:00
53 | Fenchuganj | 34 | 12:00 | 119 | Naogaon | 130 | 00:00
54 | Feni | 116 | 00:00 | 120 | Narail | 59 | 19:00
55 | GPH | 81 | 11:00 | 121 | Narinda | 77.5 | 13:00
56 | Ghatail | 84 | 00:00 | 122 | Narshingdi | 168 | 00:00
57 | Ghorashal | 17 | 04:00 | 123 | Natore | 144 | 00:00
58 | Ghorashal-230 | 77 | 00:00 | 124 | Nawabganj | 55.4 | 00:00
59 | Goalpara | 32 | 13:00 | 125 | Netrakona | 121 | 18:30
60 | Gollamari | 90 | 13:00 | 126 | New | 88 | 11:00
61 | Gopalganj | 98.3 | 00:00 | 127 | Niamatpur | 96 | 09:00
62 | Gulshan | 132 | 13:00 | 128 | Noapara | 43 | 19:30
63 | Halishahar | 72 | 15:00 | 129 | PHP | 9 | 09:00
64 | HaripurSBU | 178 | 00:00 | 130 | Pabna | 124 | 13:00
65 | Hasnabad | 82 | 00:00 | 131 | Palashbari | 116 | 13:00
66 | Hathazari | 88 | 18:30 | 132 | Panchagarh | 56 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14660.36 | 0 |  | 14660.36
1:00 | 14121.39 | 90 |  | 14215.39
2:00 | 13657.47 | 85 |  | 13746.47
3:00 | 13239.7 | 70 |  | 13312.7
4:00 | 12930.6 | 70 |  | 13003.6
5:00 | 12714.11 | 70 |  | 12787.11
6:00 | 12160.99 | 60 |  | 12223.99
7:00 | 12346.34 | 60 |  | 12409.34
8:00 | 12456.42 | 16 |  | 12473.14
9:00 | 13003.59 | 47 |  | 13052.59
10:00 | 13516.58 | 54 |  | 13572.58
11:00 | 13738.25 | 52 |  | 13792.25
12:00 | 14052.27 | 49 |  | 14103.48
13:00 | 13895.46 | 64 |  | 13962.46
14:00 | 12664.99 | 79 |  | 12747.99
15:00 | 11275.63 | 0 |  | 11275.63
16:00 | 9063.55 | 0 |  | 9063.55
17:00 | 9801.66 | 0 |  | 9801.66
18:00 | 10645.67 | 0 |  | 10645.67
19:00 | 11924 | 0 |  | 11924
19:30 | 12450 | 0 |  | 12450
20:00 | 12468 | 0 |  | 12468
21:00 | 12625 | 0 |  | 12625
22:00 | 12640 | 0 |  | 12640
23:00 | 12532 | 0 |  | 12532
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8160.2 | 6500.16 | 14660.36 | DAILY GENERATION CURVE
00:30 | 7962.95 | 6427.925 | 14390.875
01:00 | 7765.7 | 6355.69 | 14121.39 | 16-04-2025
01:30 | 7546.7 | 6342.73 | 13889.43
02:00 | 7327.7 | 6329.77 | 13657.47
02:30 | 7187.05 | 6261.535 | 13448.585
03:00 | 7046.4 | 6193.3 | 13239.7
03:30 | 6933.9 | 6151.25 | 13085.15
04:00 | 6821.4 | 6109.2 | 12930.6
04:30 | 6809.4 | 6012.955 | 12822.355
05:00 | 6797.4 | 5916.71 | 12714.11
05:30 | 6687.415 | 5750.135 | 12437.55
06:00 | 6577.43 | 5583.56 | 12160.99
06:30 | 6612.99 | 5640.675 | 12253.665
07:00 | 6648.55 | 5697.79 | 12346.34
07:30 | 6642.5 | 5758.88 | 12401.38
08:00 | 6636.45 | 5819.97 | 12456.42
08:30 | 6760.11 | 5969.895 | 12730.005
09:00 | 6883.77 | 6119.82 | 13003.59
09:30 | 7037.565 | 6222.52 | 13260.085
10:00 | 7191.36 | 6325.22 | 13516.58
10:30 | 7321.865 | 6305.55 | 13627.415
11:00 | 7452.37 | 6285.88 | 13738.25
11:30 | 7623.625 | 6271.635 | 13895.26
12:00 | 7794.88 | 6257.39 | 14052.27
12:30 | 7766.625 | 6207.24 | 13973.865
13:00 | 7738.37 | 6157.09 | 13895.46
13:30 | 7411.455 | 5868.77 | 13280.225
14:00 | 7084.54 | 5580.45 | 12664.99
14:30 | 6527.955 | 5442.355 | 11970.31
15:00 | 5971.37 | 5304.26 | 11275.63
15:30 | 5308.155 | 4861.435 | 10169.59
16:00 | 4644.94 | 4418.61 | 9063.55
16:30 | 4890.325 | 4542.28 | 9432.605
17:00 | 5135.71 | 4665.95 | 9801.66
17:30 | 5411.75 | 4811.915 | 10223.665
18:00 | 5687.79 | 4957.88 | 10645.67
18:30 | 5979.895 | 5304.94 | 11284.835
19:00 | 6272 | 5652 | 11924
19:30 | 6336 | 6114 | 12450
20:00 | 6257 | 6211 | 12468
20:30 | 6345 | 6201.5 | 12546.5 |  | Executive Engineer
21:00 | 6433 | 6192 | 12625 |  | Network Operation Division
21:30 | 6435 | 6197.5 | 12632.5
22:00 | 6437 | 6203 | 12640
22:30 | 6455 | 6131 | 12586
23:00 | 6473 | 6059 | 12532

## En-Curve
QF-LDC-12
Date | 16-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3403 | 2269.5 | 899 | 0 | 38 | 1369.16 | 40 | 3950 | 0 | 604 | 2085.7 | 0 | 0 | 2 | 0 | DAILY ENERGY CURVE
00:30 | 3391.5 | 2295.5 | 898 | 0 | 38 | 1365.425 | 40 | 3975 | 0 | 537 | 1848.45 | 0 | 0 | 2 | 45 | 16-04-2025
01:00 | 3380 | 2321.5 | 897 | 0 | 38 | 1361.69 | 40 | 4000 | 0 | 470 | 1611.2 | 0 | 0 | 2 | 90
01:30 | 3333 | 2312.5 | 897 | 0 | 37 | 1362.73 | 40 | 3946 | 0 | 462.5 | 1497.7 | 0 | 0 | 1 | 87.5 | Energy Generated | 304.0021 |  | MKWHr
02:00 | 3286 | 2303.5 | 897 | 0 | 36 | 1363.77 | 40 | 3892 | 0 | 455 | 1384.2 | 0 | 0 | 0 | 85 | Energy not Served | 0.866 |  | MKWHr
02:30 | 3302.5 | 2285.85 | 897 | 0 | 33 | 1366.535 | 40 | 3924.5 | 0 | 438 | 1159.2 | 0 | 0 | 2 | 77.5 | Total Energy Requirement | 304.8681 |  | MKWHr
03:00 | 3319 | 2268.2 | 897 | 0 | 30 | 1369.3 | 40 | 3957 | 0 | 421 | 934.2 | 0 | 0 | 4 | 70
03:30 | 3322.5 | 2247.2 | 897 | 0 | 30 | 1372.25 | 40 | 3928.5 | 0 | 383.5 | 860.7 | 0 | 0 | 3.5 | 70
04:00 | 3326 | 2226.2 | 897 | 0 | 30 | 1375.2 | 40 | 3900 | 0 | 346 | 787.2 | 0 | 0 | 3 | 70
04:30 | 3312.5 | 2233.7 | 897 | 0 | 32 | 1323.455 | 40 | 3863 | 0 | 338 | 777.2 | 0 | 0 | 5.5 | 70
05:00 | 3299 | 2241.2 | 897 | 0 | 34 | 1271.71 | 40 | 3826 | 0 | 330 | 767.2 | 0 | 0 | 8 | 70
05:30 | 3336 | 2176.2 | 897.5 | 0 | 33 | 1244.68 | 40 | 3717 | 6.57 | 293.5 | 686.1 | 0 | 0 | 7 | 65
06:00 | 3373 | 2111.2 | 898 | 0 | 32 | 1217.65 | 40 | 3608 | 13.14 | 257 | 605 | 0 | 0 | 6 | 60
06:30 | 3411 | 2114.6 | 897.5 | 0 | 31 | 1218.735 | 40 | 3619 | 62.33 | 240.5 | 615.5 | 0 | 0 | 3.5 | 60
07:00 | 3449 | 2118 | 897 | 0 | 30 | 1219.82 | 40 | 3630 | 111.52 | 224 | 626 | 0 | 0 | 1 | 60
07:30 | 3428.5 | 2105.5 | 873 | 0 | 28 | 1238.075 | 40 | 3645 | 185.805 | 224.5 | 632.5 | 0 | 0 | 0.5 | 38
08:00 | 3408 | 2093 | 849 | 0 | 26 | 1256.33 | 40 | 3660 | 260.09 | 225 | 639 | 0 | 0 | 0 | 16
08:30 | 3397.5 | 2131.5 | 849 | 0 | 27 | 1308.025 | 40 | 3655 | 336.98 | 237.5 | 747 | 0 | 0 | 0.5 | 31.5
09:00 | 3387 | 2170 | 849 | 0 | 28 | 1359.72 | 40 | 3650 | 413.87 | 250 | 855 | 0 | 0 | 1 | 47
09:30 | 3448.5 | 2160.5 | 873 | 0 | 28 | 1360.805 | 40 | 3623 | 460.28 | 266 | 998 | 0 | 0 | 2 | 50.5
10:00 | 3510 | 2151 | 897 | 0 | 28 | 1361.89 | 40 | 3596 | 506.69 | 282 | 1141 | 0 | 0 | 3 | 54
10:30 | 3540 | 2177 | 897 | 0 | 30 | 1362.705 | 40 | 3578 | 528.71 | 293.5 | 1179 | 0 | 0 | 1.5 | 53
11:00 | 3570 | 2203 | 897 | 0 | 32 | 1363.52 | 40 | 3560 | 550.73 | 305 | 1217 | 0 | 0 | 0 | 52
11:30 | 3620 | 2176 | 897 | 0 | 32 | 1355.31 | 40 | 3562.5 | 536.45 | 323 | 1353 | 0 | 0 | 0 | 50.5
12:00 | 3670 | 2149 | 897 | 0 | 32 | 1347.1 | 40 | 3565 | 522.17 | 341 | 1489 | 0 | 0 | 0 | 49
12:30 | 3580 | 2088 | 897 | 0 | 34 | 1349.545 | 40 | 3602 | 459.32 | 374 | 1550 | 0 | 0 | 0 | 56.5
13:00 | 3490 | 2027 | 897 | 0 | 36 | 1351.99 | 40 | 3639 | 396.47 | 407 | 1611 | 0 | 0 | 0 | 64
13:30 | 3390.5 | 1961 | 897 | 0 | 37 | 1310.495 | 40 | 3458 | 319.73 | 333.5 | 1520.5 | 0 | 0 | 12.5 | 71.5
14:00 | 3291 | 1895 | 897 | 0 | 38 | 1269 | 40 | 3277 | 242.99 | 260 | 1430 | 0 | 0 | 25 | 79
14:30 | 3268 | 1785 | 897.5 | 0 | 33 | 1195.5 | 40 | 3109.5 | 299.31 | 201 | 1114 | 0 | 0 | 27.5 | 39.5
15:00 | 3245 | 1675 | 898 | 0 | 28 | 1122 | 40 | 2942 | 355.63 | 142 | 798 | 0 | 0 | 30 | 0
15:30 | 3089.5 | 1550 | 847 | 0 | 28 | 972 | 40 | 2690.5 | 299.59 | 116 | 504.5 | 0 | 0 | 32.5 | 0
16:00 | 2934 | 1425 | 796 | 0 | 28 | 822 | 40 | 2439 | 243.55 | 90 | 211 | 0 | 0 | 35 | 0
16:30 | 3172.5 | 1490 | 847 | 0 | 26 | 820.5 | 40 | 2463.5 | 176.105 | 121.5 | 247.5 | 0 | 0 | 28 | 0
17:00 | 3411 | 1555 | 898 | 0 | 24 | 819 | 40 | 2488 | 108.66 | 153 | 284 | 0 | 0 | 21 | 0
17:30 | 3456 | 1559 | 897.5 | 0 | 26 | 873 | 40 | 2636 | 63.665 | 183.5 | 469 | 0 | 0 | 20 | 0
18:00 | 3501 | 1563 | 897 | 0 | 28 | 927 | 40 | 2784 | 18.67 | 214 | 654 | 0 | 0 | 19 | 0
18:30 | 3583 | 1650.5 | 897 | 0 | 26 | 1015 | 40 | 3031.5 | 9.335 | 230 | 788.5 | 0 | 0 | 14 | 0
19:00 | 3665 | 1738 | 897 | 0 | 24 | 1103 | 40 | 3279 | 0 | 246 | 923 | 0 | 0 | 9 | 0
19:30 | 3663 | 1734 | 848 | 0 | 24 | 1190 | 40 | 3612 | 0 | 229 | 1106 | 0 | 0 | 4 | 0
20:00 | 3668 | 1765 | 849 | 0 | 26 | 1214 | 40 | 3801 | 0 | 196 | 908 | 0 | 0 | 1 | 0
20:30 | 3717.5 | 1902 | 874.5 | 0 | 27 | 1213 | 40 | 3740 | 0 | 179 | 852.5 | 0 | 0 | 1 | 0
21:00 | 3767 | 2039 | 900 | 0 | 28 | 1212 | 40 | 3679 | 0 | 162 | 797 | 0 | 0 | 1 | 0
21:30 | 3742 | 2034 | 899.5 | 0 | 28 | 1215.5 | 40 | 3689.5 | 0 | 165 | 818.5 | 0 | 0 | 0.5 | 0
22:00 | 3717 | 2029 | 899 | 0 | 28 | 1219 | 40 | 3700 | 0 | 168 | 840 | 0 | 0 | 0 | 0
22:30 | 3727 | 2049.5 | 899.5 | 0 | 28 | 1217.5 | 40 | 3700 | 0 | 167.5 | 737.5 | 0 | 0 | 19.5 | 0
23:00 | 3737 | 2070 | 900 | 0 | 28 | 1216 | 40 | 3700 | 0 | 167 | 635 | 0 | 0 | 39 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 404 | 16:00 | 376 | 12:00 | Payra | 418 | 16:00 | 408 | 01:00
Ashuganj | 412 | 6:00 | 390 | 12:00 | Rahanpur | 412 | 16:00 | 393 | 11:00
Bhulta | 409 | 16:00 | 377 | 11:00 | Rampal | 409 | 16:00 | 389 | 12:00
Bibiana | 393 | 19:30 | 281 | 11:00
BIPTC | 401 | 09:00 | 394 | 21:00
Bogura | 406 | 16:00 | 384 | 11:00
Gopalganj | 410 | 16:00 | 386 | 12:00
Kaliakoir | 374 | 15:00 | 350 | 12:00
Madunaghat | 402 | 17:00 | 391 | 13:00
Meghnaghat | 396 | 17:00 | 378 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 238 | 16:00 | 216 | 12:00 | Keranigonj | 236 | 16:00 | 214 | 12:00
AKSML | 232 | 16:00 | 221 | 11:00 | Khulna(S) | 233 | 18:30 | 218 | 12:00
Aminbazar | 232 | 15:00 | 216 | 12:00 | Madunaghat | 232 | 18:00 | 223 | 12:00
Ashuganj | 236 | 16:00 | 222 | 11:00 | Madunaghat-400 | 232 | 16:00 | 224 | 13:00
Ashuganj-400 | 234 | 6:00 | 224 | 12:00 | Maniknagar | 233 | 16:00 | 212 | 11:00
Baghabari | 234 | 15:00 | 224 | 11:00 | Meghnaghat | 240 | 16:00 | 221 | 12:00
Barapukuria | 221 | 15:00 | 212 | 07:00 | Meghnaghat-400 | 232 | 17:00 | 216 | 11:00
Barapukuria-230 | 220 | 15:00 | 213 | 7:00 | Mirsorai | 234 | 16:00 | 217 | 11:00
Barishal | 238 | 16:00 | 227 | 12:00 | Rajshahi | 234 | 05:00 | 221 | 17:00
Bheramara | 235 | 03:00 | 222 | 12:00 | Rampal | 232 | 16:00 | 220 | 12:00
Bhulta | 232 | 16:00 | 213 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 16:00 | 218 | 10:00 | Rampura | 233 | 16:00 | 210 | 12:00
BIPTC | 236 | 05:00 | 223 | 13:00 | Shikalbaha | 228 | 16:00 | 127 | 02:00
Bogura | 229 | 16:00 | 217 | 11:00 | Shyampur | 236 | 16:00 | 214 | 12:00
Bogura-400 | 228 | 16:00 | 217 | 08:00 | Siddhirganj | 230 | 19:00 | 216 | 11:00
Borhanuddin | 243 | 16:00 | 234 | 00:00 | Sirajgonj | 239 | 15:00 | 233 | 10:00
BSRM | 233 | 16:00 | 219 | 11:00 | Sreepur | 232 | 16:00 | 220 | 10:00
Cumilla(N) | 232 | 16:00 | 213 | 11:00 | Tongi | 233 | 16:00 | 214 | 09:00
Faridpur | 234 | 16:00 | 220 | 00:00
Fenchuganj | 231 | 19:30 | 219 | 08:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 234 | 16:00 | 214 | 11:00
Gopalganj | 235 | 16:00 | 221 | 12:00
GPH | 232 | 16:00 | 221 | 11:00
Haripur | 235 | 16:00 | 214 | 11:00
Hasnabad | 232 | 18:00 | 214 | 12:00
Hathazari | 233 | 16:00 | 223 | 12:00
Ishurdi | 235 | 02:00 | 224 | 12:00
Jhenaidah | 227 | 05:00 | 214 | 12:00
Kaliakoir | 234 | 16:00 | 218 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 16:00 | 123 | 12:00 | Madartek | 139 | 16:00 | 123 | 12:00
Agargaon | 140 | 16:00 | 125 | 09:00 | Madunaghat | 134 | 18:00 | 128 | 11:00
Agrabad | 134 | 18:00 | 126 | 11:00 | Magura | 132 | 03:00 | 124 | 18:30
AKS | 130 | 14:00 | 125 | 11:00 | Mahasthangarh | 132 | 15:00 | 122 | 08:00
Aminbazar | 133 | 15:00 | 122 | 12:00 | Manikganj | 134 | 15:00 | 120 | 12:00
Amnura | 135 | 00:00 | 123 | 11:00 | Maniknagar | 139 | 16:00 | 123 | 10:00
Ashuganj | 140 | 15:00 | 134 | 11:00 | Matarbari | 122 | 16:00 | 96 | 11:00
Bagerhat | 136 | 15:00 | 122 | 19:00 | Matuail | 139 | 16:00 | 123 | 12:00
Bajitpur | 135 | 17:00 | 127 | 10:00 | Millgate | 136 | 16:00 | 121 | 11:00
Bakulia | 138 | 18:00 | 128 | 12:00 | Mirpur | 133 | 16:00 | 120 | 12:00
Banani | 138 | 16:00 | 122 | 12:00 | Mirzapur | 135 | 15:00 | 117 | 12:00
Bangabhaban | 138 | 16:00 | 122 | 12:00 | Mithapukur | 131 | 15:00 | 121 | 07:00
Barapukuria | 134 | 00:00 | 126 | 07:00 | MI_Cement | 140 | 16:00 | 123 | 11:00
Barguna | 136 | 16:00 | 131 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 15:00 | 124 | 12:00 | Mogbazar | 140 | 16:00 | 124 | 12:00
Barishal-230 | 133 | 15:00 | 126 | 00:00 | Mongla | 136 | 15:00 | 123 | 19:00
Baroaulia | 134 | 16:00 | 128 | 11:00 | Motijheel | 138 | 16:00 | 122 | 12:00
Baroirhat | 129 | 19:00 | 117 | 11:00 | Muktagacha | 133 | 15:00 | 116 | 12:00
Bashundhara | 138 | 16:00 | 120 | 11:00 | Munshiganj | 138 | 16:00 | 122 | 11:00
BashundharaCement | 136 | 17:00 | 122 | 11:00 | Muradnagar | 137 | 16:00 | 119 | 11:00
Beanibazar | 135 | 16:00 | 126 | 11:00 | Mymensingh | 133 | 17:00 | 115 | 12:00
Benapole | 129 | 05:00 | 123 | 11:00 | Naogaon | 132 | 15:00 | 119 | 10:00
Bhaluka | 134 | 13:00 | 125 | 10:00 | Narail | 132 | 05:00 | 121 | 18:30
Bhandaria | 130 | 16:00 | 118 | 21:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 134 | 14:00 | 127 | 09:00 | Narshingdi | 138 | 16:00 | 119 | 00:00
Bheramara | 135 | 05:00 | 127 | 12:00 | Natore | 133 | 15:00 | 125 | 11:00
Bheramara(GK) | 135 | 04:00 | 127 | 12:00 | Nawabganj | 140 | 16:00 | 123 | 11:00
Bhulta | 135 | 16:00 | 120 | 09:00 | Netrakona | 128 | 17:00 | 118 | 10:00
Bog-Sherpur | 132 | 15:00 | 123 | 11:00 | New | 133 | 15:00 | 121 | 11:00
Bogura | 134 | 15:00 | 126 | 08:00 | Niamatpur | 136 | 16:00 | 127 | 12:00
Bogura-230 | 134 | 15:00 | 125 | 11:00 | Noapara | 134 | 15:00 | 124 | 19:00
Brahmanbaria | 137 | 18:00 | 133 | 13:00 | Pabna | 134 | 05:00 | 127 | 12:00
Cantonment | 140 | 16:00 | 125 | 09:00 | Palashbari | 130 | 15:00 | 117 | 07:00
Chandina | 136 | 16:00 | 122 | 12:00 | Panchagarh | 137 | 00:00 | 119 | 07:00
Chandpur | 132 | 15:00 | 120 | 11:00 | Patuakhali | 136 | 15:00 | 131 | 00:00
Chandraghona | 134 | 15:00 | 127 | 12:00 | Payra | 137 | 16:00 | 133 | 00:00
Chapai | 133 | 17:00 | 126 | 00:00 | PHP | 128 | 16:00 | 116 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 139 | 16:00 | 123 | 11:00 | Postogola | 139 | 16:00 | 132 | 23:00
Chauddagram | 129 | 17:00 | 116 | 11:00 | Purbachal | 140 | 16:00 | 122 | 12:00
Chhatak | 133 | 16:00 | 126 | 00:00 | Purbasadipur | 132 | 00:00 | 116 | 11:00
Chowmuhani | 128 | 15:00 | 111 | 01:00 | Rahanpur | 137 | 16:00 | 130 | 10:00
Chuadanga | 132 | 05:00 | 119 | 19:00 | Rahanpur-400 | 137 | 16:00 | 130 | 12:00
Coxsbazar | 121 | 09:00 | 103 | 11:00 | Rahim | 139 | 16:00 | 123 | 11:00
Cumilla(N) | 136 | 16:00 | 121 | 11:00 | Rajbari | 138 | 16:00 | 128 | 00:00
Cumilla(S) | 134 | 17:00 | 119 | 11:00 | Rajendrapur | 137 | 16:00 | 122 | 11:00
Daudkandi | 137 | 16:00 | 118 | 11:00 | Rajshahi | 133 | 15:00 | 126 | 11:00
Dhaka | 139 | 16:00 | 123 | 12:00 | Rajshahi-230 | 134 | 05:00 | 117 | 12:00
Dhamrai | 141 | 15:00 | 121 | 09:00 | Ramganj | 129 | 15:00 | 114 | 01:00
Dhanmondi | 140 | 16:00 | 123 | 12:00 | Rampur | 134 | 17:00 | 125 | 12:00
Dohazari | 135 | 16:00 | 123 | 12:00 | Rampura | 139 | 16:00 | 123 | 12:00
Faridpur | 140 | 16:00 | 130 | 00:00 | Rangamati | 133 | 16:00 | 126 | 11:00
Fatullah | 138 | 16:00 | 124 | 11:00 | Rangpur | 131 | 04:00 | 117 | 08:00
Fenchuganj | 138 | 15:00 | 132 | 00:00 | Ruppur | 136 | 02:00 | 132 | 10:00
Feni | 128 | 15:00 | 114 | 11:00 | Saidpur | 130 | 00:00 | 118 | 18:30
Ghatail | 132 | 15:00 | 112 | 07:00 | Satkhira | 134 | 15:00 | 122 | 21:00
Ghorashal | 137 | 14:00 | 133 | 07:00 | Satmasjid | 140 | 16:00 | 125 | 09:00
Goalpara | 139 | 15:00 | 127 | 18:30 | Savar | 133 | 16:00 | 121 | 08:00
Gollamari | 138 | 15:00 | 128 | 18:30 | SevenRings | 140 | 16:00 | 128 | 11:00
Gopalganj | 138 | 16:00 | 128 | 12:00 | ShahCement | 139 | 16:00 | 123 | 11:00
Gopalganj-400 | 140 | 16:00 | 131 | 12:00 | Shahjadpur | 136 | 15:00 | 130 | 11:00
Gulshan | 137 | 16:00 | 123 | 12:00 | Shahjibazar | 137 | 18:00 | 126 | 00:00
Halishahar | 135 | 18:00 | 128 | 10:00 | Shahmirpur | 137 | 19:30 | 128 | 11:00
Haripur | 139 | 16:00 | 124 | 11:00 | Shariatpur | 137 | 16:00 | 127 | 00:00
HaripurSBU | 139 | 16:00 | 124 | 11:00 | Sherpur | 136 | 19:30 | 116 | 12:00
Hasnabad | 140 | 16:00 | 125 | 12:00 | Shikalbaha | 127 | 18:00 | 118 | 12:00
Hathazari | 136 | 18:00 | 128 | 12:00 | Shikalbaha-230 | 137 | 14:00 | 128 | 11:00
Ishurdi | 138 | 05:00 | 131 | 12:00 | Shitalakhya | 139 | 16:00 | 123 | 11:00
Jaldhaka | 129 | 00:00 | 115 | 11:00 | Sholosohor | 134 | 16:00 | 127 | 12:00
Jamalpur | 137 | 19:30 | 121 | 01:00 | Shyampur | 138 | 16:00 | 123 | 11:00
Jashore | 131 | 15:00 | 120 | 19:00 | Shyampur-230 | 139 | 16:00 | 123 | 12:00
Jhenaidah | 132 | 05:00 | 124 | 18:30 | Siddhirganj | 139 | 16:00 | 124 | 11:00
Jhenaidah-230 | 134 | 05:00 | 124 | 12:00 | Sirajganj | 132 | 14:00 | 123 | 11:00
Joydebpur | 145 | 15:00 | 132 | 11:00 | Sonargaon | 137 | 16:00 | 121 | 11:00
Joypurhat | 130 | 15:00 | 115 | 11:00 | Sreemongol | 135 | 18:00 | 127 | 00:00
Juldah | 138 | 18:00 | 128 | 11:00 | Sreepur | 136 | 16:00 | 128 | 09:00
Kabirpur | 136 | 15:00 | 118 | 11:00 | Srinagar | 140 | 16:00 | 123 | 12:00
Kachua | 132 | 15:00 | 118 | 12:00 | SSM | 139 | 16:00 | 129 | 17:00
Kaliakoir | 143 | 15:00 | 124 | 12:00 | Sunamganj | 131 | 15:00 | 124 | 11:00
Kallyanpur | 134 | 16:00 | 122 | 12:00 | Sylhet | 135 | 16:00 | 128 | 00:00
Kalurghat | 134 | 18:00 | 128 | 11:00 | Sylhet-132 | 133 | 16:00 | 128 | 12:00
Kamrangirchar | 140 | 16:00 | 122 | 12:00 | Tangail | 133 | 15:00 | 117 | 06:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 22:00 | 116 | 07:00
Kasba | 135 | 16:00 | 118 | 11:00 | TK | 137 | 18:00 | 128 | 12:00
Kazla | 135 | 16:00 | 122 | 12:00 | Tongi | 136 | 16:00 | 125 | 09:00
Keranigonj | 140 | 16:00 | 123 | 12:00 | Ullahpara | 135 | 15:00 | 126 | 11:00
Khagrachori | 132 | 16:00 | 125 | 11:00 | Ullon | 136 | 17:00 | 123 | 12:00
Khulna | 137 | 15:00 | 127 | 12:00 | Uttara | 133 | 16:00 | 120 | 11:00
Khulna(S) | 139 | 15:00 | 129 | 12:00 | UttaraNew | 132 | 16:00 | 120 | 12:00
Khulshi | 133 | 16:00 | 124 | 11:00 | Zigatola | 139 | 16:00 | 123 | 12:00
Kishoreganj | 132 | 13:00 | 126 | 10:00
Kodda | 140 | 15:00 | 119 | 12:00
KSRM | 133 | 14:00 | 126 | 12:00
Kulaura | 136 | 14:00 | 131 | 00:00
Kurigram | 130 | 00:00 | 117 | 07:00
Kushtia | 134 | 05:00 | 126 | 12:00
Lalbag | 140 | 16:00 | 122 | 12:00
Lalmonirhat | 128 | 00:00 | 118 | 18:30
Madanganj | 138 | 16:00 | 122 | 11:00
Madaripur | 138 | 16:00 | 128 | 12:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division