## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-04-2025 | during | 18-04-2025 | during | 18-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 363 | 355 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 301 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 99 | 102 | 208.13 | 208.13 | 100 | 100 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 297 | 280 | 335 | 335 | 310 | 310 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 35 | 35 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 64 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 17.5 | 30 | 30 | 18 | 18 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 0 | 20 | 20 | 17 | 17 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 16 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 87 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 52 | 105 | 105 | 50 | 50 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 14 | 104 | 104 | 50 | 101 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 0 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 36 | 55 | 55 | 35 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 500 | 350 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2016 | 2361.5 | 5262.9 | 5331.9 | 3518.16 | 3638.16
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 147 | 151 | 145 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 81 | 64 | 81 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 14 | 2 | 25 | 2 | 25 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 50 | 50 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.31 | 0 | 4.31 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 80 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 803 | 850 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 158 | 252 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1197 | 1538 | 3400.03 | 3421.72 | 3347.03 | 3363.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 353 | 359 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 285 | 100 | 285 | 285 | 285 | 285 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 36 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 53 | 53 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 102 | 175 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 9 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 45 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 32 | 29 | 200 | 200 | 200 | 200 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 32 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 15 | 29 | 105.3 | 105.3 | 66 | 66 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 34 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 34 | 115 | 115 | 90 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1175 | 1010 | 2161.29 | 2091.29 | 1884.55 | 1839.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-04-2025 | during | 18-04-2025 | during | 18-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.3 | 0 | 1.3 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 120 | 200 | 200 | 125 | 170 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 85 | 115 | 115 | 68 | 75 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 2.19 | 0 | 48.2 | 0 | 48.2 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 31.19 | 217 | 598.5 | 549 | 309 | 311.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 37 | 37 | 37 | 37 | 37 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 135 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 172 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 383 | 320 | 380 | 380 | 352 | 352 | Fgmo activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1563 | 1482 | 1606 | 1606 | 1544 | 1544
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 901 | 857 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 53 | 53 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 53.09 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 408 | 382 | 617.1 | 617.1 | 617.1 | 617.1 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1362.09 | 1239 | 2983.1 | 2895.1 | 2416.11 | 2328.11
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 620 | 520 | 1190 | 1190 | 1190 | 1190 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 6 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 100 | 130 | 130 | 130 | 130 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 570 | 747 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.29 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1737.29 | 1900 | 3362.12 | 3361.12 | 3322.12 | 3321.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 178 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 142 | 161 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 153 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 22 | 22 | 22 | 22 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 103 | 103 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 830.71 | 1215.5 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.98 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 18 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1733.69 | 2121.5 | 3096.63 | 2930.53 | 3044.84 | 2878.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 62 | 58 | 58 | 58 | 56 | 56 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 158 | 170 | 170 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 38 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 0.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 12 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 73 | 0 | 78.27 | 0 | 78.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 316.9 | 289 | 578.67 | 476 | 576.67 | 474
System Total |  |  |  |  | 27566.2 | 28535.742 | 11132.16 | 12158 | 23049.24 | 22662.66 | 19962.48 | 19698.9
Forecast Scenario (18-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11190 |  | 0 |  | 11190
|  |  |  | 1:00 | 11040 |  | 0 |  | 11040
|  |  |  | 2:00 | 10900 |  | 0 |  | 10900
|  |  |  | 3:00 | 10840 |  | 0 |  | 10840
|  |  |  | 4:00 | 10640 |  | 0 |  | 10640
|  |  |  | 5:00 | 10380 |  | 0 |  | 10380
|  |  |  | 6:00 | 9910 |  | 0 |  | 9910
|  |  |  | 7:00 | 9850 |  | 0 |  | 9850
|  |  |  | 8:00 | 10040 |  | 0 |  | 10040
|  |  |  | 9:00 | 10420 |  | 0 |  | 10420
|  |  |  | 10:00 | 10720 |  | 0 |  | 10720
|  |  |  | 11:00 | 11200 |  | 0 |  | 11200
|  |  |  | 12:00 | 12100 |  | 0 |  | 12100
|  |  |  | 13:00 | 12710 |  | 0 |  | 12710
|  |  |  | 14:00 | 12230 |  | 0 |  | 12230
|  |  |  | 15:00 | 12420 |  | 0 |  | 12420
|  |  |  | 16:00 | 11970 |  | 0 |  | 11970
|  |  |  | 17:00 | 11700 |  | 0 |  | 11700
|  |  |  | 18:00 | 11570 |  | 0 |  | 11570
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 13490 |  | 0 |  | 13490
|  |  |  | 19:30 | 14120 |  | 0 |  | 14120
|  |  |  | 20:00 | 14040 |  | 0 |  | 14040
|  |  |  | 21:00 | 14140 |  | 0 |  | 14140
|  |  |  | 22:00 | 14120 |  | 0 |  | 14120
|  |  |  | 23:00 | 14060 |  | 0 |  | 14060
Probable Maximum Temperature: |  |  | 30.70°C
Probable Maximum Demand at Day Peak: |  |  | 12100.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14140.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14140.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 281.68 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:00 hrs on 18-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-04-2025 | [28 empty] | Date: | 17-04-2025 | [28 empty] | Date: | 17-04-2025 | [28 empty] | Date: | 17-04-2025 | [28 empty] | Date: | 17-04-2025 | [16 empty] | Date: | 17-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 34 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 305 | 400 | 0 | 0 | 0 | 283 | 104 | 0 | 0 | 17 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 62 | 10 | 0 | 40 | 0 | 22 | 160 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 355 | 285 | 5 | 198 | 37 | 68 | 50 | 77 | 17 | 20 | 31 | 28 | 25 | 0 | 0 | 310 | 320 | 323 | 39 | 40 | 0 | 133 | 16 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 55 | 120 | 0 | 0 | 0 | 9 | 6302 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 518 | 0 | 1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 130 | 0 | 137 | 0 | 414 | 0 | 0 | 0 | 163 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 116 | 220 | 0 | 494 | 1109 | 0 | 5978 | 12280 | 81.85
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 34 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 298 | 400 | 0 | 0 | 0 | 280 | 104 | 0 | 0 | 17 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34 | 0 | 0 | 60 | 10 | 0 | 40 | 0 | 31 | 160 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 354 | 285 | 5 | 193 | 37 | 68 | 50 | 76 | 15 | 20 | 28 | 28 | 25 | 0 | 0 | 305 | 320 | 313 | 39 | 40 | 0 | 130 | 21 | 0 | 82 | 30 | 0 | 18 | 171 | 0 | 55 | 105 | 0 | 0 | 0 | 12 | 6270 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 466 | 0 | 1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 130 | 0 | 136 | 0 | 414 | 0 | 0 | 0 | 162 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 116 | 220 | 0 | 496 | 1070 | 0 | 5762 | 12032 | 81.84
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 302 | 400 | 0 | 0 | 0 | 275 | 104 | 0 | 0 | 17 | 17 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34 | 0 | 0 | 60 | 10 | 0 | 40 | 0 | 31 | 161 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 355 | 285 | 5 | 192 | 33 | 68 | 50 | 77 | 9 | 20 | 14 | 30 | 25 | 0 | 0 | 300 | 320 | 316 | 39 | 40 | 0 | 132 | 21 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 55 | 105 | 0 | 0 | 0 | 12 | 6224 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 130 | 0 | 136 | 0 | 414 | 0 | 0 | 0 | 162 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 116 | 220 | 0 | 493 | 902 | 0 | 5273 | 11497 | 81.84
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 17 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 298 | 400 | 0 | 0 | 0 | 278 | 104 | 0 | 0 | 17 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 60 | 10 | 0 | 40 | 0 | 31 | 160 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 355 | 285 | 5 | 192 | 33 | 68 | 50 | 74 | 9 | 20 | 14 | 26 | 8 | 0 | 0 | 295 | 320 | 312 | 39 | 40 | 0 | 129 | 21 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 49 | 97 | 0 | 0 | 0 | 12 | 6117 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 130 | 0 | 137 | 0 | 350 | 0 | 0 | 0 | 165 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 116 | 220 | 0 | 497 | 740 | 0 | 4909 | 11026 | 81.83
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 305 | 400 | 0 | 0 | 0 | 266 | 105 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 33 | 20 | 0 | 40 | 0 | 31 | 160 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 8 | 0 | 349 | 285 | 5 | 183 | 33 | 68 | 70 | 72 | 9 | 20 | 14 | 32 | 8 | 0 | 0 | 305 | 320 | 312 | 39 | 40 | 0 | 130 | 21 | 0 | 82 | 30 | 0 | 18 | 171 | 0 | 49 | 85 | 0 | 0 | 0 | 12 | 5877 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 130 | 0 | 137 | 0 | 350 | 0 | 0 | 0 | 167 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 108 | 220 | 0 | 496 | 700 | 0 | 4862 | 10739 | 81.83
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 302 | 350 | 0 | 0 | 0 | 283 | 104 | 0 | 0 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 33 | 50 | 0 | 40 | 0 | 16 | 160 | 0 | 0 | 0 | 8 | 0 | 151 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 8 | 0 | 300 | 285 | 5 | 193 | 33 | 34 | 70 | 51 | 9 | 20 | 14 | 24 | 8 | 0 | 0 | 305 | 320 | 316 | 39 | 40 | 0 | 130 | 21 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 49 | 75 | 0 | 0 | 0 | 12 | 5634 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 135 | 0 | 137 | 0 | 300 | 0 | 0 | 0 | 166 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 5 | 110 | 180 | 0 | 493 | 620 | 0 | 4698 | 10332 | 81.82
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 301 | 300 | 0 | 0 | 0 | 285 | 104 | 0 | 1 | 0 | 14 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 22 | 0 | 0 | 40 | 0 | 33 | 160 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 1 | 51 | 0 | 8 | 0 | 300 | 285 | 5 | 41 | 36 | 16 | 70 | 36 | 9 | 20 | 14 | 22 | 8 | 3 | 0 | 300 | 320 | 366 | 39 | 40 | 0 | 130 | 21 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 0 | 0 | 0 | 0 | 0.23 | 10 | 5275.23 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 414 | 0 | 835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 160 | 0 | 136 | 0 | 137 | 0 | 300 | 0 | 0.08 | 0 | 166 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 150 | 8 | 110 | 180 | 0 | 495 | 550 | 0 | 4606.35 | 9881.58 | 81.82
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 51 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 300 | 350 | 0 | 0 | 0 | 279 | 103 | 0 | 5 | 0 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 22 | 0 | 1 | 40 | 0 | 33 | 163 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 2 | 51 | 0 | 65 | 0 | 354 | 285 | 10 | 0 | 37 | 16 | 70 | 32 | 9 | 20 | 14 | 22 | 8 | 15 | 0 | 305 | 320 | 313 | 39 | 40 | 0 | 139 | 8 | 0 | 82 | 30 | 0 | 18 | 171 | 0 | 64 | 43 | 0 | 0 | 1.5 | 8 | 5631.5 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 414 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 5.76 | 164 | 0 | 141 | 0 | 137 | 0 | 400 | 0 | 0.43 | 0 | 161 | 59 | 0 | 0 | 0 | 0 | 0 | 0.4 | 1.2 | 0.08 | 0 | 150 | 7 | 110 | 180 | 0 | 495 | 550 | 0 | 4739.87 | 10371.37 | 81.81
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 17 | 51 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 320 | 0 | 0 | 0 | 284 | 102 | 0 | 13 | 0 | 17.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 40 | 0 | 8 | 237 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 706 | 6 | 51 | 0 | 112 | 0 | 300 | 285 | 41 | 0 | 37 | 16 | 70 | 29 | 9 | 0 | 16 | 30 | 8 | 33 | 0 | 290 | 320 | 338 | 39 | 40 | 0 | 129 | 16 | 0 | 82 | 20 | 0 | 18 | 172 | 0 | 45 | 85 | 0 | 0 | 9.47 | 12 | 5678.97 | 856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.08 | 412 | 0 | 827.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 9.41 | 140 | 0 | 145 | 0 | 142 | 0 | 300 | 0 | 1.49 | 0 | 164 | 61 | 0 | 3 | 0 | 0 | 0 | 2.1 | 1 | 0.27 | 0 | 150 | 7 | 100 | 180 | 0 | 497 | 550 | 0 | 4636.15 | 10315.12 | 81.81
09:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 16 | 51 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 307 | 320 | 0 | 0 | 0 | 305 | 100 | 0 | 13 | 0 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 40 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 802 | 16 | 51 | 0 | 102 | 0 | 355 | 285 | 52 | 0 | 33 | 17 | 70 | 33 | 9 | 20 | 17 | 30 | 8 | 51 | 0 | 310 | 320 | 340 | 39 | 40 | 0 | 156 | 16 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 8 | 45 | 0 | 0 | 10.26 | 12 | 5879.26 | 855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.59 | 410 | 0 | 830.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 140 | 0 | 145 | 0 | 148 | 0 | 414 | 0 | 0.25 | 0 | 170 | 61 | 0 | 4 | 0 | 0 | 0 | 4.7 | 65 | 0.46 | 0 | 150 | 6 | 108 | 180 | 0 | 550 | 550 | 0 | 4899.14 | 10778.4 | 81.8
10:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 298 | 500 | 0 | 0 | 0 | 297 | 99 | 0 | 0 | 0 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 4 | 40 | 0 | 3 | 158 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 803 | 17 | 51 | 0 | 102 | 0 | 353 | 285 | 53 | 0 | 35 | 48 | 70 | 32 | 9 | 20 | 15 | 34 | 8 | 60 | 0 | 310 | 320 | 383 | 39 | 40 | 0 | 155 | 16 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 8 | 8 | 0 | 1 | 2.19 | 12 | 5982.19 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.09 | 408 | 0 | 830.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 48.98 | 140 | 0 | 142 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 169 | 62 | 0 | 12 | 0 | 0 | 0 | 0.9 | 73 | 0.29 | 0 | 200 | 7 | 120 | 220 | 0 | 620 | 570 | 0 | 5149.97 | 11132.16 | 81.8
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 16 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 258 | 500 | 0 | 0 | 0 | 306 | 40 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 30 | 2 | 40 | 0 | 2 | 160 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 874 | 6 | 51 | 0 | 102 | 0 | 300 | 285 | 52 | 0 | 35 | 50 | 50 | 57 | 12 | 20 | 42 | 28 | 8 | 59 | 0 | 290 | 320 | 313 | 39 | 40 | 0 | 152 | 16 | 0 | 82 | 30 | 0 | 18 | 171 | 0 | 8 | 8 | 0 | 3 | 15.81 | 12 | 5855.81 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.63 | 408 | 0 | 819.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 69.3 | 140 | 0 | 137 | 0 | 130 | 0 | 300 | 0 | 5.49 | 0 | 170 | 61 | 0 | 3 | 0 | 0 | 0 | 6.4 | 69 | 0.7 | 0 | 233 | 7 | 108 | 180 | 0 | 690 | 620 | 0 | 5125.47 | 10981.28 | 81.79
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 282 | 320 | 0 | 0 | 0 | 250 | 38 | 0 | 1 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 30 | 5 | 40 | 0 | 3 | 155 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 723 | 9 | 5 | 0 | 71 | 0 | 280 | 285 | 43 | 0 | 36 | 52 | 50 | 73 | 9 | 20 | 42 | 34 | 8 | 11 | 0 | 290 | 320 | 310 | 39 | 40 | 0 | 129 | 16 | 0 | 22 | 20 | 0 | 18 | 171 | 0 | 8 | 8 | 0 | 2 | 32.94 | 0 | 5147.44 | 901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.2 | 378 | 0 | 825.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 70.34 | 140 | 0 | 136 | 0 | 134 | 0 | 270 | 0 | 6.31 | 0 | 165 | 61 | 0 | 11 | 0 | 0 | 0 | 7.7 | 191 | 0.18 | 0 | 150 | 4 | 112 | 180 | 0 | 728 | 580 | 0 | 5195.57 | 10343.01 | 81.79
13:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 0 | 0 | 300 | 283 | 430 | 0 | 0 | 0 | 265 | 37 | 0 | 4 | 0 | 16.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 33 | 60 | 1 | 40 | 0 | 7 | 155 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 700 | 19 | 5 | 0 | 75 | 0 | 354 | 285 | 5 | 0 | 36 | 50 | 50 | 108 | 9 | 0 | 14 | 38 | 8 | 7 | 0 | 300 | 320 | 315 | 39 | 40 | 0 | 149 | 8 | 0 | 22 | 20 | 0 | 18 | 172 | 0 | 24 | 20 | 0 | 2 | 51.55 | 0 | 5408.45 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.18 | 378 | 0 | 824.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.28 | 140 | 0 | 139 | 0 | 137 | 0 | 360 | 0 | 5.67 | 0 | 163 | 62 | 0 | 3 | 0 | 0 | 0 | 6.9 | 65 | 0.37 | 0 | 150 | 0 | 100 | 220 | 0 | 614 | 580 | 0 | 4985.35 | 10393.8 | 81.78
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 300 | 308 | 350 | 0 | 0 | 0 | 322 | 39 | 0 | 8 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 11 | 0 | 0 | 0 | 33 | 88 | 3 | 40 | 0 | 7 | 155 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 707 | 17 | 5 | 0 | 78 | 0 | 300 | 285 | 5 | 0 | 33 | 0 | 50 | 0 | 9 | 0 | 0 | 28 | 0 | 66 | 0 | 290 | 320 | 395 | 39 | 40 | 0 | 135 | 16 | 0 | 22 | 20 | 0 | 18 | 172 | 0 | 24 | 32 | 0 | 2 | 30.53 | 0 | 5334.53 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.76 | 378 | 0 | 831.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 28.84 | 140 | 0 | 139 | 0 | 138 | 0 | 270 | 0 | 2.52 | 0 | 162 | 61 | 0 | 15 | 0 | 0 | 0 | 6.9 | 97 | 0.05 | 0 | 150 | 4 | 100 | 180 | 0 | 511 | 570 | 0 | 4718.98 | 10053.51 | 81.78
15:00 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 10 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 283 | 350 | 0 | 0 | 0 | 282 | 39 | 0 | 1 | 17 | 16.5 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 15 | 17 | 0 | 0 | 33 | 88 | 3 | 40 | 0 | 2 | 154 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 706 | 13 | 5 | 0 | 78 | 0 | 300 | 285 | 13 | 0 | 33 | 0 | 50 | 0 | 9 | 0 | 0 | 38 | 0 | 23 | 0 | 305 | 320 | 360 | 39 | 40 | 0 | 153 | 0 | 0 | 22 | 30 | 0 | 18 | 173 | 0 | 36 | 75 | 0 | 1 | 18.34 | 0 | 5397.84 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.75 | 379 | 0 | 817.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 18.72 | 140 | 0 | 139 | 0 | 144 | 0 | 320 | 0 | 1.71 | 0 | 165 | 59 | 0 | 25 | 0 | 0 | 0 | 4.9 | 97 | 0.13 | 0 | 150 | 5 | 88 | 220 | 0 | 502 | 540 | 0 | 4759.66 | 10157.5 | 81.77
16:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 14 | 50 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 380 | 290 | 350 | 0 | 0 | 0 | 274 | 38 | 0 | 2 | 17 | 16.5 | 15 | 0 | 0 | 0 | 0 | 28 | 0 | 17 | 17 | 0 | 0 | 44 | 88 | 2 | 40 | 0 | 3 | 154 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 730 | 8 | 24 | 0 | 123 | 0 | 360 | 160 | 25 | 0 | 33 | 0 | 50 | 0 | 0 | 5 | 0 | 34 | 0 | 10 | 0 | 310 | 320 | 392 | 39 | 40 | 0 | 146 | 0 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 54 | 75 | 0 | 1 | 20.33 | 0 | 5704.83 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 376 | 0 | 816.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 13.83 | 156 | 0 | 143 | 0 | 144 | 0 | 250 | 0 | 1.21 | 0 | 166 | 60 | 0 | 16 | 0 | 0 | 0 | 3 | 65 | 0.58 | 0 | 170 | 0 | 120 | 220 | 0 | 308 | 587 | 0 | 4582.34 | 10287.17 | 81.77
17:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 17 | 65 | 32 | 0 | 0 | 17 | 0 | 0 | 0 | 340 | 296 | 350 | 0 | 0 | 0 | 277 | 38 | 0 | 5 | 17 | 16.5 | 15 | 0 | 0 | 0 | 0 | 38 | 0 | 8 | 17 | 0 | 0 | 44 | 88 | 0 | 40 | 0 | 7 | 154 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 730 | 3 | 24 | 0 | 123 | 0 | 360 | 0 | 28 | 0 | 36 | 0 | 50 | 0 | 0 | 14 | 0 | 16 | 0 | 10 | 0 | 305 | 320 | 355 | 38 | 40 | 0 | 159 | 8 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 54 | 75 | 0 | 0 | 6.67 | 0 | 5502.17 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 381 | 0 | 815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 9.91 | 175 | 0 | 150 | 0 | 147 | 0 | 250 | 0 | 0.88 | 0 | 165 | 59 | 0 | 6 | 0 | 0 | 0 | 1.3 | 56 | 0 | 0 | 170 | 0 | 120 | 220 | 0 | 402 | 591 | 0 | 4648.09 | 10150.26 | 81.76
18:00 | 0 | 44 | 16 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 26 | 87 | 48 | 0 | 0 | 17 | 10 | 0 | 0 | 340 | 308 | 350 | 0 | 0 | 0 | 317 | 38 | 0 | 0 | 17 | 17 | 15 | 0 | 0 | 0 | 0 | 38 | 0 | 1 | 17 | 0 | 0 | 44 | 100 | 0 | 40 | 0 | 12 | 215 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 730 | 0 | 24 | 0 | 142 | 0 | 356 | 33 | 50 | 0 | 34 | 0 | 50 | 0 | 1 | 18 | 0 | 24 | 0 | 1 | 0 | 300 | 320 | 386 | 38 | 40 | 0 | 155 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 56 | 88 | 0 | 0 | 0.76 | 0 | 5829.76 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 381 | 0 | 866.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.13 | 175 | 0 | 161 | 0 | 155 | 0 | 300 | 0 | 0.05 | 0 | 163 | 58 | 0 | 1 | 18 | 0 | 0 | 0.1 | 11 | 0 | 0 | 172 | 2 | 120 | 220 | 0 | 410 | 589 | 0 | 4708.98 | 10538.74 | 81.76
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 10 | 35 | 87 | 64 | 45 | 0 | 32 | 95 | 0 | 10 | 420 | 275 | 350 | 0 | 17 | 0 | 266 | 104 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 51 | 0 | 0 | 100 | 100 | 0 | 40 | 0 | 12 | 250 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 859 | 0 | 51 | 28 | 175 | 0 | 359 | 100 | 53 | 0 | 36 | 21 | 45 | 4 | 14 | 20 | 28 | 32 | 0 | 0 | 3 | 305 | 320 | 338 | 37 | 40 | 0 | 156 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 83 | 120 | 0 | 0 | 0 | 6 | 6592 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 1221.18 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 162 | 0 | 156 | 0 | 414 | 0 | 0 | 0 | 160 | 58 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 4 | 100 | 220 | 0 | 510 | 648 | 0 | 5451.18 | 12043.18 | 81.76
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 36 | 87 | 64 | 0 | 0 | 35 | 108 | 0 | 14 | 420 | 301 | 350 | 0 | 17 | 0 | 280 | 102 | 0 | 0 | 90 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 80 | 0 | 40 | 0 | 14 | 252 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 175 | 0 | 359 | 100 | 53 | 0 | 36 | 34 | 45 | 29 | 38 | 20 | 29 | 32 | 0 | 0 | 9 | 310 | 320 | 320 | 37 | 40 | 0 | 135 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 85 | 120 | 0 | 0 | 0 | 12 | 6608.5 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 1215.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 161 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 158 | 58 | 35 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 100 | 220 | 0 | 520 | 747 | 0 | 5549.5 | 12158 | 81.76
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 23 | 35 | 85 | 64 | 0 | 0 | 17 | 90 | 0 | 0 | 420 | 306 | 350 | 0 | 0 | 0 | 294 | 103 | 0 | 0 | 70 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 24 | 0 | 40 | 0 | 19 | 255 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 175 | 0 | 360 | 114 | 53 | 0 | 36 | 16 | 45 | 26 | 37 | 14 | 0 | 26 | 0 | 0 | 7 | 300 | 320 | 336 | 37 | 40 | 0 | 137 | 16 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 85 | 95 | 0 | 0 | 0 | 12 | 6440.5 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 1206.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 160 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 160 | 58 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 5 | 120 | 220 | 0 | 573 | 751 | 0 | 5613.64 | 12054.14 | 81.76
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 36 | 60 | 48 | 0 | 0 | 17 | 35 | 0 | 0 | 420 | 292 | 400 | 0 | 0 | 0 | 268 | 103 | 0 | 0 | 70 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 12 | 0 | 40 | 0 | 23 | 252 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 177 | 0 | 359 | 195 | 53 | 0 | 37 | 16 | 50 | 15 | 37 | 21 | 0 | 34 | 0 | 0 | 7 | 305 | 320 | 326 | 37 | 40 | 0 | 150 | 16 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 85 | 95 | 0 | 0 | 0 | 12 | 6411.5 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 159 | 0 | 151 | 0 | 414 | 0 | 0 | 0 | 163 | 58 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 7 | 120 | 220 | 0 | 641 | 700 | 0 | 5631 | 12042.5 | 81.76
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 36 | 45 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 296 | 400 | 0 | 0 | 0 | 273 | 103 | 0 | 0 | 70 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 51 | 0 | 0 | 100 | 12 | 0 | 40 | 0 | 26 | 252 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 178 | 0 | 359 | 255 | 54 | 0 | 37 | 16 | 50 | 15 | 39 | 21 | 0 | 32 | 0 | 0 | 0 | 310 | 320 | 337 | 37 | 40 | 0 | 152 | 16 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 85 | 95 | 0 | 0 | 0 | 12 | 6322.5 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 156 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 165 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 110 | 220 | 0 | 667 | 647 | 0 | 5430 | 11752.5 | 81.76
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 36 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 293 | 400 | 0 | 0 | 0 | 266 | 103 | 0 | 0 | 35 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 100 | 12 | 0 | 40 | 0 | 30 | 252 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 178 | 0 | 358 | 255 | 53 | 0 | 37 | 16 | 50 | 0 | 39 | 20 | 0 | 58 | 0 | 0 | 0 | 295 | 320 | 356 | 40 | 40 | 0 | 148 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 65 | 95 | 0 | 0 | 0 | 12 | 6154.5 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 1068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 154 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 164 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 112 | 220 | 0 | 724 | 652 | 0 | 5391 | 11545.5 | 81.76
Total KWH | 0 | 628800 | 275520 | 0 | 0 | 0 | 0 | 0 | 8398800 | 0 | 0 | 34200 | 434520 | 1020672 | 796800 | 22331 | 0 | 186897 | 250560 | 0 | 14400 | 8777500 | 7173993 | 9186364 | 0 | 25292 | 0 | 6835603 | 2146000 | 0 | 84526 | 494400 | 395400 | 274320 | 0 | 0 | 0 | 0 | 164160 | 0 | 99360 | 359685 | 0 | 0 | 1267200 | 880320 | 26480 | 957300 | 0 | 397440 | 4501818.18 | 8364 | 0 | 0 | 43903.8 | 836 | 3512516 | 0 | 0 | 0 | 18496362 | 118800 | 1014580 | 41818 | 2241455 | 0 | 8532900 | 5712000 | 733440 | 1091000 | 845568 | 770880 | 1292060 | 855360 | 361200 | 368440 | 316920 | 757440 | 158712 | 325973 | 14336 | 7346000 | 7670200 | 8514000 | 914000 | 934800 | 0 | 3439964 | 320616 | 0 | 1770240 | 664992 | 0 | 432000 | 4575320 | 0 | 1190400 | 1747200 | 0 | 11950 | 191470 | 198960 | 143647636.98 | 21679727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477360 | 9898182 | 0 | 22285694 | 0 | 0 | 0 | 15744 | 0 | 0 | 0 | 0 | 0 | 298030 | 0 | 311248 | 3843091 | 0 | 3659336 | 0 | 3672727 | 0 | 8740000 | 0 | 24600 | 0 | 4009000 | 1425164 | 94296 | 93445 | 152332 | 0 | 0 | 41703.72 | 771840 | 2905 | 0 | 4865000 | 119883 | 2626000 | 5222740 | 0 | 12827808 | 16401454.55 | 0 | 123559310.27 | 267206947.25

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11132.16 | MW | 10:00 Hr. | Energy Generated |  |  | 267.2069 |  | MKWHr.
| Day Peak Demand |  |  | 11132.16 | MW | 10:00 Hr. | Energy Unserverd |  |  | 0.055 |  | MKWHr.
| Evening Peak Generation |  |  | 12158 | MW | 19:30 Hr. | Energy Demand |  |  | 267.2619 |  | MKWHr.
| Evening Peak Demand |  |  | 12158 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.6 |  | °C
| Minimum Generation of the Day |  |  | 9881.58 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 971.65 |  | MMCFD
| Maximum Generation of the Day |  |  | 12280 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.0958 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.188 | 0 | 4.1844 | 0 | 0 | 0.084526 | 0 | 0 | 47.4569 | Gas | 133.3953 | Gas | 432279604.44
| Chattogram Zone |  |  | 3.91 | 22.9982 | 2.7245 | 0 | 0.9573 | 0.14528 | 0 | 0.09936 | 30.8345 | Coal | 72.4248 | Coal | 432541646.4109
| Cumilla Zone |  |  | 21.8314 | 0 | 2.5192 | 0 | 0 | 0.32597 | 0.75744 | 0 | 25.4341 | HFO | 12.827 | HFO | 230755117.796
| Mymensingh Zone |  |  | 0 | 0 | 3.1366 | 0 | 0 | 0.20342 | 0 | 0 | 3.34 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.5821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.5821 | Hydro | 0.9573 | Hydro | 95730
| Khulna Zone |  |  | 0 | 9.8982 | 0 | 0 | 0 | 0.47736 | 21.6797 | 0 | 32.0553 | Solar | 2.7803 | Solar | 44862371.5492
| Barishal Zone |  |  | 7.9686 | 34.0943 | 0 | 0 | 0 | 0.002905 | 0 | 0 | 42.0658 | Import | 44.7229 | Import | 219649018.93
| Rajshahi Zone |  |  | 19.9152 | 0 | 0.015744 | 0 | 0 | 0.63388 | 22.2857 | 0 | 42.8505 | Wind | 0.09936 | Wind | 1454630.4
| Rangpur Zone |  |  | 0 | 5.4342 | 0.24663 | 0 | 0 | 0.90699 | 0 | 0 | 6.5878
| Total |  |  | 133.3953 | 72.4248 | 12.827 | 0 | 0.9573 | 2.7803 | 44.7229 | 0.09936 | 267.2069
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 432279604.44 |  | Hydro | 95730
|  |  |  | Coal | 432541646.4109 |  | Solar | 44862371.5492
|  |  |  | HFO | 230755117.796 |  | Import | 219649018.93
|  |  |  | HSD | 0 |  | Wind | 1454630.4
[5 empty] | Total: | 136,16,38,119 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6797 | Peak Hr Flow | 857.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41190927.36 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.2857 | Peak Hr Flow | 1215.50 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 876 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.75744 | Peak Hr Flow | 32.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 996 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.7229 | Peak Hr Flow | 2104.50 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4644
|  |  |  | Chattogram |  | 0 |  | 1389
|  |  |  | Cumilla |  | 0 |  | 1004
|  |  |  | Mymensingh |  | 0 |  | 983
|  |  |  | Sylhet |  | 0 |  | 439
|  |  |  | Khulna |  | 0 |  | 1125
|  |  |  | Barishal |  | 0 |  | 168
|  |  |  | Rajshahi |  | 0 |  | 1214
|  |  |  | Rangpur |  | 0 |  | 764
|  |  |  | Total |  | 0 |  | 11730
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:23 | Kabirpur -Tongi 132kV Ckt-1 is restored.
|  | 08:23 | Kabirpur -Tongi 132kV Ckt-2 is restored.
| 08:37 |  | Bibiyana-Fenchuganj 230 kV Ckt-2 Scheduled S/D from Fenchuganj 230/132/33kV end Due to
Deadline checking
|  | 09:12 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
| 09:57 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to Dismantle the D/S near
the BUS -1
| 11:02 |  | Muktagacha 132/33kV S/S T-2(414T) LT Forced S/D
| 11:03 |  | Muktagacha 132/33kV S/S T-2(414T) HT Forced S/D
| 11:16 | 15:34 | BIPTC S/S 20DF11 Forced S/D Due to Shutdown is taken by Abdullah Al Farabi, AE
Troubleshooting.
| 11:25 | 11:46 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end Due to
tree trimming by maintenance team
| 11:30 | 11:36 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent relay relays.
| 11:46 | 12:31 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Forced S/D from Brahmanbaria 132/33kV end Due to
tree trimming by maintenance team
| 11:53 | 12:10 | Khagrachari-Rangamati 132kV Ckt-1 Forced S/D from Khagrachori 132/33kV end Due to
Emergency maintenance at Rangamati SS and from Rangamati 132/33kV end Due to Destroyed
nest
| 12:00 |  | Bad weather observed around periphery of Dhaka.
| 12:13 | 13:36 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Due to Load
Management by NLDC
| 12:13 | 12:26 | Brahmanbaria-Shahjibazar 132 kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing
Distance Realy relays Due to Heavy Rain & Wind flow and from Brahmanbaria 132/33kV end
showing distance relay relays.
| 13:38 | 18:18 | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to For Ten Delta Test By RTs
| 13:44 | 18:18 | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to For Ten Delta Test By RTS
| 13:50 | 14:50 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) LT Scheduled S/D Due to
Redhot removal work at 33kV side
| 13:50 | 14:49 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D Due to Red
hot maintenance
| 14:00 | 21:06 | Kulaura 132/33kV S/S TR-1 LT Scheduled S/D Due to TR-3 Relay testing
| 14:01 | 21:05 | Kulaura 132/33kV S/S TR-1 HT Scheduled S/D Due to TR-3 Relay testing
| 14:18 | 18:39 | Madaripur 132/33kV S/S T3-426T HT Tripped showing Earth fault B phase relays Due to 33kv
west zone bus section fault
| 14:20 | 14:58 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing REF630 relays Due to Heavy | [7 empty] | 35.0MW load
|  |  | Storm ( Benapole,Sharsha) feeder fault simultaneously. | [7 empty] | interrup.
| 16:27 |  | Ashuganj 450 MW CCPP(South) Shutdown with remarks:- GT
| 17:04 | 17:20 | Goalpara 132/33kV S/S T-6 LT Tripped showing O/C relays Due to ৩৩ কেভি সেনেরবাজার ফিডার | [7 empty] | 3.0MW load
|  |  | ফল্ট | [7 empty] | interrup.
| 17:04 | 17:20 | Goalpara 132/33kV S/S T-5 LT Tripped showing O/C relays Due to ৩৩ কেভি সেনেরবাজার ফিডার | [7 empty] | 3.0MW load
|  |  | ফল্ট | [7 empty] | interrup.
| 17:41 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 19:30 |  | Evening peak Generation is 12157 MW
| 19:36 | 21:04 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to 33 kv bus section (extension)
y-phase female contact burn out .
| 19:36 | 21:06 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to 33 kv bus section (extension)
y-phase female contact burn out .
| 19:37 |  | Ashuganj 450 MW CCPP(South) Synchronized with remarks:- ST
| 21:57 | 21:58 | Cumilla(S) 132/33kV S/S TR-3 LT Scheduled S/D Due to T3 shift from Bangladesh to India | [7 empty] | 30.0MW load
|  |  | Bus | [7 empty] | interrup.
| 21:57 | 21:58 | Cumilla(S) 132/33kV S/S TR-3 HT Scheduled S/D
| 03:30 |  | Bhangura 132/33kV S/S Tr-2(413T) HT Scheduled S/D Due to Project development work | [7 empty] | 10.0MW load
interrup.
| 03:37 |  | Bhangura 132/33kV S/S Tr-2(413T) LT Scheduled S/D Due to Project development work | [7 empty] | 10.0MW load
interrup.
| 04:29 |  | Bhangura 132/33kV S/S Tr-1(403T) HT Scheduled S/D Due to Project development work | [7 empty] | 20.0MW load
interrup.
| 04:35 |  | Bhangura 132/33kV S/S Tr-1(403T) LT Scheduled S/D Due to Project development work | [7 empty] | 10.0MW load
interrup.
| 04:40 |  | Bhangura 132/33kV S/S 132KV Single Bus Scheduled S/D Due to Project development work | [7 empty] | 10.0MW load
interrup.
| 07:51 |  | BIPTC S/S 20D09C 20MVA LT Scheduled S/D Due to 20D09C 20MVA Auxiliary Trafo-1 tripped by
87T (Differential Relay) Over Current Stage-2 Operated
| 07:51 |  | BIPTC S/S 20D09C 20MVA HT Scheduled S/D Due to 20D09C 20MVA Auxiliary Trafo-1 tripped by
87T (Differential Relay) Over Current Stage-2 Operated
| 07:58 |  | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D from Mirpur 132/33kV end Due to CVT, LA and
Loop of DS Replacement work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 355 | 8398800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8777500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 301 | 7173993 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 102 | 2146000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6835603 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 34200 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 64 | 796800 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 186897 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 25292 | FGMO
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17.5 | 395400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 274320 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 275520 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 22331 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 87 | 1020672 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 628800 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 14 | 14400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 250560 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 84526 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 36 | 434520 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 350 | 9186364 | Allocation limit by Titas Gas
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 494400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2361.5 | 47456898
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 43903.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 118800 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 957300 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 151 | 3512516 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 836 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | -
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 359685 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1267200 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 14 | 397440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 164160 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 80 | 880320 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 8364 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 850 | 18496362 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 99360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 252 | 4501818.18 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1538 | 30834544.98
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 0 | 1091000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 359 | 8532900 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 100 | 5712000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 845568 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 53 | 733440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 175 | 2241455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1014580 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 41818 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 9 | 14336 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 45 | 1292060 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 29 | 855360 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 32 | 757440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 158712 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 368440 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 29 | 316920 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 361200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 770880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 325973 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1010 | 25434082
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 120 | 1747200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1190400 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 191470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 198960 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 217 | 3339980
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 37 | 914000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 934800 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 135 | 3439964 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 664992 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1770240 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 4575320 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 320616 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7346000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 320 | 8514000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7670200 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1482 | 36582132
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 857 | 21679727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 477360 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 382 | 9898182 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1239 | 32055269
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 520 | 12827808 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 6 | 119883 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 100 | 2626000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 747 | 16401454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5222740 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4865000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2905 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1900 | 42065790.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 178 | 3843091 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 161 | 3659336 | Low gas pressure
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 153 | 3672727 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8740000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 15744 | FGMO
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1215.5 | 22285694 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 311248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 298030 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2121.5 | 42850470
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1425164 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 4009000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 38 | 152332 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 41703.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 94296 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 93445 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 771840 | -
Rangpur Area Total |  |  |  |  | 950 | 289 | 6587780.72
Eastern Grid Total |  |  |  |  | 16921.242 | 6608.5 | 143647636.98
Western Grid Total |  |  |  |  | 11614.5 | 5549.5 | 123559310.27
National Grid Total |  |  |  |  | 28535.742 | 12158 | 267206947.25
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8458.57 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3270.4 | MW
i) Dhaka area |  |  | 4643.57 |  | MW | i) Khulna area |  |  |  | 1124.8 | MW
ii) Chattogram area |  |  | 1389 |  | MW | ii) Barishal area |  |  |  | 168 | MW
iii) Cumilla area |  |  | 1004 |  | MW | iii) Rajshahi area |  |  |  | 1213.6 | MW
iv) Mymensingh area |  |  | 983 |  | MW | iv) Rangpur area |  |  |  | 764 | MW
v) Sylhet area |  |  | 439 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11728.97 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 63 | 19:00 | 133 | Patuakhali | 57.5 | 00:00
2 | AKSML | 123 | 01:00 | 68 | Jaldhaka | 62 | 19:00 | 134 | Payra | 26 | 00:00
3 | Aftabnagar | 30 | 11:00 | 69 | Jamalpur | 103 | 07:00 | 135 | Postogola | 51 | 12:00
4 | Agargaon | 111 | 11:00 | 70 | Jashore | 143 | 13:00 | 136 | Purbachal | 14 | 00:00
5 | Agrabad | 94 | 15:00 | 71 | Jhenaidah | 108 | 00:00 | 137 | Purbasadipur | 102 | 00:00
6 | Amnura | 32 | 20:00 | 72 | Joydebpur | 124 | 10:00 | 138 | Rahanpur | 22 | 21:00
7 | Ashuganj | 78 | 23:00 | 73 | Joypurhat | 53 | 19:30 | 139 | Rahim | 40 | 15:00
8 | BSRM | 194 | 00:00 | 74 | Juldah | 17 | 23:00 | 140 | Rajbari | 52 | 10:00
9 | Bagerhat | 68 | 00:00 | 75 | KSRM | 15 | 00:00 | 141 | Rajendrapur | 114 | 20:00
10 | Bajitpur | 37 | 18:30 | 76 | Kabirpur | 260 | 16:00 | 142 | Rajshahi | 110 | 19:00
11 | Bakulia | 95 | 16:00 | 77 | Kachua | 70 | 00:00 | 143 | Rajshahi-230 | 78 | 10:00
12 | Banani | 40 | 11:00 | 78 | Kallyanpur | 84 | 00:00 | 144 | Ramganj | 94 | 00:00
13 | Bangabhaban | 16 | 11:00 | 79 | Kalurghat | 40 | 16:00 | 145 | Rampur | 39 | 16:00
14 | Barapukuria | 54 | 19:30 | 80 | Kamrangirchar | 66 | 13:00 | 146 | Rangamati | 14 | 12:00
15 | Barguna | 16 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 116 | 18:30
16 | Barishal | 100 | 11:00 | 82 | Kasba | 25 | 02:00 | 148 | Ruppur | 6.8 | 09:00
17 | Barishal-230 | 70 | 11:00 | 83 | Kazla | 102 | 18:30 | 149 | SSM | 10 | 01:00
18 | Baroaulia | 63 | 09:00 | 84 | Keranigonj | 76 | 19:00 | 150 | Saidpur | 94 | 18:30
19 | Baroirhat | 58 | 21:00 | 85 | Khagrachori | 26 | 13:00 | 151 | Satkhira | 110 | 00:00
20 | Bashundhara | 179 | 11:00 | 86 | Khulna | 77 | 13:00 | 152 | Satmasjid | 92 | 14:00
21 | BashundharaCement | 12 | 08:00 | 87 | Khulshi | 168 | 16:00 | 153 | Savar | 204 | 16:00
22 | Beanibazar | 56 | 18:30 | 88 | Kishoreganj | 99 | 19:00 | 154 | SevenRings | 17.35 | 12:00
23 | Benapole | 62 | 13:00 | 89 | Kodda | 297 | 18:00 | 155 | ShahCement | 34 | 06:00
24 | Bhaluka | 126 | 19:00 | 90 | Kulaura | 31 | 19:00 | 156 | Shahjadpur | 68 | 07:00
25 | Bhandaria | 40 | 00:00 | 91 | Kurigram | 60 | 19:00 | 157 | Shahjibazar | 97 | 21:00
26 | Bhangura | 26 | 07:00 | 92 | Kushtia | 114 | 19:00 | 158 | Shahmirpur | 56 | 17:00
27 | Bheramara(GK) | 53 | 00:00 | 93 | Lalbag | 65 | 12:00 | 159 | Shariatpur | 68 | 00:00
28 | Bhulta | 231 | 21:00 | 94 | Lalmonirhat | 51 | 19:00 | 160 | Sherpur | 118 | 18:30
29 | Bog-Sherpur | 60 | 19:00 | 95 | MI_Cement | 18.5 | 21:00 | 161 | Shikalbaha | 28 | 18:30
30 | Bogura | 146 | 19:30 | 96 | Madanganj | 40 | 21:00 | 162 | Shitalakhya | 76 | 12:00
31 | Borhanuddin | 75 | 00:00 | 97 | Madaripur | 85 | 00:00 | 163 | Sholosohor | 33 | 15:00
32 | Brahmanbaria | 97 | 18:30 | 98 | Madartek | 67.29 | 11:00 | 164 | Shyampur | 150 | 14:00
33 | Cantonment | 113 | 11:00 | 99 | Madunaghat | 48 | 12:00 | 165 | Siddhirganj | 118 | 11:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 47 | 00:00 | 166 | Sirajganj | 88 | 19:00
35 | Chandpur | 59 | 00:00 | 101 | Mahasthangarh | 64 | 19:30 | 167 | Sonargaon | 103 | 11:00
36 | Chandraghona | 32 | 18:30 | 102 | Manikganj | 109 | 19:00 | 168 | Sreemongol | 50 | 21:00
37 | Chapai | 68 | 00:00 | 103 | Maniknagar | 67 | 11:00 | 169 | Sreepur | 82 | 09:00
38 | Charsaidpur | 49 | 18:30 | 104 | Matarbari | 50 | 22:00 | 170 | Srinagar | 35.8 | 21:00
39 | Chauddagram | 63 | 12:00 | 105 | Matuail | 61 | 11:00 | 171 | Sunamganj | 42 | 19:00
40 | Chhatak | 27 | 19:00 | 106 | Millgate | 96 | 11:00 | 172 | Sylhet | 33 | 21:00
41 | Chowmuhani | 178 | 00:00 | 107 | Mirpur | 120 | 11:00 | 173 | Sylhet-132 | 103 | 18:30
42 | Chuadanga | 104 | 00:00 | 108 | Mirsorai | 8 | 09:00 | 174 | TK | 30.8 | 00:00
43 | Coxsbazar | 132 | 18:30 | 109 | Mirzapur | 43 | 07:00 | 175 | Tangail | 144 | 19:00
44 | Cumilla(N) | 136 | 12:00 | 110 | Mithapukur | 42 | 00:00 | 176 | Thakurgaon | 81 | 19:30
45 | Cumilla(S) | 162 | 12:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 124 | 09:00
46 | Daudkandi | 122 | 21:00 | 112 | Mogbazar | 110.4 | 11:00 | 178 | Ullahpara | 40 | 03:00
47 | Dhaka | 52 | 11:00 | 113 | Mongla | 42 | 11:00 | 179 | Ullon | 38 | 00:00
48 | Dhamrai | 124 | 09:00 | 114 | Motijheel | 34 | 11:00 | 180 | Uttara | 85 | 11:00
49 | Dhanmondi | 131 | 11:00 | 115 | Muktagacha | 27 | 18:30 | 181 | UttaraNew | 39 | 10:00
50 | Dohazari | 97 | 19:00 | 116 | Munshiganj | 97 | 20:00 | 182 | Zigatola | 82 | 14:00
51 | Faridpur | 120 | 00:00 | 117 | Muradnagar | 20 | 11:00
52 | Fatullah | 100 | 11:00 | 118 | Mymensingh | 173 | 19:00
53 | Fenchuganj | 22 | 18:30 | 119 | Naogaon | 109 | 19:00
54 | Feni | 94 | 01:00 | 120 | Narail | 46 | 13:00
55 | GPH | 78 | 15:00 | 121 | Narinda | 67 | 11:00
56 | Ghatail | 78 | 19:00 | 122 | Narshingdi | 151 | 20:00
57 | Ghorashal | 13 | 18:00 | 123 | Natore | 121 | 19:00
58 | Ghorashal-230 | 70 | 21:00 | 124 | Nawabganj | 41 | 21:00
59 | Goalpara | 32 | 13:00 | 125 | Netrakona | 108 | 19:00
60 | Gollamari | 92 | 13:00 | 126 | New | 84 | 11:00
61 | Gopalganj | 81 | 00:00 | 127 | Niamatpur | 81 | 21:00
62 | Gulshan | 114 | 11:00 | 128 | Noapara | 41 | 13:00
63 | Halishahar | 73.5 | 09:00 | 129 | PHP | 9 | 07:00
64 | HaripurSBU | 169 | 18:00 | 130 | Pabna | 89 | 10:00
65 | Hasnabad | 67 | 09:00 | 131 | Palashbari | 92 | 19:00
66 | Hathazari | 76 | 12:00 | 132 | Panchagarh | 46 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12280 | 0 |  | 12280
1:00 | 12032 | 0 |  | 12032
2:00 | 11497 | 0 |  | 11497
3:00 | 11026 | 0 |  | 11026
4:00 | 10739 | 0 |  | 10739
5:00 | 10332 | 0 |  | 10332
6:00 | 9881.58 | 0 |  | 9881.58
7:00 | 10371.37 | 0 |  | 10371.37
8:00 | 10315.12 | 0 |  | 10315.12
9:00 | 10778.4 | 0 |  | 10778.4
10:00 | 11132.16 | 0 |  | 11132.16
11:00 | 10981.28 | 0 |  | 10981.28
12:00 | 10343.01 | 0 |  | 10343.01
13:00 | 10393.8 | 0 |  | 10393.8
14:00 | 10053.51 | 0 |  | 10053.51
15:00 | 10157.5 | 0 |  | 10157.5
16:00 | 10287.17 | 0 |  | 10287.17
17:00 | 10150.26 | 22 |  | 10173.26
18:00 | 10538.74 | 0 |  | 10538.74
19:00 | 12043.18 | 0 |  | 12043.18
19:30 | 12158 | 0 |  | 12158
20:00 | 12054.14 | 16 |  | 12071.14
21:00 | 12042.5 | 17 |  | 12060.5
22:00 | 11752.5 | 0 |  | 11752.5
23:00 | 11545.5 | 0 |  | 11545.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6302 | 5978 | 12280 | DAILY GENERATION CURVE
00:30 | 6286 | 5870 | 12156
01:00 | 6270 | 5762 | 12032 | 17-04-2025
01:30 | 6247 | 5517.5 | 11764.5
02:00 | 6224 | 5273 | 11497
02:30 | 6170.5 | 5091 | 11261.5
03:00 | 6117 | 4909 | 11026
03:30 | 5997 | 4885.5 | 10882.5
04:00 | 5877 | 4862 | 10739
04:30 | 5755.5 | 4780 | 10535.5
05:00 | 5634 | 4698 | 10332
05:30 | 5454.615 | 4652.175 | 10106.79
06:00 | 5275.23 | 4606.35 | 9881.58
06:30 | 5453.365 | 4673.11 | 10126.475
07:00 | 5631.5 | 4739.87 | 10371.37
07:30 | 5655.235 | 4688.01 | 10343.245
08:00 | 5678.97 | 4636.15 | 10315.12
08:30 | 5779.115 | 4767.645 | 10546.76
09:00 | 5879.26 | 4899.14 | 10778.4
09:30 | 5930.725 | 5024.555 | 10955.28
10:00 | 5982.19 | 5149.97 | 11132.16
10:30 | 5919 | 5137.72 | 11056.72
11:00 | 5855.81 | 5125.47 | 10981.28
11:30 | 5501.625 | 5160.52 | 10662.145
12:00 | 5147.44 | 5195.57 | 10343.01
12:30 | 5277.945 | 5090.46 | 10368.405
13:00 | 5408.45 | 4985.35 | 10393.8
13:30 | 5371.49 | 4852.165 | 10223.655
14:00 | 5334.53 | 4718.98 | 10053.51
14:30 | 5366.185 | 4739.32 | 10105.505
15:00 | 5397.84 | 4759.66 | 10157.5
15:30 | 5551.335 | 4671 | 10222.335
16:00 | 5704.83 | 4582.34 | 10287.17
16:30 | 5603.5 | 4615.215 | 10218.715
17:00 | 5502.17 | 4648.09 | 10150.26
17:30 | 5665.965 | 4678.535 | 10344.5
18:00 | 5829.76 | 4708.98 | 10538.74
18:30 | 6210.88 | 5080.08 | 11290.96
19:00 | 6592 | 5451.18 | 12043.18
19:30 | 6608.5 | 5549.5 | 12158
20:00 | 6440.5 | 5613.64 | 12054.14
20:30 | 6426 | 5622.32 | 12048.32 |  | Executive Engineer
21:00 | 6411.5 | 5631 | 12042.5 |  | Network Operation Division
21:30 | 6367 | 5530.5 | 11897.5
22:00 | 6322.5 | 5430 | 11752.5
22:30 | 6238.5 | 5410.5 | 11649
23:00 | 6154.5 | 5391 | 11545.5

## En-Curve
QF-LDC-12
Date | 17-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3702 | 2061 | 900 | 0 | 28 | 1217 | 40 | 3659 | 0 | 100 | 567 | 0 | 0 | 6 | 0 | DAILY ENERGY CURVE
00:30 | 3684.5 | 2060.5 | 902 | 0 | 28 | 1169.5 | 40 | 3614 | 0 | 112 | 540 | 0 | 0 | 5.5 | 0 | 17-04-2025
01:00 | 3667 | 2060 | 904 | 0 | 28 | 1122 | 40 | 3569 | 0 | 124 | 513 | 0 | 0 | 5 | 0
01:30 | 3666 | 2060 | 904 | 0 | 29 | 1018 | 40 | 3429 | 0 | 116 | 497.5 | 0 | 0 | 5 | 0 | Energy Generated | 267.2069 |  | MKWHr
02:00 | 3665 | 2060 | 904 | 0 | 30 | 914 | 40 | 3289 | 0 | 108 | 482 | 0 | 0 | 5 | 0 | Energy not Served | 0.055 |  | MKWHr
02:30 | 3627.5 | 2049 | 904 | 0 | 28 | 869 | 40 | 3187 | 0 | 92 | 462.5 | 0 | 0 | 2.5 | 0 | Total Energy Requirement | 267.2619 |  | MKWHr
03:00 | 3590 | 2038 | 904 | 0 | 26 | 824 | 40 | 3085 | 0 | 76 | 443 | 0 | 0 | 0 | 0
03:30 | 3585.5 | 1997 | 903.5 | 0 | 29 | 826 | 40 | 3014.5 | 0 | 58.5 | 427.5 | 0 | 0 | 1 | 0
04:00 | 3581 | 1956 | 903 | 0 | 32 | 828 | 40 | 2944 | 0 | 41 | 412 | 0 | 0 | 2 | 0
04:30 | 3551.5 | 1879.5 | 903 | 0 | 28 | 826.5 | 40 | 2877 | 0 | 41 | 386 | 0 | 0 | 3 | 0
05:00 | 3522 | 1803 | 903 | 0 | 24 | 825 | 40 | 2810 | 0 | 41 | 360 | 0 | 0 | 4 | 0
05:30 | 3477 | 1785 | 903.5 | 0 | 23 | 830 | 40 | 2752 | 3.79 | 41 | 247.5 | 0 | 0 | 4 | 0
06:00 | 3432 | 1767 | 904 | 0 | 22 | 835 | 40 | 2694 | 7.58 | 41 | 135 | 0 | 0 | 4 | 0
06:30 | 3461 | 1849 | 904 | 0 | 22 | 831.5 | 40 | 2693 | 35.975 | 83 | 201 | 0 | 0 | 6 | 0
07:00 | 3490 | 1931 | 904 | 0 | 22 | 828 | 40 | 2692 | 64.37 | 125 | 267 | 0 | 0 | 8 | 0
07:30 | 3398 | 1897.25 | 880 | 0 | 26 | 827.9 | 40 | 2734.5 | 116.095 | 131 | 288.5 | 0 | 0 | 4 | 0
08:00 | 3306 | 1863.5 | 856 | 0 | 30 | 827.8 | 40 | 2777 | 167.82 | 137 | 310 | 0 | 0 | 0 | 0
08:30 | 3442 | 1897.25 | 855.5 | 0 | 30 | 828.97 | 40 | 2845 | 221.54 | 112.5 | 274 | 0 | 0 | 0 | 0
09:00 | 3578 | 1931 | 855 | 0 | 30 | 830.14 | 40 | 2913 | 275.26 | 88 | 238 | 0 | 0 | 0 | 0
09:30 | 3592.5 | 2038.5 | 878 | 0 | 32 | 830.425 | 40 | 2951.5 | 282.855 | 73 | 236.5 | 0 | 0 | 0 | 0
10:00 | 3607 | 2146 | 901 | 0 | 34 | 830.71 | 40 | 2990 | 290.45 | 58 | 235 | 0 | 0 | 0 | 0
10:30 | 3437.5 | 2087.5 | 901 | 0 | 31 | 825.33 | 40 | 3103 | 299.39 | 42.5 | 289.5 | 0 | 0 | 0 | 0
11:00 | 3268 | 2029 | 901 | 0 | 28 | 819.95 | 40 | 3216 | 308.33 | 27 | 344 | 0 | 0 | 0 | 0
11:30 | 3199 | 1865.25 | 901 | 0 | 31 | 822.895 | 40 | 3078 | 400 | 13.5 | 311.5 | 0 | 0 | 0 | 0
12:00 | 3130 | 1701.5 | 901 | 0 | 34 | 825.84 | 40 | 2940 | 491.67 | 0 | 279 | 0 | 0 | 0 | 0
12:30 | 3231 | 1761 | 901.5 | 0 | 36 | 825.395 | 40 | 2871 | 395.81 | 0 | 303.2 | 0 | 0 | 3.5 | 0
13:00 | 3332 | 1820.5 | 902 | 0 | 38 | 824.95 | 40 | 2802 | 299.95 | 0 | 327.4 | 0 | 0 | 7 | 0
13:30 | 3315 | 1768.75 | 903 | 0 | 33 | 828.43 | 40 | 2748 | 303.275 | 8.5 | 266.7 | 0 | 0 | 9 | 0
14:00 | 3298 | 1717 | 904 | 0 | 28 | 831.91 | 40 | 2694 | 306.6 | 17 | 206 | 0 | 0 | 11 | 0
14:30 | 3300 | 1734.75 | 903.5 | 0 | 33 | 824.68 | 40 | 2674.5 | 277.075 | 62 | 243 | 0 | 0 | 13 | 0
15:00 | 3302 | 1752.5 | 903 | 0 | 38 | 817.45 | 40 | 2655 | 247.55 | 107 | 280 | 0 | 0 | 15 | 0
15:30 | 3273 | 1871 | 903.5 | 0 | 36 | 817.085 | 40 | 2603 | 226.25 | 111.5 | 325 | 0 | 0 | 16 | 0
16:00 | 3244 | 1989.5 | 904 | 0 | 34 | 816.72 | 40 | 2551 | 204.95 | 116 | 370 | 0 | 0 | 17 | 0
16:30 | 3166.5 | 1989 | 903.5 | 0 | 25 | 815.86 | 40 | 2601.5 | 164.855 | 116 | 384 | 0 | 0 | 12.5 | 11
17:00 | 3089 | 1988.5 | 903 | 0 | 16 | 815 | 40 | 2652 | 124.76 | 116 | 398 | 0 | 0 | 8 | 22
17:30 | 3189.5 | 2020.25 | 903 | 0 | 20 | 840.85 | 40 | 2685 | 70.9 | 129 | 441.5 | 0 | 0 | 4.5 | 11
18:00 | 3290 | 2052 | 903 | 0 | 24 | 866.7 | 40 | 2718 | 17.04 | 142 | 485 | 0 | 0 | 1 | 0
18:30 | 3323 | 2096 | 880 | 0 | 28 | 1043.94 | 40 | 2944 | 8.52 | 209 | 718 | 0 | 0 | 0.5 | 0
19:00 | 3356 | 2140 | 857 | 0 | 32 | 1221.18 | 40 | 3170 | 0 | 276 | 951 | 0 | 0 | 0 | 0
19:30 | 3372 | 2171.5 | 857 | 0 | 32 | 1215.5 | 40 | 3274 | 0 | 282 | 914 | 0 | 0 | 0 | 0
20:00 | 3430 | 2183.5 | 857 | 0 | 26 | 1206.64 | 40 | 3331 | 0 | 260 | 720 | 0 | 0 | 0 | 16
20:30 | 3449.5 | 2217 | 884.5 | 0 | 30 | 1212.82 | 40 | 3325.5 | 0 | 252 | 637 | 0 | 0 | 0 | 16.5
21:00 | 3469 | 2250.5 | 912 | 0 | 34 | 1219 | 40 | 3320 | 0 | 244 | 554 | 0 | 0 | 0 | 17
21:30 | 3502 | 2259 | 912 | 0 | 33 | 1193.5 | 40 | 3219.5 | 0 | 232.5 | 504.5 | 0 | 0 | 1.5 | 8.5
22:00 | 3535 | 2267.5 | 912 | 0 | 32 | 1168 | 40 | 3119 | 0 | 221 | 455 | 0 | 0 | 3 | 0
22:30 | 3533 | 2257.5 | 914.5 | 0 | 45 | 1118 | 40 | 3148.5 | 0 | 153 | 431.5 | 0 | 0 | 8 | 0
23:00 | 3531 | 2247.5 | 917 | 0 | 58 | 1068 | 40 | 3178 | 0 | 85 | 408 | 0 | 0 | 13 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 399 | 06:00 | 385 | 09:00 | Payra | 417 | 17:00 | 411 | 00:00
Ashuganj | 407 | 4:00 | 393 | 10:00 | Rahanpur | 417 | 11:00 | 403 | 00:00
Bhulta | 403 | 03:00 | 388 | 10:00 | Rampal | 408 | 15:00 | 393 | 00:00
Bibiana | 392 | 07:00 | 384 | 01:00
BIPTC | 402 | 19:30 | 393 | 13:00
Bogura | 410 | 05:00 | 393 | 00:00
Gopalganj | 405 | 05:00 | 392 | 00:00
Kaliakoir | 369 | 07:00 | 358 | 10:00
Madunaghat | 403 | 06:00 | 392 | 15:00
Meghnaghat | 400 | 07:00 | 389 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 233 | 04:00 | 223 | 10:00 | Keranigonj | 231 | 04:00 | 221 | 10:00
AKSML | 231 | 04:00 | 224 | 00:00 | Khulna(S) | 236 | 16:00 | 222 | 00:00
Aminbazar | 232 | 06:00 | 224 | 09:00 | Madunaghat | 233 | 04:00 | 227 | 10:00
Ashuganj | 234 | 08:00 | 227 | 10:00 | Madunaghat-400 | 234 | 14:00 | 228 | 00:00
Ashuganj-400 | 234 | 08:00 | 227 | 10:00 | Maniknagar | 229 | 05:00 | 220 | 10:00
Baghabari | 234 | 05:00 | 227 | 18:30 | Meghnaghat | 238 | 07:00 | 229 | 10:00
Barapukuria | 226 | 06:00 | 216 | 00:00 | Meghnaghat-400 | 232 | 04:00 | 224 | 10:00
Barapukuria-230 | 226 | 06:00 | 216 | 00:00 | Mirsorai | 230 | 14:00 | 221 | 10:00
Barishal | 238 | 17:00 | 229 | 00:00 | Rajshahi | 234 | 03:00 | 223 | 19:30
Bheramara | 235 | 02:00 | 224 | 20:00 | Rampal | 235 | 16:00 | 222 | 00:00
Bhulta | 230 | 04:00 | 220 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 03:00 | 221 | 00:00 | Rampura | 228 | 03:00 | 218 | 10:00
BIPTC | 236 | 02:00 | 224 | 19:30 | Shikalbaha | 231 | 13:00 | 222 | 10:00
Bogura | 231 | 08:00 | 221 | 00:00 | Shyampur | 233 | 11:00 | 222 | 10:00
Bogura-400 | 230 | 04:00 | 220 | 19:30 | Siddhirganj | 230 | 02:00 | 222 | 10:00
Borhanuddin | 243 | 15:00 | 237 | 00:00 | Sirajgonj | 240 | 04:00 | 235 | 00:00
BSRM | 230 | 15:00 | 220 | 10:00 | Sreepur | 232 | 03:00 | 226 | 00:00
Cumilla(N) | 230 | 13:00 | 219 | 10:00 | Tongi | 226 | 04:00 | 217 | 09:00
Faridpur | 232 | 15:00 | 223 | 00:00
Fenchuganj | 229 | 07:00 | 224 | 18:30
Ghorashal | 235 | 11:00 | 230 | 00:00
Ghorashal-230 | 229 | 04:00 | 219 | 10:00
Gopalganj | 232 | 04:00 | 225 | 00:00
GPH | 232 | 08:00 | 223 | 10:00
Haripur | 230 | 03:00 | 222 | 10:00
Hasnabad | 230 | 05:00 | 225 | 00:00
Hathazari | 233 | 13:00 | 227 | 00:00
Ishurdi | 236 | 02:00 | 227 | 18:30
Jhenaidah | 233 | 16:00 | 217 | 00:00
Kaliakoir | 231 | 04:00 | 221 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 04:00 | 127 | 10:00 | Madartek | 136 | 03:00 | 128 | 10:00
Agargaon | 138 | 04:00 | 130 | 11:00 | Madunaghat | 134 | 13:00 | 129 | 10:00
Agrabad | 134 | 01:00 | 127 | 10:00 | Magura | 138 | 15:00 | 127 | 12:00
AKS | 130 | 00:00 | 125 | 10:00 | Mahasthangarh | 134 | 08:00 | 125 | 19:30
Aminbazar | 131 | 06:00 | 125 | 09:00 | Manikganj | 132 | 11:00 | 122 | 09:00
Amnura | 135 | 02:00 | 129 | 00:00 | Maniknagar | 135 | 05:00 | 128 | 10:00
Ashuganj | 139 | 13:00 | 135 | 00:00 | Matarbari | 123 | 01:00 | 114 | 18:30
Bagerhat | 142 | 16:00 | 125 | 00:00 | Matuail | 134.5 | 13:00 | 128 | 10:00
Bajitpur | 134 | 17:00 | 128 | 14:00 | Millgate | 134 | 08:00 | 123 | 10:00
Bakulia | 136 | 02:00 | 129 | 10:00 | Mirpur | 131 | 04:00 | 123 | 11:00
Banani | 137 | 03:00 | 128 | 10:00 | Mirzapur | 133 | 11:00 | 124 | 14:00
Bangabhaban | 135 | 03:00 | 128 | 11:00 | Mithapukur | 134 | 06:00 | 123 | 01:00
Barapukuria | 139 | 06:00 | 129 | 00:00 | MI_Cement | 134.6 | 04:00 | 128 | 10:00
Barguna | 138 | 18:00 | 132 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 17:00 | 125 | 00:00 | Mogbazar | 137 | 05:00 | 129 | 11:00
Barishal-230 | 134 | 17:00 | 127 | 00:00 | Mongla | 142 | 16:00 | 127 | 00:00
Baroaulia | 135 | 11:00 | 131 | 21:00 | Motijheel | 135 | 03:00 | 128 | 11:00
Baroirhat | 137 | 13:00 | 118 | 10:00 | Muktagacha | 133 | 09:00 | 122 | 12:00
Bashundhara | 137 | 03:00 | 123 | 10:00 | Munshiganj | 133 | 13:00 | 127 | 11:00
BashundharaCement | 133 | 02:00 | 127 | 10:00 | Muradnagar | 136 | 13:00 | 124 | 10:00
Beanibazar | 132 | 06:00 | 129 | 18:30 | Mymensingh | 134 | 08:00 | 122 | 14:00
Benapole | 139 | 15:00 | 124 | 00:00 | Naogaon | 131 | 08:00 | 124 | 00:00
Bhaluka | 132 | 03:00 | 127 | 14:00 | Narail | 139 | 15:00 | 127 | 00:00
Bhandaria | 135 | 16:00 | 120 | 00:00 | Narinda | 135 | 05:00 | 128 | 10:00
Bhangura | 134 | 02:00 | 130 | 18:30 | Narshingdi | 132 | 12:00 | 123 | 10:00
Bheramara | 135 | 02:00 | 130 | 00:00 | Natore | 134 | 11:00 | 128 | 19:00
Bheramara(GK) | 136 | 15:00 | 130 | 00:00 | Nawabganj | 136 | 06:00 | 128 | 10:00
Bhulta | 130 | 12:00 | 124 | 11:00 | Netrakona | 129 | 16:00 | 122 | 12:00
Bog-Sherpur | 134 | 09:00 | 127 | 00:00 | New | 136 | 07:00 | 125 | 10:00
Bogura | 135 | 08:00 | 128 | 01:00 | Niamatpur | 138 | 11:00 | 133 | 00:00
Bogura-230 | 135 | 08:00 | 128 | 00:00 | Noapara | 141 | 15:00 | 128 | 00:00
Brahmanbaria | 134 | 13:00 | 128 | 11:00 | Pabna | 135 | 02:00 | 131 | 00:00
Cantonment | 138 | 04:00 | 131 | 10:00 | Palashbari | 133 | 08:00 | 121 | 19:00
Chandina | 135 | 13:00 | 125 | 10:00 | Panchagarh | 140 | 06:00 | 122 | 14:00
Chandpur | 138 | 13:00 | 120 | 10:00 | Patuakhali | 135 | 03:00 | 133 | 00:00
Chandraghona | 133 | 02:00 | 129 | 10:00 | Payra | 137 | 04:00 | 134 | 00:00
Chapai | 136 | 12:00 | 129 | 00:00 | PHP | 136 | 13:00 | 117 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 03:00 | 128 | 10:00 | Postogola | 136 | 04:00 | 130 | 10:00
Chauddagram | 133 | 13:00 | 117 | 10:00 | Purbachal | 137 | 02:00 | 129 | 10:00
Chhatak | 132 | 03:00 | 129 | 00:00 | Purbasadipur | 134 | 05:00 | 119 | 00:00
Chowmuhani | 136 | 13:00 | 115 | 00:00 | Rahanpur | 139 | 05:00 | 134 | 00:00
Chuadanga | 137 | 15:00 | 125 | 00:00 | Rahanpur-400 | 139 | 07:00 | 135 | 00:00
Coxsbazar | 122 | 05:00 | 115 | 11:00 | Rahim | 134 | 04:00 | 129 | 10:00
Cumilla(N) | 138 | 13:00 | 125 | 10:00 | Rajbari | 138 | 15:00 | 131 | 00:00
Cumilla(S) | 136 | 13:00 | 124 | 11:00 | Rajendrapur | 136 | 12:00 | 125 | 15:00
Daudkandi | 135 | 13:00 | 122 | 10:00 | Rajshahi | 134 | 04:00 | 128 | 18:30
Dhaka | 137 | 03:00 | 129 | 10:00 | Rajshahi-230 | 135 | 03:00 | 123 | 00:00
Dhamrai | 137 | 11:00 | 128 | 09:00 | Ramganj | 134 | 13:00 | 115 | 10:00
Dhanmondi | 135 | 04:00 | 130 | 10:00 | Rampur | 133 | 03:00 | 126 | 10:00
Dohazari | 132 | 18:00 | 123 | 11:00 | Rampura | 137 | 04:00 | 129 | 10:00
Faridpur | 138 | 15:00 | 133 | 00:00 | Rangamati | 134 | 17:00 | 128 | 10:00
Fatullah | 135 | 04:00 | 129 | 10:00 | Rangpur | 134 | 08:00 | 122 | 00:00
Fenchuganj | 138 | 17:00 | 134 | 18:30 | Ruppur | 137 | 03:00 | 133 | 18:30
Feni | 134 | 13:00 | 117 | 00:00 | Saidpur | 136 | 06:00 | 122 | 00:00
Ghatail | 130 | 09:00 | 122 | 14:00 | Satkhira | 142 | 16:00 | 126 | 00:00
Ghorashal | 137 | 00:00 | 132 | 10:00 | Satmasjid | 137 | 03:00 | 131 | 09:00
Goalpara | 142 | 16:00 | 128 | 00:00 | Savar | 132 | 19:00 | 123 | 10:00
Gollamari | 141 | 15:00 | 132 | 00:00 | SevenRings | 138 | 07:00 | 132 | 10:00
Gopalganj | 140 | 15:00 | 131 | 00:00 | ShahCement | 134 | 03:00 | 128 | 02:00
Gopalganj-400 | 139 | 15:00 | 133 | 00:00 | Shahjadpur | 138 | 03:00 | 134 | 19:00
Gulshan | 136 | 05:00 | 128 | 10:00 | Shahjibazar | 135 | 07:00 | 130 | 10:00
Halishahar | 140 | 15:00 | 126 | 10:00 | Shahmirpur | 135 | 08:00 | 129 | 12:00
Haripur | 134 | 03:00 | 129 | 10:00 | Shariatpur | 138 | 14:00 | 128 | 12:00
HaripurSBU | 134 | 03:00 | 129 | 10:00 | Sherpur | 138 | 08:00 | 121 | 14:00
Hasnabad | 137 | 07:00 | 130 | 09:00 | Shikalbaha | 125 | 02:00 | 118 | 10:00
Hathazari | 136 | 13:00 | 132 | 00:00 | Shikalbaha-230 | 136 | 04:00 | 129 | 10:00
Ishurdi | 138 | 02:00 | 133 | 19:30 | Shitalakhya | 134.8 | 04:00 | 128 | 10:00
Jaldhaka | 136 | 06:00 | 119 | 19:00 | Sholosohor | 133 | 04:00 | 128 | 10:00
Jamalpur | 138 | 08:00 | 122 | 12:00 | Shyampur | 135 | 07:00 | 127 | 11:00
Jashore | 139 | 15:00 | 126 | 00:00 | Shyampur-230 | 135 | 04:00 | 128 | 10:00
Jhenaidah | 140 | 15:00 | 128 | 00:00 | Siddhirganj | 135 | 13:00 | 129 | 10:00
Jhenaidah-230 | 138 | 15:00 | 129 | 00:00 | Sirajganj | 133 | 11:00 | 127 | 19:00
Joydebpur | 141 | 11:00 | 132 | 00:00 | Sonargaon | 134 | 13:00 | 128 | 00:00
Joypurhat | 131 | 08:00 | 121 | 00:00 | Sreemongol | 135 | 08:00 | 131 | 00:00
Juldah | 135 | 16:00 | 130 | 09:00 | Sreepur | 136 | 05:00 | 130 | 18:30
Kabirpur | 134 | 11:00 | 121 | 10:00 | Srinagar | 136 | 06:00 | 128 | 10:00
Kachua | 136 | 13:00 | 119 | 10:00 | SSM | 138 | 17:00 | 131 | 12:00
Kaliakoir | 139 | 07:00 | 127 | 14:00 | Sunamganj | 130 | 05:00 | 127 | 18:30
Kallyanpur | 132 | 18:30 | 127 | 00:00 | Sylhet | 134 | 08:00 | 131 | 00:00
Kalurghat | 134 | 07:00 | 129 | 10:00 | Sylhet-132 | 133 | 07:00 | 131 | 00:00
Kamrangirchar | 137 | 04:00 | 128 | 11:00 | Tangail | 132 | 11:00 | 124 | 14:00
Kaptai | 136 | 16:00 | 130 | 11:00 | Thakurgaon | 140 | 06:00 | 124 | 14:00
Kasba | 135 | 13:00 | 126 | 11:00 | TK | 135 | 14:00 | 129 | 10:00
Kazla | 135 | 03:00 | 128 | 11:00 | Tongi | 133 | 04:00 | 126 | 09:00
Keranigonj | 136 | 04:00 | 129 | 10:00 | Ullahpara | 135 | 11:00 | 130 | 00:00
Khagrachori | 134 | 17:00 | 126 | 12:00 | Ullon | 137 | 07:00 | 128 | 11:00
Khulna | 142 | 15:00 | 128 | 13:00 | Uttara | 131 | 03:00 | 125 | 10:00
Khulna(S) | 142 | 15:00 | 131 | 00:00 | UttaraNew | 132 | 06:00 | 123 | 11:00
Khulshi | 133 | 05:00 | 126 | 10:00 | Zigatola | 136 | 05:00 | 128 | 11:00
Kishoreganj | 133 | 15:00 | 126 | 14:00
Kodda | 135 | 11:00 | 121 | 10:00
KSRM | 133 | 05:00 | 128 | 10:00
Kulaura | 136 | 07:00 | 133 | 18:30
Kurigram | 132 | 05:00 | 119 | 18:30
Kushtia | 137 | 14:00 | 129 | 00:00
Lalbag | 136 | 05:00 | 127 | 11:00
Lalmonirhat | 132 | 07:00 | 119 | 19:00
Madanganj | 133 | 02:00 | 127 | 10:00
Madaripur | 138 | 17:00 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division