## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-04-2025 | during | 19-04-2025 | during | 19-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 366 | 330 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 380 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 264 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 198 | 78 | 208.13 | 208.13 | 105 | 105 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 176 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 95 | 145 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 15.5 | 30 | 30 | 22 | 22 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 22 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 17 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 10 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 450 | 400 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 35 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 1954 | 2023.5 | 5267.9 | 5331.9 | 3682.56 | 3746.56
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 16 | 0 | 16 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 137 | 151 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 56 | 80 | 56 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 28 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 24 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 27 | 0 | 7 | 22 | 7 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 4.78 | 0 | 4.78 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 655 | 790 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 19 | 0 | 7 | 15 | 7 | 15 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 360 | 494 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1270 | 1527 | 3401.5 | 3432.72 | 3401.5 | 3432.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 353 | 359 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 255 | 255 | 285 | 285 | 255 | 255 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 32 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 51 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 172 | 83 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 24 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 16 | 14 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 50 | 56 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20.83 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 105.3 | 105.3 | 105.3 | 105.3 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 37 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 16 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 79 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1118 | 1024 | 2157.62 | 2091.29 | 1982.85 | 1912.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-04-2025 | during | 19-04-2025 | during | 19-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 105 | 135 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 95 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 39.07 | 0 | 49 | 0 | 49 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 225.07 | 242 | 600.2 | 549 | 442.7 | 391.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 38 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 147 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 174 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 380 | 400 | 400 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1507 | 1526 | 1629 | 1629 | 1540 | 1540
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 915 | 868 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 102 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 385 | 408 | 617.1 | 617.1 | 617.1 | 617.1 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1402 | 1276 | 2975.1 | 2895.1 | 2460.11 | 2380.11
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 462 | 612 | 1260 | 1260 | 1190 | 1190 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 6 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 96 | 110 | 130 | 130 | 0 | 0 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 590 | 800 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 250 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.76 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1574.76 | 1998 | 3432.12 | 3431.12 | 3192.12 | 3191.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 201 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 135 | 200 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 200 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 350 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 103 | 103 | FGMO
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.26 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 823.21 | 902 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.96 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 44 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1689.43 | 1917 | 3111.53 | 2950.53 | 3048.74 | 2887.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 60 | 58 | 56 | 56 | 56 | 56 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 160 | 150 | 150 | 170 | 170 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.1 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 103 | 103 | FGMO
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 7 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 75 | 0 | 78.27 | 0 | 78.27 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 306.1 | 287 | 568.67 | 454 | 576.67 | 462
System Total |  |  |  |  | 27566.2 | 28535.742 | 11046.36 | 11820.5 | 23143.64 | 22764.66 | 20327.25 | 19944.6
Forecast Scenario (19-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11400 |  | 0 |  | 11400
|  |  |  | 1:00 | 10990 |  | 0 |  | 10990
|  |  |  | 2:00 | 10680 |  | 0 |  | 10680
|  |  |  | 3:00 | 10260 |  | 0 |  | 10260
|  |  |  | 4:00 | 9930 |  | 0 |  | 9930
|  |  |  | 5:00 | 9490 |  | 0 |  | 9490
|  |  |  | 6:00 | 9010 |  | 0 |  | 9010
|  |  |  | 7:00 | 9230 |  | 0 |  | 9230
|  |  |  | 8:00 | 9480 |  | 0 |  | 9480
|  |  |  | 9:00 | 9870 |  | 0 |  | 9870
|  |  |  | 10:00 | 10080 |  | 0 |  | 10080
|  |  |  | 11:00 | 10650 |  | 0 |  | 10650
|  |  |  | 12:00 | 10990 |  | 0 |  | 10990
|  |  |  | 13:00 | 11150 |  | 0 |  | 11150
|  |  |  | 14:00 | 11440 |  | 0 |  | 11440
|  |  |  | 15:00 | 11650 |  | 0 |  | 11650
|  |  |  | 16:00 | 11450 |  | 0 |  | 11450
|  |  |  | 17:00 | 11350 |  | 0 |  | 11350
|  |  |  | 18:00 | 11310 |  | 0 |  | 11310
|  |  |  | 18:30 | 12150 |  | 0 |  | 12150
|  |  |  | 19:00 | 12710 |  | 0 |  | 12710
|  |  |  | 19:30 | 12810 |  | 0 |  | 12810
|  |  |  | 20:00 | 12910 |  | 0 |  | 12910
|  |  |  | 21:00 | 13000 |  | 0 |  | 13000
|  |  |  | 22:00 | 12950 |  | 0 |  | 12950
|  |  |  | 23:00 | 12840 |  | 0 |  | 12840
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 10990.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 264.82 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:09 hrs on 19-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-04-2025 | [28 empty] | Date: | 18-04-2025 | [28 empty] | Date: | 18-04-2025 | [28 empty] | Date: | 18-04-2025 | [28 empty] | Date: | 18-04-2025 | [16 empty] | Date: | 18-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [16 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 36 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 280 | 400 | 0 | 0 | 0 | 266 | 103 | 0 | 0 | 35 | 19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 12 | 0 | 40 | 0 | 32 | 253 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 720 | 0 | 51 | 0 | 178 | 0 | 360 | 255 | 54 | 0 | 36 | 16 | 50 | 0 | 38 | 20 | 0 | 52 | 0 | 0 | 0 | 290 | 320 | 350 | 40 | 40 | 0 | 148 | 16 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 65 | 95 | 0 | 0 | 0 | 9 | 6069 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 154 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 167 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 8 | 108 | 220 | 0 | 730 | 650 | 0 | 5283 | 11352 | 81.76
01:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 21 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 272 | 400 | 0 | 0 | 0 | 265 | 103 | 0 | 0 | 17 | 17.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 0 | 40 | 0 | 31 | 254 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 178 | 0 | 358 | 255 | 54 | 0 | 36 | 16 | 50 | 0 | 13 | 20 | 0 | 58 | 0 | 0 | 0 | 285 | 320 | 349 | 37 | 40 | 0 | 148 | 16 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 45 | 85 | 0 | 0 | 0 | 12 | 5888.5 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 153 | 0 | 141 | 0 | 414 | 0 | 0 | 0 | 165 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 108 | 220 | 0 | 700 | 620 | 0 | 5028 | 10916.5 | 81.76
02:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 277 | 400 | 0 | 0 | 0 | 265 | 103 | 0 | 0 | 0 | 18.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 50 | 0 | 40 | 0 | 31 | 252 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 702 | 0 | 51 | 0 | 138 | 0 | 360 | 255 | 54 | 0 | 36 | 0 | 50 | 0 | 9 | 20 | 0 | 50 | 0 | 0 | 0 | 290 | 320 | 349 | 37 | 40 | 0 | 129 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 45 | 65 | 0 | 0 | 0 | 12 | 5698.5 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 151 | 0 | 131 | 0 | 414 | 0 | 0 | 0 | 162 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 88 | 180 | 0 | 606 | 580 | 0 | 4820 | 10518.5 | 81.76
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 294 | 400 | 0 | 0 | 0 | 265 | 37 | 0 | 0 | 0 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 22 | 50 | 0 | 40 | 0 | 32 | 252 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 704 | 0 | 10 | 0 | 78 | 0 | 359 | 255 | 22 | 0 | 36 | 0 | 50 | 0 | 9 | 20 | 0 | 56 | 0 | 0 | 0 | 295 | 320 | 347 | 37 | 40 | 0 | 128 | 16 | 0 | 41 | 30 | 0 | 18 | 174 | 0 | 45 | 65 | 0 | 0 | 0 | 12 | 5463.5 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 149 | 0 | 126 | 0 | 414 | 0 | 0 | 0 | 160 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 90 | 180 | 0 | 492 | 590 | 0 | 4672 | 10135.5 | 81.76
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 291 | 400 | 0 | 0 | 0 | 265 | 39 | 0 | 0 | 0 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22 | 40 | 0 | 40 | 0 | 34 | 255 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 700 | 0 | 10 | 0 | 78 | 0 | 358 | 255 | 10 | 0 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 54 | 0 | 0 | 0 | 300 | 320 | 311 | 37 | 40 | 0 | 129 | 16 | 0 | 41 | 30 | 0 | 18 | 174 | 0 | 45 | 65 | 0 | 0 | 0 | 12 | 5354.5 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 145 | 0 | 122 | 0 | 350 | 0 | 0 | 0 | 160 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 90 | 180 | 0 | 462 | 540 | 0 | 4513 | 9867.5 | 81.76
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 267 | 400 | 0 | 0 | 0 | 265 | 38 | 0 | 0 | 0 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 22 | 30 | 0 | 40 | 0 | 35 | 251 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 700 | 0 | 10 | 0 | 78 | 0 | 300 | 255 | 10 | 0 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 52 | 0 | 0 | 0 | 290 | 320 | 313 | 37 | 40 | 0 | 128 | 16 | 0 | 41 | 30 | 0 | 18 | 173 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 5234.5 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 143 | 0 | 118 | 0 | 300 | 0 | 0 | 0 | 162 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 90 | 180 | 0 | 462 | 540 | 0 | 4463 | 9697.5 | 81.76
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 270 | 320 | 0 | 0 | 0 | 0 | 39 | 0 | 1 | 0 | 14.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 22 | 30 | 0 | 40 | 0 | 35 | 252 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 700 | 0 | 10 | 0 | 78 | 0 | 300 | 255 | 10 | 0 | 36 | 0 | 50 | 0 | 0 | 20 | 0 | 50 | 0 | 2 | 0 | 275 | 320 | 313 | 37 | 40 | 0 | 129 | 16 | 0 | 41 | 30 | 0 | 18 | 173 | 0 | 45 | 55 | 0 | 0 | 1.43 | 12 | 4881.93 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.24 | 381 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.72 | 140 | 0 | 139 | 0 | 116 | 0 | 300 | 0 | 0 | 0 | 160 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 3.28 | 0.02 | 0 | 150 | 5 | 90 | 180 | 0 | 462 | 540 | 0 | 4469.26 | 9351.19 | 81.76
07:00 | 0 | 7 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 278 | 320 | 0 | 0 | 0 | 0 | 80 | 0 | 5 | 0 | 16.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 22 | 11 | 1 | 40 | 0 | 36 | 252 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 700 | 7 | 10 | 0 | 78 | 0 | 300 | 255 | 10 | 0 | 36 | 0 | 50 | 0 | 0 | 17 | 0 | 46 | 0 | 16 | 0 | 285 | 320 | 313 | 37 | 40 | 0 | 128 | 16 | 0 | 41 | 30 | 0 | 18 | 173 | 0 | 69 | 85 | 0 | 0 | 10.9 | 12 | 5085.4 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.94 | 383 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 6.29 | 140 | 0 | 130 | 0 | 110 | 0 | 250 | 0 | 0.51 | 0 | 161 | 58 | 0 | 4 | 0 | 0 | 0 | 1 | 22.44 | 0.18 | 0 | 150 | 6 | 90 | 180 | 0 | 463 | 540 | 0 | 4467.36 | 9552.76 | 81.76
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 257 | 320 | 0 | 0 | 0 | 0 | 80 | 0 | 16 | 0 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | 2 | 40 | 0 | 26 | 302 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 11 | 10 | 0 | 78 | 0 | 280 | 255 | 10 | 0 | 36 | 0 | 50 | 0 | 0 | 10 | 0 | 40 | 0 | 35 | 0 | 290 | 320 | 315 | 37 | 40 | 0 | 129 | 16 | 0 | 41 | 30 | 0 | 18 | 173 | 0 | 69 | 85 | 0 | 1 | 23.89 | 12 | 5117.89 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 381 | 0 | 816.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 21.83 | 140 | 0 | 136 | 0 | 113 | 0 | 250 | 0 | 2.12 | 0 | 161 | 59 | 0 | 6 | 0 | 0 | 0 | 1.4 | 45.58 | 0.34 | 0 | 150 | 5 | 88 | 180 | 0 | 461 | 540 | 0 | 4534.39 | 9652.28 | 81.76
09:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 286 | 270 | 0 | 0 | 0 | 0 | 82 | 0 | 24 | 0 | 16.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 0 | 3 | 40 | 0 | 25 | 303 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 655 | 13 | 10 | 0 | 78 | 0 | 280 | 255 | 10 | 0 | 36 | 0 | 70 | 0 | 0 | 12 | 0 | 46 | 0 | 53 | 0 | 295 | 320 | 325 | 39 | 40 | 0 | 129 | 16 | 0 | 10 | 20 | 0 | 18 | 174 | 0 | 69 | 85 | 0 | 1 | 37.03 | 12 | 5072.53 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 380 | 0 | 826.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 47.28 | 140 | 0 | 135 | 0 | 149 | 0 | 250 | 0 | 3.38 | 0 | 161 | 59 | 0 | 25 | 0 | 0 | 0 | 1.7 | 117 | 0.39 | 0 | 150 | 5 | 88 | 180 | 0 | 463 | 540 | 0 | 4711.67 | 9784.2 | 81.75
10:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 292 | 270 | 0 | 0 | 0 | 0 | 82 | 0 | 29 | 0 | 16.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 0 | 4 | 40 | 0 | 25 | 304 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 655 | 12 | 10 | 0 | 78 | 0 | 280 | 255 | 10 | 0 | 36 | 0 | 70 | 0 | 0 | 20 | 0 | 52 | 0 | 20 | 0 | 305 | 320 | 344 | 39 | 40 | 0 | 133 | 0 | 0 | 10 | 20 | 0 | 18 | 174 | 0 | 69 | 85 | 0 | 1 | 47.46 | 12 | 5078.96 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 381 | 0 | 813.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 52.45 | 140 | 0 | 135 | 0 | 191 | 0 | 250 | 0 | 4.53 | 0 | 163 | 59 | 0 | 18 | 0 | 0 | 0 | 1 | 118 | 0.6 | 0 | 150 | 5 | 88 | 180 | 0 | 460 | 540 | 0 | 4812.15 | 9891.11 | 81.75
11:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 17 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 300 | 360 | 0 | 0 | 0 | 0 | 137 | 0 | 25 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 0 | 27 | 305 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 655 | 7 | 10 | 0 | 78 | 0 | 320 | 255 | 13 | 0 | 31 | 9 | 70 | 4 | 0 | 12 | 0 | 58 | 0 | 13 | 0 | 310 | 320 | 405 | 39 | 39 | 0 | 143 | 16 | 0 | 10 | 20 | 0 | 18 | 174 | 0 | 68 | 85 | 0 | 1 | 51.4 | 12 | 5396.4 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 382 | 0 | 821.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 54.91 | 140 | 0 | 135 | 0 | 194 | 0 | 320 | 0 | 4.2 | 0 | 162 | 60 | 0 | 26 | 0 | 0 | 0 | 2.4 | 86 | 0.68 | 0 | 150 | 6 | 100 | 180 | 0 | 466 | 540 | 0 | 4869.21 | 10265.61 | 81.75
12:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 17 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 296 | 450 | 0 | 0 | 0 | 0 | 198 | 0 | 27 | 35 | 21 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 12 | 0 | 3 | 40 | 0 | 27 | 360 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 655 | 17 | 24 | 0 | 172 | 0 | 353 | 255 | 47 | 0 | 34 | 18 | 50 | 16 | 0 | 20 | 0 | 50 | 0 | 79 | 0 | 300 | 320 | 350 | 39 | 40 | 0 | 140 | 16 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 68 | 105 | 0 | 1 | 39.07 | 12 | 6074.07 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 385 | 0 | 823.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 51.96 | 140 | 0 | 135 | 0 | 140 | 0 | 350 | 0 | 5.26 | 0 | 161 | 60 | 0 | 7 | 0 | 0 | 0 | 3.1 | 75 | 0.76 | 0 | 200 | 6 | 96 | 220 | 0 | 462 | 590 | 0 | 4972.29 | 11046.36 | 81.74
13:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 254 | 450 | 0 | 0 | 0 | 0 | 197 | 0 | 22 | 82 | 19 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12 | 0 | 1 | 40 | 0 | 32 | 400 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 750 | 13 | 51 | 0 | 170 | 0 | 355 | 255 | 48 | 0 | 34 | 33 | 50 | 29 | 4 | 20 | 0 | 54 | 0 | 73 | 0 | 300 | 320 | 350 | 39 | 40 | 0 | 134 | 16 | 0 | 80 | 30 | 0 | 18 | 173 | 0 | 78 | 106 | 0 | 1 | 16.23 | 12 | 6247.23 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 380 | 0 | 916.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 35.21 | 170 | 0 | 178 | 0 | 140 | 0 | 350 | 0 | 3.7 | 0 | 163 | 60 | 0 | 9 | 0 | 0 | 0 | 4.7 | 89 | 0.09 | 0 | 247 | 7 | 90 | 220 | 0 | 463 | 710 | 0 | 5283.01 | 11530.24 | 81.74
14:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 300 | 0 | 0 | 0 | 0 | 79 | 0 | 28 | 70 | 11 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 12 | 0 | 1 | 40 | 0 | 25 | 371 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 650 | 18 | 10 | 0 | 107 | 0 | 300 | 255 | 48 | 0 | 33 | 34 | 50 | 29 | 9 | 18 | 0 | 52 | 0 | 64 | 0 | 290 | 320 | 386 | 38 | 40 | 0 | 131 | 16 | 0 | 41 | 30 | 0 | 18 | 174 | 0 | 66 | 106 | 0 | 1 | 19.18 | 12 | 5538.18 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 383 | 0 | 830.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 54.65 | 150 | 0 | 150 | 0 | 140 | 0 | 260 | 0 | 4.53 | 0 | 163 | 60 | 0 | 18 | 0 | 0 | 0 | 4.3 | 45 | 0.01 | 0 | 150 | 7 | 100 | 180 | 0 | 460 | 650 | 0 | 4863.08 | 10401.26 | 81.74
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0 | 4 | 0 | 0 | 0 | 300 | 279 | 350 | 0 | 0 | 0 | 0 | 204 | 0 | 24 | 70 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 21 | 372 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 650 | 13 | 10 | 0 | 107 | 0 | 300 | 255 | 49 | 0 | 33 | 33 | 50 | 32 | 9 | 0 | 0 | 54 | 0 | 16 | 0 | 305 | 320 | 350 | 38 | 39 | 0 | 134 | 16 | 0 | 41 | 30 | 0 | 18 | 175 | 0 | 59 | 107 | 0 | 1 | 22.62 | 12 | 5592.62 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 380 | 0 | 820.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 37.84 | 150 | 0 | 150 | 0 | 140 | 0 | 260 | 0 | 4.23 | 0 | 162 | 58 | 0 | 22 | 0 | 0 | 0 | 4.3 | 79 | 0.49 | 0 | 150 | 0 | 100 | 180 | 0 | 458 | 591 | 0 | 4696.82 | 10289.44 | 81.73
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 300 | 271 | 300 | 0 | 0 | 0 | 0 | 79 | 0 | 4 | 35 | 18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 12 | 0 | 1 | 40 | 0 | 21 | 370 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 650 | 9 | 10 | 0 | 80 | 0 | 280 | 255 | 46 | 0 | 33 | 0 | 50 | 0 | 9 | 8 | 0 | 60 | 0 | 1 | 0 | 295 | 320 | 302 | 38 | 39 | 0 | 129 | 16 | 0 | 10 | 30 | 0 | 18 | 175 | 0 | 65 | 107 | 0 | 1 | 11.88 | 12 | 5134.88 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 378 | 0 | 819.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 10.16 | 150 | 0 | 150 | 0 | 130 | 0 | 260 | 0 | 0.97 | 0 | 163 | 58 | 0 | 7 | 0 | 0 | 0 | 3.2 | 42 | 0.14 | 0 | 150 | 2 | 88 | 180 | 0 | 456 | 560 | 0 | 4561.16 | 9696.04 | 81.73
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 292 | 300 | 0 | 0 | 0 | 22 | 82 | 0 | 3 | 35 | 16 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 25 | 371 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 650 | 3 | 10 | 0 | 26 | 0 | 280 | 255 | 14 | 0 | 33 | 0 | 50 | 0 | 0 | 12 | 0 | 52 | 0 | 0 | 0 | 300 | 320 | 306 | 38 | 40 | 0 | 129 | 8 | 0 | 10 | 30 | 0 | 18 | 175 | 0 | 65 | 107 | 0 | 0 | 3.49 | 12 | 5030.49 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 380 | 0 | 832.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 5.74 | 130 | 0 | 140 | 0 | 130 | 0 | 260 | 0 | 0.48 | 0 | 163 | 58 | 0 | 10 | 0 | 0 | 0 | 1.9 | 23 | 0.07 | 0 | 150 | 4 | 100 | 180 | 0 | 465 | 560 | 0 | 4524.51 | 9555 | 81.73
18:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 295 | 300 | 0 | 0 | 0 | 26 | 141 | 0 | 0 | 42 | 14 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 20 | 4 | 0 | 40 | 0 | 25 | 371 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 695 | 0 | 10 | 0 | 26 | 0 | 280 | 255 | 11 | 0 | 34 | 0 | 50 | 0 | 0 | 12 | 0 | 48 | 0 | 1 | 0 | 300 | 320 | 310 | 38 | 40 | 0 | 133 | 8 | 0 | 10 | 30 | 0 | 18 | 174 | 0 | 65 | 125 | 0 | 0 | 0.66 | 12 | 5325.66 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 380 | 0 | 818.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.1 | 130 | 0 | 140 | 0 | 130 | 0 | 320 | 0 | 0.09 | 0 | 163 | 58 | 0 | 2 | 2 | 0 | 0 | 0.3 | 10 | 0 | 0 | 175 | 7 | 90 | 180 | 0 | 468 | 560 | 0 | 4556.93 | 9882.59 | 81.72
19:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 276 | 400 | 0 | 0 | 0 | 117 | 80 | 0 | 0 | 108 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 24 | 0 | 40 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 800 | 0 | 36 | 0 | 83 | 0 | 359 | 255 | 31 | 0 | 34 | 24 | 50 | 22 | 6 | 20 | 0 | 52 | 0 | 0 | 0 | 310 | 320 | 347 | 38 | 40 | 0 | 145 | 16 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 115 | 135 | 0 | 0 | 0 | 12 | 6326.5 | 874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 918.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 199 | 0 | 200 | 0 | 414 | 0 | 0 | 0 | 160 | 58 | 35 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 110 | 220 | 0 | 553 | 664 | 0 | 5260.65 | 11587.15 | 81.72
19:30 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 10 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 264 | 400 | 0 | 0 | 0 | 176 | 78 | 0 | 0 | 108 | 15.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 0 | 494 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 790 | 0 | 51 | 0 | 83 | 0 | 359 | 255 | 51 | 0 | 32 | 16 | 50 | 14 | 37 | 20 | 0 | 56 | 0 | 0 | 0 | 280 | 320 | 380 | 38 | 40 | 0 | 147 | 16 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 95 | 135 | 0 | 0 | 0 | 12 | 6342.5 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 200 | 0 | 200 | 0 | 414 | 0 | 0 | 0 | 160 | 58 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 110 | 220 | 0 | 612 | 800 | 0 | 5478 | 11820.5
20:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 15 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 300 | 450 | 0 | 0 | 0 | 328 | 40 | 0 | 0 | 90 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 83 | 0 | 359 | 255 | 49 | 0 | 32 | 16 | 50 | 0 | 36 | 20 | 0 | 66 | 0 | 0 | 0 | 290 | 320 | 382 | 38 | 40 | 0 | 141 | 16 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 75 | 135 | 22 | 0 | 0 | 12 | 6313 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 917.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 200 | 0 | 150 | 0 | 380 | 0 | 0 | 0 | 160 | 58 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 120 | 180 | 0 | 613 | 784 | 0 | 5368.7 | 11681.7 | 81.72
21:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 35 | 34 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 290 | 450 | 0 | 0 | 0 | 275 | 40 | 0 | 0 | 90 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 22 | 405 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 710 | 0 | 51 | 0 | 81 | 0 | 359 | 255 | 53 | 0 | 36 | 16 | 50 | 0 | 37 | 20 | 0 | 74 | 0 | 0 | 0 | 300 | 320 | 356 | 38 | 40 | 0 | 147 | 16 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 75 | 105 | 22 | 0 | 0 | 12 | 6296 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 909.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 200 | 0 | 182 | 0 | 414 | 0 | 0 | 0 | 162 | 59 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 0 | 220 | 0 | 610 | 814 | 0 | 5444.16 | 11740.16 | 81.71
22:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 35 | 65 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 290 | 450 | 0 | 0 | 0 | 277 | 100 | 0 | 0 | 70 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 28 | 404 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 81 | 0 | 359 | 255 | 51 | 0 | 36 | 16 | 50 | 0 | 18 | 20 | 0 | 76 | 0 | 0 | 0 | 300 | 320 | 356 | 39 | 40 | 0 | 150 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 55 | 105 | 22 | 0 | 0 | 12 | 6244 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 908.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 200 | 0 | 201 | 0 | 414 | 0 | 0 | 0 | 164 | 59 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 0 | 220 | 0 | 610 | 843 | 0 | 5493.26 | 11737.26 | 81.71
23:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 35 | 80 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 294 | 450 | 0 | 0 | 0 | 298 | 100 | 0 | 0 | 70 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 40 | 0 | 28 | 362 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 135 | 0 | 360 | 255 | 53 | 0 | 36 | 16 | 50 | 0 | 18 | 20 | 0 | 76 | 0 | 0 | 0 | 305 | 320 | 383 | 39 | 40 | 0 | 150 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 55 | 105 | 22 | 0 | 0 | 12 | 6354 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 863.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 200 | 0 | 202 | 0 | 407 | 0 | 0 | 0 | 164 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 6 | 0 | 220 | 0 | 615 | 800 | 0 | 5291.01 | 11645.01 | 81.71
Total KWH | 0 | 580800 | 270240 | 0 | 0 | 0 | 0 | 0 | 8355600 | 0 | 0 | 0 | 428400 | 376560 | 1491360 | 0 | 0 | 72854 | 0 | 0 | 0 | 8385500 | 6860189 | 9020000 | 0 | 0 | 0 | 2953410 | 2466000 | 0 | 212822 | 832800 | 369000 | 371160 | 0 | 0 | 0 | 0 | 0 | 0 | 151680 | 46752 | 0 | 0 | 454080 | 292800 | 21961 | 928800 | 0 | 645600 | 7963636.36 | 0 | 0 | 0 | 0 | 0 | 3428727 | 0 | 0 | 0 | 16636362 | 113805 | 701640 | 0 | 2358545 | 0 | 8206600 | 6256000 | 768960 | 0 | 844992 | 279360 | 1257110 | 164160 | 212520 | 398820 | 0 | 1316160 | 0 | 426127 | 0 | 7232000 | 7690100 | 8617000 | 906000 | 925680 | 0 | 3281891 | 329280 | 0 | 1290240 | 684480 | 0 | 437000 | 4590100 | 0 | 1575600 | 2289600 | 79680 | 10000 | 304630 | 298800 | 137463973.36 | 21964363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 568800 | 9469091 | 0 | 19526546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412650 | 0 | 349504 | 3953909 | 0 | 4004964 | 0 | 3880882 | 0 | 8137818 | 0 | 29940 | 0 | 3993000 | 1354909 | 77457 | 139195 | 154713 | 0 | 0 | 31634.76 | 743040 | 3645 | 0 | 4604000 | 150469 | 1989000 | 5054910 | 0 | 12529656 | 15832727.27 | 0 | 118956823.03 | 256420796.39

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11046.36 | MW | 12:00 Hr. | Energy Generated |  |  | 256.4208 |  | MKWHr.
| Day Peak Demand |  |  | 11046.36 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.229 |  | MKWHr.
| Evening Peak Generation |  |  | 11820.5 | MW | 19:30 Hr. | Energy Demand |  |  | 256.6498 |  | MKWHr.
| Evening Peak Demand |  |  | 11820.5 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.9 |  | °C
| Minimum Generation of the Day |  |  | 9351.19 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 928.44 |  | MMCFD
| Maximum Generation of the Day |  |  | 11820.5 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 4.976 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.7809 | 0 | 4.053 | 0 | 0 | 0.21282 | 0 | 0 | 43.0467 | Gas | 126.8833 | Gas | 411696951.19
| Chattogram Zone |  |  | 4.0743 | 24.6 | 0.79363 | 0 | 0.9288 | 0.13577 | 0 | 0.15168 | 30.6842 | Coal | 72.3834 | Coal | 432474772.6789
| Cumilla Zone |  |  | 20.7927 | 0 | 0.65604 | 0 | 0 | 0.42613 | 1.3162 | 0 | 23.191 | HFO | 9.8989 | HFO | 171429411.25
| Mymensingh Zone |  |  | 0.07968 | 0 | 4.164 | 0 | 0 | 0.31463 | 0 | 0 | 4.5583 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.9838 | Hydro | 0.9288 | Hydro | 92880
| Khulna Zone |  |  | 0 | 9.4691 | 0 | 0 | 0 | 0.5688 | 21.9644 | 0 | 32.0023 | Solar | 3.3678 | Solar | 54226569.6336
| Barishal Zone |  |  | 7.1944 | 32.9664 | 0 | 0 | 0 | 0.003645 | 0 | 0 | 40.1644 | Import | 42.8071 | Import | 203810910.17
| Rajshahi Zone |  |  | 19.9776 | 0 | 0 | 0 | 0 | 0.79209 | 19.5265 | 0 | 40.2962 | Wind | 0.15168 | Wind | 2220595.2
| Rangpur Zone |  |  | 0 | 5.3479 | 0.23217 | 0 | 0 | 0.91387 | 0 | 0 | 6.4939
| Total |  |  | 126.8833 | 72.3834 | 9.8989 | 0 | 0.9288 | 3.3678 | 42.8071 | 0.15168 | 256.4208
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 411696951.19 |  | Hydro | 92880
|  |  |  | Coal | 432474772.6789 |  | Solar | 54226569.6336
|  |  |  | HFO | 171429411.25 |  | Import | 203810910.17
|  |  |  | HSD | 0 |  | Wind | 2220595.2
[5 empty] | Total: | 127,59,52,090 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9644 | Peak Hr Flow | 868.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 12839727.37 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 19.5265 | Peak Hr Flow | 902.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 766 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.3162 | Peak Hr Flow | 56.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 964 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 42.8071 | Peak Hr Flow | 1826.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4287
|  |  |  | Chattogram |  | 0 |  | 1111
|  |  |  | Cumilla |  | 0 |  | 982
|  |  |  | Mymensingh |  | 0 |  | 1062
|  |  |  | Sylhet |  | 0 |  | 455
|  |  |  | Khulna |  | 0 |  | 1253
|  |  |  | Barishal |  | 0 |  | 283
|  |  |  | Rajshahi |  | 0 |  | 1174
|  |  |  | Rangpur |  | 0 |  | 740
|  |  |  | Total |  | 0 |  | 11347
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:43 | 17:41 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Project Work S/D Due to Tree
Trimming
| 09:44 | 17:42 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Project Work S/D Due to Tree
Trimming
| 12:00 |  | Day Peak Gen. 11046 MW
|  | 13:10 | BIPTC S/S 20D09C 20MVA HT is restored.
|  | 13:10 | BIPTC S/S 20D09C 20MVA LT is restored.
| 13:20 | 13:31 | Khagrachari-Rangamati 132kV Ckt-2 Tripped from Khagrachori 132/33kV end showing REL670
relays.
| 13:54 | 14:13 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Tripped from Patuakhali 132/33kV
end showing Distance Relay relays.
| 13:57 | 14:18 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Distance A | [7 empty] | 3.0MW load
|  |  | phase relays Due to Unknown | [7 empty] | interrup. Barishal
132/33kV end
|  | 14:18 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
| 14:40 | 14:49 | Candpur- Kachua 132kV Ckt-2 Tripped from Chandpur 132/33kV end showing Distance relay
relays Due to Kachua end CB not trip
| 14:44 |  | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to বামনা ৩৩ কে‌ভি ফিডা‌রের লোড
এবং সোর্স সাইডে‌র ডিএস ক্ষয় হ‌য়ে যাওয়া এবং পাওয়া‌র ক‌্যা‌বে‌লের হিট ষ্ক্রিংক পু‌ড়ে
যাওয়ায়
| 14:45 |  | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to বামনা ৩৩ কে‌ভি ফিডা‌রের লোড
এবং সোর্স সাইডে‌র ডিএস ক্ষয় হ‌য়ে যাওয়া এবং পাওয়া‌র ক‌্যা‌বে‌লের হিট ষ্ক্রিংক পু‌ড়ে
যাওয়ায়
|  | 14:46 | Cumilla(N)-Meghnaghat 230 kV Ckt-2 is restored.
|  | 14:50 | Barishal-Barishal(N) 132 kV Ckt-2 is restored.
| 15:35 | 17:08 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to OLTC Oil refilling
| 15:36 | 17:09 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to OLTC Oil refilling
| 15:46 | 16:51 | Mirpur 132/33kV S/S Reserve Bus Scheduled S/D
| 16:37 | 16:52 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing REF815 relays Due to 33KV Laksam REB | [7 empty] | 17.0MW load
|  |  | Feeder Fault | [7 empty] | interrup.
|  | 17:29 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT is restored.
|  | 17:34 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT is restored.
|  | 18:20 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
| 18:48 | 19:22 | Bakulia-MSML 132 kV Ckt-2 Tripped from Bakulia 132/33kV end showing Relay
trip-A,B,C. Relay TRip-3Ph. Z1- Fault relays.
| 19:30 |  | Peak generation 11820MW
|  | 21:32 | Joydebpur-Kodda B 132 kV Ckt-2 is restored.
|  | 21:36 | Joydebpur-Kodda B 132 kV Ckt-1 is restored.
| 06:00 |  | Minimum Generation is 9519 MW
| 06:27 | 07:43 | Kabirpur 132/33kV S/S Aux. X-former-1 HT Scheduled S/D
| 06:29 | 07:46 | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to High temperature maintenance by | [7 empty] | 50.0MW load
|  |  | DPBD-1 | [7 empty] | interrup.
| 06:30 | 07:45 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to High temoerature maintenance by | [7 empty] | 50.0MW load
|  |  | DPBS-1 | [7 empty] | interrup.
| 06:36 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 LT Scheduled S/D Due to Tendelta Test By RTS
| 06:42 |  | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 HT Scheduled S/D
| 07:12 |  | Naogaon 132/33kV S/S T-3 LT Scheduled S/D Due to Baludanga 33 KV feeder (NESCO) Bus DS
Emergency maintenance under Transformer-3 (425T).
| 07:13 |  | Naogaon 132/33kV S/S T-3 HT Scheduled S/D Due to Baludanga 33 KV feeder (NESCO) Bus DS
Emergency maintenance under Transformer-3 (425T).
| 07:18 |  | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Redhot maintenance by PBS.
| 07:18 |  | Naogaon 132/33kV S/S T-3 33kV BUS Scheduled S/D Due to Baludanga 33 KV feeder (NESCO) Bus
DS Emergency maintenance under Transformer-3 (425T).
| 07:18 |  | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Project Work S/D
| 07:19 |  | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT Project Work S/D
| 07:19 |  | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Redhot maintenance by PBS.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 330 | 8355600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8385500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 264 | 6860189 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 78 | 2466000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 176 | 2953410 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 0 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 1491360 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 72854 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 0 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15.5 | 369000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 371160 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 270240 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 376560 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 580800 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 212822 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 10 | 428400 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 9020000 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 832800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2023.5 | 43046695
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 113805 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 928800 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 151 | 3428727 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 28 | 46752 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 24 | 454080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 645600 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21961 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 292800 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 790 | 16636362 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 151680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 494 | 7963636.36 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1527 | 30684203.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 359 | 8206600 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 255 | 6256000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 32 | 844992 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 768960 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 83 | 2358545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 701640 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 0 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1257110 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 14 | 164160 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 56 | 1316160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 398820 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 212520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 16 | 279360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 426127 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1024 | 23190994
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 79680 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 135 | 2289600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 95 | 1575600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 304630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 298800 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 242 | 4558310
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 906000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 925680 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3281891 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 684480 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1290240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 174 | 4590100 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 437000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 329280 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7232000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 380 | 8617000 | Fgmo activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7690100 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1526 | 35983771
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 868 | 21964363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 568800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 408 | 9469091 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1276 | 32002254
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 612 | 12529656 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 6 | 150469 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 110 | 1989000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 800 | 15832727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5054910 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 4604000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3645 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1998 | 40164407.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 201 | 3953909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 200 | 4004964 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 200 | 3880882 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8137818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 902 | 19526546 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 349504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 412650 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1917 | 40296213
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1354909 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3993000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 154713 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 31634.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 77457 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 139195 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 743040 | -
Rangpur Area Total |  |  |  |  | 950 | 287 | 6493948.76
Eastern Grid Total |  |  |  |  | 16921.242 | 6342.5 | 137463973.36
Western Grid Total |  |  |  |  | 11614.5 | 5478 | 118956823.03
National Grid Total |  |  |  |  | 28535.742 | 11820.5 | 256420796.39
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7896.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3449.7 | MW
i) Dhaka area |  |  | 4286.69 |  | MW | i) Khulna area |  |  |  | 1252.7 | MW
ii) Chattogram area |  |  | 1111.3 |  | MW | ii) Barishal area |  |  |  | 283 | MW
iii) Cumilla area |  |  | 982 |  | MW | iii) Rajshahi area |  |  |  | 1174 | MW
iv) Mymensingh area |  |  | 1062 |  | MW | iv) Rangpur area |  |  |  | 740 | MW
v) Sylhet area |  |  | 455 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11346.69 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 59 | 19:30 | 133 | Patuakhali | 57.3 | 13:00
2 | AKSML | 120 | 07:00 | 68 | Jaldhaka | 62 | 19:00 | 134 | Payra | 24 | 21:00
3 | Aftabnagar | 30 | 12:00 | 69 | Jamalpur | 101 | 19:30 | 135 | Postogola | 42 | 12:00
4 | Agargaon | 101 | 13:00 | 70 | Jashore | 106 | 13:00 | 136 | Purbachal | 16 | 13:00
5 | Agrabad | 78 | 18:30 | 71 | Jhenaidah | 86 | 19:30 | 137 | Purbasadipur | 94 | 19:00
6 | Amnura | 31 | 19:00 | 72 | Joydebpur | 113 | 15:00 | 138 | Rahanpur | 20 | 00:00
7 | Ashuganj | 88 | 23:00 | 73 | Joypurhat | 52 | 00:00 | 139 | Rahim | 50 | 01:00
8 | BSRM | 205 | 12:00 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 60 | 19:00
9 | Bagerhat | 71 | 19:00 | 75 | KSRM | 8 | 13:00 | 141 | Rajendrapur | 106 | 19:30
10 | Bajitpur | 46 | 20:00 | 76 | Kabirpur | 214 | 16:00 | 142 | Rajshahi | 96 | 00:00
11 | Bakulia | 78 | 00:00 | 77 | Kachua | 61 | 22:00 | 143 | Rajshahi-230 | 70 | 13:00
12 | Banani | 28 | 12:00 | 78 | Kallyanpur | 102 | 13:00 | 144 | Ramganj | 106 | 14:00
13 | Bangabhaban | 4 | 11:00 | 79 | Kalurghat | 30 | 00:00 | 145 | Rampur | 39 | 00:00
14 | Barapukuria | 47 | 22:00 | 80 | Kamrangirchar | 52.95 | 01:00 | 146 | Rangamati | 16 | 18:30
15 | Barguna | 16 | 21:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 119 | 19:00
16 | Barishal | 111 | 13:00 | 82 | Kasba | 29 | 20:00 | 148 | Ruppur | 6.2 | 10:00
17 | Barishal-230 | 52 | 22:00 | 83 | Kazla | 96 | 12:00 | 149 | SSM | 11 | 01:00
18 | Baroaulia | 57 | 00:00 | 84 | Keranigonj | 66 | 13:00 | 150 | Saidpur | 78 | 12:00
19 | Baroirhat | 55 | 15:00 | 85 | Khagrachori | 22 | 21:00 | 151 | Satkhira | 94 | 21:00
20 | Bashundhara | 163 | 13:00 | 86 | Khulna | 75 | 13:00 | 152 | Satmasjid | 88 | 13:00
21 | BashundharaCement | 12 | 00:00 | 87 | Khulshi | 148 | 12:00 | 153 | Savar | 174 | 15:00
22 | Beanibazar | 58 | 19:00 | 88 | Kishoreganj | 116 | 19:00 | 154 | SevenRings | 14.57 | 20:00
23 | Benapole | 47 | 20:00 | 89 | Kodda | 269 | 16:00 | 155 | ShahCement | 25 | 02:00
24 | Bhaluka | 124 | 19:00 | 90 | Kulaura | 32 | 19:00 | 156 | Shahjadpur | 67 | 19:00
25 | Bhandaria | 39 | 23:00 | 91 | Kurigram | 56 | 19:00 | 157 | Shahjibazar | 102 | 21:00
26 | Bhangura | 26 | 20:00 | 92 | Kushtia | 102 | 19:00 | 158 | Shahmirpur | 46 | 01:00
27 | Bheramara(GK) | 42 | 19:30 | 93 | Lalbag | 58 | 00:00 | 159 | Shariatpur | 59 | 20:00
28 | Bhulta | 245 | 22:00 | 94 | Lalmonirhat | 50 | 19:00 | 160 | Sherpur | 118 | 19:00
29 | Bog-Sherpur | 60 | 19:00 | 95 | MI_Cement | 18 | 23:00 | 161 | Shikalbaha | 26 | 00:00
30 | Bogura | 134 | 22:00 | 96 | Madanganj | 39 | 00:00 | 162 | Shitalakhya | 54 | 13:00
31 | Borhanuddin | 66 | 23:00 | 97 | Madaripur | 80 | 12:00 | 163 | Sholosohor | 28 | 00:00
32 | Brahmanbaria | 110 | 19:00 | 98 | Madartek | 66.5 | 13:00 | 164 | Shyampur | 154 | 06:00
33 | Cantonment | 114 | 12:00 | 99 | Madunaghat | 48 | 12:00 | 165 | Siddhirganj | 105 | 12:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 48 | 19:00 | 166 | Sirajganj | 88 | 19:00
35 | Chandpur | 57 | 18:30 | 101 | Mahasthangarh | 58 | 00:00 | 167 | Sonargaon | 91 | 00:00
36 | Chandraghona | 30 | 19:00 | 102 | Manikganj | 114 | 19:00 | 168 | Sreemongol | 49 | 18:30
37 | Chapai | 51 | 00:00 | 103 | Maniknagar | 54 | 13:00 | 169 | Sreepur | 76 | 19:00
38 | Charsaidpur | 46 | 00:00 | 104 | Matarbari | 47 | 19:00 | 170 | Srinagar | 40.8 | 13:00
39 | Chauddagram | 59 | 19:00 | 105 | Matuail | 52 | 12:00 | 171 | Sunamganj | 47 | 22:00
40 | Chhatak | 29 | 19:30 | 106 | Millgate | 67 | 11:00 | 172 | Sylhet | 36 | 19:00
41 | Chowmuhani | 154 | 03:00 | 107 | Mirpur | 105 | 22:00 | 173 | Sylhet-132 | 88 | 17:00
42 | Chuadanga | 71 | 19:30 | 108 | Mirsorai | 3 | 09:00 | 174 | TK | 30.6 | 19:00
43 | Coxsbazar | 124 | 19:00 | 109 | Mirzapur | 42 | 19:30 | 175 | Tangail | 172 | 19:00
44 | Cumilla(N) | 129 | 12:00 | 110 | Mithapukur | 42 | 19:00 | 176 | Thakurgaon | 80 | 19:30
45 | Cumilla(S) | 127 | 23:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 105 | 23:00
46 | Daudkandi | 124 | 13:00 | 112 | Mogbazar | 86.4 | 15:00 | 178 | Ullahpara | 36 | 19:00
47 | Dhaka | 22 | 12:00 | 113 | Mongla | 36 | 08:00 | 179 | Ullon | 41 | 13:00
48 | Dhamrai | 110 | 20:00 | 114 | Motijheel | 27 | 12:00 | 180 | Uttara | 77 | 19:00
49 | Dhanmondi | 101 | 12:00 | 115 | Muktagacha | 30 | 19:00 | 181 | UttaraNew | 42 | 13:00
50 | Dohazari | 91 | 18:30 | 116 | Munshiganj | 92 | 22:00 | 182 | Zigatola | 80 | 13:00
51 | Faridpur | 124 | 21:00 | 117 | Muradnagar | 22 | 19:00
52 | Fatullah | 76 | 00:00 | 118 | Mymensingh | 184 | 19:00
53 | Fenchuganj | 26 | 18:00 | 119 | Naogaon | 103 | 00:00
54 | Feni | 81 | 22:00 | 120 | Narail | 48 | 19:30
55 | GPH | 79 | 11:00 | 121 | Narinda | 49 | 13:00
56 | Ghatail | 80 | 18:30 | 122 | Narshingdi | 160 | 21:00
57 | Ghorashal | 11 | 21:00 | 123 | Natore | 123 | 19:30
58 | Ghorashal-230 | 68 | 19:00 | 124 | Nawabganj | 47.2 | 21:00
59 | Goalpara | 32 | 13:00 | 125 | Netrakona | 123 | 19:00
60 | Gollamari | 66 | 13:00 | 126 | New | 60.8 | 12:00
61 | Gopalganj | 77.8 | 20:00 | 127 | Niamatpur | 74 | 00:00
62 | Gulshan | 76 | 12:00 | 128 | Noapara | 30 | 18:30
63 | Halishahar | 56 | 13:00 | 129 | PHP | 9 | 06:00
64 | HaripurSBU | 164 | 20:00 | 130 | Pabna | 100 | 19:30
65 | Hasnabad | 60 | 23:00 | 131 | Palashbari | 86 | 19:00
66 | Hathazari | 70 | 20:00 | 132 | Panchagarh | 45 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11352 | 0 |  | 11352
1:00 | 10916.5 | 32 |  | 10949.5
2:00 | 10518.5 | 31 |  | 10550.5
3:00 | 10135.5 | 29 |  | 10165.5
4:00 | 9867.5 | 27 |  | 9895.5
5:00 | 9697.5 | 27 |  | 9725.5
6:00 | 9351.19 | 25 |  | 9377.19
7:00 | 9552.76 | 58 |  | 9613.76
8:00 | 9652.28 | 0 |  | 9652.28
9:00 | 9784.2 | 0 |  | 9784.2
10:00 | 9891.11 | 0 |  | 9891.11
11:00 | 10265.61 | 0 |  | 10265.61
12:00 | 11046.36 | 0 |  | 11046.36
13:00 | 11530.24 | 0 |  | 11530.24
14:00 | 10401.26 | 0 |  | 10401.26
15:00 | 10289.44 | 0 |  | 10289.44
16:00 | 9696.04 | 0 |  | 9696.04
17:00 | 9555 | 0 |  | 9555
18:00 | 9882.59 | 0 |  | 9882.59
19:00 | 11587.15 | 0 |  | 11587.15
19:30 | 11820.5 | 0 |  | 11820.5
20:00 | 11681.7 | 0 |  | 11681.7
21:00 | 11740.16 | 0 |  | 11740.16
22:00 | 11737.26 | 0 |  | 11737.26
23:00 | 11645.01 | 0 |  | 11645.01
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6069 | 5283 | 11352 | DAILY GENERATION CURVE
00:30 | 5978.75 | 5155.5 | 11134.25
01:00 | 5888.5 | 5028 | 10916.5 | 18-04-2025
01:30 | 5793.5 | 4924 | 10717.5
02:00 | 5698.5 | 4820 | 10518.5
02:30 | 5581 | 4746 | 10327
03:00 | 5463.5 | 4672 | 10135.5
03:30 | 5409 | 4592.5 | 10001.5
04:00 | 5354.5 | 4513 | 9867.5
04:30 | 5294.5 | 4488 | 9782.5
05:00 | 5234.5 | 4463 | 9697.5
05:30 | 5058.215 | 4466.13 | 9524.345
06:00 | 4881.93 | 4469.26 | 9351.19
06:30 | 4983.665 | 4468.31 | 9451.975
07:00 | 5085.4 | 4467.36 | 9552.76
07:30 | 5101.645 | 4500.875 | 9602.52
08:00 | 5117.89 | 4534.39 | 9652.28
08:30 | 5095.21 | 4623.03 | 9718.24
09:00 | 5072.53 | 4711.67 | 9784.2
09:30 | 5075.745 | 4761.91 | 9837.655
10:00 | 5078.96 | 4812.15 | 9891.11
10:30 | 5237.68 | 4840.68 | 10078.36
11:00 | 5396.4 | 4869.21 | 10265.61
11:30 | 5735.235 | 4920.75 | 10655.985
12:00 | 6074.07 | 4972.29 | 11046.36
12:30 | 6160.65 | 5127.65 | 11288.3
13:00 | 6247.23 | 5283.01 | 11530.24
13:30 | 5892.705 | 5073.045 | 10965.75
14:00 | 5538.18 | 4863.08 | 10401.26
14:30 | 5565.4 | 4779.95 | 10345.35
15:00 | 5592.62 | 4696.82 | 10289.44
15:30 | 5363.75 | 4628.99 | 9992.74
16:00 | 5134.88 | 4561.16 | 9696.04
16:30 | 5082.685 | 4542.835 | 9625.52
17:00 | 5030.49 | 4524.51 | 9555
17:30 | 5178.075 | 4540.72 | 9718.795
18:00 | 5325.66 | 4556.93 | 9882.59
18:30 | 5826.08 | 4908.79 | 10734.87
19:00 | 6326.5 | 5260.65 | 11587.15
19:30 | 6342.5 | 5478 | 11820.5
20:00 | 6313 | 5368.7 | 11681.7
20:30 | 6304.5 | 5406.43 | 11710.93 |  | Executive Engineer
21:00 | 6296 | 5444.16 | 11740.16 |  | Network Operation Division
21:30 | 6270 | 5468.71 | 11738.71
22:00 | 6244 | 5493.26 | 11737.26
22:30 | 6299 | 5392.135 | 11691.135
23:00 | 6354 | 5291.01 | 11645.01

## En-Curve
QF-LDC-12
Date | 18-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3522 | 2234 | 916 | 0 | 52 | 980 | 40 | 3134 | 0 | 70 | 404 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3512.5 | 2226.25 | 915.5 | 0 | 55 | 903.5 | 40 | 3079 | 0 | 52 | 350.5 | 0 | 0 | 0 | 16 | 18-04-2025
01:00 | 3503 | 2218.5 | 915 | 0 | 58 | 827 | 40 | 3024 | 0 | 34 | 297 | 0 | 0 | 0 | 32
01:30 | 3488 | 2139.5 | 915.5 | 0 | 54 | 823.5 | 40 | 2959.5 | 0 | 25.5 | 272 | 0 | 0 | 0 | 31.5 | Energy Generated | 256.4208 |  | MKWHr
02:00 | 3473 | 2060.5 | 916 | 0 | 50 | 820 | 40 | 2895 | 0 | 17 | 247 | 0 | 0 | 0 | 31 | Energy not Served | 0.229 |  | MKWHr
02:30 | 3422 | 1982 | 915.5 | 0 | 53 | 822.5 | 40 | 2838.5 | 0 | 8.5 | 243 | 0 | 0 | 2 | 30 | Total Energy Requirement | 256.6498 |  | MKWHr
03:00 | 3371 | 1903.5 | 915 | 0 | 56 | 825 | 40 | 2782 | 0 | 0 | 239 | 0 | 0 | 4 | 29
03:30 | 3318 | 1874.5 | 915.5 | 0 | 55 | 819.5 | 40 | 2743.5 | 0 | 0 | 229 | 0 | 0 | 6.5 | 28
04:00 | 3265 | 1845.5 | 916 | 0 | 54 | 814 | 40 | 2705 | 0 | 0 | 219 | 0 | 0 | 9 | 27
04:30 | 3206.5 | 1828 | 916 | 0 | 53 | 816.5 | 40 | 2704 | 0 | 0 | 208.5 | 0 | 0 | 10 | 27
05:00 | 3148 | 1810.5 | 916 | 0 | 52 | 819 | 40 | 2703 | 0 | 0 | 198 | 0 | 0 | 11 | 27
05:30 | 3012.5 | 1764.5 | 915.5 | 0 | 51 | 822.5 | 40 | 2703 | 5.845 | 0 | 198 | 0 | 0 | 11.5 | 26
06:00 | 2877 | 1718.5 | 915 | 0 | 50 | 826 | 40 | 2703 | 11.69 | 0 | 198 | 0 | 0 | 12 | 25
06:30 | 2866 | 1727.5 | 916 | 0 | 48 | 825.5 | 40 | 2705 | 57.975 | 48.5 | 207 | 0 | 0 | 10.5 | 41.5
07:00 | 2855 | 1736.5 | 917 | 0 | 46 | 825 | 40 | 2707 | 104.26 | 97 | 216 | 0 | 0 | 9 | 58
07:30 | 2849.5 | 1719.75 | 892.5 | 0 | 43 | 820.56 | 40 | 2730.5 | 189.71 | 102 | 210.5 | 0 | 0 | 4.5 | 29
08:00 | 2844 | 1703 | 868 | 0 | 40 | 816.12 | 40 | 2754 | 275.16 | 107 | 205 | 0 | 0 | 0 | 0
08:30 | 2873.5 | 1680.25 | 867.5 | 0 | 43 | 821.52 | 40 | 2732.5 | 361.97 | 94.5 | 200 | 0 | 0 | 3.5 | 0
09:00 | 2903 | 1657.5 | 867 | 0 | 46 | 826.92 | 40 | 2711 | 448.78 | 82 | 195 | 0 | 0 | 7 | 0
09:30 | 2926.5 | 1663.5 | 891 | 0 | 49 | 820.245 | 40 | 2711.5 | 451.91 | 82 | 195 | 0 | 0 | 7 | 0
10:00 | 2950 | 1669.5 | 915 | 0 | 52 | 813.57 | 40 | 2712 | 455.04 | 82 | 195 | 0 | 0 | 7 | 0
10:30 | 3079.5 | 1733.25 | 915.5 | 0 | 55 | 817.295 | 40 | 2716 | 425.815 | 82 | 201 | 0 | 0 | 13 | 0
11:00 | 3209 | 1797 | 916 | 0 | 58 | 821.02 | 40 | 2720 | 396.59 | 82 | 207 | 0 | 0 | 19 | 0
11:30 | 3217 | 2015.5 | 915.5 | 0 | 54 | 822.115 | 40 | 2796.5 | 425.87 | 123 | 227.5 | 0 | 0 | 19 | 0
12:00 | 3225 | 2234 | 915 | 0 | 50 | 823.21 | 40 | 2873 | 455.15 | 164 | 248 | 0 | 0 | 19 | 0
12:30 | 3255.5 | 2221 | 915.5 | 0 | 52 | 869.76 | 40 | 3023 | 427.04 | 202 | 269.5 | 0 | 0 | 13 | 0
13:00 | 3286 | 2208 | 916 | 0 | 54 | 916.31 | 40 | 3173 | 398.93 | 240 | 291 | 0 | 0 | 7 | 0
13:30 | 3147 | 1996.5 | 916 | 0 | 53 | 873.45 | 40 | 3030 | 396.8 | 216.5 | 288 | 0 | 0 | 8.5 | 0
14:00 | 3008 | 1785 | 916 | 0 | 52 | 830.59 | 40 | 2887 | 394.67 | 193 | 285 | 0 | 0 | 10 | 0
14:30 | 3061.5 | 1795.5 | 915.5 | 0 | 53 | 825.775 | 40 | 2854 | 326.575 | 186 | 276.5 | 0 | 0 | 11 | 0
15:00 | 3115 | 1806 | 915 | 0 | 54 | 820.96 | 40 | 2821 | 258.48 | 179 | 268 | 0 | 0 | 12 | 0
15:30 | 2994.5 | 1753.5 | 915.5 | 0 | 57 | 820.325 | 40 | 2803 | 193.415 | 159.5 | 244.5 | 0 | 0 | 11.5 | 0
16:00 | 2874 | 1701 | 916 | 0 | 60 | 819.69 | 40 | 2785 | 128.35 | 140 | 221 | 0 | 0 | 11 | 0
16:30 | 2865 | 1671 | 915.5 | 0 | 56 | 826.005 | 40 | 2791 | 97.515 | 140 | 217 | 0 | 0 | 6.5 | 0
17:00 | 2856 | 1641 | 915 | 0 | 52 | 832.32 | 40 | 2797 | 66.68 | 140 | 213 | 0 | 0 | 2 | 0
17:30 | 2930.5 | 1644.5 | 915 | 0 | 50 | 825.38 | 40 | 2833.5 | 44.415 | 204.5 | 229 | 0 | 0 | 2 | 0
18:00 | 3005 | 1648 | 915 | 0 | 48 | 818.44 | 40 | 2870 | 22.15 | 269 | 245 | 0 | 0 | 2 | 0
18:30 | 3213.5 | 1847.25 | 894.5 | 0 | 50 | 868.545 | 40 | 3131.5 | 11.075 | 325.5 | 352 | 0 | 0 | 1 | 0
19:00 | 3422 | 2046.5 | 874 | 0 | 52 | 918.65 | 40 | 3393 | 0 | 382 | 459 | 0 | 0 | 0 | 0
19:30 | 3556 | 2038.5 | 868 | 0 | 56 | 902 | 40 | 3572 | 0 | 376 | 412 | 0 | 0 | 0 | 0
20:00 | 3629 | 2100 | 868 | 0 | 66 | 917.7 | 40 | 3373 | 0 | 330 | 358 | 0 | 0 | 0 | 0
20:30 | 3575 | 2129.5 | 891.5 | 0 | 70 | 913.43 | 40 | 3424 | 0 | 314.5 | 353 | 0 | 0 | 0 | 0
21:00 | 3521 | 2159 | 915 | 0 | 74 | 909.16 | 40 | 3475 | 0 | 299 | 348 | 0 | 0 | 0 | 0
21:30 | 3553.5 | 2163 | 915 | 0 | 75 | 908.71 | 40 | 3484.5 | 0 | 255 | 344 | 0 | 0 | 0 | 0
22:00 | 3586 | 2167 | 915 | 0 | 76 | 908.26 | 40 | 3494 | 0 | 211 | 340 | 0 | 0 | 0 | 0
22:30 | 3607.5 | 2218 | 915.5 | 0 | 76 | 885.635 | 40 | 3415 | 0 | 189 | 344.5 | 0 | 0 | 0 | 0
23:00 | 3629 | 2269 | 916 | 0 | 76 | 863.01 | 40 | 3336 | 0 | 167 | 349 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 401 | 05:00 | 389 | 11:00 | Payra | 417 | 05:00 | 413 | 21:00
Ashuganj | 411 | 18:00 | 394 | 11:00 | Rahanpur | 416 | 05:00 | 409 | 00:00
Bhulta | 406 | 05:00 | 392 | 11:00 | Rampal | 409 | 05:00 | 397 | 22:00
Bibiana | 393 | 05:00 | 383 | 11:00
BIPTC | 403 | 05:00 | 397 | 12:00
Bogura | 410 | 06:00 | 401 | 00:00
Gopalganj | 408 | 06:00 | 397 | 13:00
Kaliakoir | 376 | 19:00 | 360 | 11:00
Madunaghat | 405 | 07:00 | 398 | 13:00
Meghnaghat | 402 | 05:00 | 392 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 235 | 08:00 | 226 | 13:00 | Keranigonj | 233 | 08:00 | 224 | 13:00
AKSML | 234 | 08:00 | 225 | 23:00 | Khulna(S) | 236 | 05:00 | 227 | 12:00
Aminbazar | 234 | 06:00 | 228 | 11:00 | Madunaghat | 234 | 07:00 | 228 | 10:00
Ashuganj | 235 | 04:00 | 227 | 13:00 | Madunaghat-400 | 234 | 06:00 | 229 | 00:00
Ashuganj-400 | 235 | 04:00 | 227 | 13:00 | Maniknagar | 231 | 04:00 | 221 | 13:00
Baghabari | 235 | 05:00 | 227 | 18:30 | Meghnaghat | 237 | 03:00 | 233 | 00:00
Barapukuria | 225 | 06:00 | 218 | 19:00 | Meghnaghat-400 | 233 | 05:00 | 227 | 11:00
Barapukuria-230 | 225 | 06:00 | 218 | 19:00 | Mirsorai | 231 | 08:00 | 223 | 13:00
Barishal | 241 | 05:00 | 232 | 13:00 | Rajshahi | 234 | 06:00 | 222 | 13:00
Bheramara | 233 | 05:00 | 223 | 13:00 | Rampal | 235 | 05:00 | 225 | 13:00
Bhulta | 231 | 04:00 | 223 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 18:30 | 221 | 11:00 | Rampura | 230 | 05:00 | 222 | 11:00
BIPTC | 235 | 05:00 | 222 | 13:00 | Shikalbaha | 231 | 06:00 | 224 | 22:00
Bogura | 231 | 05:00 | 225 | 00:00 | Shyampur | 233 | 20:00 | 221 | 04:00
Bogura-400 | 230 | 06:00 | 199 | 02:00 | Siddhirganj | 233 | 08:00 | 225 | 11:00
Borhanuddin | 243 | 04:00 | 238 | 13:00 | Sirajgonj | 240 | 05:00 | 235 | 21:00
BSRM | 231 | 08:00 | 223 | 12:00 | Sreepur | 232 | 01:00 | 226 | 21:00
Cumilla(N) | 229 | 06:00 | 219 | 11:00 | Tongi | 228 | 05:00 | 218 | 11:00
Faridpur | 234 | 04:00 | 226 | 22:00
Fenchuganj | 229 | 20:00 | 223 | 01:00
Ghorashal | 235 | 01:00 | 230 | 00:00
Ghorashal-230 | 230 | 05:00 | 222 | 11:00
Gopalganj | 234 | 04:00 | 227 | 21:00
GPH | 232 | 08:00 | 226 | 00:00
Haripur | 231 | 05:00 | 224 | 11:00
Hasnabad | 232 | 06:00 | 226 | 15:00
Hathazari | 233 | 06:00 | 226 | 23:00
Ishurdi | 236 | 05:00 | 226 | 13:00
Jhenaidah | 233 | 05:00 | 220 | 13:00
Kaliakoir | 232 | 06:00 | 224 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 06:00 | 131 | 11:00 | Madartek | 138 | 05:00 | 132 | 11:00
Agargaon | 139 | 05:00 | 133 | 12:00 | Madunaghat | 135 | 07:00 | 130 | 01:00
Agrabad | 134 | 19:30 | 128 | 22:00 | Magura | 136 | 06:00 | 127 | 13:00
AKS | 132 | 19:00 | 127 | 12:00 | Mahasthangarh | 133 | 05:00 | 127 | 19:00
Aminbazar | 133 | 05:00 | 129 | 11:00 | Manikganj | 129 | 18:00 | 121 | 11:00
Amnura | 136 | 04:00 | 128 | 21:00 | Maniknagar | 136 | 05:00 | 131 | 11:00
Ashuganj | 140 | 05:00 | 135 | 10:00 | Matarbari | 122 | 12:00 | 113 | 00:00
Bagerhat | 139 | 05:00 | 126 | 21:00 | Matuail | 135.5 | 08:00 | 121 | 13:00
Bajitpur | 135 | 06:00 | 129 | 11:00 | Millgate | 134 | 05:00 | 125 | 12:00
Bakulia | 135 | 18:30 | 129 | 23:00 | Mirpur | 133 | 08:00 | 128 | 11:00
Banani | 138 | 05:00 | 131 | 12:00 | Mirzapur | 130 | 07:00 | 124 | 11:00
Bangabhaban | 137 | 04:00 | 131 | 11:00 | Mithapukur | 133 | 05:00 | 125 | 19:00
Barapukuria | 137 | 06:00 | 131 | 13:00 | MI_Cement | 135 | 05:00 | 130 | 12:00
Barguna | 137 | 04:00 | 134 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 05:00 | 128 | 12:00 | Mogbazar | 140 | 08:00 | 133 | 11:00
Barishal-230 | 135 | 04:00 | 129 | 13:00 | Mongla | 136 | 07:00 | 128 | 19:30
Baroaulia | 133 | 04:00 | 129 | 13:00 | Motijheel | 137 | 04:00 | 131 | 11:00
Baroirhat | 131 | 17:00 | 120 | 13:00 | Muktagacha | 132 | 18:30 | 128 | 06:00
Bashundhara | 139 | 05:00 | 125 | 12:00 | Munshiganj | 134 | 07:00 | 129 | 12:00
BashundharaCement | 134 | 08:00 | 130 | 11:00 | Muradnagar | 130 | 06:00 | 124 | 13:00
Beanibazar | 132 | 04:00 | 130 | 18:30 | Mymensingh | 134 | 20:00 | 122 | 11:00
Benapole | 136 | 05:00 | 125 | 13:00 | Naogaon | 131 | 05:00 | 126 | 00:00
Bhaluka | 133 | 07:00 | 126 | 11:00 | Narail | 136 | 05:00 | 127 | 13:00
Bhandaria | 132 | 04:00 | 121 | 12:00 | Narinda | 136 | 05:00 | 131 | 11:00
Bhangura | 134 | 04:00 | 130 | 19:30 | Narshingdi | 132 | 07:00 | 123 | 22:00
Bheramara | 136 | 05:00 | 123 | 15:00 | Natore | 134 | 06:00 | 128 | 21:00
Bheramara(GK) | 136 | 05:00 | 130 | 12:00 | Nawabganj | 137 | 07:00 | 130 | 13:00
Bhulta | 129 | 06:00 | 125 | 12:00 | Netrakona | 131 | 05:00 | 120 | 12:00
Bog-Sherpur | 133 | 04:00 | 128 | 19:00 | New | 135 | 07:00 | 127 | 11:00
Bogura | 135 | 06:00 | 130 | 00:00 | Niamatpur | 138 | 05:00 | 135 | 00:00
Bogura-230 | 134 | 05:00 | 130 | 00:00 | Noapara | 137 | 06:00 | 129 | 21:00
Brahmanbaria | 132 | 03:00 | 127 | 22:00 | Pabna | 136 | 04:00 | 130 | 19:00
Cantonment | 139 | 05:00 | 133 | 11:00 | Palashbari | 131 | 03:00 | 123 | 19:00
Chandina | 133 | 17:00 | 120 | 02:00 | Panchagarh | 135 | 04:00 | 125 | 13:00
Chandpur | 128 | 16:00 | 116 | 13:00 | Patuakhali | 136 | 03:00 | 134 | 13:00
Chandraghona | 135 | 19:30 | 130 | 22:00 | Payra | 137 | 02:00 | 136 | 00:00
Chapai | 135 | 04:00 | 133 | 00:00 | PHP | 130 | 17:00 | 118 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 05:00 | 130 | 11:00 | Postogola | 138 | 08:00 | 132 | 11:00
Chauddagram | 131 | 17:00 | 120 | 10:00 | Purbachal | 139 | 07:00 | 131 | 13:00
Chhatak | 132 | 05:00 | 128 | 20:00 | Purbasadipur | 130 | 02:00 | 122 | 13:00
Chowmuhani | 128 | 17:00 | 115 | 13:00 | Rahanpur | 139 | 05:00 | 136 | 00:00
Chuadanga | 137 | 05:00 | 127 | 21:00 | Rahanpur-400 | 139 | 04:00 | 137 | 00:00
Coxsbazar | 122 | 10:00 | 111 | 22:00 | Rahim | 135 | 07:00 | 129 | 22:00
Cumilla(N) | 132 | 05:00 | 125 | 12:00 | Rajbari | 139 | 05:00 | 133 | 13:00
Cumilla(S) | 131 | 00:00 | 123 | 11:00 | Rajendrapur | 134 | 05:00 | 121 | 12:00
Daudkandi | 129 | 06:00 | 123 | 12:00 | Rajshahi | 135 | 04:00 | 129 | 19:00
Dhaka | 138 | 05:00 | 132 | 11:00 | Rajshahi-230 | 135 | 05:00 | 127 | 13:00
Dhamrai | 137 | 04:00 | 131 | 11:00 | Ramganj | 127 | 16:00 | 112 | 13:00
Dhanmondi | 139 | 05:00 | 131.5 | 11:00 | Rampur | 134 | 19:00 | 128 | 22:00
Dohazari | 131 | 08:00 | 123 | 22:00 | Rampura | 138 | 04:00 | 132 | 11:00
Faridpur | 139 | 04:00 | 134 | 13:00 | Rangamati | 134 | 05:00 | 128 | 23:00
Fatullah | 136 | 07:00 | 131 | 11:00 | Rangpur | 130 | 04:00 | 122 | 19:00
Fenchuganj | 136 | 03:00 | 134 | 02:00 | Ruppur | 138 | 04:00 | 133 | 11:00
Feni | 128 | 17:00 | 120 | 13:00 | Saidpur | 131 | 04:00 | 124 | 19:00
Ghatail | 129 | 07:00 | 125 | 11:00 | Satkhira | 138 | 05:00 | 127 | 21:00
Ghorashal | 140 | 08:00 | 134 | 10:00 | Satmasjid | 139 | 07:00 | 131 | 13:00
Goalpara | 140 | 05:00 | 131 | 20:00 | Savar | 132 | 07:00 | 126 | 21:00
Gollamari | 139 | 06:00 | 132 | 20:00 | SevenRings | 140 | 07:00 | 133 | 13:00
Gopalganj | 139 | 05:00 | 133 | 19:00 | ShahCement | 135 | 06:00 | 130 | 11:00
Gopalganj-400 | 140 | 05:00 | 135 | 22:00 | Shahjadpur | 138 | 10:00 | 133 | 22:00
Gulshan | 138 | 05:00 | 132 | 11:00 | Shahjibazar | 133 | 01:00 | 129 | 14:00
Halishahar | 134 | 20:00 | 128 | 23:00 | Shahmirpur | 135 | 19:00 | 130 | 04:00
Haripur | 135 | 05:00 | 131 | 11:00 | Shariatpur | 138 | 05:00 | 132 | 23:00
HaripurSBU | 135 | 05:00 | 131 | 11:00 | Sherpur | 138 | 16:00 | 129 | 06:00
Hasnabad | 137 | 05:00 | 133 | 11:00 | Shikalbaha | 124 | 07:00 | 119 | 00:00
Hathazari | 136 | 05:00 | 131 | 23:00 | Shikalbaha-230 | 135 | 06:00 | 130 | 13:00
Ishurdi | 139 | 05:00 | 133 | 13:00 | Shitalakhya | 135 | 05:00 | 130 | 12:00
Jaldhaka | 130 | 05:00 | 122 | 13:00 | Sholosohor | 133 | 01:00 | 130 | 13:00
Jamalpur | 139 | 19:00 | 130 | 06:00 | Shyampur | 135 | 08:00 | 130 | 13:00
Jashore | 136 | 05:00 | 127 | 13:00 | Shyampur-230 | 136 | 08:00 | 123 | 20:00
Jhenaidah | 138 | 05:00 | 130 | 21:00 | Siddhirganj | 135 | 04:00 | 131 | 11:00
Jhenaidah-230 | 138 | 05:00 | 130 | 13:00 | Sirajganj | 134 | 05:00 | 127 | 19:00
Joydebpur | 142 | 07:00 | 131 | 23:00 | Sonargaon | 134 | 08:00 | 128 | 11:00
Joypurhat | 130 | 05:00 | 124 | 00:00 | Sreemongol | 133 | 01:00 | 129 | 15:00
Juldah | 135 | 06:00 | 130 | 13:00 | Sreepur | 136 | 01:00 | 132 | 10:00
Kabirpur | 134 | 18:00 | 122 | 12:00 | Srinagar | 136 | 04:00 | 131 | 11:00
Kachua | 129 | 17:00 | 117 | 13:00 | SSM | 140 | 07:00 | 134 | 00:00
Kaliakoir | 139 | 18:30 | 128 | 15:00 | Sunamganj | 132 | 07:00 | 127 | 20:00
Kallyanpur | 133 | 01:00 | 128 | 12:00 | Sylhet | 134 | 08:00 | 131 | 13:00
Kalurghat | 135 | 08:00 | 130 | 00:00 | Sylhet-132 | 133 | 05:00 | 131 | 20:00
Kamrangirchar | 137 | 08:00 | 130 | 12:00 | Tangail | 126 | 00:00 | 122 | 13:00
Kaptai | 135 | 7:00 | 122 | 12:00 | Thakurgaon | 135 | 05:00 | 126 | 13:00
Kasba | 131 | 18:00 | 124 | 11:00 | TK | 135 | 19:30 | 131 | 13:00
Kazla | 136 | 06:00 | 130 | 12:00 | Tongi | 134 | 05:00 | 129 | 11:00
Keranigonj | 137 | 07:00 | 131 | 13:00 | Ullahpara | 136 | 05:00 | 129 | 19:00
Khagrachori | 133 | 06:00 | 129 | 11:00 | Ullon | 138 | 05:00 | 132 | 11:00
Khulna | 139 | 07:00 | 130 | 20:00 | Uttara | 133 | 08:00 | 124 | 13:00
Khulna(S) | 141 | 05:00 | 131 | 21:00 | UttaraNew | 132 | 06:00 | 128 | 11:00
Khulshi | 132 | 05:00 | 127 | 13:00 | Zigatola | 137 | 07:00 | 131 | 11:00
Kishoreganj | 133 | 00:00 | 127 | 11:00
Kodda | 132 | 06:00 | 120 | 11:00
KSRM | 134 | 05:00 | 130 | 10:00
Kulaura | 136 | 07:00 | 134 | 11:00
Kurigram | 132 | 05:00 | 120 | 19:00
Kushtia | 136 | 03:00 | 130 | 13:00
Lalbag | 137 | 08:00 | 131 | 00:00
Lalmonirhat | 129 | 04:00 | 120 | 10:00
Madanganj | 134 | 08:00 | 130 | 11:00
Madaripur | 137 | 05:00 | 134 | 11:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division