## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-04-2025 | during | 20-04-2025 | during | 20-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 377 | 330 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 280 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 97 | 101 | 208.13 | 208.13 | 105 | 105 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 275 | 265 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 1 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 132 | 149.36 | 149.36 | 143 | 143 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 20 | 30 | 30 | 22 | 22 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 16 | 16 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 68 | 132 | 149 | 149 | 132 | 132 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 105 | 105 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 30 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 83 | 584 | 584 | 584 | 584 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2149 | 2999 | 5267.9 | 5331.9 | 4235.76 | 4299.76
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 150 | 150 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 31 | 64 | 81 | 64 | 81 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 44 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 7 | 7 | 22 | 7 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 3.18 | 0 | 3.18 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 10 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 650 | 1076 | 1224 | 1224 | 612 | 612 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 39 | 7 | 3 | 14 | 3 | 14 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 456 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1408 | 1991 | 3405.9 | 3432.72 | 2793.9 | 2820.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 0 | 0 | 150 | 221 | 134 | 134 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 255 | 255 | 285 | 285 | 285 | 285 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 34 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 167 | 174 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 20 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 3 | 100 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 29 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 61 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 62 | 88 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 5 | 19 | 20.83 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 44 | 105.3 | 105.3 | 105.3 | 105.3 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 39 | 39 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 56 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 16 | 0 | 25 | 0 | 25 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1074 | 1404 | 2262.62 | 2312.29 | 2067.85 | 2042.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-04-2025 | during | 20-04-2025 | during | 20-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 6 | 0 | 157.5 | 157.5 | 22 | 22 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 113 | 123 | 200 | 200 | 134 | 134 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 50 | 104 | 115 | 115 | 105 | 105 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.09 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 0 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 220.09 | 227 | 601.2 | 549 | 379.7 | 327.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 38 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 0 | 0 | 40 | 40 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 150 | 163 | 163 | 156 | 156 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 28 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 82 | 82 | 82 | 82 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 175 | 175 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 349 | 380 | 380 | 352 | 352 | Fgmo activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | Machine Problem
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1559 | 1516 | 1567 | 1567 | 1538 | 1538
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 916 | 868 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 88.26 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 380 | 430 | 617.1 | 617.1 | 617 | 617 | Coal shortage
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1384.26 | 1298 | 2980.1 | 2895.1 | 2465.01 | 2380.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 707 | 580 | 1260 | 1260 | 600 | 600 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 5 | 9 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 20 | 80 | 130 | 130 | 118 | 118 | FGMO
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 612 | 1050 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 220 | 250 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.55 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1784.55 | 2189 | 3432.12 | 3431.12 | 2760.12 | 2759.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 137 | 194 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 182 | 192 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 180 | 197 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 374 | 370 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 20 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 33 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.39 | 0 | 5.1 | 0 | 5.1 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 887 | 1359.41 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.9 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 101 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1931.29 | 2415.41 | 3110.63 | 2949.53 | 3057.84 | 2896.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 57 | 57 | 58 | 58 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 168 | 164 | 150 | 150 | 165 | 165 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 105 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 86 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 15 | 0 | 15 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 192 | 0 | 139.72 | 0 | 139.72 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 460.9 | 412 | 631.12 | 470 | 643.12 | 482
System Total |  |  |  |  | 27566.2 | 28535.742 | 11971.09 | 14451.41 | 23258.59 | 22938.66 | 19941.3 | 19546.7
Forecast Scenario (20-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13750 |  | 0 |  | 13750
|  |  |  | 1:00 | 13420 |  | 0 |  | 13420
|  |  |  | 2:00 | 13000 |  | 0 |  | 13000
|  |  |  | 3:00 | 12370 |  | 0 |  | 12370
|  |  |  | 4:00 | 12000 |  | 0 |  | 12000
|  |  |  | 5:00 | 11550 |  | 0 |  | 11550
|  |  |  | 6:00 | 11190 |  | 0 |  | 11190
|  |  |  | 7:00 | 11400 |  | 0 |  | 11400
|  |  |  | 8:00 | 11560 |  | 0 |  | 11560
|  |  |  | 9:00 | 11900 |  | 0 |  | 11900
|  |  |  | 10:00 | 12320 |  | 0 |  | 12320
|  |  |  | 11:00 | 12750 |  | 0 |  | 12750
|  |  |  | 12:00 | 13150 |  | 0 |  | 13150
|  |  |  | 13:00 | 13330 |  | 0 |  | 13330
|  |  |  | 14:00 | 13540 |  | 0 |  | 13540
|  |  |  | 15:00 | 13500 |  | 0 |  | 13500
|  |  |  | 16:00 | 13430 |  | 0 |  | 13430
|  |  |  | 17:00 | 13200 |  | 0 |  | 13200
|  |  |  | 18:00 | 12900 |  | 0 |  | 12900
|  |  |  | 18:30 | 13200 |  | 0 |  | 13200
|  |  |  | 19:00 | 14400 |  | 0 |  | 14400
|  |  |  | 19:30 | 14650 |  | 0 |  | 14650
|  |  |  | 20:00 | 14650 |  | 0 |  | 14650
|  |  |  | 21:00 | 14680 |  | 0 |  | 14680
|  |  |  | 22:00 | 14480 |  | 0 |  | 14480
|  |  |  | 23:00 | 14230 |  | 0 |  | 14230
Probable Maximum Temperature: |  |  | 31.40°C
Probable Maximum Demand at Day Peak: |  |  | 13150.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14680.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14680.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 312.70 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:07 hrs on 20-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-04-2025 | [28 empty] | Date: | 19-04-2025 | [28 empty] | Date: | 19-04-2025 | [28 empty] | Date: | 19-04-2025 | [28 empty] | Date: | 19-04-2025 | [16 empty] | Date: | 19-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 35 | 47 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 290 | 450 | 0 | 0 | 0 | 275 | 100 | 0 | 0 | 34 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 28 | 360 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 652 | 0 | 51 | 0 | 163 | 0 | 359 | 255 | 53 | 0 | 36 | 16 | 50 | 0 | 18 | 20 | 0 | 72 | 0 | 0 | 0 | 300 | 320 | 350 | 39 | 40 | 0 | 155 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 55 | 105 | 22 | 0 | 0 | 12 | 6190 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 842.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 200 | 0 | 200 | 0 | 401 | 0 | 0 | 0 | 163 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 0 | 220 | 0 | 610 | 794 | 0 | 5242.36 | 11432.36 | 81.7
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 270 | 450 | 0 | 0 | 0 | 265 | 101 | 0 | 0 | 37 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 28 | 362 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 163 | 0 | 359 | 255 | 53 | 0 | 33 | 16 | 50 | 0 | 18 | 20 | 0 | 70 | 0 | 0 | 0 | 295 | 320 | 346 | 38 | 40 | 0 | 149 | 16 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 55 | 105 | 22 | 0 | 0 | 12 | 6050 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 825.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 200 | 0 | 198 | 0 | 376 | 0 | 0 | 0 | 166 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 0 | 220 | 0 | 616 | 660 | 0 | 4970.57 | 11020.57 | 81.7
02:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 17 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 286 | 450 | 0 | 0 | 0 | 282 | 86 | 0 | 0 | 52 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 28 | 360 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 600 | 0 | 10 | 0 | 127 | 0 | 358 | 255 | 53 | 0 | 33 | 0 | 70 | 0 | 0 | 20 | 0 | 68 | 0 | 0 | 0 | 300 | 320 | 302 | 38 | 40 | 0 | 129 | 16 | 0 | 60 | 30 | 0 | 18 | 173 | 0 | 45 | 95 | 22 | 0 | 0 | 0 | 5826 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 818.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 150 | 0 | 150 | 0 | 338 | 0 | 0 | 0 | 166 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 0 | 180 | 0 | 615 | 540 | 0 | 4638.02 | 10464.02 | 81.7
03:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 290 | 400 | 0 | 0 | 0 | 286 | 40 | 0 | 0 | 52 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 28 | 360 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 606 | 0 | 10 | 0 | 68 | 0 | 340 | 255 | 54 | 0 | 33 | 0 | 70 | 0 | 0 | 20 | 0 | 66 | 0 | 0 | 0 | 305 | 320 | 310 | 38 | 40 | 0 | 132 | 16 | 0 | 11 | 20 | 0 | 18 | 173 | 0 | 35 | 65 | 22 | 0 | 0 | 0 | 5517 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 823.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 150 | 0 | 150 | 0 | 348 | 0 | 0 | 0 | 165 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 0 | 180 | 0 | 615 | 522 | 0 | 4616.83 | 10133.83 | 81.69
04:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 295 | 350 | 0 | 0 | 0 | 276 | 40 | 0 | 0 | 52 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 20 | 360 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 608 | 0 | 10 | 0 | 8 | 0 | 290 | 255 | 53 | 0 | 33 | 0 | 70 | 0 | 0 | 20 | 0 | 66 | 0 | 0 | 0 | 305 | 320 | 310 | 37 | 40 | 0 | 131 | 16 | 0 | 11 | 20 | 0 | 18 | 173 | 0 | 35 | 55 | 22 | 0 | 0 | 0 | 5259 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 824.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 130 | 0 | 341 | 0 | 0 | 0 | 166 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 6 | 0 | 180 | 0 | 606 | 521 | 0 | 4548.18 | 9807.18 | 81.69
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 293 | 300 | 0 | 0 | 0 | 289 | 40 | 0 | 0 | 17 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 28 | 360 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 290 | 255 | 52 | 0 | 33 | 0 | 70 | 0 | 0 | 20 | 0 | 66 | 0 | 0 | 0 | 300 | 320 | 332 | 37 | 40 | 0 | 135 | 0 | 0 | 2 | 20 | 0 | 18 | 174 | 0 | 35 | 55 | 22 | 0 | 0 | 0 | 5153 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 823.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 353 | 0 | 0 | 0 | 165 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 7 | 0 | 180 | 0 | 611 | 500 | 0 | 4534.25 | 9687.25 | 81.69
06:00 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 288 | 250 | 0 | 0 | 0 | 286 | 40 | 0 | 1 | 17 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 16 | 362 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 0 | 0 | 290 | 255 | 52 | 0 | 33 | 0 | 70 | 0 | 0 | 20 | 0 | 64 | 0 | 0 | 0 | 300 | 320 | 321 | 37 | 40 | 0 | 132 | 0 | 0 | 2 | 20 | 0 | 18 | 174 | 0 | 55 | 58 | 22 | 0 | 0.92 | 0 | 5083.92 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.63 | 382 | 0 | 820.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.08 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0.08 | 0 | 163 | 58 | 0 | 1 | 0 | 0 | 0 | 0 | 6 | 0.02 | 0 | 150 | 6 | 0 | 180 | 0 | 611 | 500 | 0 | 4437.27 | 9521.19 | 81.68
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 311 | 250 | 0 | 0 | 0 | 293 | 0 | 0 | 7 | 20 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 16 | 362 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 610 | 2 | 0 | 0 | 0 | 0 | 290 | 255 | 52 | 0 | 36 | 0 | 70 | 0 | 0 | 20 | 0 | 58 | 0 | 6 | 0 | 315 | 320 | 333 | 37 | 40 | 0 | 138 | 0 | 0 | 2 | 20 | 0 | 18 | 174 | 0 | 68 | 96 | 18 | 0 | 10.86 | 7 | 5202.86 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.15 | 381 | 0 | 822.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 9.86 | 130 | 0 | 130 | 0 | 130 | 0 | 353 | 0 | 0.84 | 0 | 163 | 59 | 0 | 6 | 0 | 0 | 0 | 0.9 | 39 | 0.02 | 0 | 150 | 6 | 0 | 220 | 0 | 613 | 500 | 0 | 4659.17 | 9862.03 | 81.68
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 17 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 308 | 250 | 0 | 0 | 0 | 303 | 36 | 0 | 8 | 35 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 7 | 360 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 290 | 255 | 53 | 0 | 36 | 1 | 50 | 1 | 1 | 8 | 0 | 60 | 0 | 12 | 0 | 310 | 320 | 338 | 37 | 40 | 0 | 142 | 0 | 0 | 2 | 20 | 0 | 18 | 174 | 0 | 45 | 115 | 17 | 1 | 25.76 | 12 | 5231.76 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.83 | 380 | 0 | 822.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 24.4 | 130 | 0 | 130 | 0 | 130 | 0 | 381 | 0 | 2.08 | 0 | 158 | 58 | 0 | 16 | 0 | 0 | 0 | 3.7 | 89 | 0.09 | 0 | 150 | 3 | 0 | 220 | 0 | 615 | 500 | 0 | 4765.84 | 9997.6 | 81.68
09:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 17 | 47 | 16 | 0 | 0 | 0.8 | 0 | 0 | 0 | 350 | 284 | 350 | 0 | 0 | 0 | 286 | 101 | 0 | 12 | 35 | 21.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 4 | 364 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 600 | 5 | 0 | 0 | 8 | 0 | 358 | 255 | 52 | 0 | 36 | 32 | 50 | 13 | 9 | 8 | 0 | 62 | 0 | 22 | 0 | 310 | 320 | 331 | 38 | 40 | 0 | 144 | 0 | 0 | 2 | 20 | 0 | 18 | 174 | 0 | 45 | 115 | 10 | 2 | 39.62 | 12 | 5641.92 | 869 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.57 | 381 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 40.34 | 130 | 0 | 130 | 0 | 130 | 0 | 356 | 0 | 3.52 | 0 | 155 | 58 | 0 | 25 | 0 | 0 | 0 | 5.3 | 132 | 0.09 | 0 | 150 | 3 | 0 | 220 | 0 | 598 | 500 | 0 | 4825.82 | 10467.74 | 81.67
10:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 68 | 16 | 0 | 0 | 28 | 0 | 0 | 0 | 350 | 288 | 350 | 0 | 0 | 0 | 293 | 99 | 0 | 22 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 3 | 362 | 0 | 0 | 1 | 0 | 0 | 151 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 8 | 0 | 355 | 255 | 51 | 0 | 34 | 34 | 50 | 22 | 9 | 6 | 0 | 52 | 0 | 17 | 0 | 305 | 320 | 336 | 38 | 40 | 0 | 137 | 0 | 0 | 2 | 20 | 0 | 18 | 174 | 0 | 45 | 115 | 10 | 2 | 48.23 | 12 | 5697.23 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.82 | 380 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 50.42 | 130 | 0 | 130 | 0 | 130 | 0 | 352 | 0 | 4.49 | 0 | 160 | 59 | 0 | 31 | 0 | 0 | 0 | 6.5 | 178 | 0.14 | 0 | 150 | 5 | 0 | 220 | 0 | 608 | 500 | 0 | 4972.37 | 10669.6 | 81.67
11:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 17 | 68 | 16 | 0 | 0 | 35 | 0 | 0 | 0 | 400 | 285 | 350 | 0 | 0 | 0 | 290 | 98 | 0 | 14 | 35 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 360 | 0 | 0 | 4 | 0 | 0 | 149 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 130 | 0 | 351 | 255 | 46 | 0 | 34 | 34 | 50 | 17 | 9 | 6 | 0 | 60 | 0 | 21 | 0 | 310 | 320 | 385 | 38 | 40 | 0 | 152 | 10 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 45 | 115 | 5 | 1 | 49.64 | 12 | 6064.64 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.58 | 381 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 56.45 | 130 | 0 | 130 | 0 | 130 | 0 | 396 | 0 | 5.09 | 0 | 168 | 58 | 0 | 35 | 0 | 0 | 0 | 7.5 | 192 | 0.27 | 0 | 150 | 5 | 30 | 220 | 0 | 620 | 510 | 0 | 5107.89 | 11172.53 | 81.67
12:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 1 | 17 | 68 | 48 | 0 | 0 | 35 | 17 | 0 | 0 | 400 | 296 | 350 | 0 | 0 | 0 | 275 | 97 | 0 | 27 | 52 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 50 | 0 | 2 | 40 | 0 | 2 | 456 | 0 | 0 | 18 | 0 | 0 | 150 | 0 | 0 | 0 | 650 | 1 | 20 | 3 | 167 | 0 | 355 | 255 | 47 | 0 | 34 | 34 | 50 | 17 | 9 | 5 | 0 | 62 | 0 | 16 | 0 | 300 | 320 | 387 | 38 | 40 | 0 | 155 | 16 | 0 | 80 | 30 | 0 | 18 | 175 | 0 | 50 | 113 | 6 | 2 | 37.09 | 12 | 6410.09 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.26 | 380 | 0 | 887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 64.9 | 137 | 0 | 182 | 0 | 180 | 0 | 374 | 0 | 5.39 | 0 | 168 | 57 | 0 | 36 | 0 | 0 | 0 | 7.9 | 192 | 0.55 | 0 | 220 | 5 | 20 | 220 | 0 | 707 | 612 | 0 | 5561 | 11971.09 | 81.66
13:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 17 | 17 | 68 | 48 | 0 | 0 | 35 | 90 | 0 | 0 | 400 | 304 | 350 | 0 | 35 | 0 | 278 | 99 | 0 | 23 | 70 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 3 | 40 | 0 | 8 | 504 | 0 | 0 | 19 | 0 | 0 | 150 | 0 | 0 | 0 | 760 | 7 | 43 | 20 | 167 | 0 | 352 | 255 | 47 | 0 | 33 | 49 | 50 | 25 | 9 | 5 | 0 | 76 | 0 | 43 | 0 | 300 | 320 | 368 | 38 | 40 | 0 | 156 | 16 | 0 | 83 | 30 | 0 | 16 | 174 | 0 | 77 | 113 | 6 | 2 | 45.58 | 12 | 6752.58 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.94 | 381 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 57.43 | 187 | 0 | 201 | 0 | 199 | 0 | 375 | 0 | 5.22 | 0 | 168 | 57 | 0 | 36 | 0 | 0 | 0 | 7 | 204 | 0.54 | 0 | 240 | 5 | 110 | 220 | 0 | 554 | 639 | 0 | 5587.13 | 12339.71 | 81.66
14:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 17 | 68 | 48 | 0 | 0 | 35 | 90 | 0 | 0 | 400 | 304 | 350 | 0 | 17 | 0 | 275 | 98 | 0 | 24 | 90 | 16 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 12 | 0 | 3 | 40 | 0 | 6 | 575 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 800 | 11 | 43 | 20 | 165 | 0 | 346 | 255 | 47 | 0 | 33 | 22 | 50 | 20 | 9 | 5 | 0 | 80 | 0 | 59 | 0 | 305 | 320 | 354 | 38 | 40 | 0 | 150 | 16 | 0 | 83 | 30 | 0 | 16 | 175 | 0 | 75 | 113 | 5 | 2 | 48.62 | 12 | 6782.62 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.36 | 380 | 0 | 910.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 41.21 | 207 | 0 | 203 | 0 | 203 | 0 | 375 | 0 | 4.68 | 0 | 168 | 57 | 0 | 32 | 0 | 0 | 0 | 6.9 | 162 | 0.28 | 0 | 240 | 6 | 120 | 220 | 0 | 474 | 660 | 0 | 5512.57 | 12295.19 | 81.66
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 17 | 73 | 62 | 0 | 0 | 35 | 90 | 0 | 0 | 450 | 303 | 0 | 0 | 17 | 0 | 275 | 96 | 0 | 20 | 125 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 0 | 3 | 575 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 972 | 11 | 35 | 20 | 163 | 0 | 340 | 255 | 46 | 0 | 33 | 20 | 50 | 16 | 12 | 8 | 0 | 76 | 0 | 47 | 0 | 300 | 320 | 354 | 37 | 40 | 0 | 150 | 16 | 0 | 83 | 30 | 0 | 16 | 175 | 0 | 76 | 113 | 5 | 2 | 35.58 | 12 | 6652.58 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.71 | 380 | 0 | 963.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 36.96 | 203 | 0 | 202 | 0 | 194 | 0 | 393 | 0 | 3.51 | 0 | 160 | 57 | 0 | 25 | 0 | 0 | 0 | 5.7 | 115 | 0 | 0 | 240 | 6 | 80 | 220 | 0 | 350 | 783 | 0 | 5412.74 | 12065.32 | 81.65
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 98 | 78 | 0 | 0 | 35 | 90 | 0 | 0 | 450 | 302 | 0 | 0 | 17 | 0 | 284 | 99 | 0 | 12 | 125 | 17 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 0 | 3 | 502 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1055 | 3 | 35 | 20 | 175 | 0 | 348 | 255 | 46 | 0 | 32 | 34 | 50 | 29 | 28 | 9 | 14 | 76 | 0 | 27 | 0 | 300 | 320 | 354 | 36 | 40 | 0 | 148 | 22 | 0 | 83 | 30 | 0 | 16 | 175 | 0 | 76 | 113 | 0 | 1 | 23.22 | 12 | 6722.22 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.69 | 488 | 0 | 1014.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 20.68 | 202 | 0 | 200 | 0 | 196 | 0 | 371 | 0 | 2.13 | 0 | 160 | 57 | 0 | 16 | 0 | 0 | 0 | 2.6 | 101 | 0.35 | 0 | 250 | 6 | 80 | 180 | 0 | 258 | 961 | 0 | 5578.91 | 12301.13 | 81.65
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 96 | 82 | 0 | 0 | 35 | 90 | 0 | 0 | 450 | 304 | 115 | 0 | 17 | 0 | 275 | 99 | 0 | 6 | 108 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 12 | 0 | 1 | 40 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1020 | 2 | 43 | 20 | 127 | 0 | 348 | 255 | 47 | 0 | 33 | 34 | 50 | 30 | 29 | 12 | 14 | 72 | 0 | 9 | 0 | 300 | 320 | 350 | 36 | 40 | 0 | 148 | 22 | 0 | 83 | 30 | 0 | 16 | 173 | 0 | 76 | 113 | 0 | 0 | 9.61 | 12 | 6698.61 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.08 | 428 | 0 | 1016.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 9.71 | 203 | 0 | 150 | 0 | 150 | 0 | 377 | 0 | 0.84 | 0 | 165 | 57 | 0 | 7 | 0 | 0 | 0 | 1.8 | 44 | 0.13 | 0 | 250 | 6 | 80 | 180 | 0 | 360 | 1000 | 0 | 5440.09 | 12138.7 | 81.65
18:00 | 0 | 52 | 12 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 17 | 17 | 88 | 105 | 15 | 0 | 35 | 90 | 0 | 6 | 380 | 304 | 250 | 0 | 17 | 0 | 278 | 99 | 0 | 1 | 125 | 20 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 8 | 500 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1015 | 0 | 43 | 20 | 127 | 0 | 300 | 255 | 47 | 0 | 33 | 34 | 50 | 29 | 38 | 18 | 14 | 78 | 0 | 1 | 0 | 295 | 320 | 354 | 38 | 40 | 0 | 149 | 22 | 0 | 83 | 30 | 0 | 16 | 173 | 0 | 104 | 123 | 0 | 0 | 1.25 | 12 | 6841.25 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.71 | 430 | 0 | 1107.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.14 | 160 | 0 | 150 | 0 | 150 | 0 | 333 | 0 | 0.12 | 0 | 164 | 57 | 0 | 1 | 18 | 0 | 0 | 0.4 | 7 | 0.02 | 0 | 200 | 6 | 80 | 180 | 0 | 456 | 951 | 0 | 5370.94 | 12212.19 | 81.64
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17 | 29 | 114 | 127 | 95 | 0 | 35 | 144 | 0 | 20 | 450 | 300 | 583 | 0 | 0 | 0 | 295 | 99 | 0 | 0 | 160 | 20 | 22 | 0 | 82 | 0 | 0 | 0 | 0 | 7 | 34 | 31 | 0 | 44 | 10 | 0 | 40 | 0 | 5 | 577 | 17 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1100 | 0 | 43 | 50 | 174 | 0 | 353 | 255 | 48 | 0 | 35 | 44 | 50 | 47 | 38 | 19 | 50 | 92 | 1 | 0 | 7 | 300 | 320 | 379 | 38 | 40 | 0 | 153 | 16 | 0 | 83 | 30 | 0 | 16 | 175 | 0 | 104 | 123 | 0 | 0 | 0 | 8 | 8133 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 1316.81 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 8 | 0 | 178 | 0 | 190 | 0 | 182 | 0 | 405 | 0 | 0 | 0 | 164 | 57 | 63 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 8 | 80 | 220 | 0 | 548 | 990 | 0 | 6052.81 | 14185.81 | 81.64
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 35 | 132 | 132 | 95 | 0 | 35 | 144 | 0 | 30 | 450 | 280 | 583 | 0 | 17 | 0 | 265 | 101 | 0 | 0 | 160 | 20 | 22 | 0 | 83 | 0 | 0 | 0 | 0 | 7 | 34 | 31 | 0 | 44 | 10 | 0 | 40 | 0 | 7 | 575 | 17 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1076 | 0 | 43 | 100 | 174 | 0 | 354 | 255 | 50 | 0 | 35 | 56 | 50 | 61 | 38 | 19 | 44 | 88 | 8 | 0 | 29 | 300 | 320 | 349 | 38 | 40 | 0 | 150 | 16 | 0 | 83 | 28 | 0 | 17 | 175 | 0 | 104 | 123 | 0 | 0 | 0 | 0 | 8137 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 1359.41 | 0 | 0 | 0 | 50 | 0 | 33 | 0 | 0 | 0 | 0 | 20 | 0 | 194 | 0 | 192 | 0 | 197 | 0 | 370 | 0 | 0 | 0 | 164 | 57 | 86 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 80 | 220 | 0 | 580 | 1050 | 0 | 6314.41 | 14451.41
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 35 | 132 | 137 | 95 | 0 | 35 | 144 | 0 | 35 | 400 | 302 | 583 | 0 | 17 | 0 | 266 | 101 | 0 | 0 | 160 | 20 | 22 | 0 | 83 | 0 | 0 | 0 | 0 | 4 | 34 | 31 | 0 | 33 | 10 | 0 | 40 | 0 | 12 | 500 | 17 | 0 | 0 | 1 | 0 | 150 | 0 | 0 | 0 | 1000 | 0 | 43 | 92 | 175 | 0 | 354 | 255 | 50 | 0 | 35 | 61 | 80 | 62 | 39 | 20 | 62 | 92 | 8 | 0 | 34 | 295 | 320 | 350 | 38 | 40 | 0 | 148 | 22 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 104 | 123 | 0 | 0 | 0 | 4 | 8033 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 0 | 1353.32 | 0 | 0 | 0 | 32 | 0 | 33 | 0 | 0 | 0 | 0 | 22 | 0 | 194 | 0 | 191 | 0 | 195 | 0 | 320 | 0 | 0 | 0 | 165 | 57 | 87 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 80 | 220 | 0 | 585 | 1048 | 0 | 6251.32 | 14284.32 | 81.63
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 17 | 35 | 132 | 143 | 45 | 0 | 35 | 144 | 0 | 62 | 450 | 296 | 583 | 0 | 17 | 0 | 266 | 101 | 0 | 0 | 160 | 20 | 22 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 33 | 0 | 0 | 40 | 0 | 16 | 501 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 970 | 0 | 43 | 70 | 178 | 0 | 355 | 255 | 51 | 0 | 36 | 72 | 90 | 71 | 39 | 20 | 47 | 92 | 0 | 0 | 40 | 290 | 320 | 350 | 38 | 40 | 0 | 147 | 22 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 104 | 134 | 0 | 0 | 0 | 12 | 8026 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 10 | 1364 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 26 | 0 | 193 | 0 | 191 | 0 | 196 | 0 | 372 | 0 | 0 | 0 | 166 | 57 | 61 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 80 | 220 | 0 | 581 | 1020 | 0 | 6278 | 14304 | 81.63
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 35 | 132 | 143 | 15 | 0 | 35 | 108 | 0 | 74 | 450 | 290 | 583 | 0 | 17 | 0 | 266 | 101 | 0 | 0 | 160 | 19 | 22 | 0 | 110 | 0 | 0 | 0 | 0 | 1 | 34 | 16 | 0 | 33 | 0 | 0 | 40 | 0 | 20 | 502 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 970 | 0 | 43 | 40 | 178 | 0 | 359 | 255 | 52 | 0 | 36 | 62 | 80 | 60 | 39 | 20 | 29 | 92 | 0 | 0 | 46 | 295 | 320 | 348 | 37 | 40 | 0 | 149 | 22 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 105 | 134 | 0 | 0 | 0 | 12 | 7919 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427 | 17 | 1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 187 | 0 | 191 | 0 | 370 | 0 | 0 | 0 | 169 | 56 | 61 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 80 | 220 | 0 | 584 | 1000 | 0 | 6162 | 14081 | 81.62
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 35 | 134 | 132 | 0 | 0 | 0 | 35 | 0 | 84 | 450 | 298 | 520 | 0 | 0 | 0 | 289 | 101 | 0 | 0 | 160 | 20 | 22 | 0 | 125 | 0 | 0 | 0 | 0 | 5 | 34 | 0 | 0 | 33 | 0 | 0 | 40 | 0 | 22 | 504 | 0 | 0 | 0 | 8 | 0 | 152 | 0 | 0 | 0 | 970 | 0 | 51 | 0 | 178 | 0 | 359 | 255 | 52 | 0 | 36 | 50 | 80 | 59 | 39 | 20 | 30 | 92 | 0 | 0 | 47 | 300 | 320 | 371 | 39 | 40 | 0 | 149 | 22 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 105 | 144 | 0 | 0 | 0 | 12 | 7731 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 185 | 0 | 188 | 0 | 370 | 0 | 0 | 0 | 165 | 56 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 80 | 180 | 0 | 592 | 950 | 0 | 5971 | 13702 | 81.62
Total KWH | 0 | 568320 | 252480 | 0 | 0 | 0 | 0 | 0 | 8571600 | 0 | 0 | 217440 | 537840 | 1767456 | 1295040 | 272487 | 0 | 503667 | 1198080 | 0 | 333120 | 9175000 | 7186705 | 8773359 | 0 | 203433 | 0 | 6863203 | 2101000 | 0 | 181799 | 1988400 | 436200 | 526320 | 0 | 572727 | 0 | 0 | 0 | 0 | 253920 | 191661 | 97606 | 0 | 713280 | 30720 | 18684 | 994260 | 0 | 80880 | 10618181.82 | 26764 | 0 | 174240 | 34446.6 | 0 | 3411098 | 0 | 0 | 0 | 18839998 | 38070 | 620944 | 531927 | 2609455 | 0 | 8435500 | 6252000 | 1200480 | 0 | 816048 | 709440 | 1424390 | 588480 | 443520 | 346910 | 264480 | 1753920 | 14174 | 316145 | 199232 | 7342000 | 7662200 | 8750000 | 888000 | 924960 | 0 | 3487009 | 304752 | 0 | 1312320 | 635904 | 0 | 413000 | 3586620 | 0 | 1680000 | 2601600 | 210240 | 15300 | 375720 | 224880 | 155991035.42 | 21941818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552240 | 9781818 | 33120 | 23797091 | 0 | 0 | 0 | 63168 | 0 | 90560 | 0 | 0 | 0 | 648010 | 53948 | 410248 | 4137909 | 0 | 4290773 | 0 | 4245518 | 0 | 8791854 | 0 | 37140 | 0 | 3983000 | 1354909 | 348016 | 259786 | 472780 | 0 | 0 | 48000 | 1461600 | 2396 | 0 | 4865000 | 161133 | 1034000 | 5209390 | 0 | 13512727 | 18075636.36 | 0 | 129663588.36 | 285654623.78

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11971.09 | MW | 12:00 Hr. | Energy Generated |  |  | 285.6546 |  | MKWHr.
| Day Peak Demand |  |  | 11971.09 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.109 |  | MKWHr.
| Evening Peak Generation |  |  | 14451.41 | MW | 19:30 Hr. | Energy Demand |  |  | 285.7636 |  | MKWHr.
| Evening Peak Demand |  |  | 14500.41 | MW | 19:30 Hr. | Maximum Temperature |  |  | 32.5 |  | °C
| Minimum Generation of the Day |  |  | 9521.19 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1030.38 |  | MMCFD
| Maximum Generation of the Day |  |  | 14451.41 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.3938 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 44.2061 | 0 | 9.1378 | 0 | 0 | 0.1818 | 0 | 0 | 53.5257 | Gas | 132.7914 | Gas | 427255558.7
| Chattogram Zone |  |  | 3.492 | 29.4582 | 1.2687 | 0 | 0.99426 | 0.056754 | 0 | 0.25392 | 35.5238 | Coal | 81.0313 | Coal | 484241328.0224
| Cumilla Zone |  |  | 21.7057 | 0 | 2.7513 | 0 | 0 | 0.31615 | 1.7539 | 0 | 26.527 | HFO | 18.7258 | HFO | 311741416.142
| Mymensingh Zone |  |  | 0.21024 | 0 | 4.5065 | 0 | 0 | 0.39102 | 0 | 0 | 5.1077 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.3068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.3068 | Hydro | 0.99426 | Hydro | 99426
| Khulna Zone |  |  | 0 | 9.7818 | 0.03312 | 0 | 0 | 0.55224 | 21.9418 | 0 | 32.309 | Solar | 4.3651 | Solar | 72573854.98
| Barishal Zone |  |  | 6.4045 | 36.4534 | 0 | 0 | 0 | 0.002396 | 0 | 0 | 42.8603 | Import | 47.4928 | Import | 241134463.22
| Rajshahi Zone |  |  | 21.4661 | 0 | 0.20768 | 0 | 0 | 1.0954 | 23.7971 | 0 | 46.5662 | Wind | 0.25392 | Wind | 3717388.8
| Rangpur Zone |  |  | 0 | 5.3379 | 0.8208 | 0 | 0 | 1.7694 | 0 | 0 | 7.9281
| Total |  |  | 132.7914 | 81.0313 | 18.7258 | 0 | 0.99426 | 4.3651 | 47.4928 | 0.25392 | 285.6546
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 427255558.7 |  | Hydro | 99426
|  |  |  | Coal | 484241328.0224 |  | Solar | 72573854.98
|  |  |  | HFO | 311741416.142 |  | Import | 241134463.22
|  |  |  | HSD | 0 |  | Wind | 3717388.8
[5 empty] | Total: | 154,07,63,435 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9418 | Peak Hr Flow | 868.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38088927.35 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 23.7971 | Peak Hr Flow | 1359.41 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 675 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.7539 | Peak Hr Flow | 88.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 964 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.4928 | Peak Hr Flow | 2315.41 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5149
|  |  |  | Chattogram |  | 0 |  | 1225
|  |  |  | Cumilla |  | 0 |  | 1240
|  |  |  | Mymensingh |  | 35 |  | 1166
|  |  |  | Sylhet |  | 0 |  | 571
|  |  |  | Khulna |  | 0 |  | 1636
|  |  |  | Barishal |  | 0 |  | 393
|  |  |  | Rajshahi |  | 0 |  | 1539
|  |  |  | Rangpur |  | 12 |  | 939
|  |  |  | Total |  | 47 |  | 13858
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 17:29 | Baghabari-Bangura 132 kV Ckt-1 Scheduled S/D from Bhangura 132/33kV end Due to Piling | [7 empty] | 25.0MW load
|  |  | work at Bhangura -Bhagabari ckt-2 bay | [7 empty] | interrup. Bhangura
132/33kV end
| 08:54 | 13:12 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to BCIC 33kv fedder bus DS maintenance | [7 empty] | 8.0MW load
|  |  | work. | [7 empty] | interrup.
| 08:54 | 13:10 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to BCIC 33kv fedder bus DS maintenance | [7 empty] | 8.0MW load
|  |  | work. | [7 empty] | interrup.
| 09:20 | 17:38 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Project Work S/D Due to Tree
Trimming work
| 09:21 | 17:37 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Project Work S/D Due to Tree
Trimming work
|  | 09:23 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 09:24 | Naogaon 132/33kV S/S T-3 LT is restored.
|  | 09:24 | Naogaon 132/33kV S/S T-3 33kV BUS is restored.
| 09:27 | 14:16 | Faridpur-Gopalganj(N) 132 kV Ckt-1 Project Work S/D from Gopalganj 400/132kV end.
| 09:36 | 14:17 | Faridpur-Gopalganj(N) 132 kV Ckt-2 Project Work S/D from Gopalganj 400/132kV end.
| 09:48 | 14:50 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to DS maintenance
| 09:49 | 11:05 | Shahjadpur 132/33kV S/S T-4(435T) LT Forced S/D Due to Redhot Remove
| 09:49 | 14:50 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to DS maintenance
| 09:50 | 11:04 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to Redhot Remove
| 09:55 | 14:50 | Savar 132/33kV S/S Main Bus-II Scheduled S/D Due to DS MAINTENANCE
| 10:06 |  | BSRM 230/33kV S/S 230/33 kV Transformer-1 (125/140 MVA) HT Scheduled S/D Due to Annual
Maintenance
| 10:08 | 16:44 | Cox'sbazar-Dohazari 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to disk
cleaning
| 10:15 | 12:17 | Fatullah-Madanganj 132 kV Ckt-2 Scheduled S/D from Fatullah 132/33kV end Due to
Maintenance
| 10:16 | 12:18 | Madanganj 132/33kV S/S Madanganj-Fatullah 132KV Ckt Scheduled S/D Due to red hot
maintenance
| 10:27 | 13:56 | Rampur 230/132/33 S/S Khulshi-1 Scheduled S/D Due to red ot maintenance
| 10:34 | 18:20 | Madanganj 132/33kV S/S Main Bus Scheduled S/D
| 10:40 | 14:13 | Hasnabad 132/33kV S/S 33kv Main Bus Scheduled S/D
| 10:42 | 15:55 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 LT Scheduled S/D
| 10:42 | 15:53 | Hasnabad 132/33kV S/S 132/33kV 424 T-5 HT Scheduled S/D
| 10:47 | 12:45 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D Due to 33kV
side CT to CB Redhot remove, 132 kV GT-2 X-former Main tank Oil filling.
| 10:47 | 12:48 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to 33kV
side CT to CB Redhot remove, 132 kV GT-2 X-former Main tank Oil filling.
| 10:47 | 12:45 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to 33kV
side CT to CB Redhot remove, 132 kV GT-2 X-former Main tank Oil filling.
| 10:52 | 15:38 | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
|  | 11:00 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 HT is restored.
| 11:10 | 13:22 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T LT Scheduled S/D Due to 33KV Bus PT | [7 empty] | 15.0MW load
|  |  | test. | [7 empty] | interrup.
|  | 11:10 | Cumilla(N) 230/132/33kV S/S 230KV ATR-03 LT is restored.
| 11:12 | 13:18 | Barapukuria 230/132/33kV S/S 132/33 KV T-3, 404T HT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 12:00 |  | Day Peak Gen. 11971 MW
| 12:21 |  | From NLDC: Bhola 225 MW CCPP GT-2 Synchronizd.
| 12:35 | 12:54 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 Forced S/D Due to Tap change problem work EGCB
ends
|  | 12:50 | Dhamrai 132/33kV S/S Transformer-2 LT is restored.
|  | 12:50 | Dhamrai 132/33kV S/S Transformer-2 HT is restored.
| 14:13 | 15:30 | Hasnabad 132/33kV S/S 33kv Reserve Bus Scheduled S/D
| 14:58 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 16:28 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 16:28 |  | Meghnaghat CCPP(Summit)-2 GT Synchronized with remarks:- None
| 16:58 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 16:58 |  | Meghnaghat CCPP(Summit)-2 ST Synchronized with remarks:- None
| 18:09 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- GT
| 18:09 |  | Unique Meghnaghat Power Limited (UMPL) GT Synchronized with remarks:- None
|  | 18:18 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT is restored.
|  | 18:19 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT is restored.
| 20:12 |  | Unique Meghnaghat Power Limited (UMPL) ST Synchronized with remarks:- None
| 20:12 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 07:19 |  | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
| 07:40 |  | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to PBS taken SD | [7 empty] | 3.0MW load
interrup.
| 07:40 |  | Purbasadipur-Saidpur 132kV Ckt-2 Tripped from Purbasadipur 132/33kV end showing Distance | [7 empty] | 90.0MW load
|  |  | Relay (SIMENS SIPROTEC, Model :- SA87 ) relays. | [7 empty] | interrup.
Purbasadipur
132/33kV end
| 07:40 |  | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Tripped from Purbasadipur 132/33kV end showing | [7 empty] | 55.0MW load
|  |  | Ditance Relay relays. | [7 empty] | interrup.
Purbasadipur
132/33kV end
| 07:41 |  | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to PBS taken SD | [7 empty] | 3.0MW load
interrup.
| 07:43 |  | Purbasadipur-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing Distance
relays.
| 07:45 |  | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to PBS taken SD | [7 empty] | 3.0MW load
interrup.
| 07:46 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to PBS taken SD | [7 empty] | 3.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 330 | 8571600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9175000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 7186705 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 101 | 2101000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 265 | 6863203 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 217440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 132 | 1295040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 503667 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 203433 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 436200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 526320 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 252480 | -
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 272487 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 1767456 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 568320 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 30 | 333120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1198080 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 181799 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 537840 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 83 | 572727 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 8773359 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1988400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2999 | 53525676
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 34446.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 38070 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 174240 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 994260 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3411098 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 31 | 97606 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 191661 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 44 | 713280 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 80880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 18684 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 30720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 26764 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1076 | 18839998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 7 | 253920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 10618181.82 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1991 | 35523809.42
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 0 | 0 | Under Maintenance
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8435500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 255 | 6252000 | Gas shortage
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | Under Maintenance
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 816048 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1200480 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 174 | 2609455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 620944 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 531927 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 29 | 199232 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1424390 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 61 | 588480 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 88 | 1753920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 14174 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 346910 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 44 | 264480 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 443520 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 56 | 709440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 316145 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1404 | 26527045
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 210240 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 123 | 2601600 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1680000 | -
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 375720 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 224880 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 227 | 5107740
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 888000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 924960 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3487009 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 28 | 635904 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1312320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 175 | 3586620 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 413000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 16 | 304752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7342000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 349 | 8750000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7662200 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1516 | 35306765
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 868 | 21941818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 33120 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 552240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 430 | 9781818 | Coal shortage
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1298 | 32308996
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 580 | 13512727 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 9 | 161133 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 80 | 1034000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1050 | 18075636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5209390 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 4865000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2396 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2189 | 42860282.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 194 | 4137909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4290773 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 197 | 4245518 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 370 | 8791854 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 20 | 53948 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 33 | 90560 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 63168 | FGMO
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 37140 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1359.41 | 23797091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 410248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 648010 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2415.41 | 46566219
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 57 | 1354909 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 3983000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 472780 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 48000 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 86 | 348016 | FGMO
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 259786 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1461600 | -
Rangpur Area Total |  |  |  |  | 950 | 412 | 7928091
Eastern Grid Total |  |  |  |  | 16921.242 | 8137 | 155991035.42
Western Grid Total |  |  |  |  | 11614.5 | 6314.41 | 129663588.36
National Grid Total |  |  |  |  | 28535.742 | 14451.41 | 285654623.78
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9315.86 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4494.6 | MW
i) Dhaka area |  |  | 5149.16 |  | MW | i) Khulna area |  |  |  | 1635.5 | MW
ii) Chattogram area |  |  | 1224.7 |  | MW | ii) Barishal area |  |  |  | 393 | MW
iii) Cumilla area |  |  | 1240 |  | MW | iii) Rajshahi area |  |  |  | 1539.1 | MW
iv) Mymensingh area |  |  | 1131 |  | MW | iv) Rangpur area |  |  |  | 927 | MW
v) Sylhet area |  |  | 571 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13810.46 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 76 | 19:00 | 133 | Patuakhali | 68 | 22:00
2 | AKSML | 114.1 | 17:00 | 68 | Jaldhaka | 81 | 19:30 | 134 | Payra | 28 | 21:00
3 | Aftabnagar | 32 | 18:30 | 69 | Jamalpur | 131 | 21:00 | 135 | Postogola | 53 | 13:00
4 | Agargaon | 99 | 13:00 | 70 | Jashore | 131 | 19:30 | 136 | Purbachal | 18 | 19:00
5 | Agrabad | 74 | 00:00 | 71 | Jhenaidah | 120 | 19:30 | 137 | Purbasadipur | 113 | 20:00
6 | Amnura | 40 | 19:30 | 72 | Joydebpur | 144 | 19:00 | 138 | Rahanpur | 26 | 22:00
7 | Ashuganj | 93 | 23:00 | 73 | Joypurhat | 60 | 22:00 | 139 | Rahim | 45 | 18:00
8 | BSRM | 190 | 00:00 | 74 | Juldah | 13 | 20:00 | 140 | Rajbari | 75 | 19:00
9 | Bagerhat | 77 | 19:30 | 75 | KSRM | 10 | 11:00 | 141 | Rajendrapur | 133 | 19:00
10 | Bajitpur | 51 | 19:30 | 76 | Kabirpur | 278 | 18:30 | 142 | Rajshahi | 144 | 21:00
11 | Bakulia | 84 | 19:00 | 77 | Kachua | 79 | 19:00 | 143 | Rajshahi-230 | 58 | 00:00
12 | Banani | 34 | 13:00 | 78 | Kallyanpur | 99 | 18:30 | 144 | Ramganj | 112 | 18:30
13 | Bangabhaban | 6 | 10:00 | 79 | Kalurghat | 36 | 09:00 | 145 | Rampur | 36 | 23:00
14 | Barapukuria | 62 | 21:00 | 80 | Kamrangirchar | 64.4 | 13:00 | 146 | Rangamati | 16 | 18:30
15 | Barguna | 18 | 19:30 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 144 | 20:00
16 | Barishal | 117 | 13:00 | 82 | Kasba | 33 | 22:00 | 148 | Ruppur | 5.1 | 19:30
17 | Barishal-230 | 80 | 19:00 | 83 | Kazla | 111 | 18:30 | 149 | SSM | 9 | 00:00
18 | Baroaulia | 55.8 | 15:00 | 84 | Keranigonj | 80 | 13:00 | 150 | Saidpur | 112 | 19:30
19 | Baroirhat | 60 | 19:30 | 85 | Khagrachori | 24 | 19:00 | 151 | Satkhira | 121 | 21:00
20 | Bashundhara | 160 | 13:00 | 86 | Khulna | 72 | 21:00 | 152 | Satmasjid | 99 | 19:00
21 | BashundharaCement | 7 | 09:00 | 87 | Khulshi | 142 | 22:00 | 153 | Savar | 204 | 16:00
22 | Beanibazar | 72 | 18:30 | 88 | Kishoreganj | 110 | 00:00 | 154 | SevenRings | 18.2 | 15:00
23 | Benapole | 59 | 20:00 | 89 | Kodda | 309 | 18:00 | 155 | ShahCement | 35 | 23:00
24 | Bhaluka | 146 | 19:00 | 90 | Kulaura | 42 | 19:00 | 156 | Shahjadpur | 85 | 19:00
25 | Bhandaria | 44 | 21:00 | 91 | Kurigram | 68 | 18:30 | 157 | Shahjibazar | 118 | 21:00
26 | Bhangura | 45 | 19:30 | 92 | Kushtia | 138 | 19:00 | 158 | Shahmirpur | 49 | 00:00
27 | Bheramara(GK) | 57 | 21:00 | 93 | Lalbag | 66 | 12:00 | 159 | Shariatpur | 75 | 21:00
28 | Bhulta | 253 | 23:00 | 94 | Lalmonirhat | 64 | 19:00 | 160 | Sherpur | 148 | 19:30
29 | Bog-Sherpur | 70 | 19:00 | 95 | MI_Cement | 18 | 12:00 | 161 | Shikalbaha | 26 | 19:00
30 | Bogura | 173 | 19:30 | 96 | Madanganj | 42 | 18:30 | 162 | Shitalakhya | 76.1 | 15:00
31 | Borhanuddin | 74 | 22:00 | 97 | Madaripur | 101 | 19:00 | 163 | Sholosohor | 32 | 15:00
32 | Brahmanbaria | 120 | 20:00 | 98 | Madartek | 67.14 | 22:00 | 164 | Shyampur | 180 | 12:00
33 | Cantonment | 106 | 12:00 | 99 | Madunaghat | 47 | 18:30 | 165 | Siddhirganj | 114 | 16:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 61 | 19:30 | 166 | Sirajganj | 114 | 19:30
35 | Chandpur | 62 | 21:00 | 101 | Mahasthangarh | 74 | 19:30 | 167 | Sonargaon | 97 | 15:00
36 | Chandraghona | 32 | 19:00 | 102 | Manikganj | 131 | 19:00 | 168 | Sreemongol | 70 | 18:30
37 | Chapai | 63 | 22:00 | 103 | Maniknagar | 59 | 13:00 | 169 | Sreepur | 102 | 12:00
38 | Charsaidpur | 40 | 15:00 | 104 | Matarbari | 45 | 01:00 | 170 | Srinagar | 43.08 | 21:00
39 | Chauddagram | 57 | 19:30 | 105 | Matuail | 62 | 15:00 | 171 | Sunamganj | 57 | 20:00
40 | Chhatak | 35 | 19:30 | 106 | Millgate | 90 | 12:00 | 172 | Sylhet | 43 | 19:00
41 | Chowmuhani | 195 | 22:00 | 107 | Mirpur | 128 | 19:00 | 173 | Sylhet-132 | 117 | 19:00
42 | Chuadanga | 107 | 20:00 | 108 | Mirsorai | 6 | 11:00 | 174 | TK | 29.8 | 00:00
43 | Coxsbazar | 118 | 00:00 | 109 | Mirzapur | 47 | 22:00 | 175 | Tangail | 178 | 20:00
44 | Cumilla(N) | 132 | 18:30 | 110 | Mithapukur | 52 | 19:00 | 176 | Thakurgaon | 99 | 19:30
45 | Cumilla(S) | 170 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 138 | 19:30
46 | Daudkandi | 135 | 19:30 | 112 | Mogbazar | 105.1 | 15:00 | 178 | Ullahpara | 38 | 19:00
47 | Dhaka | 46 | 13:00 | 113 | Mongla | 30 | 12:00 | 179 | Ullon | 42 | 19:30
48 | Dhamrai | 126 | 21:00 | 114 | Motijheel | 34 | 13:00 | 180 | Uttara | 83 | 13:00
49 | Dhanmondi | 127 | 13:00 | 115 | Muktagacha | 38 | 19:00 | 181 | UttaraNew | 45 | 19:00
50 | Dohazari | 88 | 19:00 | 116 | Munshiganj | 99 | 23:00 | 182 | Zigatola | 84 | 13:00
51 | Faridpur | 153 | 19:30 | 117 | Muradnagar | 26 | 20:00
52 | Fatullah | 98 | 12:00 | 118 | Mymensingh | 218 | 21:00
53 | Fenchuganj | 35 | 22:00 | 119 | Naogaon | 131 | 19:30
54 | Feni | 89 | 21:00 | 120 | Narail | 54.5 | 19:30
55 | GPH | 92 | 15:00 | 121 | Narinda | 70 | 13:00
56 | Ghatail | 86 | 21:00 | 122 | Narshingdi | 180 | 20:00
57 | Ghorashal | 16 | 14:00 | 123 | Natore | 158 | 19:30
58 | Ghorashal-230 | 86 | 21:00 | 124 | Nawabganj | 52.4 | 21:00
59 | Goalpara | 30 | 16:00 | 125 | Netrakona | 129 | 22:00
60 | Gollamari | 84 | 19:30 | 126 | New | 78.9 | 12:00
61 | Gopalganj | 95.8 | 21:00 | 127 | Niamatpur | 88 | 19:30
62 | Gulshan | 94 | 13:00 | 128 | Noapara | 42 | 19:00
63 | Halishahar | 73 | 10:00 | 129 | PHP | 9 | 16:00
64 | HaripurSBU | 165 | 09:00 | 130 | Pabna | 120 | 19:30
65 | Hasnabad | 76 | 20:00 | 131 | Palashbari | 102 | 19:30
66 | Hathazari | 75 | 19:30 | 132 | Panchagarh | 56 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11432.36 | 0 |  | 11432.36
1:00 | 11020.57 | 0 |  | 11020.57
2:00 | 10464.02 | 0 |  | 10464.02
3:00 | 10133.83 | 0 |  | 10133.83
4:00 | 9807.18 | 0 |  | 9807.18
5:00 | 9687.25 | 0 |  | 9687.25
6:00 | 9521.19 | 0 |  | 9521.19
7:00 | 9862.03 | 0 |  | 9862.03
8:00 | 9997.6 | 0 |  | 9997.6
9:00 | 10467.74 | 0 |  | 10467.74
10:00 | 10669.6 | 0 |  | 10669.6
11:00 | 11172.53 | 0 |  | 11172.53
12:00 | 11971.09 | 0 |  | 11971.09
13:00 | 12339.71 | 0 |  | 12339.71
14:00 | 12295.19 | 0 |  | 12295.19
15:00 | 12065.32 | 0 |  | 12065.32
16:00 | 12301.13 | 0 |  | 12301.13
17:00 | 12138.7 | 0 |  | 12138.7
18:00 | 12212.19 | 0 |  | 12212.19
19:00 | 14185.81 | 43 |  | 14230.81
19:30 | 14451.41 | 47 |  | 14500.41
20:00 | 14284.32 | 49 |  | 14335.53
21:00 | 14304 | 0 |  | 14304
22:00 | 14081 | 0 |  | 14081
23:00 | 13702 | 17 |  | 13720
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6190 | 5242.36 | 11432.36 | DAILY GENERATION CURVE
00:30 | 6120 | 5106.465 | 11226.465
01:00 | 6050 | 4970.57 | 11020.57 | 19-04-2025
01:30 | 5938 | 4804.295 | 10742.295
02:00 | 5826 | 4638.02 | 10464.02
02:30 | 5671.5 | 4627.425 | 10298.925
03:00 | 5517 | 4616.83 | 10133.83
03:30 | 5388 | 4582.505 | 9970.505
04:00 | 5259 | 4548.18 | 9807.18
04:30 | 5206 | 4541.215 | 9747.215
05:00 | 5153 | 4534.25 | 9687.25
05:30 | 5118.46 | 4485.76 | 9604.22
06:00 | 5083.92 | 4437.27 | 9521.19
06:30 | 5143.39 | 4548.22 | 9691.61
07:00 | 5202.86 | 4659.17 | 9862.03
07:30 | 5217.31 | 4712.505 | 9929.815
08:00 | 5231.76 | 4765.84 | 9997.6
08:30 | 5436.84 | 4795.83 | 10232.67
09:00 | 5641.92 | 4825.82 | 10467.74
09:30 | 5669.575 | 4899.095 | 10568.67
10:00 | 5697.23 | 4972.37 | 10669.6
10:30 | 5880.935 | 5040.13 | 10921.065
11:00 | 6064.64 | 5107.89 | 11172.53
11:30 | 6237.365 | 5334.445 | 11571.81
12:00 | 6410.09 | 5561 | 11971.09
12:30 | 6581.335 | 5574.065 | 12155.4
13:00 | 6752.58 | 5587.13 | 12339.71
13:30 | 6767.6 | 5549.85 | 12317.45
14:00 | 6782.62 | 5512.57 | 12295.19
14:30 | 6717.6 | 5462.655 | 12180.255
15:00 | 6652.58 | 5412.74 | 12065.32
15:30 | 6687.4 | 5495.825 | 12183.225
16:00 | 6722.22 | 5578.91 | 12301.13
16:30 | 6710.415 | 5509.5 | 12219.915
17:00 | 6698.61 | 5440.09 | 12138.7
17:30 | 6769.93 | 5405.515 | 12175.445
18:00 | 6841.25 | 5370.94 | 12212.19
18:30 | 7487.125 | 5711.875 | 13199
19:00 | 8133 | 6052.81 | 14185.81
19:30 | 8137 | 6314.41 | 14451.41
20:00 | 8033 | 6251.32 | 14284.32
20:30 | 8029.5 | 6264.66 | 14294.16 |  | Executive Engineer
21:00 | 8026 | 6278 | 14304 |  | Network Operation Division
21:30 | 7972.5 | 6220 | 14192.5
22:00 | 7919 | 6162 | 14081
22:30 | 7825 | 6066.5 | 13891.5
23:00 | 7731 | 5971 | 13702

## En-Curve
QF-LDC-12
Date | 19-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3580 | 2294 | 916 | 0 | 72 | 842.36 | 40 | 3265 | 0 | 75 | 348 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3547.5 | 2278.5 | 915 | 0 | 71 | 833.965 | 40 | 3127.5 | 0 | 76.5 | 332.5 | 0 | 0 | 4 | 0 | 19-04-2025
01:00 | 3515 | 2263 | 914 | 0 | 70 | 825.57 | 40 | 2990 | 0 | 78 | 317 | 0 | 0 | 8 | 0
01:30 | 3419 | 2194 | 915 | 0 | 69 | 821.795 | 40 | 2929 | 0 | 65 | 280 | 0 | 0 | 9.5 | 0 | Energy Generated | 285.6546 |  | MKWHr
02:00 | 3323 | 2125 | 916 | 0 | 68 | 818.02 | 40 | 2868 | 0 | 52 | 243 | 0 | 0 | 11 | 0 | Energy not Served | 0.109 |  | MKWHr
02:30 | 3293.5 | 2017.5 | 916.5 | 0 | 67 | 820.925 | 40 | 2862 | 0 | 52 | 218.5 | 0 | 0 | 11 | 0 | Total Energy Requirement | 285.7636 |  | MKWHr
03:00 | 3264 | 1910 | 917 | 0 | 66 | 823.83 | 40 | 2856 | 0 | 52 | 194 | 0 | 0 | 11 | 0
03:30 | 3193 | 1826.5 | 916.5 | 0 | 66 | 824.005 | 40 | 2852.5 | 0 | 52 | 189 | 0 | 0 | 11 | 0
04:00 | 3122 | 1743 | 916 | 0 | 66 | 824.18 | 40 | 2849 | 0 | 52 | 184 | 0 | 0 | 11 | 0
04:30 | 3131.5 | 1699 | 916 | 0 | 66 | 823.715 | 40 | 2837 | 0 | 34.5 | 184 | 0 | 0 | 15.5 | 0
05:00 | 3141 | 1655 | 916 | 0 | 66 | 823.25 | 40 | 2825 | 0 | 17 | 184 | 0 | 0 | 20 | 0
05:30 | 3078 | 1619.5 | 916 | 0 | 65 | 821.855 | 40 | 2830 | 6.365 | 17.5 | 183.5 | 0 | 0 | 26.5 | 0
06:00 | 3015 | 1584 | 916 | 0 | 64 | 820.46 | 40 | 2835 | 12.73 | 18 | 183 | 0 | 0 | 33 | 0
06:30 | 3062 | 1626 | 916 | 0 | 61 | 821.43 | 40 | 2836.5 | 62.18 | 47.5 | 202.5 | 0 | 0 | 16.5 | 0
07:00 | 3109 | 1668 | 916 | 0 | 58 | 822.4 | 40 | 2838 | 111.63 | 77 | 222 | 0 | 0 | 0 | 0
07:30 | 3141.5 | 1654.5 | 892 | 0 | 59 | 822.57 | 40 | 2829.5 | 189.245 | 76.5 | 224 | 0 | 0 | 1 | 0
08:00 | 3174 | 1641 | 868 | 0 | 60 | 822.74 | 40 | 2821 | 266.86 | 76 | 226 | 0 | 0 | 2 | 0
08:30 | 3240.5 | 1709.75 | 868.5 | 0 | 61 | 822.37 | 40 | 2813.5 | 335.65 | 80 | 258.4 | 0 | 0 | 3 | 0
09:00 | 3307 | 1778.5 | 869 | 0 | 62 | 822 | 40 | 2806 | 404.44 | 84 | 290.8 | 0 | 0 | 4 | 0
09:30 | 3300.5 | 1773.25 | 892.5 | 0 | 57 | 822 | 40 | 2812.5 | 453.02 | 84 | 320.9 | 0 | 0 | 13 | 0
10:00 | 3294 | 1768 | 916 | 0 | 52 | 822 | 40 | 2819 | 501.6 | 84 | 351 | 0 | 0 | 22 | 0
10:30 | 3363 | 1903.5 | 916 | 0 | 56 | 824 | 40 | 2833 | 513.565 | 84 | 353.5 | 0 | 0 | 34.5 | 0
11:00 | 3432 | 2039 | 916 | 0 | 60 | 826 | 40 | 2847 | 525.53 | 84 | 356 | 0 | 0 | 47 | 0
11:30 | 3466 | 2070 | 916 | 0 | 61 | 856.5 | 40 | 3048.5 | 553.31 | 117.5 | 400 | 0 | 0 | 43 | 0
12:00 | 3500 | 2101 | 916 | 0 | 62 | 887 | 40 | 3250 | 581.09 | 151 | 444 | 0 | 0 | 39 | 0
12:30 | 3568.5 | 2121.5 | 916 | 0 | 69 | 903 | 40 | 3276.5 | 560.4 | 160 | 521 | 0 | 0 | 19.5 | 0
13:00 | 3637 | 2142 | 916 | 0 | 76 | 919 | 40 | 3303 | 539.71 | 169 | 598 | 0 | 0 | 0 | 0
13:30 | 3640.5 | 2140 | 916 | 0 | 78 | 914.57 | 40 | 3328.5 | 530.38 | 166 | 562.5 | 0 | 0 | 1 | 0
14:00 | 3644 | 2138 | 916 | 0 | 80 | 910.14 | 40 | 3354 | 521.05 | 163 | 527 | 0 | 0 | 2 | 0
14:30 | 3625 | 1980 | 915.5 | 0 | 78 | 937 | 40 | 3435.5 | 452.255 | 187.5 | 528.5 | 0 | 0 | 1 | 0
15:00 | 3606 | 1822 | 915 | 0 | 76 | 963.86 | 40 | 3517 | 383.46 | 212 | 530 | 0 | 0 | 0 | 0
15:30 | 3592 | 1810 | 915 | 0 | 76 | 989.16 | 40 | 3624 | 346.065 | 220 | 571 | 0 | 0 | 0 | 0
16:00 | 3578 | 1798 | 915 | 0 | 76 | 1014.46 | 40 | 3731 | 308.67 | 228 | 612 | 0 | 0 | 0 | 0
16:30 | 3526.5 | 1838.5 | 915 | 0 | 74 | 1015.495 | 40 | 3755.5 | 219.42 | 221.5 | 612 | 0 | 0 | 2 | 0
17:00 | 3475 | 1879 | 915 | 0 | 72 | 1016.53 | 40 | 3780 | 130.17 | 215 | 612 | 0 | 0 | 4 | 0
17:30 | 3410 | 1916.5 | 915.5 | 0 | 75 | 1062.04 | 40 | 3776.5 | 72.905 | 254.5 | 650.5 | 0 | 0 | 2 | 0
18:00 | 3345 | 1954 | 916 | 0 | 78 | 1107.55 | 40 | 3773 | 15.64 | 294 | 689 | 0 | 0 | 0 | 0
18:30 | 3491 | 2240 | 891.5 | 0 | 85 | 1212.18 | 40 | 3944.5 | 7.82 | 381 | 902.5 | 0 | 0 | 3.5 | 21.5
19:00 | 3637 | 2526 | 867 | 0 | 92 | 1316.81 | 40 | 4116 | 0 | 468 | 1116 | 0 | 0 | 7 | 43
19:30 | 3540 | 2509 | 868 | 0 | 88 | 1359.41 | 40 | 4182 | 0 | 507 | 1351 | 0 | 0 | 7 | 47
20:00 | 3529 | 2487 | 867 | 0 | 92 | 1353.32 | 40 | 4035 | 0 | 519 | 1358 | 0 | 0 | 4 | 49
20:30 | 3558.5 | 2522.5 | 891 | 0 | 92 | 1358.66 | 40 | 4005 | 0 | 519 | 1305.5 | 0 | 0 | 2 | 24.5
21:00 | 3588 | 2558 | 915 | 0 | 92 | 1364 | 40 | 3975 | 0 | 519 | 1253 | 0 | 0 | 0 | 0
21:30 | 3583 | 2561.5 | 914.5 | 0 | 92 | 1363.5 | 40 | 3966.5 | 0 | 493 | 1178 | 0 | 0 | 0.5 | 0
22:00 | 3578 | 2565 | 914 | 0 | 92 | 1363 | 40 | 3958 | 0 | 467 | 1103 | 0 | 0 | 1 | 0
22:30 | 3597.5 | 2533 | 913.5 | 0 | 92 | 1360.5 | 40 | 3910.5 | 0 | 445 | 996.5 | 0 | 0 | 3 | 8.5
23:00 | 3617 | 2501 | 913 | 0 | 92 | 1358 | 40 | 3863 | 0 | 423 | 890 | 0 | 0 | 5 | 17
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 400 | 06:00 | 377 | 16:00 | Payra | 417 | 06:00 | 407 | 16:00
Ashuganj | 406 | 6:00 | 382 | 15:00 | Rahanpur | 415 | 03:00 | 395 | 19:00
Bhulta | 402 | 02:00 | 380 | 16:00 | Rampal | 408 | 03:00 | 388 | 19:00
Bibiana | 391 | 01:00 | 383 | 15:00
BIPTC | 404 | 04:00 | 393 | 15:00
Bogura | 409 | 04:00 | 384 | 19:00
Gopalganj | 407 | 04:00 | 386 | 19:00
Kaliakoir | 374 | 07:00 | 353 | 18:30
Madunaghat | 404 | 06:00 | 390 | 17:00
Meghnaghat | 400 | 02:00 | 374 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 234 | 07:00 | 216 | 16:00 | Keranigonj | 232 | 07:00 | 214 | 16:00
AKSML | 234 | 05:00 | 222 | 16:00 | Khulna(S) | 235 | 05:00 | 218 | 19:00
Aminbazar | 231 | 05:00 | 218 | 15:00 | Madunaghat | 234 | 06:00 | 224 | 16:00
Ashuganj | 233 | 07:00 | 222 | 16:00 | Madunaghat-400 | 235 | 08:00 | 225 | 16:00
Ashuganj-400 | 233 | 07:00 | 222 | 16:00 | Maniknagar | 229 | 04:00 | 214 | 16:00
Baghabari | 233 | 06:00 | 224 | 18:30 | Meghnaghat | 240 | 05:00 | 223 | 16:00
Barapukuria | 223 | 04:00 | 211 | 19:00 | Meghnaghat-400 | 232 | 04:00 | 218 | 16:00
Barapukuria-230 | 223 | 04:00 | 211 | 19:00 | Mirsorai | 231 | 05:00 | 217 | 16:00
Barishal | 237 | 03:00 | 225 | 19:00 | Rajshahi | 230 | 05:00 | 219 | 19:00
Bheramara | 232 | 20:00 | 222 | 17:00 | Rampal | 234 | 04:00 | 217 | 19:00
Bhulta | 229 | 03:00 | 215 | 16:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 01:00 | 218 | 17:00 | Rampura | 229 | 06:00 | 213 | 16:00
BIPTC | 233 | 04:00 | 223 | 19:00 | Shikalbaha | 232 | 08:00 | 222 | 16:00
Bogura | 229 | 02:00 | 214 | 19:00 | Shyampur | 231 | 05:00 | 215 | 16:00
Bogura-400 | 229 | 03:00 | 215 | 19:00 | Siddhirganj | 232 | 05:00 | 221 | 13:00
Borhanuddin | 240 | 04:00 | 232 | 20:00 | Sirajgonj | 239 | 05:00 | 232 | 19:00
BSRM | 231 | 06:00 | 217 | 16:00 | Sreepur | 229 | 02:00 | 221 | 17:00
Cumilla(N) | 228 | 07:00 | 216 | 16:00 | Tongi | 226 | 04:00 | 210 | 15:00
Faridpur | 233 | 05:00 | 218 | 19:00
Fenchuganj | 228 | 12:00 | 222 | 18:30
Ghorashal | 235 | 01:00 | 225 | 14:00
Ghorashal-230 | 230 | 11:00 | 214 | 15:00
Gopalganj | 233 | 04:00 | 221 | 19:00
GPH | 233 | 06:00 | 220 | 16:00
Haripur | 230 | 04:00 | 215 | 16:00
Hasnabad | 232 | 05:00 | 214 | 16:00
Hathazari | 235 | 08:00 | 224 | 19:00
Ishurdi | 233 | 04:00 | 224 | 19:00
Jhenaidah | 230 | 05:00 | 214 | 19:00
Kaliakoir | 232 | 07:00 | 218 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 02:00 | 126 | 16:00 | Madartek | 137 | 04:00 | 125 | 16:00
Agargaon | 138 | 04:00 | 127 | 16:00 | Madunaghat | 134 | 05:00 | 127 | 16:00
Agrabad | 134 | 06:00 | 126 | 16:00 | Magura | 134 | 05:00 | 119 | 19:00
AKS | 132 | 04:00 | 125 | 16:00 | Mahasthangarh | 132 | 04:00 | 119 | 19:00
Aminbazar | 131 | 06:00 | 122 | 15:00 | Manikganj | 128 | 07:00 | 118 | 12:00
Amnura | 134 | 01:00 | 127 | 19:00 | Maniknagar | 136 | 06:00 | 125 | 16:00
Ashuganj | 138 | 07:00 | 130 | 17:00 | Matarbari | 129 | 08:00 | 112 | 00:00
Bagerhat | 135 | 05:00 | 116 | 19:00 | Matuail | 134.5 | 05:00 | 125 | 16:00
Bajitpur | 133 | 03:00 | 124 | 17:00 | Millgate | 132 | 07:00 | 119 | 16:00
Bakulia | 134 | 05:00 | 120 | 16:00 | Mirpur | 133 | 05:00 | 121 | 16:00
Banani | 137 | 02:00 | 126 | 15:00 | Mirzapur | 131 | 08:00 | 121 | 18:30
Bangabhaban | 135 | 03:00 | 125 | 16:00 | Mithapukur | 131 | 04:00 | 117 | 19:00
Barapukuria | 136 | 05:00 | 126 | 19:00 | MI_Cement | 135 | 05:00 | 125 | 16:00
Barguna | 136 | 03:00 | 131 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 05:00 | 123 | 19:00 | Mogbazar | 139 | 05:00 | 127 | 16:00
Barishal-230 | 134 | 05:00 | 124 | 19:00 | Mongla | 135 | 06:00 | 118 | 19:00
Baroaulia | 134 | 06:00 | 127 | 16:00 | Motijheel | 138 | 07:00 | 125 | 16:00
Baroirhat | 126 | 05:00 | 118 | 16:00 | Muktagacha | 134 | 09:00 | 117 | 18:30
Bashundhara | 137 | 02:00 | 120 | 15:00 | Munshiganj | 134 | 04:00 | 124 | 16:00
BashundharaCement | 132 | 01:00 | 124 | 17:00 | Muradnagar | 130 | 06:00 | 120 | 16:00
Beanibazar | 132 | 04:00 | 126 | 18:30 | Mymensingh | 136 | 09:00 | 116 | 18:30
Benapole | 133 | 05:00 | 116 | 19:00 | Naogaon | 130 | 03:00 | 117 | 19:00
Bhaluka | 131 | 02:00 | 124 | 18:30 | Narail | 136 | 06:00 | 118 | 19:00
Bhandaria | 130 | 05:00 | 114 | 21:00 | Narinda | 136 | 06:00 | 125 | 16:00
Bhangura | 133 | 02:00 | 125 | 19:00 | Narshingdi | 130 | 05:00 | 118 | 19:00
Bheramara | 135 | 05:00 | 127 | 19:00 | Natore | 133 | 05:00 | 123 | 19:00
Bheramara(GK) | 135 | 04:00 | 128 | 11:00 | Nawabganj | 136 | 06:00 | 124 | 16:00
Bhulta | 127 | 05:00 | 120 | 16:00 | Netrakona | 128 | 03:00 | 114 | 18:30
Bog-Sherpur | 132 | 04:00 | 121 | 19:00 | New | 134 | 07:00 | 121 | 17:00
Bogura | 134 | 05:00 | 123 | 19:00 | Niamatpur | 137 | 01:00 | 130 | 18:30
Bogura-230 | 134 | 04:00 | 122 | 19:00 | Noapara | 136 | 04:00 | 124 | 19:00
Brahmanbaria | 128 | 04:00 | 123 | 17:00 | Pabna | 134 | 03:00 | 126 | 19:00
Cantonment | 138 | 04:00 | 127 | 15:00 | Palashbari | 129 | 03:00 | 115 | 19:00
Chandina | 132 | 01:00 | 122 | 16:00 | Panchagarh | 133 | 05:00 | 119 | 12:00
Chandpur | 124 | 20:00 | 116 | 14:00 | Patuakhali | 136 | 09:00 | 132 | 19:00
Chandraghona | 135 | 06:00 | 128 | 16:00 | Payra | 137 | 02:00 | 133 | 19:30
Chapai | 135 | 01:00 | 127 | 19:30 | PHP | 126 | 06:00 | 115 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 03:00 | 125 | 15:00 | Postogola | 137 | 06:00 | 126 | 16:00
Chauddagram | 127 | 05:00 | 117 | 16:00 | Purbachal | 137 | 01:00 | 126 | 15:00
Chhatak | 131 | 05:00 | 125 | 18:30 | Purbasadipur | 129 | 05:00 | 115 | 19:00
Chowmuhani | 123 | 06:00 | 113 | 16:00 | Rahanpur | 139 | 06:00 | 132 | 19:00
Chuadanga | 134 | 04:00 | 118 | 18:30 | Rahanpur-400 | 139 | 03:00 | 132 | 19:00
Coxsbazar | 128 | 07:00 | 112 | 00:00 | Rahim | 134 | 04:00 | 127 | 13:00
Cumilla(N) | 131 | 05:00 | 122 | 15:00 | Rajbari | 137 | 04:00 | 127 | 19:00
Cumilla(S) | 130 | 04:00 | 120 | 15:00 | Rajendrapur | 133 | 02:00 | 122 | 15:00
Daudkandi | 129 | 06:00 | 118 | 21:00 | Rajshahi | 134 | 03:00 | 124 | 19:00
Dhaka | 138 | 06:00 | 127 | 16:00 | Rajshahi-230 | 133 | 05:00 | 124 | 19:00
Dhamrai | 142 | 07:00 | 129 | 23:00 | Ramganj | 123 | 20:00 | 112 | 16:00
Dhanmondi | 138 | 05:00 | 127 | 15:00 | Rampur | 134 | 07:00 | 126 | 16:00
Dohazari | 132 | 09:00 | 122 | 00:00 | Rampura | 137 | 02:00 | 126 | 15:00
Faridpur | 137 | 03:00 | 129 | 19:00 | Rangamati | 134 | 06:00 | 127 | 16:00
Fatullah | 135 | 04:00 | 125 | 16:00 | Rangpur | 130 | 05:00 | 113 | 19:00
Fenchuganj | 136 | 01:00 | 132 | 15:00 | Ruppur | 137 | 05:00 | 130 | 19:00
Feni | 132 | 19:00 | 117 | 15:00 | Saidpur | 130 | 02:00 | 117 | 19:00
Ghatail | 132 | 07:00 | 115 | 19:00 | Satkhira | 135 | 04:00 | 117 | 19:00
Ghorashal | 137 | 01:00 | 129 | 14:00 | Satmasjid | 138 | 05:00 | 127 | 16:00
Goalpara | 137 | 05:00 | 123 | 19:00 | Savar | 132 | 04:00 | 120 | 12:00
Gollamari | 138 | 05:00 | 124 | 19:00 | SevenRings | 137 | 07:00 | 128 | 17:00
Gopalganj | 137 | 03:00 | 125 | 19:00 | ShahCement | 134 | 03:00 | 125 | 15:00
Gopalganj-400 | 139 | 04:00 | 130 | 19:00 | Shahjadpur | 136 | 06:00 | 129 | 19:00
Gulshan | 137 | 04:00 | 126 | 16:00 | Shahjibazar | 130 | 02:00 | 125 | 19:00
Halishahar | 133 | 05:00 | 127 | 16:00 | Shahmirpur | 135 | 06:00 | 129 | 18:00
Haripur | 134 | 02:00 | 125 | 16:00 | Shariatpur | 137 | 05:00 | 126 | 19:00
HaripurSBU | 134 | 02:00 | 125 | 16:00 | Sherpur | 136 | 09:00 | 122 | 18:30
Hasnabad | 137 | 03:00 | 127 | 16:00 | Shikalbaha | 124 | 03:00 | 118 | 16:00
Hathazari | 136 | 04:00 | 130 | 16:00 | Shikalbaha-230 | 136 | 08:00 | 129 | 16:00
Ishurdi | 137 | 04:00 | 131 | 19:00 | Shitalakhya | 135 | 05:00 | 125 | 16:00
Jaldhaka | 126 | 04:00 | 113 | 19:00 | Sholosohor | 134 | 05:00 | 127 | 16:00
Jamalpur | 137 | 01:00 | 125 | 19:00 | Shyampur | 133 | 07:00 | 125 | 15:00
Jashore | 134 | 05:00 | 117 | 19:00 | Shyampur-230 | 135 | 05:00 | 124 | 16:00
Jhenaidah | 134 | 06:00 | 122 | 19:00 | Siddhirganj | 135 | 05:00 | 126 | 16:00
Jhenaidah-230 | 136 | 04:00 | 122 | 19:00 | Sirajganj | 132 | 03:00 | 120 | 19:00
Joydebpur | 133 | 06:00 | 124 | 17:00 | Sonargaon | 133 | 04:00 | 123 | 15:00
Joypurhat | 130 | 04:00 | 113 | 19:00 | Sreemongol | 132 | 02:00 | 126 | 21:00
Juldah | 134 | 05:00 | 128 | 18:30 | Sreepur | 134 | 02:00 | 128 | 17:00
Kabirpur | 133 | 07:00 | 117 | 15:00 | Srinagar | 135 | 03:00 | 124 | 16:00
Kachua | 124 | 06:00 | 116 | 16:00 | SSM | 139 | 09:00 | 125 | 17:00
Kaliakoir | 142 | 07:00 | 126 | 11:00 | Sunamganj | 130 | 07:00 | 123 | 19:00
Kallyanpur | 134 | 04:00 | 122 | 16:00 | Sylhet | 132 | 04:00 | 128 | 19:00
Kalurghat | 134 | 04:00 | 128 | 16:00 | Sylhet-132 | 132 | 00:00 | 129 | 18:30
Kamrangirchar | 135 | 04:00 | 123 | 16:00 | Tangail | 129 | 09:00 | 118 | 19:00
Kaptai | 137 | 8:00 | 131 | 16:00 | Thakurgaon | 134 | 05:00 | 120 | 19:00
Kasba | 130 | 06:00 | 119 | 16:00 | TK | 135 | 05:00 | 128 | 16:00
Kazla | 135 | 04:00 | 124 | 16:00 | Tongi | 134 | 04:00 | 122 | 15:00
Keranigonj | 136 | 05:00 | 124 | 16:00 | Ullahpara | 133 | 04:00 | 124 | 19:00
Khagrachori | 134 | 06:00 | 126 | 16:00 | Ullon | 137 | 03:00 | 126 | 15:00
Khulna | 137 | 05:00 | 121 | 19:00 | Uttara | 132 | 02:00 | 120 | 16:00
Khulna(S) | 138 | 05:00 | 124 | 19:00 | UttaraNew | 134 | 06:00 | 121 | 12:00
Khulshi | 133 | 05:00 | 125 | 15:00 | Zigatola | 136 | 05:00 | 124 | 16:00
Kishoreganj | 131 | 04:00 | 123 | 17:00
Kodda | 132 | 06:00 | 122 | 16:00
KSRM | 134 | 06:00 | 126 | 16:00
Kulaura | 135 | 03:00 | 131 | 15:00
Kurigram | 129 | 15:00 | 110 | 19:00
Kushtia | 134 | 03:00 | 126 | 19:00
Lalbag | 136 | 06:00 | 123 | 16:00
Lalmonirhat | 128 | 05:00 | 111 | 19:00
Madanganj | 133 | 03:00 | 124 | 16:00
Madaripur | 136 | 01:00 | 128 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division