## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID BANGLADESH PLC
SYSTEM OPERATION DATA
Month: March 2025
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2025-03-02 |  | 2025-02-01 |  | 2024-03-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15336.92 | 2025-03-15 | 12659.87 | 2025-02-25 | 13898 | 2024-03-31 | 16477 | 2024-04-30
|  |  | 21:00 Hr. |  | 19:00 Hr. |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 8360.79 | 2025-03-08 | 6902.27 | 2025-02-08 | 7249 | 2024-03-22 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 11385.54 | 2025-01-31 | 12659.87 | 2025-02-25 | 13898 | 2024-03-31 | 16477 | 2024-04-30
|  |  | 19:00 Hr. |  | 19:00 Hr. |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 13926.95 | 2025-03-27 | 11609.39 | 2025-02-18 | 11821 | 2024-03-27 | 14488 | 2024-05-16
|  |  | 12:00 Hr. |  | 12:00 Hr. |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14658 | 2025-03-15 | 12119 | 2025-02-25 | 14050 | 2024-03-30 | 17200 | 2024-04-29
|  |  | 21:00 Hr. |  | 19:00 Hr. |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 13455.0287 |  | 11482.7239 |  | 11984.9032 |  | - | -
7 | Average Generation (MW) at Day Peak | 12259.0329 |  | 10803.4786 |  | 10819.7097 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 936 | 2025-03-01 | 936 | 2025-02-24 | 964 | 2024-03-28 | 970 | 2024-07-06
|  |  | 2:00 |  | 23:30 |  | 13:30 |  | 14:30
9 | Maximum Power Import from Tripura, India (MW) | 173 | 2025-03-19 | 157 | 2025-02-27 | 165 | 2024-03-31 | 194 | 12/06/19
|  |  | 21:00 |  | 14:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 113 | 2025-03-16 | 198 | 2025-02-24 | 666 | 2024-03-30 | 4395 | 04/10/2022
|  |  | 19:00 |  | 19:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14425 | 2025-03-16 | 11673 | 2025-02-24 | 13353 | 45381 | 14965 | 2024-05-16
|  |  | 19:00 |  | 19:00 | - | 0.875 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2025-03-03 | 0 | 2025-02-02 | 0 | 45377 | - | -
|  |  | 19:00 |  | 19:00 |  | 21:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12195 | 2025-03-03 | 10784 | 2025-02-02 | 12107 | 2024-03-26 | - | -
|  |  | 19:00 |  | 19:00 |  | 21:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 175 | 2025-03-20 | 153 | 2025-02-25 | 513 | 45365 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12899 | 2025-03-20 | 11072 | 2025-02-25 | 11763 | 45365 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2025-03-01 | 0 | 2025-02-02 | 0 | 45377 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 11795 | 2025-03-03 | 10451 | 2025-02-02 | 9801 | 45377 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 4 |  | 21 |  | 23 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 13 |  | 24 |  | 23 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1723.1429 |  | 1181.7677 |  | 2159.2989 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 135.2017 |  | 92.8264 |  | 33.0767 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1587.9412 |  | 1088.9413 |  | 2126.2221 |  | - | -
23 | Net Generation of IPP (MKWH) | 2881.8044 |  | 2334.8935 |  | 2618.3608 |  | - | -
23b | Net Generation by Generation Companies | 2640.4845 |  | 1804.9675 |  | 2178.3732
24 | Net Generation of REB (MKWH) | 154.781 |  | 67.3293 |  | 99.727 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 239.0099 |  | 257.6077 |  | 104.0822 |  | - | -
25 | Total Net Generation (MKHWh) (Excluding Import) | 7504.021 |  | 5553.7393 |  | 7126.7654 |  | - | -
26 | Energy Generation by Gas (MKWH) | 4228.5203 |  | 2920.098 |  | 3706.1266 |  | - | -
27 | Energy Generation by Diesel (MKWH) | 432.8368 |  | 259.6658 |  | 23.3688 |  | - | -
28 | Energy Generation by Furnace Oil (MKWH) | 708.9829 |  | 888.4431 |  | 598.11 |  | - | -
29 | Energy Generation by Hydro (MKWH) | 0.74082 |  | 0.60499 |  | 23.5131 |  | - | -
30 | Energy Generation by Solar (MKWH) | 142.698 |  | 124.2522 |  | 91.681 |  | - | -
30b | Energy Generation by Wind (MKWH) | 0 |  | 0 |  | 8.0323 |  | - | -
31 | Energy Generation by Coal (MKWH) | 2125.4439 |  | 1453.5016 |  | 2708.9996 |  | - | -
32 | Enegry Import from India (MKWH) | 1468.4092 |  | 1050.6819 |  | 724.0301 |  | - | -
33 | Monthly Load Factor (%) | 79.8168 |  | 78.7223 |  | 73.5217 |  | - | -

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: March 2025
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 15336.92 | 2025-03-15 | 21:00 Hr.
Generation Period
| Dhaka | MW | 5369.74
| Chattogram | MW | 1432
| Cumilla | MW | 1419.5
| Mymensingh | MW | 1233
| Sylhet | MW | 549
a) | Total supply in East zone | MW | 10003.24
| Khulna | MW | 1829.2
| Barisal | MW | 460.5
| Rajshahi | MW | 1535.4
| Rangpur | MW | 792
b) | Total supply in West zone | MW | 4617.1
c) | Total supply in both zone ( a+b) | MW | 14620.34
Ref: | 27.21.0000.603.16.087.20.905 | Date: 17/04/2025
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:March 2025
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | -28 | 2025-03-30 | 17:00
| b) Ishurdi end | MW | 393 | 2025-03-15 | 11:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 952 | 2025-03-15 | 11:00
| b) Ishurdi end | MW | -6 | 2025-03-30 | 17:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.11209
| b) Ishurdi end | MKWH | 147.7654
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 143.3324
| b) Ishurdi end | MKWH | 0.10883
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 380 | 2025-03-03 | 2:00
| b)Serajganj end | MW | 690 | 2025-03-14 | 23:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 340 | 2025-03-03 | 15:00
| b)Sirajganj end | MW | 130 | 2025-03-25 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 336.9872
| b)Sirajganj end | MKWH | 0
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end(Sreepur) | MKWH | 2e-08
| b)Sirajganj end | MKWH | 347.808
30 | Transmission loss of EWI /NO-2 | % | 3.11'%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2224 | 2025-03-16 | 12:00
|  | MW | 1458
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2210 | 2025-03-16 | 12:00
|  | MW | 1457
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 26300 | 2025-03-16 | N/A
| a) Aminbazar end | MWh | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 26225 | 2025-03-16
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MKWH | 676.946
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MKWH | 674.467
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.366
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2025
| Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bajitpur 132/33kV | Tr-1(404T) HT | 2025-03-25 11:30 | 2025-03-25 14:50 | 0.13889 | E/O | 33 kV Bus section -1 Red hot remove maintenance . | 25 | 83.3333 | Power interruption
Bajitpur 132/33kV | Tr-2(414T) HT | 2025-03-25 13:23 | 2025-03-25 14:45 | 0.056944 | E/O | 33 kV Bus Section-2 nest cleaning maintenance | 8 | 10.9333 | Power interruption
Bhaluka 132/33kV | Transformer- 02 LT | 2025-03-25 19:50 | 2025-03-25 19:58 | 0.0055556 | T | Low frequency df/dt | 65 | 8.6667 | Power interruption
Bhaluka 132/33kV | Transformer- 01 LT | 2025-03-25 19:50 | 2025-03-25 19:57 | 0.0048611 | T | Opened by NLDC No | 65 | 7.5833 | Power interruption
Dhamrai 132/33kV | Transformer-2 HT | 2025-03-20 06:34 | 2025-03-20 09:09 | 0.10764 | E/O | High temperature LT bushing | 0 | 0 | No interruption
Kodda 132/33kV | Tr-1 (406T) HT | 2025-03-25 19:35 | 2025-03-25 19:47 | 0.0083333 | E/O | Rope remove from 33 kv B phase bushing | 55 | 11 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2025-03-18 09:38 | 2025-03-18 11:21 | 0.071528 | E/O | Maintenance Work | 0 | 0 | No interruption
Muktagacha 132/33kV | T-2(414T) HT | 2025-03-24 22:36 | 2025-03-24 22:36 | 0 | E/O | Maintenance Work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2025-03-17 13:36 | 2025-03-17 13:36 | 0 | E/O | Bird nest Cleaning | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2025-03-17 13:40 | 2025-03-17 14:00 | 0.013889 | E/O | Bird nest Cleaning | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2025-03-18 11:10 | 2025-03-18 11:48 | 0.026389 | E/O | Project work for Rajendrapur line bay commissioning. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2025-03-18 12:15 | 2025-03-18 12:39 | 0.016667 | E/O | Project work for Rajendrapur line Commissioning | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132/33 kV T-2 HT | 2025-03-27 07:16 | 2025-03-27 09:09 | 0.078472 | E/O | Red Hot at 33kV Bus section DS (2nd Section) | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 LT | 2025-03-02 09:04 | 2025-03-02 11:19 | 0.09375 | E/O | 33KV MAINTANANCE | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 HT | 2025-03-07 01:03 | 2025-03-07 02:43 | 0.069444 | E/O | high temperature at 33kv T-2 bus section | 75 | 125 | Power interruption
Tangail 132/33kV | Tr-4 HT | 2025-03-19 14:26 | 2025-03-19 15:28 | 0.043056 | E/O | Oil Leakage | 0 | 0 | No interruption
Tangail 132/33kV | Tr-1 LT | 2025-03-22 11:17 | 2025-03-22 11:42 | 0.017361 | T | Due to 33kv New REB, Porabari, Ghatail REB Feeder Fault. ABB REF 615 | 36 | 15 | Power interruption
Tangail 132/33kV | Tr-4 HT | 2025-03-22 12:01 | 2025-03-22 15:58 | 0.16458 | E/O | 33kv shakhipur feeder RED HOT. | 0 | 0 | No interruption
Tangail 132/33kV | Tr-2 HT | 2025-03-22 12:10 | 2025-03-22 15:47 | 0.15069 | E/O | 33Kv T-2 BUS Fault | 0 | 0 | No interruption
Tangail 132/33kV | Tr-4 HT | 2025-03-25 23:21 | 2025-03-26 10:33 | 0.46667 | E/O | Under Ground Cable problem | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 12:50 |  | Unserved Energy: |  | 261.5167
Dhaka (South) Grid Circle :
Keranigonj 230/132/33kV | TR-1 LT | 2025-03-21 14:55 | 2025-03-21 15:08 | 0.0090278 | T | PBS 33kV feeder fault Trip relay operated | 26 | 5.6333 | Power interruption
Nawabganj 132/33kV | TR-2 LT | 2025-03-09 17:05 | 2025-03-09 17:14 | 0.00625 | T | Overcurrent protection relay Trip due to 33Kv Feeder Nikra(PBS) Fault. Overcurrent protection relay | 0 | 0 | No interruption
Nawabganj 132/33kV | TR-2 LT | 2025-03-24 12:32 | 2025-03-24 12:50 | 0.0125 | T | 33 kv pbs agla feeder cable fault. Lockout relay -1 & 2, | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 02 LT | 2025-03-12 12:00 | 2025-03-12 15:42 | 0.15417 | T | Lockout relay operated Differential relay trip | 0 | 0 | No interruption
Siddhirganj 132/33kV | T-2 HT | 2025-03-29 06:24 | 2025-03-29 09:28 | 0.12778 | E/O | Red hot maintenance work | 0 | 0 | No interruption
Sonargaon 132/33kV | Tr-2 LT | 2025-03-08 22:12 | 2025-03-09 00:34 | 0.098611 | T | 33 kv Langolbandh and Norsingdhi feeder fault. Auxiliary transformer T-2 fuse R -Y -B phase burn DIR O/C & E/F Relay | 12 | 28.4 | Power interruption
Sonargaon 132/33kV | Tr-1 LT | 2025-03-08 22:15 | 2025-03-09 00:15 | 0.083333 | T | 33 kv Astha feed feeder fault. DIR O/C and E/F Relay. | 27 | 54 | Power interruption
Sonargaon 132/33kV | Tr-2 HT | 2025-03-11 10:50 | 2025-03-11 11:58 | 0.047222 | E/O | Auxiliary Transformer-2 corrective maintenance work. Shutdown taken by PBS. | 28 | 31.7333 | Power interruption
Sonargaon 132/33kV | Tr-1 HT | 2025-03-11 12:14 | 2025-03-11 13:25 | 0.049306 | E/O | Transformer-1 corrective maintenance purpose Shutdown taken. | 27 | 31.95 | Power interruption
|  |  | Total : | 0.58819 |  | Unserved Energy: |  | 151.7167
Chattogram Grid Circle :
Dohazari 132/33kV | Power Transformer -T-2 HT | 2025-03-18 22:56 | 2025-03-19 00:05 | 0.047917 | E/O | Keranihat REB red hot maintenance. | 60 | 69 | Power interruption
Halishahar 132/33kV | 423T(TR-3) LT | 2025-03-26 07:15 | 2025-03-26 07:15 | 0 | T | Due to pdb 33 kv cable fault O/C & E/F | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-02 HT | 2025-03-16 12:25 | 2025-03-16 13:45 | 0.055556 | E/O | Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 0.10347 |  | Unserved Energy: |  | 69
Cumilla Grid Circle :
Ashuganj 230/132/33kV | T-3 Kalabagan HT | 2025-03-12 22:51 | 2025-03-13 00:08 | 0.053472 | E/O | conductor demaged | 20 | 25.6667 | Power interruption
Beanibazar 132/33kV | 132 KV Transformer TR-01 LT | 2025-03-30 09:38 | 2025-03-30 11:24 | 0.073611 | E/O | 33 KV Incomer CT -B phase Red hot | 0 | 0 | No interruption
Chandpur 132/33kV | 412T LT | 2025-03-10 21:55 | 2025-03-12 12:07 | 1899-12-31 14:12 | E/O | Maintenance Work | 0 | 0 | No interruption
Chandpur 132/33kV | 422T LT | 2025-03-17 16:28 | 2025-03-17 17:16 | 0.033333 | T | 33kv T-5 bus coupler DS heavy flashing O/C & E/F | 14 | 11.2 | Power interruption
Chandpur 132/33kV | 402T LT | 2025-03-17 16:28 | 2025-03-17 17:00 | 0.022222 | T | E/F E/F | 12 | 6.4 | Power interruption
Chowmuhani 132/33kV | TR2-425T LT | 2025-03-03 08:52 | 2025-03-03 09:08 | 0.011111 | T | Don't operate 33 kv companigonj feeder relay . No relay shown | 35 | 9.3333 | Power interruption
Chowmuhani 132/33kV | TR3-435T LT | 2025-03-03 08:52 | 2025-03-03 09:08 | 0.011111 | T | Don't operate 33 kv companigonj feeder relay . E/F Ins. | 35 | 9.3333 | Power interruption
Chowmuhani 132/33kV | TR3-435T LT | 2025-03-20 18:35 | 2025-03-20 23:48 | 0.21736 | E/O | 33kv side CT (R phase) red-hot | 15 | 78.25 | Power interruption
Chowmuhani 132/33kV | TR3 | 2025-03-29 12:57 | 2025-03-29 15:20 | 0.099306 | E/O | 33KV CT B-Phase Oil Leakage Check. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV ATR-02 HT | 2025-03-15 07:27 | 2025-03-15 11:15 | 0.15833 | E/O | Red hot remove | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 LT | 2025-03-08 07:24 | 2025-03-08 07:37 | 0.0090278 | T | Pran Jamuna-2 33 kv feeder CT blust B phase Trip relay-1, OC/EF | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 LT | 2025-03-08 07:24 | 2025-03-08 07:37 | 0.0090278 | T | Pran Jamuna-2, 33 kv feeder CT blust B phase OC/EF, ABC inst. fault | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-2 LT | 2025-03-08 22:21 | 2025-03-08 22:27 | 0.0041667 | T | fault O/C and E/F | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 LT | 2025-03-08 22:21 | 2025-03-08 22:27 | 0.0041667 | T | Fault O/C | 13 | 1.3 | Power interruption
Sunamganj 132/33kV | Tr-1 HT | 2025-03-17 14:31 | 2025-03-17 15:40 | 0.047917 | T | Mechanical Faulty RET670 REC650 | 2 | 2.3 | Power interruption
Sunamganj 132/33kV | Tr-1 LT | 2025-03-29 10:22 | 2025-03-29 10:40 | 0.0125 | E/O | Red Hot Manintenance. | 4 | 1.2 | Power interruption
Sylhet 132/33kV | T1 LT | 2025-03-16 02:56 | 2025-03-16 03:03 | 0.0048611 | T | O/C and E/F. O/C and E/F. | 10 | 1.1667 | Power interruption
Sylhet 132/33kV | T1 LT | 2025-03-26 07:02 | 2025-03-26 07:08 | 0.0041667 | T | Trip Ins O/C due to 33 KV MC College feeder fault. Over current relay. | 18 | 1.8 | Power interruption
Chowmuhani 132/33kV | TR1 | 2025-03-29 09:30 | 2025-03-29 12:40 | 0.13194 | E/O | 33KV Tr-01 Bus Shut Down for 33KV incoming Isulator B-Phase abnormal sound Maintenance work | 20 | 63.3333 | Power interruption
|  |  | Total : | 1900-01-01 08:49 |  | Unserved Energy: |  | 211.2833
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) LT | 2025-03-06 20:25 | 2025-03-06 20:39 | 0.0097222 | T | 33 kv amirpur feeder fault K86-1,k86-2 | 9 | 2.1 | Power interruption
Barishal 132/33kV | T-1 (405T) LT | 2025-03-18 11:45 | 2025-03-18 12:20 | 0.024306 | T | Wzpdcl dopdopia 2 feeder fault and fire. O/c, E/F | 56 | 32.6667 | Power interruption
Faridpur 132/33kV | Transformer-1 LT | 2025-03-17 16:50 | 2025-03-17 17:15 | 0.017361 | T | 33kV khalil Mondol Hat feeder fault 33kV CB Tripping | 50 | 20.8333 | Power interruption
Faridpur 132/33kV | Transformer-2 LT | 2025-03-17 16:50 | 2025-03-17 17:15 | 0.017361 | T | 33kV khalil Mondol Hat feeder fault 33kV CB tripping | 50 | 20.8333 | Power interruption
Goalpara 132/33kV | T-5 LT | 2025-03-22 10:31 | 2025-03-22 10:43 | 0.0083333 | T | Due to 33 kV feeder fault | 11 | 2.2 | Power interruption
Goalpara 132/33kV | T-6 LT | 2025-03-22 10:31 | 2025-03-22 10:44 | 0.0090278 | T | Due to 33 kV feeder fault | 11 | 2.3833 | Power interruption
Gollamari 132/33kV | Tr-2 HT | 2025-03-16 16:14 | 2025-03-16 16:46 | 0.022222 | E/O | Kite Remove Work | 0 | 0 | No interruption
Narail 132/33kV | TR1 (403-T) LT | 2025-03-16 22:29 | 2025-03-16 23:16 | 0.032639 | T | Trip for B-phase fault,overcurrent trip & earth fault. Overcurrent protection-p142 | 25 | 19.5833 | Power interruption
Narail 132/33kV | TR2 (413-T) LT | 2025-03-16 22:29 | 2025-03-16 23:19 | 0.034722 | T | Trip for R-phase fault,overcurrent trip & earth fault. Overcurrent protection-p 142 | 29 | 24.1667 | Power interruption
Payra 400/132/33kV | 400/132/33 kV Auto Transformer-02 HT | 2025-03-06 00:24 | 2025-03-06 02:17 | 0.078472 | E/O | red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 0.25417 |  | Unserved Energy: |  | 124.7667
HVDC Grid Circle :
BIPTC | 20DF24 | 2025-03-03 18:14 | 2025-03-04 14:31 | 0.84514 | T | Tripped | 0 | 0 | No interruption
BIPTC | 20DF24 | 2025-03-04 11:17 | 2025-03-04 14:31 | 0.13472 | E/O | Tripped by Impedence 21R | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-03-06 15:09 | 2025-03-07 11:17 | 0.83889 | T | Tripped by Capacitor unbalance 60/61 instant L2 87.1 Differential realay | 0 | 0 | No interruption
BIPTC | 10CF15 | 2025-03-07 10:21 | 2025-03-07 11:17 | 0.038889 | E/O | Shutdown is taken for emergency maintenance work | 0 | 0 | No interruption
BIPTC | 20DF24 | 2025-03-11 12:08 | 2025-03-11 13:36 | 0.061111 | E/O | Emergency due CB pole discrepancy & CB general fault. | 0 | 0 | No interruption
BIPTC | 20DF24 | 2025-03-17 05:11 | 2025-03-18 13:01 | 1899-12-31 07:50 | T | Tripped by Impedance 21R Impedance 21R | 0 | 0 | No interruption
BIPTC | 20DF11 | 2025-03-17 05:55 | 2025-03-17 15:06 | 0.38264 | T | ACF Backup protection CPR04 fault 87.1 Differential Relay | 0 | 0 | No interruption
BIPTC | 20DF24 | 2025-03-19 18:22 | 2025-03-19 18:22 | 0 | T | Distance relay | 0 | 0 | No interruption
Bhangura 132/33kV | Tr-1(403T) LT | 2025-03-24 05:09 | 2025-03-24 05:45 | 0.025 | T | Pbs 33kv feeder fault 51 | 24 | 14.4 | Power interruption
Bhangura 132/33kV | Tr-2(413T) LT | 2025-03-24 05:09 | 2025-03-24 05:49 | 0.027778 | T | Due to pbs 33 kv feeder fault 51 | 24 | 16 | Power interruption
Bheramara 230/132kV | Transformer-1 HT | 2025-03-19 05:58 | 2025-03-19 08:45 | 0.11597 | E/O | GTG CABLE FIRE | 47 | 130.8167 | Power interruption
Bheramara 230/132kV | Transformer-2 HT | 2025-03-19 05:58 | 2025-03-19 08:45 | 0.11597 | E/O | GTG CABLE FIRE | 47 | 130.8167 | Power interruption
Bheramara(GK) 132/33kV | TR-2 HT | 2025-03-14 10:49 | 2025-03-14 11:42 | 0.036806 | E/O | Replacement H-T lead of Aux.-1 (WZPDCL) | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-3 HT | 2025-03-15 11:26 | 2025-03-15 12:23 | 0.039583 | E/O | 33kV Pbs feeder heatsink Problem | 0 | 0 | No interruption
Bheramara(GK) 132/33kV | TR-3 HT | 2025-03-15 16:05 | 2025-03-15 17:07 | 0.043056 | E/O | 33kV Mirpur Feeder Heatsink Problem | 3 | 3.1 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) HT | 2025-03-20 16:39 | 2025-03-20 17:41 | 0.043056 | E/O | 33 kv bus bar Fault | 25 | 25.8333 | Power interruption
Chuadanga 132/33kV | 132kV Tr. T1(416T) LT | 2025-03-21 09:17 | 2025-03-21 11:42 | 0.10069 | E/O | 33KV PBS FEDER FAULT | 20 | 48.3333 | Power interruption
Kushtia 132/33kV | T2 HT | 2025-03-02 07:11 | 2025-03-02 09:00 | 0.075694 | E/O | Oil leakage of Tr-02 33 kv side | 0 | 0 | No interruption
Pabna 132/33kV | T-3 LT | 2025-03-22 09:07 | 2025-03-22 13:11 | 0.16944 | E/O | Maintenance Work | 0 | 0 | No interruption
Pabna 132/33kV | T-1 HT | 2025-03-23 10:36 | 2025-03-23 12:35 | 0.082639 | E/O | Redhot Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | T-4(435T) HT | 2025-03-24 09:58 | 2025-03-24 11:17 | 0.054861 | E/O | Red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-03 13:24 |  | Unserved Energy: |  | 369.3
Bogura Grid Circle:
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T LT | 2025-03-19 20:02 | 2025-03-19 23:19 | 0.13681 | E/O | 33kV incommer "CB" gas filling work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-3, 404T HT | 2025-03-19 21:37 | 2025-03-19 23:17 | 0.069444 | E/O | 33kV incommer "CB" gas filling work | 0 | 0 | No interruption
Barapukuria 230/132/33kV | 132/33 KV T-4, 444T HT | 2025-03-23 11:41 | 2025-03-23 12:34 | 0.036806 | E/O | 33KV SF6 Gas Filling. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) LT | 2025-03-11 11:28 | 2025-03-11 11:58 | 0.020833 | T | Nesco Hazipur 33kV Feeder Fault O/C Protection P142 | 34 | 17 | Power interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) LT | 2025-03-11 11:28 | 2025-03-11 11:58 | 0.020833 | T | Nesco Hazipur 33kV Feeder Fault O/C Protection P142 | 34 | 17 | Power interruption
Bog-Sherpur 132/33kV | Transformer-1 (404T) HT | 2025-03-27 07:01 | 2025-03-27 11:25 | 0.18333 | E/O | Redhot Maintenance work. | 40 | 176 | Power interruption
Jaldhaka 132/33kV | 406T-1 LT | 2025-03-07 07:00 | 2025-03-07 07:29 | 0.020139 | T | 33 kv Bus fault 50/51 ,.50N/51N | 22 | 10.6333 | Power interruption
Jaldhaka 132/33kV | 416T-2 LT | 2025-03-07 07:00 | 2025-03-07 07:29 | 0.020139 | T | 33 kv Bus fault 50/51 ,.50N/51N | 22 | 10.6333 | Power interruption
Joypurhat 132/33kV | Transformer T-1 (407 T) HT | 2025-03-30 06:45 | 2025-03-30 07:56 | 0.049306 | E/O | Emergency Maintenance for over temperature in 33kv Bus. | 13 | 15.3833 | Power interruption
Joypurhat 132/33kV | Transformer T-2 (417 T) HT | 2025-03-30 06:46 | 2025-03-30 07:57 | 0.049306 | E/O | Emergency Maintenance for over temperature in 33kv Bus. | 13 | 15.3833 | Power interruption
Panchagarh 132/33kV | T-3(A+B)(427T) LT | 2025-03-22 10:20 | 2025-03-22 19:48 | 0.39444 | T | Due to underground cable blast in 33kV R-Phase. MICOM P-122 | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-1(405T) LT | 2025-03-17 15:06 | 2025-03-17 15:21 | 0.010417 | T | Tripped due to O/C & E/F MCGG | 24 | 6 | Power interruption
Sirajganj 132/33kV | T4-(445) HT | 2025-03-04 12:24 | 2025-03-04 14:30 | 0.0875 | E/O | 33 KV T-4 Bus Shutdown for CT Testing for Tarash 33kv Feeder. | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 02:23 |  | Unserved Energy: |  | 268.0333
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-09 12:08 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID BANGLADESH PLC
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Manikgonj Power Plant-01 | 2025-03-28 04:47 | 2025-03-29 01:20 | 0.85625 | T | Conductor Broken of Y-Phage Zone-1 | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-02 | 2025-03-09 04:39 | 2025-03-09 04:51 | 0.0083333 | T | Trip Micom | 0 | 0 | No interruption
Joydebpur 132/33kV | Joydebpur- Kodda ckt-2 | 2025-03-19 20:30 | 2025-03-19 20:52 | 0.015278 | T | None General Trip | 139 | 50.9667 | Power interruption
Kabirpur 132/33kV | Tongi-2 | 2025-03-21 23:41 | 2025-03-21 23:57 | 0.011111 | T | Distance relay, Zone-1, C-phase. | 30 | 8 | Power interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-03-11 07:37 | 2025-03-11 11:46 | 0.17292 | E/O | Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2025-03-11 07:43 | 2025-03-11 11:49 | 0.17083 | E/O | Maintenance | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Mill Gate Ckt-1 | 2025-03-20 14:08 | 2025-03-20 15:30 | 0.056944 | T | PH B/DEF RCV 87L/2ND HR BLKD Z1/5th HR BLKD Z3/Dist.SEND | 48 | 65.6 | Power interruption
Tongi 230/132/33kV | Tongi-Mill Gate Ckt-2 | 2025-03-20 14:08 | 2025-03-20 15:48 | 0.069444 | T | Z4/DEF.SEND | 36 | 60 | Power interruption
Tongi 230/132/33kV | Tongi-Mill Gate Ckt-1 | 2025-03-20 15:30 | 2025-03-20 15:30 | 0 | E/O | Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1899-12-31 08:40 |  | Unserved Energy: |  | 184.5667
Dhaka (South) Grid Circle :
Fatullah 132/33kV | 132 kV Shyampur-1 | 2025-03-01 15:09 | 2025-03-01 17:40 | 0.10486 | T | Trip 21 trip, zone-1 trip | 0 | 0 | No interruption
Haripur 230/132kV | 132KV Bhulta-1 (Old Narsingdi) | 2025-03-16 13:18 | 2025-03-16 14:13 | 0.038194 | E/O | Work on other end. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-03-22 15:27 | 2025-03-22 19:06 | 0.15208 | T | Unknown Distance protection relay | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-03-28 13:03 | 2025-03-28 14:49 | 0.073611 | T | Distance Protection Relay | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Aminbazar 400KV Ckt-2 | 2025-03-01 10:40 | 2025-03-01 15:30 | 0.20139 | E/O | Shutdown instructed by NLDC | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2025-03-29 02:18 | 2025-03-29 03:31 | 0.050694 | T | Distance protection Distance Relay | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2025-03-29 12:22 | 2025-03-29 16:26 | 0.16944 | E/O | Emergency maintenance purpose | 0 | 0 | No interruption
Narshingdi 132/33kV | Brahmanbaria-01 | 2025-03-22 16:55 | 2025-03-22 17:09 | 0.0097222 | T | N/A Distance | 0 | 0 | No interruption
Rampura 230/132kV | Basundhara-02 | 2025-03-23 07:36 | 2025-03-23 10:31 | 0.12153 | T | Unknown. Distance Protection (21/1): Z1 A B | 0 | 0 | No interruption
Sonargaon 132/33kV | Bashundhara Line | 2025-03-08 22:10 | 2025-03-10 11:31 | 1899-12-31 13:21 | T | Transformer Tripped. 87T Trip P- 632 87N Trip P-632 REF-2 | 0 | 0 | No interruption
Sonargaon 132/33kV | OPSL(IEL-2) | 2025-03-11 08:54 | 2025-03-11 09:26 | 0.022222 | T | Line Distance Relay (21L) | 0 | 0 | No interruption
Sonargaon 132/33kV | Daudkandi-01 | 2025-03-22 10:44 | 2025-03-22 12:28 | 0.072222 | E/O | Corrective maintenance due to high temperature. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 13:44 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
BSRM 230/33kV | Cumilla Ckt-1 | 2025-03-16 01:25 | 2025-03-16 01:34 | 0.00625 | T | trip distance | 0 | 0 | No interruption
BSRM 230/33kV | Cumilla Ckt-1 | 2025-03-16 10:08 | 2025-03-16 14:08 | 0.16667 | E/O | Emergency Maintenance | 0 | 0 | No interruption
BSRM 230/33kV | Cumilla Ckt-1 | 2025-03-19 13:56 | 2025-03-19 16:20 | 0.1 | E/O | To remove Kite , Tower No 272-273 | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -02 | 2025-03-23 09:52 | 2025-03-23 15:17 | 0.22569 | E/O | Disk Cleaning | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-2 | 2025-03-28 07:49 | 2025-03-28 12:53 | 0.21111 | E/O | founding kite in midspan at baroaulia s/s side. | 0 | 0 | No interruption
Kalurghat 132/33kV | MODUNAGHAT-01 | 2025-03-12 05:45 | 2025-03-20 13:25 | 1900-01-07 07:40 | E/O | Maintenance | 0 | 0 | No interruption
Kalurghat 132/33kV | MODUNAGHAT-01 | 2025-03-12 05:45 | 2025-03-20 13:25 | 1900-01-07 07:40 | E/O | Maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-03-11 16:16 | 2025-03-11 17:58 | 0.070833 | E/O | Maintenance | 0 | 0 | No interruption
|  |  | Total : | 1900-01-16 10:04 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2025-03-07 11:06 | 2025-03-07 16:18 | 0.21667 | E/O | Isulator (Q89L) T-Phase Red hot. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-03-13 05:17 | 2025-03-13 05:55 | 0.026389 | T | Distance Relay Auto reclose Relay | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-03-28 04:34 | 2025-03-28 04:44 | 0.0069444 | T | None Distance protection A-Phase Earth Fault (Yellow Led) | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-2 | 2025-03-31 06:58 | 2025-03-31 08:14 | 0.052778 | T | Distance Protection | 0 | 0 | No interruption
Cumilla(S) 132/33kV | 53.2MW Lakthanavi | 2025-03-29 07:36 | 2025-04-03 14:22 | 1900-01-04 06:46 | T | REB500 REC650 | 0 | 0 | No interruption
Daudkandi 132/33kV | Sonargaon-1 | 2025-03-22 10:26 | 2025-03-22 12:33 | 0.088194 | E/O | Maintenance Work for Sonergaon SS | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-01 | 2025-03-18 07:41 | 2025-03-18 08:01 | 0.013889 | T | N/A distance, (zone-01. C phase, ABC trip, D-0, R-0.01) | 0 | 0 | No interruption
Shahjibazar 132/33kV | SPCL 86 MW | 2025-03-18 07:41 | 2025-03-18 08:01 | 0.013889 | T | N/A N/A | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shajibazar-Sreemongal Ckt-02 | 2025-03-18 07:41 | 2025-03-18 08:01 | 0.013889 | E/O | due to 86 SPCL & Sreemongal-01 trip, sreemoingal-ckt-02 was source out | 0 | 0 | No interruption
Sreemongol 132/33kV | Sreemangal - Shahjibazar circuit-1 | 2025-03-18 07:41 | 2025-03-18 08:01 | 0.013889 | T | stromy weather Distanve relay | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2025-03-15 03:57 | 2025-03-15 08:53 | 0.20556 | T | 21 Trip ZCOM Trip OC/EF START/TRIP Pole Discrepancy Distance Relay | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-90MW P/S | 2025-03-16 00:40 | 2025-03-16 00:51 | 0.0076389 | T | Distance Protection. Distance Protection. | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-03-24 07:27 | 2025-03-24 07:46 | 0.013194 | T | Distance C -phase ,Z-1 | 0 | 0 | No interruption
Sylhet 132/33kV | Sylhet-Chhatak Ckt-1 | 2025-03-25 01:32 | 2025-03-25 02:24 | 0.036111 | T | Distance Phase-C, Zone 2 | 21 | 18.2 | Power interruption
|  |  | Total : | 1900-01-04 23:47 |  | Unserved Energy: |  | 18.2
Khulna Grid Circle :
Barishal 132/33kV | 132kv Bhandaria ckt | 2025-03-13 06:47 | 2025-03-13 06:55 | 0.0055556 | T | Unknown Distance Relay -Y Phase, Zone -1 | 25 | 3.3333 | Power interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2025-03-28 10:07 | 2025-03-28 10:15 | 0.0055556 | E/O | Due to ALDC work | 0 | 0 | No interruption
Khulna (C) | 132 kV Central- South -1 | 2025-03-27 12:08 | 2025-03-27 13:59 | 0.077083 | E/O | RED HOT MAINTENANCE. | 0 | 0 | No interruption
Khulna (C) | 132kV Central-Goalpara-1 | 2025-03-28 18:14 | 2025-03-29 12:45 | 0.77153 | E/O | Problem of circuit breaker | 0 | 0 | No interruption
Khulna(S) 230/132kV | Khulna Central Ckt-1 | 2025-03-27 12:11 | 2025-03-27 13:55 | 0.072222 | E/O | Red hot maintenance work | 0 | 0 | No interruption
|  |  | Total : | 0.93194 |  | Unserved Energy: |  | 3.3333
HVDC Grid Circle :
Bheramara 230/132kV | Kushtia 2 | 2025-03-19 06:19 | 2025-03-19 08:56 | 0.10903 | E/O | GTG CABLE FIRE | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia -Bheramara-1 | 2025-03-19 07:20 | 2025-03-19 08:58 | 0.068056 | E/O | Shout down by ALDC | 0 | 0 | No interruption
Kushtia 132/33kV | Kushtia-Bheramara-2 | 2025-03-19 07:22 | 2025-03-19 08:58 | 0.066667 | E/O | Shout down by ALDC | 0 | 0 | No interruption
Bheramara 230/132kV | GTG (NW) | 2025-03-19 05:32 | 2025-03-19 05:32 | 0 | T | GTG cable fire cable differential E/F, O/C | 0 | 0 | No interruption
Bheramara 230/132kV | STG (NW) | 2025-03-19 05:36 | 2025-03-19 05:36 | 0 | T | STG CABLE FIRE CABLE DIFFERENTIAL ,E/F ,O/C | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 1 | 2025-03-19 06:18 | 2025-03-19 07:48 | 0.0625 | E/O | GTG CABLE FIRE | 0 | 0 | No interruption
Bheramara 230/132kV | Ishurdi 2 | 2025-03-19 06:18 | 2025-03-19 07:48 | 0.0625 | E/O | GTG CABLE FIRE | 0 | 0 | No interruption
Bheramara 230/132kV | GK 2 | 2025-03-19 06:21 | 2025-03-19 07:53 | 0.063889 | E/O | GTG CABLE FIRE | 29 | 44.4667 | Power interruption
Ishurdi 132/33kV | 132 kV Pabna | 2025-03-01 20:27 | 2025-03-01 21:57 | 0.0625 | E/O | RED HOT at pabna end | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2025-03-13 05:43 | 2025-03-13 06:21 | 0.026389 | T | BBC LZ 32 | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -1 | 2025-03-19 06:22 | 2025-03-19 07:46 | 0.058333 | E/O | Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-03-19 06:22 | 2025-03-19 07:46 | 0.058333 | E/O | Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-2 | 2025-03-29 12:17 | 2025-03-29 12:50 | 0.022917 | T | Here reconductoring work in progress in Natore ckt-1. Contractor's(KEC) labour dropped earth wire onto the natore ckt -2 conductor. LZ-32 | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-03-22 15:26 | 2025-03-22 19:07 | 0.15347 | T | siemens siprotec | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-03-28 13:03 | 2025-03-28 14:46 | 0.071528 | T | Z1,AR BLOCK,VT FAIL | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2025-03-01 20:13 | 2025-03-01 21:57 | 0.072222 | E/O | Maintenance | 0 | 0 | No interruption
Pabna 132/33kV | Pabna-Ishwardi Line | 2025-03-22 13:27 | 2025-03-22 17:08 | 0.15347 | E/O | Maintenance | 15 | 55.25 | Power interruption
|  |  | Total : | 1899-12-31 02:41 |  | Unserved Energy: |  | 99.7167
Bogura Grid Circle:
Bogura 132/33kV | New Bogura-1 | 2025-03-02 11:06 | 2025-03-02 12:34 | 0.061111 | E/O | Isolator problem Maintenance work. | 0 | 0 | No interruption
Bogura 230/132kV | Bogra 132KV Line-1 | 2025-03-02 11:06 | 2025-03-02 12:32 | 0.059722 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | 400 KV Reactor (125 MVAR) | 2025-03-27 13:14 | 2025-03-27 13:14 | 0 | E/O | INSTRUCTION FORM NLDC | 0 | 0 | No interruption
Mahasthangarh 132/33kV | Mahasthangarh-Polashbari 2 | 2025-03-01 21:17 | 2025-03-02 00:58 | 0.15347 | E/O | 363 tower cracking | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-2 | 2025-03-29 12:40 | 2025-03-29 12:50 | 0.0069444 | T | General Trip, Z2 Trip, Block AR, Sync. Fail | 0 | 0 | No interruption
Panchagarh 132/33kV | 132KV Capacitor Bank | 2025-03-09 12:10 | 2025-03-09 13:45 | 0.065972 | E/O | Due to emergency maintenance work. | 0 | 0 | No interruption
Panchagarh 132/33kV | Thakurgaon-1 | 2025-03-20 12:56 | 2025-03-20 13:31 | 0.024306 | E/O | Removing kite from 132 kv transmissin line ckt -01 ,B Phase ( Thakurgaon to Panchagarh) | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-03-15 05:40 | 2025-03-15 06:36 | 0.038889 | T | Froce trip ordered by ALDC no relays | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-03-15 05:40 | 2025-03-15 06:36 | 0.038889 | T | forced trip no relays | 0 | 0 | No interruption
|  |  | Total : | 0.44931 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1900-01-28 20:05 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) HT | 2024-11-01 13:10 | 2024-11-01 14:20 | 1:10 | T | Due to 33kv feeder fault | 0 | 0 | No interruption
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) LT | 2024-11-03 13:55 | 2024-11-03 14:32 | 0:37 | E/O | Due to Installation of Multi-function Meter (MFT) at 33 kV | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2024-11-06 07:33 | 2024-11-06 07:33 | 0:00 | E/O | Due to emergency maint.work | 40 | 0 | Power interruption
| Ashuganj-2 | 2024-11-13 12:06 | 2024-11-13 12:18

## QF-LDC-25
QF-LDC-25
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2025-03-20 06:12 | 2025-03-20 16:54 | 10:42 | S/O | Project shutdown | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2025-03-25 09:20 | 2025-03-25 15:40 | 6:20 | S/O | Project work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Bus-2 (400kV) | 2025-03-27 10:15 | 2025-03-27 16:42 | 6:27 | S/O | Project devolvement work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-3 HT | 2025-03-11 08:49 | 2025-03-11 13:28 | 4:39 | S/O | Maintenance Work | 14 | 65.1 | Power interruption
Jamalpur 132/33kV | Bus-A | 2025-03-12 07:50 | 2025-03-12 09:44 | 1:54 | S/O | Maintenance Work | 0 | 0 | No interruption
Jamalpur 132/33kV | Bus-B | 2025-03-12 09:55 | 2025-03-12 13:50 | 3:55 | S/O | Maintenance Work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-1 HT | 2025-03-13 10:58 | 2025-03-13 12:07 | 1:09 | S/O | Maintenance Work | 0 | 0 | No interruption
Jamalpur 132/33kV | T-2 HT | 2025-03-13 12:11 | 2025-03-13 14:18 | 2:07 | S/O | Maintenance Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 1 | 2025-03-03 08:46 | 2025-03-03 17:20 | 8:34 | S/O | IDRNPP Project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-03-05 08:18 | 2025-03-05 16:58 | 8:40 | S/O | Bay Extension | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-03-06 08:52 | 2025-03-06 17:15 | 8:23 | S/O | bus 2 extension | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-03-17 09:09 | 2025-03-17 12:18 | 3:09 | S/O | IDRNPP Project work. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-03-22 08:52 | 2025-03-22 17:28 | 8:36 | S/O | Bay Extension Work | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-03-23 07:24 | 2025-03-23 17:34 | 10:10 | S/O | Project works. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | 400kV Bus 2 | 2025-03-26 10:22 | 2025-03-26 16:17 | 5:55 | S/O | Bay Extension | 0 | 0 | No interruption
Kallyanpur 132/33kV | GT-2 (132kV) HT | 2025-03-22 09:11 | 2025-03-25 09:41 | 72:30 | S/O | Oil Centrifuging | 0 | 0 | No interruption
Kishoreganj 132/33kV | BUS-B | 2025-03-01 12:10 | 2025-03-01 12:51 | 0:41 | S/O | 132 kv Bajitpur bus loop disconnection work by project | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) HT | 2025-03-01 12:28 | 2025-03-01 12:42 | 0:14 | S/O | New T1 Moving work by project | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) HT | 2025-03-22 09:06 | 2025-03-22 12:48 | 3:42 | S/O | 33 kv Bus Maintenance by PDB | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-2 (414T) HT | 2025-03-22 09:13 | 2025-03-22 12:52 | 3:39 | S/O | 33 kv Bus Maintenance by PDB | 0 | 0 | No interruption
Kishoreganj 132/33kV | Tr-1 (404T) HT | 2025-03-28 09:50 | 2025-03-28 11:20 | 1:30 | S/O | Temperature related work | 0 | 0 | No interruption
Kodda 132/33kV | Tr-2 (416T) HT | 2025-03-10 08:02 | 2025-03-10 15:40 | 7:38 | S/O | Tank colour work | 0 | 0 | No interruption
Kodda 132/33kV | Bus-1 | 2025-03-21 11:34 | 2025-03-21 19:13 | 7:39 | S/O | Maintenance Work | 0 | 0 | No interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2025-03-22 08:07 | 2025-03-22 10:21 | 2:14 | S/O | Maintenance Work | 4 | 8.9333 | Power interruption
Manikganj 132/33kV | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2025-03-22 11:22 | 2025-03-22 12:11 | 0:49 | S/O | Temperature Rising. | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2025-03-03 09:08 | 2025-03-03 16:14 | 7:06 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2025-03-04 09:11 | 2025-03-04 16:18 | 7:07 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Reserve Bus | 2025-03-05 09:05 | 2025-03-05 15:40 | 6:35 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Mirpur 132/33kV | Main Bus | 2025-03-05 15:52 | 2025-03-05 17:09 | 1:17 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Mirpur 132/33kV | T2 HT | 2025-03-28 06:17 | 2025-03-28 07:55 | 1:38 | S/O | Hotspot maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV | T1 HT | 2025-03-28 08:38 | 2025-03-28 10:04 | 1:26 | S/O | Preventive maintenance work. | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-2 (414T) LT | 2025-03-29 07:15 | 2025-03-29 11:06 | 3:51 | S/O | Due to maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Bus B | 2025-03-29 07:45 | 2025-03-29 15:00 | 7:15 | S/O | Due to maint.work | 0 | 0 | No interruption
Mymensingh 132/33kV | Transformer-1 (404T) LT | 2025-03-29 11:08 | 2025-03-29 14:37 | 3:29 | S/O | Maintenance Work | 0 | 0 | No interruption
New Tongi | T1(403T) HT | 2025-03-17 10:55 | 2025-03-17 13:50 | 2:55 | S/O | T1-A 33kv incoming panel relocation work | 0 | 0 | No interruption
Savar 132/33kV | T-1 HT | 2025-03-20 11:02 | 2025-03-20 13:12 | 2:10 | S/O | metering work of 33 KV CP. | 0 | 0 | No interruption
Savar 132/33kV | T-2 HT | 2025-03-20 13:20 | 2025-03-20 15:08 | 1:48 | S/O | metering work of 33 KV CP. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-11 12:44 | 2025-03-11 15:44 | 3:00 | S/O | Blast wall construction work | 5 | 15 | Power interruption
Sherpur 132/33kV | Transformer- 04 HT | 2025-03-11 12:45 | 2025-03-11 15:48 | 3:03 | S/O | Blast wall construction work | 5 | 15.25 | Power interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-15 08:30 | 2025-03-15 16:40 | 8:10 | S/O | Maintenance Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-03-15 08:44 | 2025-03-15 17:58 | 9:14 | S/O | Maintenance Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-03-16 08:06 | 2025-03-16 15:44 | 7:38 | S/O | Blast wall construction work. | 10 | 76.3333 | Power interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-16 08:08 | 2025-03-16 15:54 | 7:46 | S/O | Blast wall construction work. | 10 | 77.6667 | Power interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-03-17 08:55 | 2025-03-17 15:15 | 6:20 | S/O | Fire wall Construction works. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-03-18 08:15 | 2025-03-18 16:57 | 8:42 | S/O | Blast wall construction | 5 | 43.5 | Power interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-18 08:20 | 2025-03-18 15:20 | 7:00 | S/O | Blast wall construction | 20 | 140 | Power interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-19 08:30 | 2025-03-19 09:52 | 1:22 | S/O | Blast Wall Construction Work. | 10 | 13.6667 | Power interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-03-19 08:33 | 2025-03-19 15:27 | 6:54 | S/O | Blast Wall Construction Work. | 10 | 69 | Power interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-20 08:35 | 2025-03-20 17:33 | 8:58 | S/O | Fire wall Construction Works. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 HT | 2025-03-20 08:36 | 2025-03-20 17:31 | 8:55 | S/O | Fire wall Construction Works. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 HT | 2025-03-21 08:37 | 2025-03-21 16:34 | 7:57 | S/O | Blast wall Work | 5 | 39.75 | Power interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-21 08:38 | 2025-03-21 16:30 | 7:52 | S/O | Blast wall Work | 10 | 78.6667 | Power interruption
Sherpur 132/33kV | Transformer- 03 LT | 2025-03-22 09:13 | 2025-03-22 16:23 | 7:10 | S/O | Blast Wall Construction Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 LT | 2025-03-22 09:14 | 2025-03-22 14:28 | 5:14 | S/O | Blast Wall Construction Work. | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 02 HT | 2025-03-22 14:32 | 2025-03-22 16:28 | 1:56 | S/O | BLAST WALL CONSTRUCTION | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-23 08:17 | 2025-03-23 17:00 | 8:43 | S/O | Maintenance Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 HT | 2025-03-23 08:24 | 2025-03-23 16:58 | 8:34 | S/O | Maintenance Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 HT | 2025-03-24 08:17 | 2025-03-24 13:17 | 5:00 | S/O | Blast Wall Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-24 08:18 | 2025-03-24 13:20 | 5:02 | S/O | Blast Wall Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 03 HT | 2025-03-25 08:06 | 2025-03-25 10:37 | 2:31 | S/O | Maintenance Work | 0 | 0 | No interruption
Sherpur 132/33kV | Transformer- 04 HT | 2025-03-25 08:17 | 2025-03-25 10:38 | 2:21 | S/O | Maintenance Work | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-1 | 2025-03-07 09:38 | 2025-03-07 12:53 | 3:15 | S/O | To Connect Rajendrapur Line Conductor With Bus-1. | 0 | 0 | No interruption
Sreepur 230/132/33kV | 132 kV BUS-2 | 2025-03-08 09:41 | 2025-03-08 15:28 | 5:47 | S/O | Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-2 | 2025-03-05 09:43 | 2025-03-08 11:55 | 74:12 | S/O | Maintenance Work | 0 | 0 | No interruption
Tongi 230/132/33kV | 230 kV Bus-1 | 2025-03-10 10:01 | 2025-03-13 12:30 | 74:29 | S/O | R-conductoring | 0 | 0 | No interruption
|  |  | Total : | 1900-01-21 16:58 |  | Unserved Energy: |  | 642.8667
Dhaka (South) Grid Circle :
Bhulta 400/230kV | 230kV Bus-02 | 2025-03-25 12:36 | 2025-03-25 20:07 | 7:31 | S/O | Project work. | 0 | 0 | No interruption
Ghorashal 230kV | TARFO-2 HT | 2025-03-22 09:02 | 2025-03-22 12:44 | 3:42 | S/O | Shutdown requisition from Project-1 for repair control cable and insulator bussing. | 40 | 148 | Power interruption
Haripur 230/132kV | Auto TR-3 LT | 2025-03-05 10:58 | 2025-03-05 12:42 | 1:44 | S/O | High temperature maintenance at LT bushing (Y phase). | 0 | 0 | No interruption
Haripur 230/132kV | 132kV Reserve Bus Sec-1 | 2025-03-12 10:52 | 2025-03-12 16:35 | 5:43 | S/O | Clamp replacing on jackbus for 132kv Ullon line. | 0 | 0 | No interruption
Hasnabad 132/33kV | 33kv Reserve Bus | 2025-03-22 10:24 | 2025-03-22 16:30 | 6:06 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 404 T-1 LT | 2025-03-22 10:30 | 2025-03-22 11:52 | 1:22 | S/O | Red hot maintenance. | 0 | 0 | No interruption
Hasnabad 132/33kV | 132/33kV 424 T-5 LT | 2025-03-22 11:56 | 2025-03-22 15:56 | 4:00 | S/O | Red hot maintenance | 0 | 0 | No interruption
Hasnabad 230/132kV | AUTO TR-1 HT | 2025-03-25 08:22 | 2025-03-25 10:33 | 2:11 | S/O | LT bushing over temperature. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | ATR-1 HT | 2025-03-04 07:02 | 2025-03-04 08:54 | 1:52 | S/O | Maintenance work at Keraniganj end for high temperature. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | TR-2 HT | 2025-03-05 14:41 | 2025-03-05 17:06 | 2:25 | S/O | Maintenance at high junction temperature point. | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-2 HT | 2025-03-21 07:26 | 2025-03-21 09:46 | 2:20 | S/O | Maintenance Work for High Temperature | 0 | 0 | No interruption
Maniknagar 132/33kV | Transformer GT-1 HT | 2025-03-21 09:55 | 2025-03-21 12:22 | 2:27 | S/O | High Temperature Maintenance work | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 LT | 2025-03-21 07:10 | 2025-03-21 09:36 | 2:26 | S/O | Buchholz Relay Oil Leakage Maintenance Work of T-3. | 0 | 0 | No interruption
Narshingdi 132/33kV | T-3 LT | 2025-03-27 14:33 | 2025-03-27 17:08 | 2:35 | S/O | Hotspot maintenance | 10 | 25.8333 | Power interruption
Narshingdi 132/33kV | 132 kV Main Bus-2 | 2025-03-27 14:44 | 2025-03-27 15:57 | 1:13 | S/O | Hotspot maintenance | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 02 LT | 2025-03-14 08:22 | 2025-03-14 08:22 | 0:00 | S/O | To install interim tx-2 on to proper pad permanently | 0 | 0 | No interruption
Rampura 230/132kV | Auto Transformer - 03 LT | 2025-03-24 05:52 | 2025-03-24 06:43 | 0:51 | S/O | Relay change Siemens 7UT61 | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 00:28 |  | Unserved Energy: |  | 173.8333
Chattogram Grid Circle :
Bakulia 132/33kV | T-4 (432T) HT | 2025-03-07 09:20 | 2025-03-19 14:41 | 293:21 | S/O | Installation of AVR at 132KV RTCC panel & Tr. Differential Relay (P-642) at Relay panel. | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-01(406T) HT | 2025-03-08 08:25 | 2025-03-08 13:59 | 5:34 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | TR-02(416T) HT | 2025-03-09 08:20 | 2025-03-09 13:56 | 5:36 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | MAIN BUS-1 | 2025-03-10 08:39 | 2025-03-10 13:19 | 4:40 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | MAIN BUS-2 | 2025-03-11 08:25 | 2025-03-12 15:46 | 31:21 | S/O | Annual maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | MAIN BUS-2 | 2025-03-27 08:51 | 2025-03-27 12:08 | 3:17 | S/O | Oil leakage maintenance work at Y phase of Main Bus -2. | 0 | 0 | No interruption
Halishahar 132/33kV | 423T(TR-3) HT | 2025-03-26 09:10 | 2025-03-26 13:21 | 4:11 | S/O | Pdb cable maintenance work | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-02 HT | 2025-03-12 08:22 | 2025-03-13 13:34 | 29:12 | S/O | Maintenance Work | 0 | 0 | No interruption
Hathazari 230/132/33kV | MT-02 LT | 2025-03-17 07:45 | 2025-03-21 14:35 | 102:50 | S/O | Maintenance Work | 0 | 0 | No interruption
Kalurghat 132/33kV | TRFO-01(506T) HT | 2025-03-05 09:01 | 2025-03-05 15:46 | 6:45 | S/O | Annual Maintenance. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-19 06:47 |  |  |  | 0
Cumilla Grid Circle :
Chandpur 132/33kV | 412T HT | 2025-03-12 08:30 | 2025-03-12 12:03 | 3:33 | S/O | High temperature remove work | 4 | 14.2 | Power interruption
Chandpur 132/33kV | 422T LT | 2025-03-12 12:08 | 2025-03-15 21:57 | 81:49 | S/O | Checking | 0 | 0 | No interruption
Chandpur 132/33kV | 422T HT | 2025-03-15 08:41 | 2025-03-15 12:44 | 4:03 | S/O | Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 412T LT | 2025-03-15 21:58 | 2025-03-22 10:52 | 156:54 | S/O | Heating Problem | 0 | 0 | No interruption
Chandpur 132/33kV | 402T HT | 2025-03-22 08:28 | 2025-03-22 12:10 | 3:42 | S/O | 33kv bus section high temperature remove work | 12 | 44.4 | Power interruption
Chandpur 132/33kV | 412T HT | 2025-03-22 08:28 | 2025-03-22 10:50 | 2:22 | S/O | 33kv bus section high temperature remove work | 0 | 0 | No interruption
Chandpur 132/33kV | 402T LT | 2025-03-23 16:15 | 2025-03-23 16:15 | 0:00 | S/O | For the permission of higher authorities. | 0 | 0 | No interruption
Chauddagram 132/33kV | 132 kv T-2 LT | 2025-03-20 10:20 | 2025-03-20 11:23 | 1:03 | S/O | Oil leakage maintenance Work. | 0 | 0 | No interruption
Chhatak 132/33kV | T-3 HT | 2025-03-02 08:30 | 2025-03-02 09:43 | 1:13 | S/O | 33kv T-3 bus shutdown | 10 | 12.1667 | Power interruption
Chhatak 132/33kV | T-2 LT | 2025-03-13 20:01 | 2025-03-13 20:38 | 0:37 | S/O | 33kv CT dust cleaning | 4 | 2.4667 | Power interruption
Chowmuhani 132/33kV | TR3-435T LT | 2025-03-22 08:30 | 2025-03-22 16:41 | 8:11 | S/O | TR-3 33kv side CT loop red hot maintenance. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV ATR-01 HT | 2025-03-28 05:50 | 2025-03-28 08:30 | 2:40 | S/O | High Temp. Removed Purposed. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV ATR-03 LT | 2025-03-28 08:33 | 2025-03-28 09:15 | 0:42 | S/O | High Temp. Removed Purposed. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | TR-2 LT | 2025-03-26 01:58 | 2025-03-26 01:58 | 0:00 | S/O | Maintenance Work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | TR-01 HT | 2025-03-27 11:29 | 2025-03-27 13:26 | 1:57 | S/O | Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | 132 KV Bus-1 | 2025-03-27 11:32 | 2025-03-27 13:15 | 1:43 | S/O | Maintenance work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | AT-02 LT | 2025-03-27 11:33 | 2025-03-27 13:26 | 1:53 | S/O | Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) LT | 2025-03-17 07:35 | 2025-03-17 10:05 | 2:30 | S/O | 132kV Bushing (R-Ph) & 132kV DS (B-PH) Red Hot Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) LT | 2025-03-18 07:35 | 2025-03-18 09:50 | 2:15 | S/O | S/D taken by T-2, Sec 33kV (Y-Ph) Bushing & 33kV CT (B-Ph) Clamp Side Hot Spot Maintenance Work | 0 | 0 | No interruption
Feni 132/33kV | T-2(415T) LT | 2025-03-21 06:38 | 2025-03-21 10:05 | 3:27 | S/O | S/D taken by PBS-Feni for 33kV T-2 bus side Hot spot Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | T-1(405T) HT | 2025-03-22 07:30 | 2025-03-22 07:30 | 0:00 | S/O | For 33kv Hot-spot maintenance | 0 | 0 | No interruption
Kachua 132/33kV | Main Bus-1 | 2025-03-04 11:56 | 2025-03-25 12:04 | 504:08 | S/O | project work for testting pu rpose | 0 | 0 | No interruption
Kulaura 132/33kV | TR-2 LT | 2025-03-16 11:05 | 2025-03-16 16:50 | 5:45 | S/O | TR-2 33 KV. CB maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-2 HT | 2025-03-16 14:02 | 2025-03-16 14:12 | 0:10 | S/O | TR-2 33 KV. CB maintenance | 0 | 0 | No interruption
Kulaura 132/33kV | TR-1 HT | 2025-03-22 07:13 | 2025-03-22 16:19 | 9:06 | S/O | Installation of TR-3 Development work | 0 | 0 | No interruption
Kulaura 132/33kV | TR-2 HT | 2025-03-29 08:35 | 2025-03-29 10:10 | 1:35 | S/O | PDB incoming DS maintenance | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-02 HT | 2025-03-13 09:58 | 2025-03-13 16:16 | 6:18 | S/O | TR-2 PBS bus maintenance schedule shutdown | 0 | 0 | No interruption
Muradnagar 132/33kV | 132KV Transformar-01 HT | 2025-03-13 10:05 | 2025-03-13 16:14 | 6:09 | S/O | TR-1 PBS bus maintenance schedule shutdown | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer-01 LT | 2025-03-27 06:54 | 2025-03-27 08:41 | 1:47 | S/O | Bay Equipment hot spot maintenance | 10 | 17.8333 | Power interruption
Ramganj 132/33kV | Transformer -02 HT | 2025-03-28 06:55 | 2025-03-28 10:20 | 3:25 | S/O | hotspot maintenance of bay equipments | 0 | 0 | No interruption
Ramganj 132/33kV | Transformer-01 HT | 2025-03-28 09:05 | 2025-03-28 10:20 | 1:15 | S/O | hotspot maintenance of 33kV Bus Section DS by LPBS | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-06 LT | 2025-03-21 08:02 | 2025-03-21 08:15 | 0:13 | S/O | Tr-04 bushing maintenance work by Energypac | 0 | 0 | No interruption
Shahjibazar 132/33kV | TR-04 HT | 2025-03-21 08:03 | 2025-03-22 14:52 | 30:49 | S/O | Tr-04 bushing maintenance work by Energypac | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-2 HT | 2025-03-06 10:26 | 2025-03-06 10:54 | 0:28 | S/O | Tr-3 33kV GCB gas refilling work. | 0 | 0 | No interruption
Sreemongol 132/33kV | 132/33kv T-3 HT | 2025-03-06 10:26 | 2025-03-06 10:54 | 0:28 | S/O | Tr-3 33kV GCB gas refilling work. | 0 | 0 | No interruption
Sunamganj 132/33kV | Tr-1 LT | 2025-03-13 09:27 | 2025-03-13 16:40 | 7:13 | S/O | Due to R-Phase Oil Centrifuging. | 3 | 21.65 | Power interruption
Chowmuhani 132/33kV | TR1 | 2025-03-24 08:20 | 2025-03-24 11:20 | 3:00 | S/O | 33kv Incoming VCB High Temperature Maintenance | 15 | 45 | Power interruption
Sylhet (South) | Trafo-1 HT | 2025-03-05 08:52 | 2025-03-05 08:52 | 0:00 | S/O | Oil centrefuging of Trafo-1 | 0 | 0 | No interruption
|  |  | Total : | 1900-02-03 22:23 |  |  |  | 157.7167
Khulna Grid Circle :
Bagerhat 132/33kV | Transformer-3 ( 423 T) HT | 2025-03-05 06:04 | 2025-03-05 08:56 | 2:52 | S/O | Maintenance Work | 19 | 54.4667 | Power interruption
Bagerhat 132/33kV | Transformer-2 (413 T) HT | 2025-03-05 09:07 | 2025-03-05 10:43 | 1:36 | S/O | Hot spot maintenance work | 5 | 8 | Power interruption
Barguna 132/33kV | Transformer-1 HT | 2025-03-13 07:09 | 2025-03-13 08:09 | 1:00 | S/O | Auxiliary-1 Loop Tightening for High Temperature. | 2.5 | 2.5 | Power interruption
Barishal 132/33kV | T-2 (415T) HT | 2025-03-01 07:08 | 2025-03-01 09:27 | 2:19 | S/O | 33kV Kashipur (WZ) feeder red hot maintenance | 18 | 41.7 | Power interruption
Barishal 132/33kV | Bus A | 2025-03-11 12:05 | 2025-03-11 12:05 | 0:00 | S/O | For Barisal North ckt -2 CB Change Work. | 0 | 0 | No interruption
Barishal 132/33kV | T-2 (415T) HT | 2025-03-15 12:05 | 2025-03-15 12:30 | 0:25 | S/O | Oil sample collection | 10 | 4.1667 | Power interruption
Barishal 230/132kV | T-4 HT | 2025-03-22 07:08 | 2025-03-22 11:11 | 4:03 | S/O | Redhot Repair | 21 | 85.05 | Power interruption
Barishal 230/132kV | T-5 HT | 2025-03-22 07:08 | 2025-03-22 12:31 | 5:23 | S/O | Redhot Repair | 0 | 0 | No interruption
Barishal 230/132kV | 132 kV BUS | 2025-03-24 11:11 | 2025-03-24 15:32 | 4:21 | S/O | Ds Redhot Repair | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-3 LT | 2025-03-01 07:38 | 2025-03-01 13:55 | 6:17 | S/O | Maintenance Work | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-1 HT | 2025-03-01 07:46 | 2025-03-01 13:45 | 5:59 | S/O | Maintenance Work | 0 | 0 | No interruption
Faridpur 132/33kV | Bus-B | 2025-03-01 08:03 | 2025-03-01 14:30 | 6:27 | S/O | Maintenance Work | 0 | 0 | No interruption
Faridpur 132/33kV | ATR-2 LT | 2025-03-01 13:55 | 2025-03-01 14:46 | 0:51 | S/O | Hot spot Maintenance. | 0 | 0 | No interruption
Faridpur 132/33kV | Transformer-2 HT | 2025-03-29 07:27 | 2025-03-29 09:35 | 2:08 | S/O | Hot Spot Maintenance of TR-2 & Incoming-2 CB | 0 | 0 | No interruption
Goalpara 132/33kV | T-5 HT | 2025-03-22 14:54 | 2025-03-22 16:38 | 1:44 | S/O | Khulna PBS taken 33 KV bus shutdown | 0 | 0 | No interruption
Goalpara 132/33kV | T-6 LT | 2025-03-22 15:00 | 2025-03-22 16:34 | 1:34 | S/O | Khulna PBS taken 33 KV bus shutdown | 0 | 0 | No interruption
Gopalganj 132/33kV | T1 HT | 2025-03-12 08:21 | 2025-03-12 13:10 | 4:49 | S/O | Scaffolding work for blast wall. | 0 | 0 | No interruption
Khulna (C) | TR-1 425T HT | 2025-03-16 08:55 | 2025-03-21 17:29 | 128:34 | S/O | Oil centrifuging work | 0 | 0 | No interruption
Khulna(S) 230/132kV | TR-2 HT | 2025-03-01 10:14 | 2025-03-01 15:31 | 5:17 | S/O | 800MW NWPGCL Maintenance Work | 0 | 0 | No interruption
Khulna(S) 230/132kV | 230 KV Main Bus 1 | 2025-03-01 10:30 | 2025-03-01 15:15 | 4:45 | S/O | 800MW NWPGCL Maintenance Work | 0 | 0 | No interruption
Madaripur 132/33kV | T1-405T HT | 2025-03-27 07:12 | 2025-03-27 09:48 | 2:36 | S/O | High temperature maintenance work | 0 | 0 | No interruption
Mongla 132/33kV | T-2 HT | 2025-03-01 16:05 | 2025-03-01 18:27 | 2:22 | S/O | G 2 G project work | 15 | 35.5 | Power interruption
Mongla 132/33kV | T-2 HT | 2025-03-10 14:21 | 2025-03-10 14:21 | 0:00 | S/O | Due to T-1 transformer load test. | 0 | 0 | No interruption
Noapara 132/33kV | T-1 HT | 2025-03-01 07:29 | 2025-03-01 10:02 | 2:33 | S/O | Maintenance Work | 20 | 51 | Power interruption
Noapara 132/33kV | T-1 LT | 2025-03-28 10:15 | 2025-03-28 11:37 | 1:22 | S/O | Red Hot Maintenance of REB-2 Feeder. | 16 | 21.8667 | Power interruption
Payra 400/132/33kV | 132/33 kV Transformer-03 HT | 2025-03-11 09:30 | 2025-03-11 12:08 | 2:38 | S/O | 33kV head sink clean | 0 | 0 | No interruption
Rajbari 132/33kV | 132 kV Bus-I | 2025-03-04 11:41 | 2025-03-04 13:08 | 1:27 | S/O | Bheramara ckt-1 Q-2 DS SAS Operation check. | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-2 HT | 2025-03-08 11:36 | 2025-03-08 13:04 | 1:28 | S/O | SAS INTEGRATION. | 0 | 0 | No interruption
Rajbari 132/33kV | 132 kV Bus-I | 2025-03-10 13:10 | 2025-03-10 18:04 | 4:54 | S/O | Maintenance Work | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 HT | 2025-03-20 15:15 | 2025-03-20 17:13 | 1:58 | S/O | Oil leakage of TR -01 | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-2 HT | 2025-03-22 09:18 | 2025-03-22 10:38 | 1:20 | S/O | Punch & Commission point rectification work of 75MVA Transformer-2(LV Bushing oil leakage check & Rectification work) | 0 | 0 | No interruption
Rajbari 132/33kV | Transformer-1 HT | 2025-03-22 10:53 | 2025-03-22 13:28 | 2:35 | S/O | Oil Leakage Maintenance in main tank valve of Transformer-1 | 0 | 0 | No interruption
Shariatpur 132/33kV | T1-406T HT | 2025-03-01 08:12 | 2025-03-01 10:35 | 2:23 | S/O | WZPDCL Maintenance. | 15 | 35.75 | Power interruption
|  |  | Total : | 1900-01-08 02:00 |  | Unserved Energy : |  | 340
HVDC Grid Circle
Ishurdi 132/33kV | 132 kV Bus-2 | 2025-03-13 09:36 | 2025-03-13 16:41 | 7:05 | S/O | G2G project work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bus-2 | 2025-03-14 09:15 | 2025-03-14 14:50 | 5:35 | S/O | lup & clamp connector change & T03 connector join . | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bus-2 | 2025-03-25 09:10 | 2025-03-25 15:46 | 6:36 | S/O | Maintenance Work | 0 | 0 | No interruption
|  |  | Total : | 0.80278 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Amnura 132/33kV | T-1 (406T) LT | 2025-03-19 08:14 | 2025-03-19 11:09 | 2:55 | S/O | Maintenance Work | 0 | 0 | No interruption
Amnura 132/33kV | Auxiliary-1 HT | 2025-03-19 08:23 | 2025-03-19 10:58 | 2:35 | S/O | Maintenance Work | 0 | 0 | No interruption
Bog-Sherpur 132/33kV | Transformer-2 (414T) HT | 2025-03-25 07:07 | 2025-03-25 10:29 | 3:22 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Bogura 132/33kV | 132KV Bus-A | 2025-03-02 13:19 | 2025-03-14 06:40 | 281:21 | S/O | Shutdown taken for project work. | 0 | 0 | No interruption
Bogura 132/33kV | 132KV Bus-B | 2025-03-14 07:12 | 2025-03-14 07:12 | 0:00 | S/O | 132 kv Bus loop connection. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-4 LT | 2025-03-14 07:15 | 2025-03-14 08:22 | 1:07 | S/O | 132 kv loop connection. | 0 | 0 | No interruption
Bogura 132/33kV | Transformer-1 LT | 2025-03-18 06:42 | 2025-03-18 08:50 | 2:08 | S/O | 33 kV bus Spacer Change work. | 35 | 74.6667 | Power interruption
Bogura 132/33kV | Transformer-2 LT | 2025-03-18 06:42 | 2025-03-18 08:52 | 2:10 | S/O | 33 kV bus Spacer Change work. | 0 | 0 | Power interruption
Bogura 400/230kV | ATR-02 HT | 2025-03-20 09:30 | 2025-03-20 16:49 | 7:19 | S/O | The solving oil leakage problem of ATR-02 | 0 | 0 | No interruption
Jaldhaka 132/33kV | 406T-1 HT | 2025-03-07 14:22 | 2025-03-07 15:40 | 1:18 | S/O | 33kv Bus Section-1 maintenance by PBS | 25 | 32.5 | Power interruption
Mahasthangarh 132/33kV | 406T MTR1 HT | 2025-03-28 07:04 | 2025-03-28 11:38 | 4:34 | S/O | Maintenance work due to Red-hot | 0 | 0 | No interruption
Panchagarh 132/33kV | T-2(417T) HT | 2025-03-03 11:37 | 2025-03-03 12:55 | 1:18 | S/O | Due to emergency maintenance work. | 0 | 0 | No interruption
Purbasadipur 132/33kV | T-3 Transformer (423T) HT | 2025-03-14 07:22 | 2025-03-14 10:46 | 3:24 | S/O | T2 25/41MVA Transformer shifting to taraganj under PGNS project. | 25 | 85 | Power interruption
Rahanpur 400/132kV | AT-01 HT | 2025-03-21 09:05 | 2025-03-21 16:52 | 7:47 | S/O | For Project work | 0 | 0 | No interruption
Rahanpur 400/132kV | AT-02 HT | 2025-03-22 09:13 | 2025-03-22 16:55 | 7:42 | S/O | Due to project work. | 0 | 0 | No interruption
Rajshahi 132/33kV | Transformer T-3 (425T) HT | 2025-03-24 07:54 | 2025-03-24 10:39 | 2:45 | S/O | Maintenance work | 10 | 27.5 | Power interruption
Rajshahi 132/33kV | Transformer T-2(415T) HT | 2025-03-24 10:46 | 2025-03-24 12:56 | 2:10 | S/O | Maintenance work. | 10 | 21.6667 | Power interruption
Rajshahi 132/33kV | Transformer T-1(405T) HT | 2025-03-24 13:50 | 2025-03-24 15:05 | 1:15 | S/O | Maintenance work. | 0 | 0 | No interruption
Rangpur 132/33kV | T-1(414T) HT | 2025-03-01 09:30 | 2025-03-01 15:06 | 5:36 | S/O | Gas Leakages | 12 | 67.2 | Power interruption
Saidpur 132/33kV | TR-3 (424T) HT | 2025-03-18 06:11 | 2025-03-18 07:55 | 1:44 | S/O | Maintenance Work | 15 | 26 | Power interruption
Thakurgaon 132/33kV | T-3(432T) LT | 2025-03-21 09:25 | 2025-03-21 11:59 | 2:34 | S/O | Maintenance Work | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-3(432T) HT | 2025-03-28 08:39 | 2025-03-28 17:15 | 8:36 | S/O | Oil leakage from buchholz relay | 0 | 0 | No interruption
Thakurgaon 132/33kV | T-3(432T) LT | 2025-03-28 08:39 | 2025-03-28 17:16 | 8:37 | S/O | Oil leakage from buchholz relay | 0 | 0 | No interruption
|  |  | Total : | 1900-01-14 02:17 |  | Unserved Energy : |  | 334.5333
Others :Nil
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2542:09 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2025
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-03-08 08:28 | 2025-03-08 17:32 | 9:04 | S/O | Insulator Disc cleaning | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-03-09 08:36 | 2025-03-09 16:21 | 7:45 | S/O | Tower insulator disc Deep cleaning. | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-03-10 08:17 | 2025-03-10 13:11 | 4:54 | S/O | Annual Maintenance (Deep Cleaning). | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-2 | 2025-03-22 08:41 | 2025-03-22 13:52 | 5:11 | S/O | Disc change work | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2025-03-22 13:56 | 2025-03-22 20:47 | 6:51 | S/O | Insulator disc cleaning work | 0 | 0 | No interruption
Agargaon 230/132kV | Aminbazar Ckt-1 | 2025-03-23 07:47 | 2025-03-23 16:57 | 9:10 | S/O | Deep cleaning. | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-03-01 09:35 | 2025-03-01 14:30 | 4:55 | S/O | Disc cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-03-01 09:35 | 2025-03-01 14:30 | 4:55 | S/O | Disk cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Meghnaghat-02 | 2025-03-01 09:35 | 2025-03-01 14:30 | 4:55 | S/O | Disk cleaning | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-01 | 2025-03-03 09:26 | 2025-03-03 13:56 | 4:30 | S/O | Disc cleaning work | 0 | 0 | No interruption
Aminbazar 400/230/132kV | Keranigonj-02 | 2025-03-03 13:59 | 2025-03-03 17:42 | 3:43 | S/O | Disc cleaning work | 0 | 0 | No interruption
Jamalpur 132/33kV | Mymensingh Ckt-01 | 2025-03-12 09:58 | 2025-03-12 14:17 | 4:19 | S/O | Maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV | Manikganj-2 | 2025-03-29 10:26 | 2025-03-29 11:41 | 1:15 | S/O | High temperature maintenance of main bus DS Y phase | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Bibiyana1 | 2025-03-18 08:56 | 2025-03-18 14:54 | 5:58 | S/O | Line maintenance. | 0 | 0 | No interruption
Kaliakoir 400/230/132kV | Aminbazar -1 | 2025-03-19 08:35 | 2025-03-19 08:35 | 0:00 | S/O | Line Maintenance. | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2025-03-01 12:06 | 2025-03-01 12:58 | 0:52 | S/O | 132 kv Bajitpur bus loop disconnection work by project | 0 | 0 | No interruption
Kishoreganj 132/33kV | Mymensingh Ckt-2 | 2025-03-04 12:28 | 2025-03-04 15:28 | 3:00 | S/O | Loop changing of 132 KV Bajitpur Ckt-02 | 0 | 0 | No interruption
Manikganj 132/33kV | Manikganj- Kabirpur CKT-2 | 2025-03-22 11:21 | 2025-03-22 12:02 | 0:41 | S/O | Temperature Rising. | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2025-03-02 08:31 | 2025-03-02 16:35 | 8:04 | S/O | Annual maintenance work. | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-2 | 2025-03-03 08:36 | 2025-03-03 16:15 | 7:39 | S/O | Annual Maintenance | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Sector-18 | 2025-03-03 14:31 | 2025-03-09 11:49 | 141:18 | S/O | Reconstrution of boundary wall at Mirpur Grid SS. | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-03-04 08:28 | 2025-03-04 16:25 | 7:57 | S/O | Annual Maintenance on Main Bus DS & Painting works on tower no 4 &5. | 0 | 0 | No interruption
Mirpur 132/33kV | Aminbazar-1 | 2025-03-05 08:16 | 2025-03-05 17:08 | 8:52 | S/O | Annual Maintenance Work. | 0 | 0 | No interruption
Mirpur 132/33kV | Uttara Old | 2025-03-10 08:41 | 2025-03-13 15:56 | 79:15 | S/O | Piling work of Boundary wall | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-2 | 2025-03-01 12:02 | 2025-03-01 12:58 | 0:56 | S/O | NLDC SDE. | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Bhaluka Ckt-2 | 2025-03-04 06:16 | 2025-03-04 07:17 | 1:01 | S/O | 132kV Mym-Bh Ckt-2 S/D due High Temperature in CT nut of Bhaluka SS end | 70 | 71.1667 | Power interruption
Mymensingh 132/33kV | Mymensingh-Kishoreganj Ckt-2 | 2025-03-04 12:28 | 2025-03-04 15:31 | 3:03 | S/O | Maintenance | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-2 | 2025-03-29 06:39 | 2025-03-29 11:44 | 5:05 | S/O | Due to high Temperature maintenances of T-clamp and B-Bus DS-R Ph clamp Net ckt-2 | 0 | 0 | No interruption
Mymensingh 132/33kV | Mymensingh-Netrakona Ckt-1 | 2025-03-29 11:45 | 2025-03-29 14:44 | 2:59 | S/O | Maintenance | 0 | 0 | No interruption
Rajendrapur 132/33kV | Kodda-2 | 2025-03-19 10:55 | 2025-03-21 14:46 | 51:51 | S/O | To Jumpering Sreepur-Rajendrapur Ckt-01 with Kodda-Rajendrapur Ckt-02 | 0 | 0 | No interruption
Savar 132/33kV | 132kV Manikganj PS-Savar Ckt-2 | 2025-03-24 07:32 | 2025-03-24 08:22 | 0:50 | S/O | Rope removing | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Summit PS(Kodda) | 2025-03-10 10:22 | 2025-03-13 12:36 | 74:14 | S/O | Re conductoring | 0 | 0 | No interruption
Tongi 230/132/33kV | Tongi-Uttara Ckt | 2025-03-21 08:55 | 2025-03-26 11:23 | 122:28 | S/O | Shutdown taken by nldc | 0 | 0 | No interruption
|  |  | Total : | 1900-01-23 21:30 |  | Unserved Energy: |  | 71.1667
Dhaka (South) Grid Circle :
Fatullah 132/33kV | 132 kV Hasnabad | 2025-03-15 07:47 | 2025-03-15 07:47 | 0:00 | S/O | BY NLDC MANTAINENCE WORK | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal GIS- AIS Ckt-3 | 2025-03-05 11:42 | 2025-03-05 13:13 | 1:31 | S/O | Due to Telecommunication works in AIS Ckt-3. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi circuit-1 | 2025-03-17 07:05 | 2025-03-17 13:33 | 6:28 | S/O | Shutdown requisition from Dhamrai 132/33 kV SS for Insulator Disk cleaning. | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-03-18 07:13 | 2025-03-18 14:32 | 7:19 | S/O | Shutdown requisition from Dhamrai 132/33 kV SS for Insulator Disk cleaning . | 0 | 0 | No interruption
Ghorashal 230kV | Ghorashal-Ishwardi Circuit-2 | 2025-03-20 07:34 | 2025-03-20 10:18 | 2:44 | S/O | line disk cleaning | 0 | 0 | No interruption
Haripur 230/132kV | Ullon (Maniknagar-2) | 2025-03-12 10:37 | 2025-03-12 16:33 | 5:56 | S/O | Clamp replacing on jack bus. | 0 | 0 | No interruption
Haripur 230/132kV | Meghnaghat-1 | 2025-03-29 07:27 | 2025-03-29 09:46 | 2:19 | S/O | High Temperature Junction Point Maintenance of Line DS. | 0 | 0 | No interruption
Hasnabad 132/33kV | Fatulla (Pre-Brahmongaon) | 2025-03-15 07:48 | 2025-03-15 09:54 | 2:06 | S/O | Conductor armoring | 0 | 0 | No interruption
Hasnabad 132/33kV | Shitallakhya | 2025-03-15 09:57 | 2025-03-15 14:33 | 4:36 | S/O | Conductor armoring | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2025-03-02 10:52 | 2025-03-02 16:01 | 5:09 | S/O | Maintenance Work in Aminbazar end. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 1 | 2025-03-03 09:26 | 2025-03-03 13:57 | 4:31 | S/O | Maintenance work at Aminbazar End. | 0 | 0 | No interruption
Keranigonj 230/132/33kV | 230 kV Aminbazar Ckt. 2 | 2025-03-03 14:02 | 2025-03-03 17:43 | 3:41 | S/O | Maintence work at Aminbazar end. | 0 | 0 | No interruption
Maniknagar 132/33kV | Narinda Ckt-1 | 2025-03-21 08:27 | 2025-03-21 10:57 | 2:30 | S/O | High Temperature Maintenance work | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Comilla-01 | 2025-03-08 09:51 | 2025-03-08 12:18 | 2:27 | S/O | PT Oil Leakage maintenance | 0 | 0 | No interruption
Meghnaghat 230/132kV | Meghnaghat-Comilla-02 | 2025-03-08 12:21 | 2025-03-08 15:05 | 2:44 | S/O | CVT oil laekage maintenance | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat-Shyampur 230kV Ckt-1 | 2025-03-30 09:38 | 2025-03-30 13:36 | 3:58 | S/O | Maintenance Work | 0 | 0 | No interruption
Meghnaghat 400/230kV | Meghnaghat- Shyampur 230kv -Ckt 2 | 2025-03-30 13:56 | 2025-03-30 16:46 | 2:50 | S/O | Request by NLDC | 0 | 0 | No interruption
Rampura 230/132kV | Dhaka University - 01 | 2025-03-19 12:17 | 2025-03-19 14:01 | 1:44 | S/O | SCADA check | 0 | 0 | No interruption
Rampura 230/132kV | Dhaka University - 02 | 2025-03-19 14:09 | 2025-03-19 14:58 | 0:49 | S/O | Scada Implementation | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-1(D06) | 2025-03-30 09:34 | 2025-03-30 13:35 | 4:01 | S/O | Insulator disc replacement at T#23 R Phase | 0 | 0 | No interruption
Shyampur 230/132kV | 230 kV Meghnaghat-2(D05) | 2025-03-30 14:01 | 2025-03-30 16:46 | 2:45 | S/O | Disc insulator cleaning work. | 0 | 0 | No interruption
Siddhirganj 230/132kV | 335MW EGCB 1 | 2025-03-24 07:06 | 2025-03-24 07:06 | 0:00 | S/O | Emergency maintenance work | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 22:08 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Baroirhat 132/33kV | Hat-2 | 2025-03-13 05:57 | 2025-03-13 07:07 | 1:10 | S/O | Maintenance work of Hathazari ss | 0 | 0 | No interruption
BSRM 230/33kV | Cumilla Ckt-2 | 2025-03-16 14:20 | 2025-03-16 16:42 | 2:22 | S/O | Line maintenance | 0 | 0 | No interruption
BSRM 230/33kV | GPH Ispat Ckt. -02 | 2025-03-28 07:50 | 2025-03-28 12:53 | 5:03 | S/O | Line maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2025-03-15 07:37 | 2025-03-15 14:52 | 7:15 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-01 | 2025-03-16 08:21 | 2025-03-16 14:50 | 6:29 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2025-03-19 08:26 | 2025-03-19 14:34 | 6:08 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV | Chandraghona-Kaptai Ckt-02 | 2025-03-20 08:46 | 2025-03-20 14:43 | 5:57 | S/O | Maintenance | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-1 | 2025-03-18 09:45 | 2025-03-18 16:06 | 6:21 | S/O | for rust cleaning | 0 | 0 | No interruption
GPH 230/33kV | HATHAZARI | 2025-03-19 09:30 | 2025-03-19 13:54 | 4:24 | S/O | Insulator Cleaning Purpose. | 0 | 0 | No interruption
GPH 230/33kV | BSRM CKT-2 | 2025-03-23 09:54 | 2025-03-23 15:16 | 5:22 | S/O | disk maintenance | 0 | 0 | No interruption
GPH 230/33kV | ABUL KHAIR | 2025-03-25 09:48 | 2025-03-25 15:02 | 5:14 | S/O | Insulator Cleaning | 0 | 0 | No interruption
Hathazari 230/132/33kV | Baroiarhat-02 | 2025-03-13 04:57 | 2025-03-13 06:58 | 2:01 | S/O | Red hot maintenance | 0 | 0 | No interruption
Madunaghat 132/33kV | Madunaghat-T.K. chemical complex | 2025-03-28 09:36 | 2025-03-28 11:11 | 1:35 | S/O | Maintenance | 0 | 0 | No interruption
Shikalbaha 230/132kV | Interconnection-2 | 2025-03-23 09:37 | 2025-03-23 12:34 | 2:57 | S/O | Maintenance | 0 | 0 | No interruption
|  |  | Total : | 62:18 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj 230/132/33kV | Ghorashal 132 kV Ckt-2 | 2025-03-01 07:44 | 2025-03-08 16:39 | 176:55 | S/O | Re-routing of 3 nos Tower | 0 | 0 | No interruption
Beanibazar 132/33kV | Sylhet-Fenchugang -T -Branibazar-1 | 2025-03-01 06:23 | 2025-03-01 09:07 | 2:44 | S/O | Maintenance work for fenchugang 232/132/33 kV grid sub station | 30 | 82 | Power interruption
Bibiana 400/230kV | Bibi-Shahzi Ckt-II | 2025-03-01 09:13 | 2025-03-01 17:32 | 8:19 | S/O | Annual Maintenance | 0 | 0 | No interruption
Chandpur 132/33kV | 33 kV T-5 section | 2025-03-15 08:33 | 2025-03-15 11:38 | 3:05 | S/O | Maintenance | 17 | 52.4167 | Power interruption
Chandpur 132/33kV | 33 kV T-2 section | 2025-03-18 07:00 | 2025-03-18 10:47 | 3:47 | S/O | 33 Kv Bus coupler DS Maintenance | 4 | 15.1333 | Power interruption
Chandpur 132/33kV | 33 kV T-5 section | 2025-03-18 07:00 | 2025-03-18 10:47 | 3:47 | S/O | 33 Kv Bus coupler DS maintenance work | 23 | 87.0167 | Power interruption
Chauddagram 132/33kV | Feni-1 | 2025-03-14 09:00 | 2025-03-14 16:53 | 7:53 | S/O | Project work for feni grid | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2025-03-08 09:48 | 2025-03-08 12:19 | 2:31 | S/O | PT Maintenance works by Meghnaghat S/S End. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2025-03-08 12:19 | 2025-03-08 15:06 | 2:47 | S/O | CVT Oil leakage Maintenance works Meghnaghat S/S end | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2025-03-16 09:46 | 2025-03-16 14:25 | 4:39 | S/O | BUS Isolator Maintenance Purposed. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-1 | 2025-03-16 10:08 | 2025-03-16 13:57 | 3:49 | S/O | Disk Cleaning | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV | 230KV Cumilla(N)-BSRM Ckt-2 | 2025-03-16 14:20 | 2025-03-19 16:22 | 74:02 | S/O | Isolator (Q89B) red hot maintenance purposed. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | Tripura Ckt-1 | 2025-03-03 14:40 | 2025-03-03 18:13 | 3:33 | S/O | Work for Tripura end. | 0 | 0 | No interruption
Cumilla(S) 132/33kV | 53.2MW Lakthanavi | 2025-03-22 09:40 | 2025-03-22 17:40 | 8:00 | S/O | Lakhdhanvi PP will work for their Transformer Bus maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Sylhet-2 | 2025-03-01 06:21 | 2025-03-01 08:59 | 2:38 | S/O | Annual Maintenance. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-1 | 2025-03-01 09:27 | 2025-03-01 12:35 | 3:08 | S/O | Dead line checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Power Station-2 | 2025-03-01 12:38 | 2025-03-01 15:31 | 2:53 | S/O | Deadline checking | 0 | 0 | No interruption
Fenchuganj 230/132/33kV | Kulaura-2 | 2025-03-27 13:13 | 2025-03-27 14:42 | 1:29 | S/O | Maintenance work | 0 | 0 | No interruption
Feni 132/33kV | Chowddagram Ckt-2 | 2025-03-15 07:50 | 2025-03-15 15:55 | 8:05 | S/O | For EEGBPS Project. | 0 | 0 | No interruption
Kulaura 132/33kV | 132 Fenchuganj-2 | 2025-03-27 13:42 | 2025-03-27 16:05 | 2:23 | S/O | Fenchuganj ckt-2 S/D take this maintenance Red Hot | 0 | 0 | No interruption
Shahjibazar 132/33kV | Shahjibazar-Ashuganj Ckt-03 | 2025-03-02 08:50 | 2025-03-12 19:52 | 251:02 | S/O | shutdown taken by B.baria grid for A/M | 0 | 0 | No interruption
Sunamganj 132/33kV | Chhatak-Sunamgonj CKT-2 | 2025-03-24 12:35 | 2025-03-24 13:57 | 1:22 | S/O | PT MCB Change | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-1 | 2025-03-01 06:47 | 2025-03-01 08:58 | 2:11 | S/O | Emergency working of Fenchugonj end | 0 | 0 | No interruption
Sylhet (South) | Sylhet (S)-Fenchugonj 132KV Ckt-2 | 2025-03-01 06:51 | 2025-03-01 08:58 | 2:07 | S/O | Emergency working of Fenchugonj end | 0 | 0 | No interruption
|  |  | Total : | 1900-01-23 07:09 |  | Unserved Energy: |  | 236.5667
Khulna Grid Circle :
Barishal 132/33kV | 132kv Patuakhali ckt | 2025-03-06 02:19 | 2025-03-06 02:19 | 0:00 | S/O | Order by ALDC | 0 | 0 | No interruption
Barishal 132/33kV | 132 kV Barishal north ckt-2 | 2025-03-11 11:39 | 2025-03-25 17:36 | 341:57 | S/O | For removal of faulty CB and Replace New CB. | 0 | 0 | No interruption
Faridpur 132/33kV | 132 KV 50MW Power Station ckt-1 | 2025-03-07 15:43 | 2025-03-07 20:41 | 4:58 | S/O | Work at Power Station End. | 0 | 0 | No interruption
Goalpara 132/33kV | Goalpara-Khulna Central-1 | 2025-03-29 08:15 | 2025-03-29 12:47 | 4:32 | S/O | By the instruction of ALDC, Khulna | 0 | 0 | No interruption
Mongla 132/33kV | Bagerhat-Mongla Line-1 | 2025-03-01 15:46 | 2025-03-01 18:25 | 2:39 | S/O | G 2 G project work | 15 | 39.75 | Power interruption
Mongla 132/33kV | 100MW ERBL Solar PS | 2025-03-01 16:03 | 2025-03-01 18:36 | 2:33 | S/O | G 2 G project work | 15 | 38.25 | Power interruption
Mongla 132/33kV | Bagerhat-Mongla Line-2 | 2025-03-01 16:04 | 2025-03-01 18:25 | 2:21 | S/O | G 2 G project work | 15 | 35.25 | Power interruption
|  |  | Total : | 1900-01-13 23:00 |  | Unserved Energy: |  | 113.25
HVDC Grid Circle :
Bheramara 230/132kV | Ishurdi 2 | 2025-03-25 07:35 | 2025-03-25 09:02 | 1:27 | S/O | Project work | 0 | 0 | No interruption
BIPTC | Jhenaidah 1 | 2025-03-15 07:20 | 2025-03-15 15:50 | 8:30 | S/O | Cradle fixing... | 0 | 0 | No interruption
BIPTC | Jhenaidah 2 | 2025-03-15 07:23 | 2025-03-15 15:50 | 8:27 | S/O | Cradle fixing. | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kv Natore-1 | 2025-03-07 11:23 | 2025-03-29 17:05 | 533:42 | S/O | Re-conductoring Work | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-1 | 2025-03-23 10:57 | 2025-03-23 13:03 | 2:06 | S/O | Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Rupppur-2 | 2025-03-23 13:05 | 2025-03-23 16:17 | 3:12 | S/O | Maintenance | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Baghabari Line | 2025-03-24 08:11 | 2025-03-24 17:51 | 9:40 | S/O | ISD-NATORE-1 reconductoring | 0 | 0 | No interruption
Ishurdi 132/33kV | 132 kV Bheramara -2 | 2025-03-25 07:35 | 2025-03-25 09:01 | 1:26 | S/O | Project Work | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 1 | 2025-03-17 07:07 | 2025-03-17 13:32 | 6:25 | S/O | Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-03-18 07:15 | 2025-03-18 14:33 | 7:18 | S/O | Maintenance | 0 | 0 | No interruption
Ishurdi 230/132kV | 230 kV Ghorashal 2 | 2025-03-20 07:35 | 2025-03-20 10:18 | 2:43 | S/O | Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-1 | 2025-03-15 07:21 | 2025-03-15 16:00 | 8:39 | S/O | Maintenance | 0 | 0 | No interruption
Jhenaidah 230/132kV | Jhenaidah (New)-HVDC Ckt-2 | 2025-03-15 07:23 | 2025-03-15 16:01 | 8:38 | S/O | Maintenance | 0 | 0 | No interruption
Shahjadpur 132/33kV | 132 KV Shahjadpur-Bghabari-2 | 2025-03-14 09:50 | 2025-03-23 15:15 | 221:25 | S/O | Re-conducting | 0 | 0 | No interruption
|  |  | Total : | 1900-02-02 07:38 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura 230/132kV | Naogaon 132 KV Line-2 | 2025-03-13 10:44 | 2025-03-13 11:28 | 0:44 | S/O | Maintenance | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-03-12 11:58 | 2025-03-12 17:10 | 5:12 | S/O | project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-03-12 11:59 | 2025-03-12 17:10 | 5:11 | S/O | project work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-1 | 2025-03-13 09:28 | 2025-03-13 17:19 | 7:51 | S/O | Punch List Clearance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Parbotipur 230 kV Ckt-2 | 2025-03-13 09:29 | 2025-03-13 17:20 | 7:51 | S/O | Punch List Clearance work | 0 | 0 | No interruption
Bogura 400/230kV | Bogura - Rooppur 400 KV Line-1 | 2025-03-19 11:03 | 2025-03-19 17:55 | 6:52 | S/O | Project work at Rooppur end | 0 | 0 | No interruption
Natore 132/33kV | Ishurdi-1 | 2025-03-07 11:20 | 2025-03-07 11:20 | 0:00 | S/O | Reconductoring. | 0 | 0 | No interruption
Natore 132/33kV | Rajlanka | 2025-03-24 08:48 | 2025-03-24 12:38 | 3:50 | S/O | Re conducting of Ishurdi ckt-1 | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-1 | 2025-03-10 09:38 | 2025-03-10 12:49 | 3:11 | S/O | Project work | 0 | 0 | No interruption
Rangpur 132/33kV | Rangpur-Saidpur-2 | 2025-03-10 14:22 | 2025-03-10 17:02 | 2:40 | S/O | TARAGONJ LILO Line work | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-01 | 2025-03-10 09:36 | 2025-03-10 12:51 | 3:15 | S/O | Project work. | 0 | 0 | No interruption
Saidpur 132/33kV | Saidpur-Rangpur CKT-02 | 2025-03-10 14:21 | 2025-03-10 17:03 | 2:42 | S/O | As the instruction of ALDC, Bogura (499264) | 0 | 0 | No interruption
Sirajganj 132/33kV | Solar Park 1 | 2025-03-18 11:46 | 2025-03-18 13:45 | 1:59 | S/O | SCADA Commissioning at Solar park end. | 0 | 0 | No interruption
Sirajganj 132/33kV | Solar Park 2 | 2025-03-18 13:55 | 2025-03-18 15:45 | 1:50 | S/O | SCADA Commissioning at Solar park end.. | 0 | 0 | No interruption
|  |  | Total : | 1900-01-01 05:08 |  | Unserved Energy: |  | 0
Others :Nil
No interruption
|  |  | Total : | 0 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1900-04-15 04:51 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March 2025
| Area | Previous Month (February' 2025) |  |  |  | Current Month (March '2025)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 27 | 12 | 142 | 181 | 9 | 20 | 98 | 127
2 | Dhaka (South) Grid Circle. | 15 | 17 | 92 | 124 | 14 | 7 | 39 | 60
3 | Chattogram Grid Circle. | 5 | 11 | 68 | 84 | 2 | 9 | 24 | 35
4 | Cumilla Grid Circle. | 15 | 5 | 113 | 133 | 22 | 11 | 62 | 95
5 | Khulna Grid Circle. | 14 | 12 | 66 | 92 | 9 | 6 | 40 | 55
6 | HVDC Grid Circle | 3 | 3 | 38 | 44 | 13 | 25 | 17 | 55
7 | Bogura Grid Circle. | 16 | 18 | 137 | 171 | 9 | 13 | 37 | 59
8 | Others
9 | Total | 95 | 78 | 656 | 829 | 78 | 91 | 317 | 486
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March 2025
| Area | Previous Month (February' 2025) |  |  |  | Current Month (March '2025)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 225.27 | 173.33 | 5220.3 | 5618.9 | 215.82 | 230.26 | 714.1 | 1160.18
2 | Dhaka (South) Grid Circle. | 110.77 | 1381 | 175.43 | 1667.2 | 88.03 | 63.68 | 173.83 | 325.54
3 | Chattogram Grid Circle. | - | - | 1061.52 | 1061.52 | - | 69 | - | 69
4 | Cumilla Grid Circle. | 146.33 | 37.68 | 4091.92 | 4275.93 | 61.03 | 168.45 | 394.29 | 623.77
5 | Khulna Grid Circle. | 102.65 | 17 | 743.57 | 863.22 | 128.1 | - | 453.25 | 581.35
6 | HVDC Grid Circle | - | - | 284 | 284 | 30.4 | 438.62 | - | 469.02
7 | Bogura Grid Circle. | 133.85 | - | 1131.25 | 1265.1 | 61.27 | 206.77 | 334.53 | 602.57
8 | Others | Energy unserved ( MWH ) due to Total: 0
9 | Total | 718.87 | 1609.01 | 12707.99 | 15035.87 | 584.65 | 1176.78 | 2070 | 3831.43
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March 2025
1
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 7 | 12 | 19 | 4 | - | 15 | 904.39
2 | Dhaka (South) | 5031.6 | 5 | 2 | 7 | 1 | - | 6 | 325.55
3 | Chattogram | 2042 | 1 | - | 1 | - | - | 1 | 69
4 | Khulna | 2434 | 8 | 10 | 18 | 5 | 3 | 10 | 464.77
5 | HVDC | 5954.3 | 6 | - | 6 | - | 2 | 4 | 369.3
6 | Bogura | 3145.6 | 8 | 8 | 16 | 12 | - | 4 | 608.03
7 | Cumilla | 2981 | 12 | 7 | 19 | 7 | 2 | 10 | 369
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 3110.04
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.99%
4 | Khulna | 99.98%
5 | HVDC | 99.98%
6 | Bogura | 99.98%
7 | Cumilla | 99.95% | [6 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March 2025
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | 1 | 5 | 2 | - | 3 | 255.74
2 | Dhaka (South) | 990.29 | - | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | 1 | 3 | 4 | 1 | - | 3 | 116.58
5 | HVDC | 1325 | - | 2 | - | 2 | - | - | 2 | 99.72
6 | Bogura | 1803.3 | - | - | - | - | - | - | - | -
7 | Cumilla | 1648.16 | - | 1 | 4 | 5 |  | 1 | 4 | 254.77
8 | Others | - | - | [6 empty] | -
| Total | 10176.6215 | [7 empty] | 726.81
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 100%
3 | Chattogram | 100%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 100%
7 | Cumilla | 99.99% | [7 empty] | Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March 2025
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2025-03-01 | 16 | - | 5 | 11hr 33 min | 1 | 1hr 32 min | - | - |  |  | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID BANGLADESH PLC
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March 2025
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bajitpur 132/33kV | 2 | 4:42 | 94.27
Bhaluka 132/33kV | 2 | 0:15 | 16.25
Kodda 132/33kV | 1 | 0:12 | 11
Tangail 132/33kV | 2 | 2:05 | 140
Joydebpur 132/33kV | 1 | 0:22 | 50.9667
Kabirpur 132/33kV | 1 | 0:16 | 8
Tongi 230/132/33kV | 2 | 3:02 | 125.6
Jamalpur 132/33kV | 1 | 4:39 | 65.1
Manikganj 132/33kV | 1 | 2:14 | 8.9333
Sherpur 132/33kV | 10 | 61:14 | 568.83
Mymensingh 132/33kV | 1 | 1:01 | 71.1667
Keranigonj 230/132/33kV | 1 | 4:36 | 5.6333
Sonargaon 132/33kV | 4 | 4:30 | 146.08
Ghorashal 230kV | 1 | 3:42 | 148
Narshingdi 132/33kV | 1 | 2:35 | 25.8333
Dohazari 132/33kV | 1 | 1:09 | 69
Ashuganj 230/132/33kV | 1 | 1:17 | 25.6667
Chandpur 132/33kV | 2 | 1:20 | 17.6
Chowmuhani 132/33kV | 3 | 5:45 | 96.92
Sreemongol 132/33kV | 1 | 0:06 | 1.3
Sunamganj 132/33kV | 2 | 1:27 | 3.5
Sylhet 132/33kV | 2 | 0:13 | 2.97
Chowmuhani 132/33kV | 1 | 3:10 | 63.3333
Sylhet 132/33kV | 1 | 0:52 | 18.2
Chandpur 132/33kV | 2 | 7:15 | 58.6
Chhatak 132/33kV | 2 | 1:50 | 14.63
Ramganj 132/33kV | 1 | 1:47 | 17.8333
Chowmuhani 132/33kV | 1 | 3:00 | 45
Sunamganj 132/33kV | 1 | 7:13 | 21.65
Beanibazar 132/33kV | 1 | 2:44 | 82
Chandpur 132/33kV | 3 | 10:39 | 154.57
Bagerhat 132/33kV | 1 | 0:14 | 2.1
Barishal 132/33kV | 1 | 0:35 | 32.6667
Faridpur 132/33kV | 2 | 0:50 | 41.67
Goalpara 132/33kV | 2 | 0:25 | 4.58
Narail 132/33kV | 2 | 1:37 | 43.75
Barishal 132/33kV | 1 | 0:08 | 3.3333
Bagerhat 132/33kV | 2 | 4:28 | 62.47
Barguna 132/33kV | 1 | 1:00 | 2.5
Barishal 132/33kV | 3 | 6:47 | 130.92
Mongla 132/33kV | 1 | 2:22 | 35.5
Noapara 132/33kV | 2 | 3:55 | 72.87
Shariatpur 132/33kV | 1 | 2:23 | 35.75
Mongla 132/33kV | 3 | 7:33 | 113.25
Bhangura 132/33kV | 2 | 1:16 | 30.4
Bheramara 230/132kV | 2 | 5:34 | 261.63
Bheramara(GK) 132/33kV | 1 | 1:02 | 3.1
Chuadanga 132/33kV | 2 | 3:27 | 74.17
Bheramara 230/132kV | 1 | 1:32 | 44.4667
Pabna 132/33kV | 1 | 3:41 | 55.25
Bog-Sherpur 132/33kV | 3 | 5:24 | 210
Jaldhaka 132/33kV | 2 | 0:58 | 21.27
Joypurhat 132/33kV | 2 | 2:22 | 30.77
Rajshahi 132/33kV | 1 | 0:15 | 6
Bogura 132/33kV | 1 | 2:08 | 74.6667
Jaldhaka 132/33kV | 1 | 1:18 | 32.5
Purbasadipur 132/33kV | 1 | 3:24 | 85
Rajshahi 132/33kV | 2 | 4:55 | 49.17
Rangpur 132/33kV | 1 | 5:36 | 67.2
Saidpur 132/33kV | 1 | 1:44 | 26
Total Unserved energy : | 102 | 222:05 | 3831.39

## QF-LDC-33
QF-LDC-33
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: March 2025
Sl No. | Sub-station | Load (MW) | Date & Time
1 | AKS | 12 | 2025-03-26 17:00
2 | AKSML | 136 | 2025-03-26 01:00
3 | Aftabnagar | 38 | 2025-03-16 18:30
4 | Agargaon | 118 | 2025-03-17 13:00
5 | Agrabad | 94 | 2025-03-19 20:00
6 | Amnura | 58 | 2025-03-28 19:30
7 | Ashuganj | 112.5 | 2025-03-20 18:30
8 | BSRM | 209 | 2025-03-05 23:00
9 | Bagerhat | 92 | 2025-03-17 19:00
10 | Bajitpur | 59 | 2025-03-30 18:30
11 | Bakulia | 100 | 2025-03-20 19:00
12 | Banani | 42 | 2025-03-23 13:00
13 | Bangabhaban | 17 | 2025-03-16 10:00
14 | Barapukuria | 72 | 2025-03-28 22:00
15 | Barguna | 24 | 2025-03-29 22:00
16 | Barishal | 113 | 2025-03-16 19:00
17 | Barishal-230 | 110 | 2025-03-29 21:00
18 | Baroaulia | 66 | 2025-03-15 11:00
19 | Baroirhat | 65 | 2025-03-28 21:00
20 | Bashundhara | 185 | 2025-03-16 19:30
21 | BashundharaCement | 13 | 2025-03-02 23:00
22 | Beanibazar | 74 | 2025-03-29 18:30
23 | Benapole | 74 | 2025-03-27 14:00
24 | Bhaluka | 161 | 2025-03-27 15:00
25 | Bhandaria | 59 | 2025-03-30 23:00
26 | Bhangura | 44 | 2025-03-29 03:00
27 | Bheramara(GK) | 61 | 2025-03-15 22:00
28 | Bhulta | 288 | 2025-03-19 16:00
29 | Bog-Sherpur | 120 | 2025-03-25 10:00
30 | Bogura | 177 | 2025-03-29 21:00
31 | Borhanuddin | 94 | 2025-03-28 22:00
32 | Brahmanbaria | 153 | 2025-03-30 18:30
33 | Cantonment | 142 | 2025-03-20 13:00
34 | Chandina | N/A | N/A
35 | Chandpur | 78 | 2025-03-29 18:30
36 | Chandraghona | 37 | 2025-03-29 18:30
37 | Chapai | 71 | 2025-03-27 22:00
38 | Charsaidpur | 49 | 2025-03-18 15:00
39 | Chauddagram | 83 | 2025-03-29 18:30
40 | Chhatak | 36 | 2025-03-31 21:00
41 | Chowmuhani | 243 | 2025-03-17 18:30
42 | Chuadanga | 118 | 2025-03-16 03:00
43 | Coxsbazar | 135 | 2025-03-20 19:00
44 | Cumilla(N) | 193 | 2025-03-28 21:00
45 | Cumilla(S) | 176 | 2025-03-19 21:00
46 | Daudkandi | 152 | 2025-03-15 20:00
47 | Dhaka | 60 | 2025-03-16 13:00
48 | Dhamrai | 132 | 2025-03-20 10:00
49 | Dhanmondi | 149 | 2025-03-16 13:00
50 | Dohazari | 123 | 2025-03-30 19:30
51 | Faridpur | 166 | 2025-03-15 21:00
52 | Fatullah | 99 | 2025-03-16 15:00
53 | Fenchuganj | 42 | 2025-03-15 18:00
54 | Feni | 128 | 2025-03-29 18:30
55 | GPH | 97 | 2025-03-08 14:00
56 | Ghatail | 96 | 2025-03-28 18:30
57 | Ghorashal | 16 | 2025-03-23 11:00
58 | Ghorashal-230 | 89 | 2025-03-27 19:30
59 | Goalpara | 36 | 2025-03-16 19:00
60 | Gollamari | 94 | 2025-03-19 19:00
61 | Gopalganj | 120.8 | 2025-03-29 23:00
62 | Gulshan | 126 | 2025-03-17 13:00
63 | Halishahar | 78 | 2025-03-16 11:00
64 | HaripurSBU | 190 | 2025-03-10 11:00
65 | Hasnabad | 102 | 2025-03-16 17:00
66 | Hathazari | 93 | 2025-03-06 18:00
67 | Ishurdi | 77 | 2025-03-15 21:00
68 | Jaldhaka | 92 | 2025-03-27 13:00
69 | Jamalpur | 151 | 2025-03-29 18:00
70 | Jashore | 155 | 2025-03-16 19:00
71 | Jhenaidah | 139 | 2025-03-28 22:00
72 | Joydebpur | 159 | 2025-03-04 12:00
73 | Joypurhat | 72 | 2025-03-28 21:00
74 | Juldah | 17 | 2025-03-07 19:00
75 | KSRM | 42 | 2025-03-22 11:00
76 | Kabirpur | 271 | 2025-03-16 17:00
77 | Kachua | 100 | 2025-03-29 18:30
78 | Kallyanpur | 120 | 2025-03-24 23:00
79 | Kalurghat | 62 | 2025-03-08 14:00
80 | Kamrangirchar | 74.74 | 2025-03-09 04:00
81 | Kaptai | N/A | N/A
82 | Kasba | 43 | 2025-03-29 22:00
83 | Kazla | 109 | 2025-03-01 18:30
84 | Keranigonj | 85 | 2025-03-16 21:00
85 | Khagrachori | 34 | 2025-03-15 18:30
86 | Khulna | 90 | 2025-03-28 21:00
87 | Khulshi | 179 | 2025-03-16 14:00
88 | Kishoreganj | 160 | 2025-03-29 21:00
89 | Kodda | 321 | 2025-03-17 14:00
90 | Kulaura | 52 | 2025-03-29 18:30
91 | Kurigram | 73 | 2025-03-29 18:00
92 | Kushtia | 146 | 2025-03-15 21:00
93 | Lalbag | 74 | 2025-03-03 13:00
94 | Lalmonirhat | 66 | 2025-03-29 18:00
95 | MI_Cement | 18.3 | 2025-03-17 15:00
96 | Madanganj | 46 | 2025-03-27 15:00
97 | Madaripur | 126 | 2025-03-28 23:00
98 | Madartek | 90.11 | 2025-03-16 20:00
99 | Madunaghat | 52 | 2025-03-19 18:30
100 | Magura | 70 | 2025-03-28 19:30
101 | Mahasthangarh | 80 | 2025-03-28 20:00
102 | Manikganj | 147 | 2025-03-16 19:30
103 | Maniknagar | 72 | 2025-03-16 12:00
104 | Matarbari | 52 | 2025-03-31 08:00
105 | Matuail | 72 | 2025-03-16 12:00
106 | Millgate | 108 | 2025-03-17 14:00
107 | Mirpur | 153 | 2025-03-10 15:00
108 | Mirsorai | 12 | 2025-03-12 12:00
109 | Mirzapur | 49 | 2025-03-16 19:00
110 | Mithapukur | 66 | 2025-03-28 18:00
111 | Modern | 0 | 2025-03-01 00:00
112 | Mogbazar | 149.2 | 2025-03-17 14:00
113 | Mongla | 46 | 2025-03-12 19:00
114 | Motijheel | 40 | 2025-03-16 15:00
115 | Muktagacha | 45 | 2025-03-29 18:00
116 | Munshiganj | 117 | 2025-03-16 21:00
117 | Muradnagar | 32 | 2025-03-28 21:00
118 | Mymensingh | 220 | 2025-03-28 18:00
119 | Naogaon | 140 | 2025-03-27 22:00
120 | Narail | 65 | 2025-03-30 02:00
121 | Narinda | 88.5 | 2025-03-17 13:00
122 | Narshingdi | 188 | 2025-03-15 19:00
123 | Natore | 166 | 2025-03-28 20:00
124 | Nawabganj | 64.2 | 2025-03-30 23:00
125 | Netrakona | 144 | 2025-03-30 11:00
126 | New | 88.9 | 2025-03-13 14:00
127 | Niamatpur | 115 | 2025-03-28 21:00
128 | Noapara | 60.5 | 2025-03-17 15:00
129 | PHP | 20 | 2025-03-28 14:00
130 | Pabna | 120 | 2025-03-15 20:00
131 | Palashbari | 128 | 2025-03-30 20:00
132 | Panchagarh | 54 | 2025-03-28 19:00
133 | Patuakhali | 83.5 | 2025-03-28 22:00
134 | Payra | 34 | 2025-03-28 22:00
135 | Postogola | 68 | 2025-03-03 18:00
136 | Purbachal | 19 | 2025-03-15 18:30
137 | Purbasadipur | 128 | 2025-03-26 13:00
138 | Rahanpur | 32 | 2025-03-15 19:00
139 | Rahim | 45 | 2025-03-23 16:00
140 | Rajbari | 80 | 2025-03-15 21:00
141 | Rajendrapur | 136 | 2025-03-16 15:00
142 | Rajshahi | 123 | 2025-03-22 13:00
143 | Rajshahi-230 | 91 | 2025-03-27 21:00
144 | Ramganj | 124 | 2025-03-01 18:30
145 | Rampur | 41 | 2025-03-19 18:30
146 | Rangamati | 18 | 2025-03-19 18:30
147 | Rangpur | 151 | 2025-03-20 18:00
148 | Ruppur | 7.4 | 2025-03-13 15:00
149 | SSM | 16 | 2025-03-01 00:00
150 | Saidpur | 118 | 2025-03-20 17:00
151 | Satkhira | 146 | 2025-03-29 19:30
152 | Satmasjid | 104 | 2025-03-16 19:00
153 | Savar | 237 | 2025-03-17 15:00
154 | SevenRings | 22.27 | 2025-03-19 11:00
155 | ShahCement | 40 | 2025-03-18 19:30
156 | Shahjadpur | 95 | 2025-03-15 21:00
157 | Shahjibazar | 136 | 2025-03-16 21:00
158 | Shahmirpur | 60 | 2025-03-20 00:00
159 | Shariatpur | 96 | 2025-03-29 21:00
160 | Sherpur | 196 | 2025-03-31 19:00
161 | Shikalbaha | 31 | 2025-03-03 12:00
162 | Shitalakhya | 87.2 | 2025-03-17 15:00
163 | Sholosohor | 48 | 2025-03-13 21:00
164 | Shyampur | 196 | 2025-03-20 10:00
165 | Siddhirganj | 132 | 2025-03-12 14:00
166 | Sirajganj | 114 | 2025-03-15 19:30
167 | Sonargaon | 120 | 2025-03-20 23:00
168 | Sreemongol | 79 | 2025-03-16 21:00
169 | Sreepur | 106 | 2025-03-16 15:00
170 | Srinagar | 51.91 | 2025-03-29 22:00
171 | Sunamganj | 59 | 2025-03-29 21:00
172 | Sylhet | 41 | 2025-03-30 19:00
173 | Sylhet-132 | 122 | 2025-03-29 20:00
174 | TK | 32 | 2025-03-11 19:00
175 | Tangail | 206 | 2025-03-27 21:00
176 | Thakurgaon | 102 | 2025-03-28 19:00
177 | Tongi | 168 | 2025-03-17 08:00
178 | Ullahpara | 40 | 2025-03-31 21:00
179 | Ullon | 49 | 2025-03-16 19:00
180 | Uttara | 91 | 2025-03-17 13:00
181 | UttaraNew | 67 | 2025-03-13 17:00
182 | Zigatola | 81 | 2025-03-16 19:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID BANGLADESH PLC. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: March 2025
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5640.29 | 2025-03-17 | 14:00
Chattogram | 1556.5 | 2025-03-29 | 0:00
Cumilla | 1499 | 2025-03-29 | 21:00
Mymensingh | 1335 | 2025-03-28 | 18:00
Sylhet | 614 | 2025-03-29 | 21:00
Khulna | 1848.8 | 2025-03-16 | 21:00
Barishal | 499.5 | 2025-03-29 | 21:00
Rajshahi | 1603.8 | 2025-03-28 | 21:00
Rangpur | 984 | 2025-03-28 | 18:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March 2025
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 407 | 2025-03-23 05:00 | 376 | 2025-03-01 12:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 411 | 2025-03-30 06:00 | 367 | 2025-03-13 12:00
4 | Bibiana | 400 | 401 | 2025-03-07 19:30 | 380 | 2025-03-16 11:00
5 | BIPTC | 400 | 400 | 2025-03-01 05:00 | 385 | 2025-03-29 16:00
6 | Bogura | 400 | 413 | 2025-03-01 03:00 | 354 | 2025-03-27 13:00
7 | Gopalganj | 400 | 414 | 2025-03-23 05:00 | 377 | 2025-03-16 16:00
8 | Kaliakoir | 400 | 388 | 2025-03-07 18:00 | 273 | 2025-03-12 04:00
9 | Madunaghat | 400 | 408 | 2025-03-01 06:00 | 386 | 2025-03-16 22:00
10 | Meghnaghat | 400 | 409 | 2025-03-31 08:00 | 409 | 2025-03-31 08:00
11 | Payra | 400 | 422 | 2025-03-08 06:00 | 405 | 2025-03-01 12:00
12 | Rahanpur | 400 | 415 | 2025-03-01 04:00 | 369 | 2025-03-27 13:00
13 | Rampal | 400 | 415 | 2025-03-24 06:00 | 377 | 2025-03-16 16:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 244 | 2025-03-13 01:00 | 212 | 2025-03-13 12:00
2 | AKSML | 230 | 239 | 2025-03-24 05:00 | 219 | 2025-03-03 11:00
3 | Aminbazar | 230 | 260 | 2025-03-27 22:00 | 214 | 2025-03-13 12:00
4 | Ashuganj | 230 | 238 | 2025-03-24 05:00 | 218 | 2025-03-10 13:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 239 | 2025-03-07 07:00 | 222 | 2025-03-12 15:00
7 | Barapukuria | 230 | 228 | 2025-03-01 16:00 | 212 | 2025-03-26 17:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 243 | 2025-03-08 06:00 | 223 | 2025-03-16 16:00
10 | Bheramara | 230 | 237 | 2025-03-07 05:00 | 221 | 2025-03-24 11:00
11 | Bhulta | 230 | 235 | 2025-03-31 08:00 | 208 | 2025-03-13 12:00
12 | Bibiana | 230 | 236 | 2025-03-02 19:30 | 218 | 2025-03-10 14:00
13 | BIPTC | 230 | 240 | 2025-03-04 06:00 | 221 | 2025-03-12 21:00
14 | Bogura | 230 | 241 | 2025-03-31 09:00 | 217 | 2025-03-27 13:00
15 | Bogura-400 | 230 | 270 | 2025-03-02 23:00 | 218 | 2025-03-27 13:00
16 | Borhanuddin | 230 | 245 | 2025-03-01 04:00 | 232 | 2025-03-03 14:00
17 | BSRM | 230 | 239 | 2025-03-31 08:00 | 215 | 2025-03-03 11:00
18 | Cumilla(N) | 230 | 231 | 2025-03-31 08:00 | 212 | 2025-03-13 12:00
19 | Faridpur | 230 | 241 | 2025-03-01 04:00 | 216 | 2025-03-03 14:00
20 | Fenchuganj | 230 | 237 | 2025-03-02 04:00 | 222 | 2025-03-10 14:00
21 | Ghorashal | 230 | 240 | 2025-03-31 07:00 | 220 | 2025-03-02 15:00
22 | Ghorashal-230 | 230 | 234 | 2025-03-08 06:00 | 208 | 2025-03-25 08:00
23 | Gopalganj | 230 | 240 | 2025-03-01 06:00 | 214 | 2025-03-03 13:00
24 | GPH | 230 | 238 | 2025-03-31 08:00 | 218 | 2025-03-03 11:00
25 | Haripur | 230 | 235 | 2025-03-31 08:00 | 209 | 2025-03-16 14:00
26 | Hasnabad | 230 | 237 | 2025-03-31 07:00 | 212 | 2025-03-13 12:00
27 | Hathazari | 230 | 240 | 2025-03-31 08:00 | 218 | 2025-03-15 14:00
28 | Ishurdi | 230 | 239 | 2025-03-04 06:00 | 224 | 2025-03-02 12:00
29 | Jhenaidah | 230 | 238 | 2025-03-07 05:00 | 200 | 2025-03-15 14:00
30 | Kaliakoir | 230 | 239 | 2025-03-31 08:00 | 213 | 2025-03-11 14:00
31 | Keranigonj | 230 | 237 | 2025-03-31 08:00 | 211 | 2025-03-13 12:00
32 | Khulna(S) | 230 | 241 | 2025-03-04 06:00 | 211 | 2025-03-15 16:00
33 | Madunaghat | 230 | 239 | 2025-03-31 17:00 | 222 | 2025-03-03 10:00
34 | Madunaghat-400 | 230 | 239 | 2025-03-31 08:00 | 222 | 2025-03-03 10:00
35 | Maniknagar | 230 | 234 | 2025-03-30 10:00 | 208 | 2025-03-13 12:00
36 | Meghnaghat | 230 | 241 | 2025-03-08 05:00 | 219 | 2025-03-03 16:00
37 | Meghnaghat-400 | 230 | 237 | 2025-03-31 08:00 | 213 | 2025-03-13 12:00
38 | Mirsorai | 230 | 239 | 2025-03-31 08:00 | 215 | 2025-03-13 12:00
39 | Rajshahi | 230 | 238 | 2025-03-04 06:00 | 219 | 2025-03-29 21:00
40 | Rampal | 230 | 239 | 2025-03-04 06:00 | 213 | 2025-03-15 15:00
41 | Rampur | 230 | N/A | N/A | N/A | N/A
42 | Rampura | 230 | 238 | 2025-03-22 18:30 | 206 | 2025-03-13 12:00
43 | Shikalbaha | 230 | 266 | 2025-03-20 15:00 | 220 | 2025-03-03 09:00
44 | Shyampur | 230 | 266 | 2025-03-05 09:00 | 211 | 2025-03-13 12:00
45 | Siddhirganj | 230 | 239 | 2025-03-07 09:00 | 213 | 2025-03-11 14:00
46 | Sirajgonj | 230 | 253 | 2025-03-15 13:00 | 230 | 2025-03-10 14:00
47 | Sreepur | 230 | 238 | 2025-03-01 04:00 | 218 | 2025-03-10 14:00
48 | Tongi | 230 | 236 | 2025-03-31 13:00 | 208 | 2025-03-03 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 139 | 2025-03-20 18:00 | 118 | 2025-03-02 12:00
2 | Agargaon | 132 | 155 | 2025-03-02 13:00 | 123 | 2025-03-01 12:00
3 | Agrabad | 132 | 137 | 2025-03-12 18:00 | 123 | 2025-03-03 14:00
4 | AKS | 132 | 134 | 2025-03-31 08:00 | 123 | 2025-03-03 09:00
5 | Aminbazar | 132 | 140 | 2025-03-31 16:00 | 122 | 2025-03-16 16:00
6 | Amnura | 132 | 142 | 2025-03-01 19:30 | 119 | 2025-03-27 13:00
7 | Ashuganj | 132 | 140 | 2025-03-08 04:00 | 130 | 2025-03-02 15:00
8 | Bagerhat | 132 | 137 | 2025-03-05 06:00 | 113 | 2025-03-15 15:00
9 | Bajitpur | 132 | 139 | 2025-03-30 05:00 | 120 | 2025-03-16 13:00
10 | Bakulia | 132 | 138 | 2025-03-09 06:00 | 125 | 2025-03-03 11:00
11 | Banani | 132 | 165 | 2025-03-26 10:00 | 117 | 2025-03-03 14:00
12 | Bangabhaban | 132 | 138 | 2025-03-30 07:00 | 117 | 2025-03-10 14:00
13 | Barapukuria | 132 | 141 | 2025-03-07 18:30 | 126 | 2025-03-30 13:00
14 | Barguna | 132 | 139 | 2025-03-08 06:00 | 128 | 2025-03-01 11:00
15 | Barishal | 132 | 137 | 2025-03-07 06:00 | 123 | 2025-03-03 13:00
16 | Barishal-230 | 132 | 137 | 2025-03-07 06:00 | 122 | 2025-03-16 16:00
17 | Baroaulia | 132 | 136 | 2025-03-08 09:00 | 125 | 2025-03-03 03:00
18 | Baroirhat | 132 | 131 | 2025-03-01 19:00 | 116 | 2025-03-03 11:00
19 | Bashundhara | 132 | 148 | 2025-03-30 08:00 | 117 | 2025-03-03 15:00
20 | BashundharaCement | 132 | 138 | 2025-03-25 02:00 | 116 | 2025-03-26 13:00
21 | Beanibazar | 132 | 134 | 2025-03-01 10:00 | 123 | 2025-03-29 21:00
22 | Benapole | 132 | 139 | 2025-03-07 05:00 | 110 | 2025-03-15 15:00
23 | Bhaluka | 132 | 132 | 2025-03-02 06:00 | 115 | 2025-03-06 23:00
24 | Bhandaria | 132 | 135 | 2025-03-07 05:00 | 111 | 2025-03-16 22:00
25 | Bhangura | 132 | 144 | 2025-03-06 07:00 | 124 | 2025-03-27 13:00
26 | Bheramara | 132 | 138 | 2025-03-06 05:00 | 126 | 2025-03-19 21:00
27 | Bheramara(GK) | 132 | 138 | 2025-03-05 00:00 | 124 | 2025-03-31 19:00
28 | Bhulta | 132 | 135 | 2025-03-31 17:00 | 115 | 2025-03-16 14:00
29 | Bog-Sherpur | 132 | 136 | 2025-03-01 05:00 | 122 | 2025-03-12 16:00
30 | Bogura | 132 | 137 | 2025-03-01 23:00 | 123 | 2025-03-12 16:00
31 | Bogura-230 | 132 | 137 | 2025-03-01 23:00 | 122 | 2025-03-27 13:00
32 | Brahmanbaria | 132 | 139 | 2025-03-22 21:00 | 118 | 2025-03-12 15:00
33 | Cantonment | 132 | 145 | 2025-03-29 01:00 | 123 | 2025-03-01 12:00
34 | Chandina | 132 | N/A | N/A | N/A | N/A
35 | Chandpur | 132 | 155 | 2025-03-24 11:00 | 110 | 2025-03-15 15:00
36 | Chandraghona | 132 | 160 | 2025-03-25 15:00 | 127 | 2025-03-18 14:00
37 | Chapai | 132 | 138 | 2025-03-11 06:00 | 119 | 2025-03-27 13:00
39 | Charsaidpur | 132 | 139 | 2025-03-31 09:00 | 121 | 2025-03-13 12:00
40 | Chauddagram | 132 | 130 | 2025-03-01 19:00 | 114 | 2025-03-13 11:00
41 | Chhatak | 132 | 134 | 2025-03-22 05:00 | 121 | 2025-03-29 21:00
42 | Chowmuhani | 132 | 128 | 2025-03-01 19:30 | 108 | 2025-03-17 00:00
43 | Chuadanga | 132 | 138 | 2025-03-07 01:00 | 108 | 2025-03-15 15:00
44 | Coxsbazar | 132 | 130 | 2025-03-10 07:00 | 109 | 2025-03-29 18:00
45 | Cumilla(N) | 132 | 151 | 2025-03-13 13:00 | 120 | 2025-03-13 12:00
46 | Cumilla(S) | 132 | 135 | 2025-03-26 05:00 | 117 | 2025-03-13 12:00
47 | Daudkandi | 132 | 132 | 2025-03-08 06:00 | 114 | 2025-03-13 12:00
48 | Dhaka | 132 | 139 | 2025-03-23 04:00 | 118 | 2025-03-03 15:00
49 | Dhamrai | 132 | 138 | 2025-03-31 09:00 | 119 | 2025-03-03 15:00
50 | Dhanmondi | 132 | 139.5 | 2025-03-22 05:00 | 118 | 2025-03-03 15:00
51 | Dohazari | 132 | 136 | 2025-03-08 09:00 | 107 | 2025-03-20 19:30
52 | Faridpur | 132 | 136 | 2025-03-12 16:00 | 122 | 2025-03-16 22:00
53 | Fatullah | 132 | 140 | 2025-03-31 08:00 | 122 | 2025-03-13 12:00
54 | Fenchuganj | 132 | 166 | 2025-03-24 02:00 | 129 | 2025-03-10 14:00
55 | Feni | 132 | 130 | 2025-03-01 19:00 | 113 | 2025-03-11 14:00
56 | Ghatail | 132 | 133 | 2025-03-07 18:30 | 115 | 2025-03-26 13:00
57 | Ghorashal | 132 | 141 | 2025-03-07 19:30 | 127 | 2025-03-16 10:00
58 | Goalpara | 132 | 140 | 2025-03-02 06:00 | 119 | 2025-03-15 14:00
59 | Gollamari | 132 | 140 | 2025-03-04 06:00 | 120 | 2025-03-15 15:00
60 | Gopalganj | 132 | 140 | 2025-03-07 06:00 | 122 | 2025-03-16 16:00
61 | Gopalganj-400 | 132 | 141 | 2025-03-07 06:00 | 126 | 2025-03-03 13:00
62 | Gulshan | 132 | 139 | 2025-03-22 05:00 | 124 | 2025-03-17 12:00
63 | Halishahar | 132 | 136 | 2025-03-01 19:00 | 124 | 2025-03-03 11:00
64 | Haripur | 132 | 139 | 2025-03-31 09:00 | 122 | 2025-03-02 13:00
65 | HaripurSBU | 132 | 139 | 2025-03-31 09:00 | 122 | 2025-03-02 13:00
66 | Hasnabad | 132 | 140 | 2025-03-31 15:00 | 123 | 2025-03-13 11:00
67 | Hathazari | 132 | 138 | 2025-03-08 09:00 | 126 | 2025-03-03 11:00
68 | Ishurdi | 132 | 140 | 2025-03-06 06:00 | 129 | 2025-03-19 21:00
69 | Jaldhaka | 132 | 135 | 2025-03-16 18:30 | 112 | 2025-03-27 11:00
70 | Jamalpur | 132 | 140 | 2025-03-10 19:00 | 113 | 2025-03-01 04:00
71 | Jashore | 132 | 140 | 2025-03-07 05:00 | 110 | 2025-03-27 14:00
72 | Jhenaidah | 132 | 140 | 2025-03-06 05:00 | 113 | 2025-03-15 15:00
73 | Jhenaidah-230 | 132 | 139 | 2025-03-04 06:00 | 113 | 2025-03-15 15:00
74 | Joydebpur | 132 | 140 | 2025-03-02 18:00 | 120 | 2025-03-16 13:00
75 | Joypurhat | 132 | 132 | 2025-03-01 03:00 | 109 | 2025-03-13 11:00
76 | Juldah | 132 | 137 | 2025-03-12 18:30 | 124 | 2025-03-03 12:00
77 | Kabirpur | 132 | 138 | 2025-03-21 18:00 | 116 | 2025-03-03 15:00
78 | Kachua | 132 | 136 | 2025-03-01 15:00 | 114 | 2025-03-05 14:00
79 | Kaliakoir | 132 | 140 | 2025-03-02 18:00 | 122 | 2025-03-19 09:00
80 | Kallyanpur | 132 | 140 | 2025-03-31 10:00 | 123 | 2025-03-13 11:00
81 | Kalurghat | 132 | 137 | 2025-03-09 07:00 | 125 | 2025-03-01 13:00
82 | Kamrangirchar | 132 | 143 | 2025-03-05 03:00 | 122 | 2025-03-16 15:00
83 | Kaptai | 132 | N/A | N/A | N/A | N/A
84 | Kasba | 132 | 133 | 2025-03-08 06:00 | 117 | 2025-03-11 14:00
85 | Kazla | 132 | 138 | 2025-03-30 07:00 | 117 | 2025-03-03 13:00
86 | Keranigonj | 132 | 143 | 2025-03-04 06:00 | 123 | 2025-03-16 15:00
87 | Khagrachori | 132 | 136 | 2025-03-08 06:00 | 125 | 2025-03-03 11:00
88 | Khulna | 132 | 138 | 2025-03-02 05:00 | 117 | 2025-03-15 15:00
89 | Khulna(S) | 132 | 141 | 2025-03-04 06:00 | 120 | 2025-03-15 16:00
90 | Khulshi | 132 | 135 | 2025-03-08 06:00 | 122 | 2025-03-03 11:00
91 | Kishoreganj | 132 | 134 | 2025-03-23 05:00 | 114 | 2025-03-06 18:00
92 | Kodda | 132 | 149 | 2025-03-19 17:00 | 118 | 2025-03-11 14:00
93 | KSRM | 132 | 137 | 2025-03-08 10:00 | 125 | 2025-03-03 14:00
94 | Kulaura | 132 | 136 | 2025-03-01 04:00 | 128 | 2025-03-15 15:00
95 | Kurigram | 132 | 135 | 2025-03-06 18:30 | 111 | 2025-03-30 13:00
96 | Kushtia | 132 | 139 | 2025-03-06 06:00 | 121 | 2025-03-15 15:00
97 | Lalbag | 132 | 143 | 2025-03-04 06:00 | 121 | 2025-03-15 21:00
98 | Lalmonirhat | 132 | 134 | 2025-03-07 18:00 | 115 | 2025-03-19 12:00
99 | Madanganj | 132 | 138 | 2025-03-31 08:00 | 120 | 2025-03-13 12:00
100 | Madaripur | 132 | 140 | 2025-03-23 04:00 | 127 | 2025-03-03 13:00
101 | Madartek | 132 | 139 | 2025-03-23 01:00 | 117 | 2025-03-03 15:00
102 | Madunaghat | 132 | 137 | 2025-03-25 06:00 | 126 | 2025-03-03 11:00
103 | Magura | 132 | 139 | 2025-03-04 06:00 | 110 | 2025-03-15 15:00
104 | Mahasthangarh | 132 | 136 | 2025-03-01 07:00 | 120 | 2025-03-26 17:00
105 | Manikganj | 132 | 135 | 2025-03-04 18:30 | 113 | 2025-03-02 02:00
106 | Maniknagar | 132 | 138 | 2025-03-30 06:00 | 117 | 2025-03-10 13:00
107 | Matarbari | 132 | 1145 | 2025-03-03 03:00 | 108 | 2025-03-29 21:00
108 | Matuail | 132 | 138 | 2025-03-31 08:00 | 120 | 2025-03-06 17:00
109 | Millgate | 132 | 140 | 2025-03-22 03:00 | 119 | 2025-03-10 12:00
110 | Mirpur | 132 | 139 | 2025-03-31 08:00 | 134 | 2025-03-01 03:00
111 | Mirzapur | 132 | 135 | 2025-03-01 17:00 | 118 | 2025-03-19 09:00
112 | Mithapukur | 132 | 139 | 2025-03-04 18:30 | 117 | 2025-03-30 13:00
113 | MI_Cement | 132 | 139 | 2025-03-31 09:00 | 139 | 2025-03-31 09:00
114 | Modern | 132 | 0 | 2025-03-01 00:00 | N/A | N/A
115 | Mogbazar | 132 | 140 | 2025-03-22 04:00 | 119 | 2025-03-03 16:00
116 | Mongla | 132 | 139 | 2025-03-05 06:00 | 115 | 2025-03-15 15:00
117 | Motijheel | 132 | 138 | 2025-03-30 07:00 | 117 | 2025-03-10 14:00
118 | Muktagacha | 132 | 158 | 2025-03-03 17:00 | 136 | 2025-03-08 18:30
119 | Munshiganj | 132 | 138 | 2025-03-31 09:00 | 120 | 2025-03-13 12:00
120 | Muradnagar | 132 | 133 | 2025-03-08 06:00 | 117 | 2025-03-13 12:00
121 | Mymensingh | 132 | 143 | 2025-03-26 02:00 | 108 | 2025-03-16 12:00
122 | Naogaon | 132 | 133 | 2025-03-01 04:00 | 112 | 2025-03-13 11:00
123 | Narail | 132 | 140 | 2025-03-05 05:00 | 112 | 2025-03-15 15:00
124 | Narinda | 132 | 0 | 2025-03-01 00:00 | N/A | N/A
125 | Narshingdi | 132 | 135 | 2025-03-31 09:00 | 110 | 2025-03-12 13:00
126 | Natore | 132 | 137 | 2025-03-07 06:00 | 123 | 2025-03-27 13:00
127 | Nawabganj | 132 | 143 | 2025-03-04 06:00 | 123 | 2025-03-11 14:00
128 | Netrakona | 132 | 127 | 2025-03-23 06:00 | 106 | 2025-03-16 12:00
129 | New | 132 | 141 | 2025-03-20 18:00 | 120 | 2025-03-10 12:00
130 | Niamatpur | 132 | 140 | 2025-03-11 05:00 | 125 | 2025-03-27 12:00
131 | Noapara | 132 | 141 | 2025-03-08 10:00 | 115 | 2025-03-15 14:00
132 | Pabna | 132 | 138 | 2025-03-07 02:00 | 125 | 2025-03-22 16:00
133 | Palashbari | 132 | 134 | 2025-03-31 09:00 | 112 | 2025-03-05 10:00
134 | Panchagarh | 132 | 142 | 2025-03-03 18:30 | 111 | 2025-03-19 13:00
135 | Patuakhali | 132 | 137 | 2025-03-02 19:00 | 127 | 2025-03-06 15:00
136 | Payra | 132 | 166 | 2025-03-02 02:00 | 128 | 2025-03-06 01:00
137 | PHP | 132 | 129 | 2025-03-01 20:00 | 114 | 2025-03-03 01:00
139 | Postogola | 132 | 140 | 2025-03-31 08:00 | 123 | 2025-03-13 12:00
140 | Purbachal | 132 | 141 | 2025-03-30 07:00 | 117 | 2025-03-03 15:00
141 | Purbasadipur | 132 | 136 | 2025-03-12 18:00 | 110 | 2025-03-19 13:00
142 | Rahanpur | 132 | 143 | 2025-03-23 22:00 | 124 | 2025-03-27 13:00
143 | Rahanpur-400 | 132 | 142 | 2025-03-12 05:00 | 125 | 2025-03-27 13:00
144 | Rahim | 132 | 138 | 2025-03-31 08:00 | 122 | 2025-03-13 12:00
145 | Rajbari | 132 | 135 | 2025-03-01 04:00 | 118 | 2025-03-16 22:00
146 | Rajendrapur | 132 | 156 | 2025-03-27 08:00 | 116 | 2025-03-17 08:00
147 | Rajshahi | 132 | 138 | 2025-03-04 06:00 | 124 | 2025-03-27 13:00
148 | Rajshahi-230 | 132 | 138 | 2025-03-08 06:00 | 124 | 2025-03-27 13:00
149 | Ramganj | 132 | 130 | 2025-03-01 19:00 | 107 | 2025-03-16 14:00
150 | Rampur | 132 | 136 | 2025-03-08 06:00 | 123 | 2025-03-03 11:00
151 | Rampura | 132 | 139 | 2025-03-22 04:00 | 117 | 2025-03-03 16:00
152 | Rangamati | 132 | 136 | 2025-03-08 06:00 | 126 | 2025-03-03 11:00
153 | Rangpur | 132 | 136 | 2025-03-04 18:30 | 116 | 2025-03-26 17:00
154 | Ruppur | 132 | 142 | 2025-03-04 04:00 | 128 | 2025-03-19 21:00
155 | Saidpur | 132 | 136 | 2025-03-06 18:30 | 116 | 2025-03-19 12:00
156 | Satkhira | 132 | 138 | 2025-03-04 06:00 | 113 | 2025-03-11 19:00
157 | Satmasjid | 132 | 142 | 2025-03-08 06:00 | 122 | 2025-03-02 13:00
158 | Savar | 132 | 138 | 2025-03-08 06:00 | 120 | 2025-03-13 12:00
159 | SevenRings | 132 | 141 | 2025-03-07 18:30 | 127 | 2025-03-12 15:00
160 | ShahCement | 132 | 139 | 2025-03-31 09:00 | 121 | 2025-03-13 12:00
161 | Shahjadpur | 132 | 142 | 2025-03-03 10:00 | 129 | 2025-03-18 16:00
162 | Shahjibazar | 132 | 135 | 2025-03-09 07:00 | 122 | 2025-03-12 15:00
163 | Shahmirpur | 132 | 139 | 2025-03-25 14:00 | 124 | 2025-03-03 11:00
164 | Shariatpur | 132 | 140 | 2025-03-07 05:00 | 123 | 2025-03-16 19:00
165 | Sherpur | 132 | 139 | 2025-03-05 18:00 | 109 | 2025-03-01 05:00
166 | Shikalbaha | 132 | 127 | 2025-03-08 08:00 | 114 | 2025-03-03 11:00
167 | Shikalbaha-230 | 132 | 138 | 2025-03-08 06:00 | 125 | 2025-03-03 09:00
168 | Shitalakhya | 132 | 139 | 2025-03-31 09:00 | 121 | 2025-03-14 12:00
169 | Sholosohor | 132 | 136 | 2025-03-08 07:00 | 126 | 2025-03-03 10:00
170 | Shyampur | 132 | 139 | 2025-03-31 08:00 | 122 | 2025-03-12 16:00
171 | Shyampur-230 | 132 | 139 | 2025-03-31 08:00 | 121 | 2025-03-13 12:00
172 | Siddhirganj | 132 | 139 | 2025-03-31 08:00 | 122 | 2025-03-13 12:00
173 | Sirajganj | 132 | 136 | 2025-03-10 04:00 | 121 | 2025-03-20 09:00
174 | Sonargaon | 132 | 137 | 2025-03-02 18:00 | 119 | 2025-03-11 14:00
175 | Sreemongol | 132 | 136 | 2025-03-03 15:00 | 124 | 2025-03-12 16:00
176 | Sreepur | 132 | 136 | 2025-03-01 22:00 | 119 | 2025-03-03 12:00
177 | Srinagar | 132 | 142 | 2025-03-04 06:00 | 122 | 2025-03-16 15:00
178 | SSM | 132 | 140 | 2025-03-08 08:00 | 128 | 2025-03-03 08:00
179 | Sunamganj | 132 | 132 | 2025-03-09 05:00 | 119 | 2025-03-29 21:00
180 | Sylhet | 132 | 134 | 2025-03-22 01:00 | 125 | 2025-03-29 21:00
181 | Sylhet-132 | 132 | 134 | 2025-03-09 06:00 | 127 | 2025-03-29 18:30
182 | Tangail | 132 | 134 | 2025-03-21 18:00 | 114 | 2025-03-19 14:00
183 | Thakurgaon | 132 | 141 | 2025-03-03 18:30 | 107 | 2025-03-19 13:00
184 | TK | 132 | 138 | 2025-03-08 06:00 | 126 | 2025-03-03 09:00
185 | Tongi | 132 | 160 | 2025-03-12 19:00 | 122 | 2025-03-03 12:00
186 | Ullahpara | 132 | 137 | 2025-03-02 01:00 | 123 | 2025-03-20 10:00
187 | Ullon | 132 | 139 | 2025-03-22 05:00 | 113 | 2025-03-11 06:00
188 | Uttara | 132 | 139 | 2025-03-21 18:30 | 118 | 2025-03-10 12:00
189 | UttaraNew | 132 | 140 | 2025-03-22 05:00 | 119 | 2025-03-03 16:00
190 | Zigatola | 132 | 143 | 2025-03-05 06:00 | 123 | 2025-03-12 16:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## QF-LDC-36
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month: March 2025
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Aminbazar 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 11-03-2025 | 14:00 | 424 | 231 | 92.8544
Aminbazar 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 11-03-2025 | 14:00 | 424 | 234 | 93.1317
Aminbazar 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 520 | 20-03-2025 | 00:00 | 388 | 158 | 80.5648
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 325 | 11-03-2025 | 07:00 | 230 | 81 | 75.0296
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 520 | 22-03-2025 | 22:00 | -165 | -70 | 34.4682
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 520 | 03-03-2025 | 17:00 | -109 | -29 | 21.6907
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 520 | 18-03-2025 | 14:00 | -202 | 7 | 38.8695
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | 520 | 18-03-2025 | 14:00 | -193 | 12 | 37.1871
Bogura 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 750 | 20-03-2025 | 14:00 | 517 | 30 | 69.0493
Bogura 400/230kV Grid Sub-Station | ATR-02 | 400/230 | 750 | 27-03-2025 | 13:00 | 409 | 13 | 54.5609
Bogura 400/230kV Grid Sub-Station | ATR-03 | 400/230 | 750 | 20-03-2025 | 14:00 | 517 | 30 | 69.0493
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | 325 | 15-03-2025 | 03:00 | 229 | -113 | 78.5731
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | 325 | 28-03-2025 | 23:00 | -167 | -94 | 58.9654
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | 325 | 28-03-2025 | 23:00 | -167 | -94 | 58.9654
Gopalganj 400/230kV Grid Sub-Station | ATR-04 | 400/230 | 750 | 18-03-2025 | 22:00 | -134 | -67 | 19.9755
Gopalganj 400/230kV Grid Sub-Station | ATR-05 | 400/230 | 750 | 28-03-2025 | 23:00 | -114 | 46 | 16.3908
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 520 | 07-03-2025 | 15:00 | 187 | 4 | 35.9698
Kaliakoir 400/230kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 520 | 06-03-2025 | 01:00 | 275 | 108 | 56.8168
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 325 | 11-03-2025 | 03:00 | 303 | 50 | 94.4916
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 325 | 11-03-2025 | 03:00 | 303 | 50 | 94.4916
Meghnaghat 400/230kV Grid Sub-Station | ATR-1 | 400/230 | 750 | 11-03-2025 | 10:00 | -534 | -237 | 77.8974
Meghnaghat 400/230kV Grid Sub-Station | ATR-2 | 400/230 | 750 | 11-03-2025 | 10:00 | -534 | -237 | 77.8974
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | 520 | 28-03-2025 | 20:00 | -325 | -58 | 63.4875
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 520 | 26-03-2025 | 06:00 | -410 | 12 | 78.8799
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | 325 | 30-03-2025 | 00:00 | -64 | -24 | 21.0314
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | 325 | 01-03-2025 | 13:00 | -184 | -32 | 57.4652
Rahanpur 400/132kV Grid Sub-Station | AT-01 | 400/132 | 520 | 22-03-2025 | 10:00 | 221 | 76 | 44.9428
Rahanpur 400/132kV Grid Sub-Station | AT-02 | 400/132 | 520 | 21-03-2025 | 16:00 | 192 | 40 | 37.7158
Amtali 400/132kV Grid Sub-Station
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Substation | transformer | voltage_level | Capacity (MVA) | Date | Hour | MW(LT) | MVAR(LT) | Loading (%)
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 300 | 17-03-2025 | 13:00 | 176 | 66 | 62.656
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 300 | 17-03-2025 | 13:00 | 176 | 66 | 62.656
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 225 | 17-03-2025 | 07:00 | 162 | 49 | 75.2215
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 225 | 17-03-2025 | 07:00 | 162 | 49 | 75.2215
Aminbazar 230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 225 | 16-03-2025 | 15:00 | 170 | 45 | 78.1578
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 300 | 15-03-2025 | 22:00 | 200 | 116 | 77.0685
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 300 | 14-03-2025 | 05:00 | 200 | 42 | 68.1208
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 300 | 26-03-2025 | 20:00 | 158 | 70 | 57.604
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 225 | 26-03-2025 | 20:00 | 121 | 54 | 58.8901
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 225 | 04-03-2025 | 17:00 | 225 | 32 | 101.0063
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 225 | 04-03-2025 | 17:00 | 187 | 49 | 85.917
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 300 | 04-03-2025 | 17:00 | 243 | 37 | 81.9336
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 29-03-2025 | 23:00 | 128 | 26 | 43.538
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 29-03-2025 | 23:00 | 128 | 26 | 43.538
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | 225 | 05-03-2025 | 06:00 | 137 | -38 | 63.1877
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | 225 | 28-03-2025 | 21:00 | -99 | 12 | 44.3221
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 225 | 29-03-2025 | 21:00 | 171 | 45 | 78.5875
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 225 | 29-03-2025 | 21:00 | 171 | 45 | 78.5875
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 300 | 29-03-2025 | 21:00 | 229 | 64 | 79.2584
Bogura 230/132kV Grid Sub-Station | T-04 | 230/132 | 300 | 30-03-2025 | 13:00 | 169 | 80 | 62.3262
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-01 | 230/132 | 225 | 22-03-2025 | 22:00 | 181 | 63 | 85.1781
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-02 | 230/132 | 225 | 19-03-2025 | 18:00 | 182 | 74 | 87.3195
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV ATR-03 | 230/132 | 225 | 22-03-2025 | 22:00 | 193 | 66 | 90.6547
Fenchuganj 230/132/33kV Grid Sub-Station | AT-01 | 230/132 | 300 | 27-03-2025 | 13:00 | 155 | 53 | 54.6036
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 300 | 30-03-2025 | 19:00 | 148 | 51 | 52.1802
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 125 | 03-03-2025 | 03:00 | 100 | 0 | 80
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 125 | 03-03-2025 | 03:00 | 100 | 0 | 80
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 225 | 22-03-2025 | 22:00 | 134 | 78 | 68.9104
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 225 | 22-03-2025 | 22:00 | 147 | 77 | 73.7537
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 225 | 22-03-2025 | 22:00 | 138 | 82 | 71.3441
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 225 | 20-03-2025 | 00:00 | 84 | 49 | 43.2209
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 225 | 20-03-2025 | 00:00 | 84 | 49 | 43.2209
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 225 | 20-03-2025 | 00:00 | 84 | 49 | 43.2209
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 150 | 18-03-2025 | 14:00 | 104 | 57 | 79.064
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 150 | 17-03-2025 | 09:00 | 95 | 54 | 72.8499
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 150 | 18-03-2025 | 14:00 | 104 | 57 | 79.064
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 150 | 18-03-2025 | 14:00 | 104 | 57 | 79.064
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 225 | 31-03-2025 | 21:00 | 101 | 69 | 54.3641
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 225 | 31-03-2025 | 21:00 | 101 | 69 | 54.3641
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 225 | 31-03-2025 | 21:00 | 101 | 69 | 54.3641
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | 300 | 27-03-2025 | 14:00 | -216 | -95 | 78.6561
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | 300 | 27-03-2025 | 14:00 | -216 | -95 | 78.6561
Kaliakoir 230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 300 | 18-03-2025 | 23:00 | 288 | 87 | 100.2846
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 300 | 16-03-2025 | 21:00 | 198 | 63 | 69.2604
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 300 | 04-03-2025 | 08:00 | 202 | 59 | 70.1467
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 300 | 01-03-2025 | 00:00 | 0 | 0 | 0
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | 225 | 31-03-2025 | 01:00 | -152 | -51 | 71.2568
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | 225 | 31-03-2025 | 01:00 | -152 | -51 | 71.2568
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | 300 | 24-03-2025 | 00:00 | -189 | -20 | 63.3518
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 300 | 17-03-2025 | 13:00 | 154 | 67 | 55.9811
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 300 | 17-03-2025 | 13:00 | 154 | 67 | 55.9811
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | 300 | 23-03-2025 | 04:00 | -86 | 0 | 28.6667
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | 300 | 23-03-2025 | 04:00 | -86 | 0 | 28.6667
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 300 | 01-03-2025 | 00:00 | 1 | 0 | 0.33333
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 300 | 01-03-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 LT | 230/132 | 450 | 01-03-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 LT | 230/132 | 450 | 01-03-2025 | 00:00 | 0 | 0 | 0
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 04 LT | 230/132 | 450 | 17-03-2025 | 13:00 | 372 | 64 | 83.8812
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 300 | 11-03-2025 | 16:00 | 233 | 129 | 88.7756
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 300 | 17-03-2025 | 00:00 | 270 | 137 | 100.923
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 300 | 20-03-2025 | 00:00 | 145 | 40 | 50.1387
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 300 | 22-03-2025 | 08:00 | 177 | 33 | 60.0167
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 300 | 03-03-2025 | 16:00 | 147 | 21 | 49.4975
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 300 | 03-03-2025 | 16:00 | 147 | 21 | 49.4975
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 300 | 08-03-2025 | 10:00 | 187 | 54 | 64.8802
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 300 | 08-03-2025 | 10:00 | 187 | 54 | 64.8802
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 225 | 15-03-2025 | 22:00 | 210 | 35 | 94.6208
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 225 | 15-03-2025 | 15:00 | 192 | 46 | 87.7482
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 225 | 15-03-2025 | 15:00 | 192 | 46 | 87.7482
Executive Engineer
Information Management Division
[5 empty] | LDC, Power Grid, Dhaka. |  |  |  | 270

## QF_LDC_37
|  |  |  | POWER GRID BANGLADESH PLC. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID BANGLADESH PLC. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [12 empty] | Report on load shedding
Month: March 2025 |  |  |  | (For Evening Peak) | [10 empty] | Month: March 2025 |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chattogram | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur
2025-03-01 | 13037 | 13037 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-01 | 11103 | 11103 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-02 | 12357 | 12379 | 22 | 19:00 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-02 | 11868 | 11868 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-03 | 12195 | 12195 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-03 | 11795 | 11795 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-04 | 12091 | 12091 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-04 | 11700 | 11700 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-05 | 11918 | 11918 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-05 | 11281 | 11281 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-06 | 11829 | 11829 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-06 | 11227 | 11227 | 31 | 12:00 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | -
2025-03-07 | 10477 | 10477 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-07 | 10085 | 10085 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-08 | 11814 | 11814 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-08 | 10705 | 10705 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-09 | 12310 | 12310 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-09 | 11769 | 11769 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-10 | 12579 | 12579 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-10 | 11927 | 11957 | 30 | 12:00 | 25 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | - | 0
2025-03-11 | 12739 | 12739 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-11 | 11830 | 11871 | 41 | 12:00 | 31 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
2025-03-12 | 12995 | 12995 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-12 | 12033 | 12063 | 30 | 12:00 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-13 | 13796 | 13796 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-13 | 12438 | 12478 | 40 | 12:00 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-14 | 13353 | 13353 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-14 | 11682 | 11773 | 91 | 12:00 | 55 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | -
2025-03-15 | 14620 | 14658 | 38 | 21:00 | 14 | 0 | 10 | 14 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-15 | 12263 | 12263 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-16 | 14425 | 14538 | 113 | 19:00 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-16 | 13214 | 13321 | 107 | 12:00 | 97 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | -
2025-03-17 | 13926 | 13926 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-17 | 12967 | 13021 | 54 | 12:00 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-18 | 13912 | 13912 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-18 | 12676 | 12768 | 92 | 12:00 | 62 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | -
2025-03-19 | 14260 | 14306 | 46 | 19:30 | 9 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-19 | 12906 | 13013 | 107 | 12:00 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-20 | 13316 | 13316 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-20 | 12899 | 13074 | 175 | 12:00 | 130 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | -
2025-03-21 | 11539 | 11539 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-21 | 11259 | 11259 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-22 | 12020 | 12020 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-22 | 10641 | 10666 | 25 | 12:00 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-23 | 12574 | 12574 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-23 | 11828 | 11828 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-24 | 12810 | 12810 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-24 | 11953 | 11953 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-25 | 13346 | 13346 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-25 | 12195 | 12195 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-26 | 13724 | 13724 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-26 | 11994 | 11994 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-27 | 14281 | 14281 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-27 | 13306 | 13326 | 20 | 12:00 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-28 | 14275 | 14275 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2025-03-28 | 12444 | 12444 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-29 | 13803 | 13803 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-03-29 | 11830 | 11830 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-30 | 12585 | 12585 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-03-30 | 11023 | 11023 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2025-03-31 | 11782 | 11782 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2025-03-31 | 9932 | 9932 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
|  | - | - | - | [11 empty] | - | -
98
30
68

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID BANGLADESH PLC.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: March 2025
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15336.92 | 2025-03-15 | 21:00 Hr.
2 | Maximum Day Peak Genaration | MW | 13926.95 | 2025-03-27 | 12:00 Hr.
3 | Maximum Evening Peak Demand | MW | 14658 | 2025-03-15 | 21:00 Hr.
4 | Minimum Generation | MW | 8360.79 | 2025-03-08 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13455.0287 | - | -
6 | Average of the daily day peak Genaration | MW | 12259.0329 | - | -
7 | Maximum load shed (Evening Peak) | MW | 113 | 2025-03-16 | 19:00
8 | Minimum load shed | MW | 0 | 2025-03-03 | 19:00
9 | Total nos. of load shed days | Day | 21 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 7.0645 | - | -
11 | Total Generation | MkWh | 9107.6319 | - | -
12 | Total Generation by BPDB | MkWh | 1723.1429 | % of total Gen. | 18.92%
13 | Total Generation by IPP | MkWh | 2881.8044 | '' | 31.64%
14 | A) Total Generation by Generation Companies | MkWh | 2640.4845 | '' | 28.99%
| B) Total Generation by REB | MkWh | 154.781 | " | 1.699%
| C) Total Generation by RENTAL | MkWh | 239.0099 | " | 2.624%
| D) Total Imported from India (BIPTC) | MkWh | 681.1954 | " | 7.479%
| E) Total Imported from Tripura, India (A.C) | MkWh | 6.0033 | " | 0.06591%
| F) Total Imported from Nepal | MkWh | 0 | " | 0%
| E) Total Imported from India (Adani Power Jharkhanda Ltd) | MkWh | 781.2105 | " | 8.578%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4228.5203 | % of total Gen. | 46.43%
| B) Oil | MkWh | 1141.8197 | '' | 12.54%
| C) Hydro | MkWh | 0.74082 | '' | 0.008134%
| D) Solar | MkWh | 142.698 | '' | 1.567%
| E) Coal | MkWh | 2125.4439 | '' | 23.34%
| F) BIPTC (Import from India) | MkWh | 681.1954 | '' | 7.479%
| G) A.C (Import from Tripura, India) | MkWh | 6.0033 | '' | 0.06591%
| H) Total Imported from Nepal | MkWh | 0 | '' | 0%
| I) Adani (Import from India) | MkWh | 781.2105 | '' | 8.578%
| J) Wind | MkWh | 0 | '' | 0%
16 | Maximun of the daily total Generation . | MkWh | 333.5752 | 2025-03-16
17 | Monthly Load factor | % | 79.8168 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 54177.3021 | - | -
| A) Gas | M.Taka | 14212.907 | - | -
| B) Coal | M.Taka | 17454.0775 | - | -
| C) HFO | M.Taka | 12588.8288 | - | -
| D) HSD | M.Taka | 1.637 | - | -
| E) Hydro | M.Taka | 3.1952 | - | -
| F) Solar | M.Taka | 1976.5825 | - | -
| G) Total Import | M.Taka | 7940.0741 | - | -
| H) Wind |  | 63.8913
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 2193.1096 | 2025-03-15
| A) Gas | M.Taka | 505.0026 | 2025-03-30
| B) Coal | M.Taka | 632.5335 | 2025-03-28
| C) HFO | M.Taka | 794.3773 | 2025-03-15
| D) HSD | M.Taka | 1.637 | 2025-03-19 | -
| E) Hydro | M.Taka | 0.11087 | 2025-03-20 | -
| F) Solar | M.Taka | 79.3188 | 2025-03-05 | -
| G) Total Import |  | 298.8875 | 2025-03-15
| H) Wind | M.Taka | 7.9688 | 2025-03-22
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.9556
| B) Excluding Hydro, Solar & Wind | Taka/kWhR | 6.0509
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.17 | 31/03/2025 | 06:00
b) | Actual | FT (MSL) | 84.78 | 31/03/2025 | 06:00
22 | Peak Genaration of March 2024 | MW | 13898 | 2024-03-31 | 21:00
23 | Peak Demand of March 2024 | MW | 14050 | 2024-03-30 | 21:00
24 | Maximum peak Generation recorded upto 31/03/2025 | MW | 16477 | 2024-04-30 | 21:00
25 | Maximum peak Demand recorded upto 31/03/2025 | MW | 17200 | 29/04/2024 | 21:00
26 | Maximum load shed recorded upto 31/03/2025 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC, Power Grid, Dhaka.

## FGMO Weekly
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 27.03.2025 | 20.03.2025 | 13.03.2025 | 06.03.2025 | 27.02.2025 | 20.02.2025 | 13.02.2025 | 06.02.2025 | 30.01.2025 | 23.01.2025 | 16.01.2025 | 09.01.2025 | 02.01.2025 | 28.11.2024 | 21.11.2024 | 14.11.2024 | 07.11.2024 | 31.10.2024 | 24.10.2024 | 17.10.2024 | 10.10.2024 | 03.10.2024 | 26.09.2024 | 19.09.2024 | 05.09.2024 | 12.09.2024 | 29.08.2024 | 22.08.2024 | 15.08.2024 | 08.08.2024 | 01.08.2024 | 25.07.2024 | 18.07.2024 | 11.07.2024 | 04.07.2024 | 27.06.2024 | 20.06.2024 | 13.06.2024 | 06.06.2024 | 30.05.2024 | 22.05.2024 | 16.05.2024 | 09.05.2024 | 02.05.2024 | 25.04.2024 | 18.04.2024 | 11.04.2024 | 04.04.2024 | 28.03.2024 | 21.03.2024 | 14.03.2024 | 07.03.2024 | 29.02.2024 | 22.02.2024 | 15.02.2024 | 08.02.2024 | 01.02.2024 | 25.01.2024 | 18.01.2024 | 11.01.2024 | 04.01.2024 | 28.12.2023 | 21.12.2023 | 14.12.2023 | 07.12.2023 | 30.11.2023 | 16.11.2023 | 09.11.2023 | 02.11.2023 | 26.10.2023 | 19.10.2023 | 12.10.2023 | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable | 30 |  |  |  |  | 30 | 30 | 30 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 60 | 60 | [5 empty] | 22 |  |  | 60
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable | [31 empty] | 20 | [7 empty] | 20 | 20 | 20 | 20
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable | [31 empty] | 20 |  | 15 | 15 |  | 15 |  |  |  | 20 | 20 | 20 | 20
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 35 | 35 | 35 |  | 15 | 30 | [7 empty] | 35 | [6 empty] | 25 | 15 | 15 | 15 | 15 | 30 | 30 | 30 |  |  |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [21 empty] | 10 | 20 | 20 | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | [12 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 |  |  | 30 | 30 | 30 |  |  |  | 30 |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | [11 empty] | 15 | 15 | 15 | 15 | [15 empty] | 16 | 16 | 16 | 16 | 16 | [19 empty] | 20 | 20 | 20 | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable | [29 empty] | 40 | [6 empty] | 30 |  |  |  | 30 | 30 | 30 | 30 | 30
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  |  | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | [5 empty] | 40 | [20 empty] | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 |  |  |  | 40 | 40 |  |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 30 | [6 empty] | 30 |  | 30 |  | 25 | 25 |  |  | 40 | 40 | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable |  |  | 2 | 2 | [10 empty] | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [8 empty] | 2 | 2 | 2 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable | 5 | 5 | 5 | 5
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable | [29 empty] | 20 | [6 empty] | 15 | [6 empty] | 15 | 20 | 20 | 20
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable | 35 | 35 | 35 |  |  |  |  | 35 | 35 | 35 | 35 | 35 | [14 empty] | 35 | 35 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [7 empty] | 30 | 30 | 30 | 30 |  |  |  | 30 | 30 |  |  |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable | [10 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [5 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 30 | 30 | 30 | 30
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10603 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10586 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1812 | 1432 | 1464 | 1064 | 592 | 1332 | 1282 | 1682 | 1302 | 1302 | 1685 | 1685 | 1315 | 1813 | 2027 | 1475 | 1475 | 1092 | 1124 | 744 | 712 | 712 | 1802 | 1492 | 1152 | 1492 | 2442 | 2442 | 2036 | 2956 | 2416 | 2476 | 1836 | 1696 | 1696 | 1876 | 3336 | 1196 | 1196 | 1796 | 3416 | 3436 | 3076 | 3038 | 2824 | 2996 | 2996 | 2024 | 1714 | 1714 | 1524 | 1904 | 1872 | 1904 | 1124 | 1452 | 1112 | 712 | 712 | 712 | 712 | 1112 | 1186 | 804 | 1484 | 1144 | 1042 | 1042 | 1112 | 1516 | 1634 | 1634 | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 172 | 142 | 144 | 109 | 67 | 137 | 132 | 167 | 137 | 137 | 162 | 162 | 122 | 160 | 179 | 132 | 132 | 107 | 109 | 79 | 77 | 77 | 172 | 137 | 107 | 137 | 217 | 217 | 186 | 271 | 216 | 226 | 156 | 141 | 156 | 171 | 291 | 111 | 111 | 161 | 311 | 316 | 276 | 269 | 254 | 280 | 280 | 198 | 163 | 163 | 149 | 179 | 177 | 179 | 109 | 167 | 137 | 77 | 77 | 77 | 77 | 107 | 84 | 64 | 139 | 139 | 102 | 102 | 107 | 139 | 159 | 159 | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 7 | 6 | 7 | 6 | 3 | 5 | 5 | 6 | 5 | 5 | 6 | 6 | 5 | 6 | 8 | 5 | 5 | 4 | 5 | 4 | 3 | 3 | 6 | 5 | 4 | 5 | 8 | 8 | 8 | 11 | 9 | 10 | 7 | 7 | 7 | 7 | 12 | 5 | 5 | 7 | 12 | 12 | 11 | 11 | 10 | 11 | 11 | 7 | 6 | 6 | 6 | 7 | 6 | 7 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 6 | 5 | 4 | 4 | 4 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD
New FGMO capable plants under BPSREIP:
Letter date: 09/06/2024
1. Anwara 300 MW Power Plant (United)
2.Chandpur 200 MW Power Plant (Desh energy)
3. Rupsha 105 MW Power Plant (Orion rupsha)
4. Gazipur 100 MW Power Ltd
5. United Payra Power Ltd
6.Sikalbaha 105 MW Power Plant (Baraka Sikalbaha)
7.Karnaphuli Power Ltd
8. Feni Lanka Power Ltd
9. Barisal 110 MW Power Plant (Summit)
10. Madanganj-55 MW Power Plant (Summit)
11. Madhumati 100 MW Power Plant
12. Nawabganj 55 MW Power Plant(Dhaka Southern Power)
13.Manikganj 55 MW Power plant ((Dhaka Southern Power)
14. Manikganj 162 MW Power Plant (MPGL)
15. Zodiac 54 MW Power Plant

## FGMO
Power Grid Bangladesh PLC.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: March 2025
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Bibiyana-III 400 MW CCPP | BPDB | 400 |  | √ |  | √ | [18 empty] | √ | √ | √ | √ | √ | √ | √ | √ | √
3 | Bibiyana South 400 MW | BPDB | 383
4 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
5 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √ | √
6 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | [29 empty] | √
7 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
8 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
9 | Meghnaghat CCPP(Summit) | IPP | 335 |  | √ | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
10 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 450 MW CCPP(North) | APSCL | 361
12 | Ashuganj 450 MW CCPP(South) | APSCL | 360
13 | Ashuganj 420 MW CCPP(East) | APSCL | 400
14 | Ashuganj 55 MW PP (Precision) | QRPP | 55
15 | Bheramara 410 MW CCPP | NWPGCL | 410
16 | Haripur 412 MW CCPP | EGCB | 412
17 | Fenchugonj CCPP Phase-1 | BPDB | 97 | [30 empty] | √
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | [24 empty] | √ |  |  |  |  | √
19 | Siddhirganj 2x120 MW GTPP | EGCB | 210
20 | Shikalbaha 225 MW CCPP | BPDB | 225
21 | Shikalbaha Peaking GT | BPDB | 150
22 | Shahjibazar 330 MW CCPP | BPDB | 330
23 | Chandpur 150 MW CCPP | BPDB | 163
24 | Bhola 225 MW CCPP | BPDB | 194 | [11 empty] | √
25 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
26 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
27 | Siddhirganj 335 MW CCPP | EGCB | 335
28 | Bibiyana-III 400 MW CCPP | BPDB | 400
29 | Sylhet 225 MW CCPP | BPDB | 231
30 | RPCL 210 MW CCPP | IPP | 210
31 | Khulna 225 MW CCPP | NWPGCL | 230
32 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
33 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
34 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
35 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
36 | Shajibazar 100 MW PP | BPDB | 100
37 | Payra 1320 MW Unit-1 | BCPCL | 622 | √ |  | √ | √ | √ | √ | √ | √ | √ |  | √ |  | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ |  | √ | √
38 | Kushiara 163 MW CCPP (KP) | IPP | 163 | [21 empty] | √ | √ | √ |  |  |  | √ | √ | √ | √
39 | Haripur 360MW CCPP(HPL) | IPP | 360
40 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450