## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-04-2025 | during | 22-04-2025 | during | 22-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 355 | 325 | 400.75 | 400.75 | 360 | 360 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 278 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 100 | 29 | 208.13 | 208.13 | 29 | 37 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 270 | 335 | 335 | 315 | 315 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 17 | 30 | 30 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 19 | 18 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 17 | 52.19 | 52.19 | 25 | 16 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 55 | 142 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 85 | 104 | 104 | 51 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 140 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 7 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 263 | 500 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 400 | 583 | 583 | 520 | 520 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2443 | 3288 | 5226.9 | 5298.9 | 3910.38 | 4051.38
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 148 | 150 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 48 | 64 | 84 | 64 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 98 | 98 | 51 | 51 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 65 | 89 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 2 | 7 | 22 | 7 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 64 | 64 | Machine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 0 | 0 | 3.17 | 0 | 3.17 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 53 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 90 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 550 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 1 | 42 | 7 | 42 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 450 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1292 | 1953 | 2833.89 | 2816.72 | 2742.89 | 2725.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 180 | 221 | 221 | 215 | 215 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 359 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 250 | 325 | 325 | 325 | 285 | 285 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 35 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 22 | 32 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 53 | 8 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 138 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 13 | 116 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 66 | 78 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 13 | 19 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 44 | 105.3 | 105.3 | 95 | 95 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 18 | 39 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 91 | 115 | 115 | 92 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 49 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1173 | 1636 | 2402.29 | 2352.29 | 2070.55 | 2049.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-04-2025 | during | 22-04-2025 | during | 22-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 85 | 153 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 104 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.15 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 9 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 188.15 | 304 | 597.2 | 549 | 382.7 | 371.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 39 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 151 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 174 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 22 | 23 | 25 | 25 | 24 | 24 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 349 | 380 | 380 | 352 | 352 | Fgmo activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1501 | 1486 | 1600 | 1600 | 1505 | 1505
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 915 | 867 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 46 | 46 | 46 | 46 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105 | 70 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 86 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 377 | 380 | 1234.2 | 1234.2 | 617.1 | 617.1 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1378 | 1282 | 3616.2 | 3516.2 | 2449.11 | 2349.11
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 613 | 612 | 660 | 660 | 660 | 660 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 0 | 0 | 10.12 | 10.12 | 0 | 0 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 55 | 55 | 130 | 130 | 55 | 55 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 792 | 900 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.27 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1930.27 | 2094 | 2831.12 | 2831.12 | 2706 | 2706
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 18 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 20 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 22 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 106 | 150 | 214 | 214 | 160 | 160 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 166 | 153 | 220 | 220 | 166 | 153 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 151 | 220 | 220 | 150 | 151 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.97 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1164.66 | 1375 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.31 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 85 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2148.94 | 2589 | 3116.03 | 2949.53 | 2885.24 | 2706.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 156 | 150 | 150 | 150 | 150 | machine problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 27 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 82 | 0 | 139.72 | 0 | 139.72 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 309.9 | 384 | 568.12 | 392 | 568.12 | 392
System Total |  |  |  |  | 27566.2 | 28535.742 | 12364.26 | 15016 | 22791.75 | 22305.76 | 19219.99 | 18857
Forecast Scenario (22-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13620 |  | 0 |  | 13620
|  |  |  | 1:00 | 13150 |  | 0 |  | 13150
|  |  |  | 2:00 | 12780 |  | 0 |  | 12780
|  |  |  | 3:00 | 12280 |  | 0 |  | 12280
|  |  |  | 4:00 | 11910 |  | 0 |  | 11910
|  |  |  | 5:00 | 11690 |  | 0 |  | 11690
|  |  |  | 6:00 | 11240 |  | 0 |  | 11240
|  |  |  | 7:00 | 11540 |  | 0 |  | 11540
|  |  |  | 8:00 | 11460 |  | 0 |  | 11460
|  |  |  | 9:00 | 12140 |  | 0 |  | 12140
|  |  |  | 10:00 | 12610 |  | 0 |  | 12610
|  |  |  | 11:00 | 12900 |  | 0 |  | 12900
|  |  |  | 12:00 | 13420 |  | 0 |  | 13420
|  |  |  | 13:00 | 14080 |  | 0 |  | 14080
|  |  |  | 14:00 | 14150 |  | 0 |  | 14150
|  |  |  | 15:00 | 14370 |  | 0 |  | 14370
|  |  |  | 16:00 | 14200 |  | 0 |  | 14200
|  |  |  | 17:00 | 13770 |  | 0 |  | 13770
|  |  |  | 18:00 | 13720 |  | 0 |  | 13720
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15170 |  | 0 |  | 15170
|  |  |  | 19:30 | 15730 |  | 0 |  | 15730
|  |  |  | 20:00 | 15700 |  | 0 |  | 15700
|  |  |  | 21:00 | 15750 |  | 0 |  | 15750
|  |  |  | 22:00 | 15450 |  | 0 |  | 15450
|  |  |  | 23:00 | 15400 |  | 0 |  | 15400
Probable Maximum Temperature: |  |  | 33.10°C
Probable Maximum Demand at Day Peak: |  |  | 13420.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15750.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15750.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 322.50 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:58 hrs on 22-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-04-2025 | [28 empty] | Date: | 21-04-2025 | [28 empty] | Date: | 21-04-2025 | [28 empty] | Date: | 21-04-2025 | [28 empty] | Date: | 21-04-2025 | [16 empty] | Date: | 21-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 89 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 45 | 35 | 115 | 95 | 295 | 55 | 35 | 90 | 0 | 84 | 450 | 297 | 280 | 0 | 35 | 0 | 282 | 38 | 0 | 0 | 160 | 17 | 16 | 0 | 300 | 0 | 0 | 65 | 0 | 14 | 51 | 78 | 0 | 20 | 10 | 0 | 40 | 34 | 28 | 575 | 35 | 0 | 0 | 0 | 34 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 130 | 173 | 0 | 359 | 255 | 47 | 33 | 35 | 72 | 50 | 180 | 13 | 19 | 69 | 88 | 52.2 | 0 | 39 | 310 | 320 | 302 | 39 | 0 | 0 | 138 | 24 | 0 | 82 | 30 | 0 | 17 | 173 | 17 | 104 | 142 | 0 | 0 | 0 | 12 | 8332.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 35 | 1351.98 | 0 | 50 | 0 | 113 | 20 | 49 | 50 | 30 | 16 | 0 | 28 | 0 | 160 | 0 | 147 | 0 | 150 | 0 | 370 | 0 | 0 | 0 | 161 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 50 | 220 | 0 | 612 | 1215 | 0 | 6792.98 | 15125.18 | 81.49
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 113 | 48 | 295 | 55 | 35 | 35 | 0 | 68 | 450 | 289 | 280 | 0 | 35 | 0 | 295 | 38 | 0 | 0 | 160 | 17 | 16 | 0 | 300 | 0 | 0 | 64 | 0 | 6 | 51 | 72 | 0 | 20 | 10 | 0 | 40 | 34 | 33 | 575 | 35 | 0 | 0 | 0 | 34 | 152 | 0 | 0 | 0 | 612 | 0 | 51 | 130 | 108 | 0 | 355 | 255 | 47 | 38 | 35 | 72 | 50 | 167 | 9 | 19 | 73 | 82 | 52.2 | 0 | 39 | 310 | 320 | 333 | 38 | 0 | 0 | 131 | 24 | 0 | 83 | 30 | 0 | 17 | 174 | 17 | 49 | 98 | 0 | 0 | 0 | 8 | 7888.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 35 | 1310.02 | 0 | 46 | 0 | 113 | 20 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 160 | 0 | 147 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 74 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 50 | 220 | 0 | 618 | 1150 | 0 | 6532.02 | 14420.22 | 81.49
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 17 | 113 | 48 | 295 | 15 | 35 | 35 | 0 | 68 | 450 | 296 | 280 | 0 | 35 | 0 | 282 | 38 | 0 | 0 | 160 | 17 | 16 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 34 | 72 | 0 | 20 | 10 | 0 | 40 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 127 | 108 | 0 | 355 | 255 | 48 | 46 | 35 | 72 | 50 | 170 | 9 | 19 | 68 | 80 | 52.2 | 0 | 39 | 305 | 320 | 312 | 37 | 0 | 0 | 131 | 24 | 0 | 83 | 30 | 0 | 17 | 174 | 17 | 48 | 98 | 0 | 0 | 0 | 12 | 7647.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 17 | 1304.99 | 0 | 46 | 0 | 113 | 20 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 160 | 0 | 146 | 0 | 143 | 0 | 350 | 0 | 0 | 0 | 160 | 0 | 73 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 50 | 220 | 0 | 612 | 1150 | 0 | 6400.99 | 14048.19 | 81.48
03:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 17 | 95 | 48 | 145 | 15 | 35 | 35 | 0 | 51 | 450 | 296 | 280 | 0 | 35 | 0 | 289 | 37 | 0 | 0 | 108 | 17 | 16 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 17 | 72 | 0 | 20 | 0 | 0 | 40 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 127 | 16 | 0 | 355 | 255 | 48 | 148 | 35 | 52 | 50 | 167 | 9 | 19 | 69 | 78 | 8 | 0 | 39 | 310 | 320 | 321 | 37 | 0 | 0 | 131 | 22 | 0 | 83 | 30 | 0 | 17 | 174 | 17 | 48 | 97 | 0 | 0 | 0 | 12 | 7344 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 562 | 0 | 1314.74 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 134 | 0 | 134 | 0 | 350 | 0 | 0 | 0 | 161 | 0 | 54 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 50 | 220 | 0 | 613 | 1140 | 0 | 6207.74 | 13551.74 | 81.48
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 17 | 83 | 48 | 45 | 0 | 35 | 35 | 0 | 16 | 400 | 296 | 280 | 0 | 35 | 0 | 285 | 91 | 0 | 0 | 70 | 17 | 16 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 0 | 72 | 0 | 20 | 0 | 0 | 40 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 130 | 8 | 0 | 359 | 255 | 46 | 217 | 10 | 51 | 50 | 171 | 9 | 19 | 70 | 76 | 0 | 0 | 0 | 310 | 320 | 300 | 37 | 0 | 0 | 131 | 22 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 48 | 97 | 0 | 0 | 0 | 12 | 7094 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 1318.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 132 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 50 | 220 | 0 | 613 | 1140 | 0 | 6038.06 | 13132.06 | 81.47
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 70 | 48 | 0 | 0 | 17 | 17 | 0 | 16 | 400 | 298 | 280 | 0 | 0 | 0 | 282 | 91 | 0 | 0 | 0 | 14 | 16 | 0 | 300 | 0 | 0 | 0 | 0 | 35 | 0 | 48 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 50 | 8 | 0 | 358 | 255 | 48 | 189 | 10 | 51 | 50 | 169 | 9 | 19 | 66 | 74 | 0 | 0 | 0 | 300 | 320 | 308 | 37 | 0 | 0 | 132 | 22 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 48 | 97 | 0 | 0 | 0 | 12 | 6739 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 1319.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 124 | 0 | 117 | 0 | 350 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 50 | 220 | 0 | 613 | 1140 | 0 | 5981.02 | 12720.02 | 81.47
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 17 | 0 | 48 | 0 | 0 | 17 | 17 | 0 | 16 | 350 | 293 | 230 | 0 | 0 | 0 | 285 | 97 | 0 | 0 | 0 | 17 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 500 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 540 | 1 | 51 | 20 | 8 | 0 | 300 | 255 | 21 | 196 | 27 | 52 | 40 | 163 | 9 | 20 | 31 | 72 | 0 | 0 | 0 | 300 | 320 | 334 | 37 | 0 | 0 | 129 | 22 | 0 | 80 | 30 | 0 | 17 | 174 | 0 | 49 | 97 | 0 | 0 | 0 | 12 | 6250 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 560 | 0 | 1321.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.39 | 157 | 0 | 120 | 0 | 113 | 0 | 300 | 0 | 0.01 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.01 | 0 | 200 | 9 | 50 | 180 | 0 | 613 | 1060 | 0 | 5762.33 | 12012.33 | 81.46
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 17 | 0 | 48 | 0 | 0 | 17 | 17 | 0 | 0 | 350 | 293 | 230 | 0 | 0 | 0 | 285 | 101 | 0 | 4 | 0 | 17 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 0 | 16 | 0 | 0 | 0 | 0 | 40 | 0 | 33 | 501 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 500 | 4 | 51 | 12 | 8 | 0 | 300 | 255 | 20 | 186 | 27 | 50 | 40 | 96 | 9 | 20 | 28 | 66 | 0 | 3 | 0 | 305 | 320 | 300 | 37 | 0 | 0 | 136 | 22 | 0 | 80 | 30 | 0 | 17 | 175 | 0 | 45 | 85 | 0 | 0 | 0.11 | 12 | 6083.11 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.88 | 560 | 0 | 1324.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 156 | 0 | 120 | 0 | 111 | 0 | 300 | 0 | 0.31 | 0 | 151 | 0 | 0 | 3 | 0 | 0 | 0 | 1.1 | 37 | 0.12 | 0 | 200 | 8 | 50 | 180 | 0 | 607 | 1040 | 0 | 5796.25 | 11879.36 | 81.46
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17 | 0 | 20 | 48 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 289 | 230 | 0 | 0 | 0 | 281 | 37 | 0 | 11 | 0 | 17 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 460 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 500 | 5 | 51 | 12 | 8 | 0 | 300 | 255 | 20 | 181 | 30 | 50 | 40 | 73 | 9 | 0 | 15 | 34 | 0 | 17 | 0 | 305 | 320 | 300 | 37 | 0 | 0 | 131 | 22 | 0 | 41 | 30 | 0 | 17 | 174 | 0 | 45 | 75 | 0 | 0 | 0.07 | 12 | 5718.07 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 460 | 0 | 1224.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 156 | 0 | 129 | 0 | 116 | 0 | 260 | 0 | 0 | 0 | 160 | 0 | 0 | 10 | 0 | 0 | 0 | 3 | 18 | 0.28 | 0 | 200 | 7 | 50 | 180 | 0 | 607 | 889 | 0 | 5401.22 | 11119.29 | 81.45
09:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 285 | 230 | 0 | 0 | 0 | 240 | 37 | 0 | 14 | 0 | 17 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 22 | 0 | 1 | 40 | 0 | 2 | 362 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 410 | 7 | 51 | 0 | 8 | 0 | 300 | 255 | 12 | 152 | 33 | 30 | 40 | 0 | 9 | 0 | 0 | 26 | 0 | 31 | 0 | 280 | 320 | 341 | 37 | 0 | 0 | 128 | 22 | 0 | 11 | 30 | 0 | 17 | 174 | 0 | 25 | 45 | 0 | 0 | 4.64 | 12 | 5166.64 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 0 | 1016.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0.18 | 156 | 0 | 167 | 0 | 155 | 0 | 260 | 0 | 0.04 | 0 | 127 | 0 | 0 | 16 | 0 | 0 | 0 | 2.6 | 124 | 0.19 | 0 | 150 | 7 | 55 | 180 | 0 | 616 | 700 | 0 | 5043.99 | 10210.63 | 81.45
10:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 309 | 350 | 0 | 0 | 0 | 315 | 39 | 0 | 7 | 0 | 17 | 14 | 0 | 220 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 65 | 10 | 0 | 40 | 0 | 2 | 363 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 405 | 18 | 51 | 0 | 8 | 0 | 300 | 285 | 5 | 217 | 36 | 0 | 40 | 0 | 9 | 2 | 0 | 46 | 0 | 0 | 0 | 295 | 320 | 352 | 39 | 0 | 0 | 142 | 22 | 0 | 41 | 30 | 0 | 18 | 174 | 0 | 27 | 65 | 0 | 2 | 3.8 | 0 | 5581.8 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 380 | 0 | 921.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 3.31 | 180 | 0 | 180 | 0 | 167 | 0 | 330 | 0 | 0 | 0 | 125 | 0 | 0 | 25 | 0 | 0 | 0 | 3.1 | 76 | 0 | 0 | 150 | 7 | 55 | 180 | 0 | 551 | 701 | 0 | 5089.39 | 10671.19 | 81.44
11:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 9 | 16 | 30 | 32 | 0 | 0 | 14 | 72 | 0 | 0 | 400 | 297 | 450 | 0 | 0 | 0 | 300 | 37 | 0 | 4 | 0 | 17 | 17 | 0 | 76 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 65 | 10 | 0 | 40 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 500 | 15 | 51 | 0 | 16 | 0 | 355 | 285 | 11 | 202 | 36 | 0 | 30 | 0 | 9 | 2 | 0 | 52 | 0 | 4 | 0 | 305 | 320 | 390 | 39 | 0 | 0 | 153 | 22 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 54 | 85 | 0 | 2 | 24.65 | 1 | 6182.65 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 377 | 0 | 1028.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 54.26 | 181 | 0 | 160 | 0 | 139 | 0 | 414 | 0 | 4.69 | 0 | 115 | 0 | 0 | 14 | 0 | 0 | 0 | 5.1 | 181 | 0.23 | 0 | 200 | 0 | 55 | 220 | 0 | 553 | 768 | 0 | 5490.88 | 11673.53 | 81.44
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 17 | 55 | 32 | 0 | 0 | 35 | 140 | 0 | 0 | 370 | 299 | 350 | 0 | 0 | 0 | 290 | 100 | 0 | 7 | 0 | 17 | 19 | 0 | 263 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 65 | 10 | 0 | 40 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 550 | 15 | 51 | 0 | 53 | 0 | 355 | 250 | 22 | 199 | 36 | 18 | 30 | 13 | 18 | 13 | 0 | 66 | 0 | 49 | 0 | 300 | 320 | 367 | 39 | 0 | 0 | 153 | 22 | 0 | 80 | 30 | 0 | 16 | 174 | 0 | 55 | 85 | 0 | 2 | 37.15 | 9 | 6597.15 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 377 | 0 | 1164.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 58.31 | 106 | 0 | 166 | 0 | 150 | 0 | 414 | 0 | 4.97 | 0 | 158 | 0 | 35 | 27 | 0 | 0 | 0 | 7.9 | 82 | 0.27 | 0 | 250 | 0 | 55 | 220 | 0 | 613 | 792 | 0 | 5767.11 | 12364.26 | 81.43
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 17 | 17 | 86 | 32 | 30 | 0 | 35 | 162 | 0 | 5 | 370 | 286 | 350 | 0 | 0 | 0 | 270 | 99 | 0 | 14 | 17 | 17 | 19 | 0 | 271 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 65 | 10 | 0 | 40 | 0 | 3 | 452 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 550 | 18 | 51 | 6 | 55 | 0 | 360 | 285 | 25 | 182 | 34 | 45 | 30 | 42 | 9 | 19 | 0 | 72 | 0 | 52 | 0 | 295 | 320 | 349 | 39 | 0 | 0 | 152 | 22 | 0 | 80 | 30 | 0 | 16 | 175 | 0 | 55 | 85 | 0 | 2 | 33.95 | 6 | 6829.95 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 413 | 0 | 1276.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 57.88 | 106 | 0 | 162 | 0 | 147 | 0 | 414 | 0 | 4.94 | 0 | 160 | 0 | 35 | 14 | 0 | 0 | 0 | 3.5 | 149 | 0.15 | 0 | 250 | 0 | 55 | 220 | 0 | 611 | 737 | 0 | 5921.15 | 12751.1 | 81.43
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 35 | 17 | 88 | 32 | 30 | 0 | 35 | 162 | 0 | 32 | 330 | 291 | 350 | 0 | 0 | 0 | 315 | 96 | 0 | 28 | 23 | 17 | 19 | 0 | 320 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 65 | 10 | 0 | 40 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 550 | 1 | 51 | 40 | 55 | 0 | 352 | 285 | 25 | 199 | 34 | 73 | 40 | 61 | 9 | 18 | 0 | 72 | 0 | 57 | 28 | 300 | 320 | 342 | 39 | 0 | 0 | 134 | 22 | 0 | 80 | 30 | 0 | 16 | 175 | 0 | 57 | 85 | 0 | 2 | 46.36 | 12 | 6942.36 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 414 | 0 | 1267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 49.92 | 102 | 0 | 157 | 0 | 143 | 0 | 370 | 0 | 4.68 | 0 | 163 | 0 | 35 | 24 | 0 | 0 | 0 | 6.8 | 86 | 0.5 | 0 | 250 | 0 | 55 | 220 | 0 | 613 | 691 | 0 | 5735.9 | 12678.26 | 81.42
15:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 35 | 17 | 88 | 62 | 95 | 0 | 35 | 162 | 0 | 58 | 350 | 281 | 400 | 0 | 0 | 0 | 270 | 39 | 0 | 22 | 35 | 17 | 19 | 0 | 320 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 50 | 0 | 40 | 1 | 2 | 450 | 0 | 0 | 0 | 0 | 2 | 151 | 0 | 0 | 0 | 612 | 14 | 51 | 48 | 26 | 0 | 350 | 285 | 25 | 197 | 34 | 72 | 40 | 68 | 9 | 19 | 3 | 62 | 0 | 9 | 31 | 320 | 320 | 348 | 38 | 0 | 0 | 152 | 22 | 0 | 80 | 30 | 0 | 16 | 175 | 0 | 66 | 123 | 0 | 2 | 36.26 | 12 | 7191.26 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 506 | 0 | 1350 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 39.73 | 97 | 0 | 152 | 0 | 145 | 0 | 414 | 0 | 3.61 | 0 | 163 | 0 | 50 | 13 | 25 | 0 | 0 | 1.5 | 68 | 0.35 | 0 | 250 | 0 | 55 | 220 | 0 | 613 | 698 | 0 | 5913.19 | 13104.45 | 81.42
16:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 92 | 62 | 95 | 0 | 35 | 162 | 0 | 67 | 320 | 295 | 350 | 0 | 17 | 0 | 295 | 37 | 0 | 12 | 35 | 17 | 19 | 0 | 320 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 50 | 0 | 40 | 15 | 2 | 451 | 0 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 612 | 8 | 51 | 100 | 8 | 0 | 347 | 320 | 24 | 212 | 33 | 72 | 40 | 62 | 27 | 19 | 15 | 64 | 8 | 6 | 31 | 310 | 320 | 320 | 38 | 0 | 0 | 141 | 22 | 0 | 83 | 30 | 0 | 16 | 174 | 0 | 66 | 124 | 0 | 1 | 23.79 | 12 | 7302.79 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 459 | 0 | 1353 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25.25 | 63 | 0 | 150 | 0 | 146 | 0 | 414 | 0 | 0.29 | 0 | 163 | 0 | 52 | 7 | 34 | 0 | 0 | 2 | 61 | 0.29 | 0 | 200 | 0 | 55 | 220 | 0 | 611 | 698 | 0 | 5742.83 | 13045.62 | 81.41
17:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 54 | 17 | 120 | 64 | 95 | 0 | 35 | 162 | 0 | 67 | 320 | 276 | 350 | 0 | 0 | 0 | 270 | 37 | 0 | 4 | 70 | 17 | 19 | 0 | 320 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 50 | 0 | 40 | 17 | 5 | 450 | 0 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 612 | 3 | 51 | 132 | 8 | 0 | 356 | 325 | 10 | 209 | 33 | 72 | 50 | 60 | 36 | 19 | 15 | 60 | 8 | 9 | 40 | 300 | 320 | 300 | 38 | 0 | 0 | 130 | 22 | 0 | 83 | 30 | 0 | 16 | 175 | 0 | 66 | 124 | 0 | 0 | 10.6 | 12 | 7281.6 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 410 | 0 | 1357 | 0 | 0 | 0 | 35 | 4 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 59 | 0 | 151 | 0 | 151 | 0 | 383 | 0 | 0.55 | 0 | 163 | 0 | 52 | 6 | 34 | 0 | 0 | 0.6 | 20 | 0.13 | 0 | 200 | 0 | 55 | 220 | 0 | 601 | 700 | 0 | 5555.28 | 12836.88 | 81.41
18:00 | 0 | 30 | 12 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 54 | 17 | 120 | 80 | 95 | 0 | 35 | 162 | 0 | 67 | 320 | 301 | 250 | 0 | 0 | 0 | 298 | 37 | 0 | 1 | 70 | 17 | 19 | 0 | 440 | 17 | 15 | 0 | 0 | 4 | 0 | 0 | 0 | 100 | 50 | 0 | 40 | 17 | 8 | 404 | 0 | 0 | 0 | 4 | 17 | 151 | 0 | 0 | 0 | 550 | 0 | 51 | 135 | 0 | 0 | 300 | 280 | 10 | 203 | 33 | 72 | 50 | 60 | 38 | 19 | 17 | 68 | 8 | 1 | 46 | 300 | 320 | 348 | 38 | 0 | 0 | 135 | 22 | 0 | 41 | 30 | 0 | 16 | 174 | 6 | 95 | 152 | 0 | 0 | 1.45 | 12 | 7227.45 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 14 | 1269 | 0 | 0 | 0 | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 153 | 0 | 153 | 0 | 390 | 0 | 0.06 | 0 | 160 | 0 | 52 | 1 | 34 | 0 | 0 | 0.2 | 5 | 0.22 | 0 | 150 | 0 | 55 | 180 | 0 | 603 | 700 | 0 | 5380.48 | 12607.93 | 81.4
19:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 17 | 132 | 118 | 145 | 0 | 35 | 162 | 0 | 85 | 420 | 274 | 400 | 0 | 35 | 0 | 270 | 33 | 0 | 0 | 160 | 17 | 18 | 0 | 584 | 21 | 15 | 0 | 0 | 0 | 51 | 38 | 0 | 89 | 100 | 0 | 40 | 25 | 2 | 563 | 90 | 0 | 0 | 8 | 40 | 150 | 0 | 0 | 0 | 612 | 0 | 51 | 137 | 8 | 0 | 359 | 325 | 13 | 182 | 35 | 74 | 50 | 90 | 39 | 19 | 35 | 80 | 12 | 0 | 46 | 315 | 320 | 360 | 39 | 0 | 0 | 152 | 22 | 0 | 83 | 30 | 0 | 17 | 174 | 19 | 104 | 153 | 0 | 0 | 0 | 12 | 8557 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 423 | 17 | 1367 | 0 | 0 | 0 | 68 | 18 | 55 | 50 | 12 | 0 | 0 | 30 | 0 | 150 | 0 | 153 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 157 | 0 | 113 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 612 | 832 | 0 | 6135 | 14692 | 81.4
19:30 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 54 | 17 | 142 | 147 | 145 | 0 | 35 | 162 | 0 | 85 | 400 | 278 | 400 | 0 | 35 | 0 | 270 | 29 | 0 | 0 | 160 | 17 | 18 | 0 | 500 | 53 | 15 | 0 | 0 | 1 | 51 | 48 | 0 | 89 | 100 | 0 | 40 | 34 | 2 | 575 | 90 | 0 | 0 | 8 | 85 | 150 | 0 | 0 | 0 | 612 | 0 | 51 | 138 | 8 | 0 | 359 | 325 | 32 | 180 | 35 | 91 | 50 | 116 | 39 | 19 | 44 | 78 | 25 | 0 | 46 | 300 | 320 | 349 | 39 | 0 | 0 | 151 | 23 | 0 | 83 | 30 | 0 | 17 | 174 | 35 | 104 | 153 | 0 | 0 | 0 | 12 | 8667 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 35 | 1375 | 0 | 18 | 0 | 113 | 20 | 93 | 50 | 22 | 0 | 0 | 30 | 0 | 150 | 0 | 153 | 0 | 151 | 0 | 414 | 0 | 0 | 0 | 156 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 612 | 900 | 0 | 6349 | 15016
20:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 54 | 19 | 149 | 147 | 145 | 0 | 35 | 162 | 0 | 85 | 420 | 291 | 400 | 0 | 0 | 0 | 272 | 31 | 0 | 0 | 160 | 17 | 18 | 0 | 450 | 52 | 15 | 0 | 0 | 3 | 51 | 63 | 0 | 89 | 100 | 0 | 40 | 83 | 12 | 503 | 34 | 0 | 0 | 8 | 88 | 150 | 0 | 0 | 0 | 612 | 0 | 51 | 137 | 8 | 0 | 359 | 325 | 33 | 183 | 35 | 91 | 50 | 115 | 38 | 19 | 10 | 78 | 25 | 0 | 47 | 305 | 320 | 335 | 39 | 0 | 0 | 141 | 23 | 0 | 83 | 30 | 0 | 17 | 174 | 35 | 104 | 153 | 0 | 0 | 0 | 12 | 8529 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 38 | 1366 | 0 | 32 | 0 | 113 | 25 | 94 | 50 | 35 | 0 | 0 | 30 | 0 | 151 | 0 | 153 | 0 | 151 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 612 | 898 | 0 | 6373 | 14902 | 81.39
21:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 54 | 35 | 149 | 147 | 145 | 0 | 35 | 162 | 0 | 85 | 420 | 279 | 400 | 0 | 17 | 0 | 267 | 31 | 0 | 0 | 90 | 17 | 18 | 0 | 450 | 53 | 15 | 0 | 0 | 4 | 51 | 78 | 0 | 89 | 100 | 0 | 40 | 96 | 15 | 503 | 0 | 0 | 0 | 8 | 87 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 133 | 8 | 0 | 360 | 325 | 46 | 179 | 35 | 91 | 50 | 119 | 39 | 19 | 0 | 70 | 8 | 0 | 47 | 300 | 320 | 369 | 39 | 0 | 0 | 136 | 23 | 0 | 83 | 30 | 0 | 17 | 174 | 35 | 104 | 163 | 0 | 0 | 0 | 12 | 8486 | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 53 | 1372 | 0 | 50 | 0 | 113 | 25 | 94 | 35 | 35 | 0 | 0 | 30 | 0 | 155 | 0 | 153 | 0 | 151 | 0 | 414 | 0 | 0 | 0 | 162 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 612 | 910 | 0 | 6457 | 14943 | 81.39
22:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 54 | 35 | 119 | 95 | 45 | 0 | 35 | 162 | 0 | 85 | 420 | 292 | 400 | 0 | 17 | 0 | 275 | 33 | 0 | 0 | 90 | 17 | 18 | 0 | 450 | 17 | 15 | 0 | 0 | 3 | 51 | 78 | 0 | 100 | 60 | 0 | 40 | 93 | 19 | 502 | 0 | 0 | 0 | 8 | 87 | 152 | 0 | 0 | 0 | 612 | 0 | 51 | 140 | 8 | 0 | 359 | 325 | 18 | 202 | 32 | 91 | 50 | 118 | 39 | 19 | 0 | 72 | 0 | 0 | 47 | 300 | 320 | 388 | 39 | 0 | 0 | 148 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 33 | 105 | 163 | 0 | 0 | 0 | 12 | 8271 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 51 | 1372 | 0 | 50 | 0 | 113 | 25 | 94 | 0 | 35 | 0 | 0 | 30 | 0 | 157 | 0 | 152 | 0 | 148 | 0 | 414 | 0 | 0 | 0 | 166 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 612 | 981 | 0 | 6427 | 14698 | 81.38
23:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 35 | 97 | 95 | 15 | 0 | 35 | 162 | 0 | 85 | 420 | 293 | 400 | 0 | 17 | 0 | 295 | 26 | 0 | 0 | 108 | 17 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 2 | 51 | 79 | 0 | 100 | 60 | 0 | 40 | 89 | 22 | 504 | 0 | 0 | 0 | 0 | 87 | 152 | 0 | 0 | 0 | 612 | 0 | 51 | 138 | 8 | 0 | 356 | 325 | 10 | 202 | 35 | 90 | 50 | 126 | 38 | 20 | 0 | 66 | 0 | 0 | 47 | 305 | 320 | 388 | 39 | 0 | 0 | 153 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 17 | 105 | 163 | 0 | 0 | 0 | 12 | 8197 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 51 | 1353 | 0 | 50 | 0 | 70 | 27 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 157 | 0 | 147 | 0 | 146 | 0 | 414 | 0 | 0 | 0 | 165 | 0 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 612 | 1000 | 0 | 6241 | 14438 | 81.38
Total KWH | 60336 | 701760 | 288000 | 0 | 0 | 0 | 0 | 0 | 8618400 | 0 | 0 | 750240 | 471240 | 2000448 | 1501920 | 1816582 | 129506 | 743343 | 2325600 | 0 | 1038720 | 8899000 | 7046196 | 8058182 | 0 | 301908 | 0 | 6850867 | 1388000 | 0 | 134094 | 1521600 | 405600 | 403920 | 0 | 7970454 | 237109 | 153055 | 93120 | 0 | 191520 | 409208 | 770400 | 0 | 1294080 | 743040 | 4797 | 965220 | 568700 | 367680 | 11730909.09 | 170618 | 0 | 0 | 40356 | 588799 | 3616756 | 0 | 0 | 0 | 13570908 | 108000 | 1138976 | 1985527 | 635636 | 0 | 8545100 | 6932000 | 600000 | 4350000 | 764280 | 1455360 | 1052910 | 2285280 | 459480 | 385930 | 570000 | 1592640 | 217243 | 184836 | 576176 | 7384500 | 7666300 | 8487000 | 899000 | 0 | 0 | 3368455 | 487656 | 0 | 1710720 | 715872 | 0 | 407000 | 3598430 | 249480 | 1558800 | 2647200 | 0 | 12800 | 231560 | 262320 | 172468658.09 | 21736727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554400 | 10923640 | 347040 | 30621818 | 0 | 343767 | 0 | 1089312 | 176470 | 400176 | 156672 | 102739 | 0 | 624550 | 235470 | 288000 | 3443727 | 0 | 3771191 | 0 | 3641318 | 0 | 9138109 | 0 | 24540 | 0 | 3872000 | 0 | 1167370 | 153219 | 1098758 | 0 | 0 | 36968.64 | 922320 | 2683 | 0 | 5782000 | 0 | 1281000 | 5303960 | 0 | 14572364 | 22465454 | 0 | 144277762.64 | 316746420.73

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12364.26 | MW | 12:00 Hr. | Energy Generated |  |  | 316.7464 |  | MKWHr.
| Day Peak Demand |  |  | 12433.26 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.766 |  | MKWHr.
| Evening Peak Generation |  |  | 15016 | MW | 19:30 Hr. | Energy Demand |  |  | 318.5124 |  | MKWHr.
| Evening Peak Demand |  |  | 15085 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.5 |  | °C
| Minimum Generation of the Day |  |  | 10210.63 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 1027.45 |  | MMCFD
| Maximum Generation of the Day |  |  | 15125.18 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.3411 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 49.6406 | 0 | 13.6512 | 0 | 0 | 0.13409 | 0 | 0 | 63.4259 | Gas | 139.3341 | Gas | 493312644.31
| Chattogram Zone |  |  | 3.9844 | 25.3018 | 5.0685 | 0 | 0.96522 | 0.1128 | 0 | 0.19152 | 35.6243 | Coal | 82.9173 | Coal | 488535625.33
| Cumilla Zone |  |  | 24.4048 | 0 | 7.5491 | 0 | 0 | 0.18484 | 1.5926 | 0 | 33.7314 | HFO | 36.1043 | HFO | 670433682.05
| Mymensingh Zone |  |  | 0 | 0 | 4.7178 | 0 | 0 | 0.24436 | 0 | 0 | 4.9622 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.7249 | Hydro | 0.96522 | Hydro | 96522
| Khulna Zone |  |  | 0 | 10.9236 | 0.34704 | 0 | 0 | 0.5544 | 21.7367 | 0 | 33.5618 | Solar | 3.2828 | Solar | 54142130.2904
| Barishal Zone |  |  | 6.585 | 42.8198 | 0 | 0 | 0 | 0.002683 | 0 | 0 | 49.4075 | Import | 53.9512 | Import | 299203636.03
| Rajshahi Zone |  |  | 19.9943 | 0 | 2.5046 | 0 | 0 | 0.93709 | 30.6218 | 0 | 54.0579 | Wind | 0.19152 | Wind | 2803852.8
| Rangpur Zone |  |  | 0 | 3.872 | 2.2661 | 0 | 0 | 1.1125 | 0 | 0 | 7.2506
| Total |  |  | 139.3341 | 82.9173 | 36.1043 | 0 | 0.96522 | 3.2828 | 53.9512 | 0.19152 | 316.7464
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 493312644.31 |  | Hydro | 96522
|  |  |  | Coal | 488535625.33 |  | Solar | 54142130.2904
|  |  |  | HFO | 670433682.05 |  | Import | 299203636.03
|  |  |  | HSD | 0 |  | Wind | 2803852.8
[5 empty] | Total: | 200,85,28,092 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7367 | Peak Hr Flow | 867.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 8563272.77 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.6218 | Peak Hr Flow | 1375.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 444 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.5926 | Peak Hr Flow | 78.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 726 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.9512 | Peak Hr Flow | 2320.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 66 |  | 5481
|  |  |  | Chattogram |  | 0 |  | 1318
|  |  |  | Cumilla |  | 0 |  | 1296
|  |  |  | Mymensingh |  | 0 |  | 1168
|  |  |  | Sylhet |  | 0 |  | 576
|  |  |  | Khulna |  | 0 |  | 1760
|  |  |  | Barishal |  | 0 |  | 376
|  |  |  | Rajshahi |  | 0 |  | 1637
|  |  |  | Rangpur |  | 0 |  | 979
|  |  |  | Total |  | 66 |  | 14591
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 09:22 | 10:01 | Muktagacha 132/33kV S/S RPCL-2 Forced S/D Due to Due to RPCL Plant emergency maintenance
work.
| 09:56 | 11:26 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end Due to project
work
| 10:14 | 11:24 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ishurdi 132/33kV end Due to caddle
guard remove
| 10:38 | 18:19 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning
|  | 11:00 | Shyampur 230/132kV S/S Auto TR-1 HT is restored.
| 11:00 | 18:20 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Requested by Aminbazar
|  | 11:04 | Shyampur 230/132kV S/S Auto TR-1 LT is restored.
|  | 11:04 | Shyampur 230/132kV S/S Aux TR-1 HT is restored.
|  | 11:04 | Shyampur 230/132kV S/S Aux TR-1 LT is restored.
| 11:30 |  | Unique Meghnaghat Power Limited (UMPL) Synchronized with remarks:- ST
| 11:56 | 13:15 | Ishwardi-Rooppur 132kV Ckt-1 Project Work S/D from Ruppur 132/11kV end Due to project
work
| 11:57 | 13:13 | Ishwardi-Rooppur 132kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end Due to
Scaffolding remove
| 12:00 |  | Day peak Generation is 12361 MW
| 12:11 |  | Unique Meghnaghat Power Limited (UMPL) record a general event:- ST resynch at 11:30 hrs
| 12:13 |  | Unique Meghnaghat Power Limited (UMPL) record a general event:- GT DLN Tuning InProgress
by OEM, GT load set to 150 MW
| 13:15 | 14:52 | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Kachua 132/33kV end Due to Emergency
maintenance of Earth wire connection at tower no 61.
| 13:25 | 14:54 | Candpur- Kachua 132kV Ckt-2 Scheduled S/D from Chandpur 132/33kV end Due to Maintenance
| 13:30 | 18:36 | Nawabganj 132/33kV S/S TR-1 LT Scheduled S/D Due to 33 kV incomer-01 R-Phase CT change
| 13:31 | 18:34 | Nawabganj 132/33kV S/S TR-1 HT Scheduled S/D Due to 33 kV incomer-01 R-Phase CT change
| 13:34 |  | Khulna (C) S/S TR-1 425T LT Tripped showing Differential Relay ( 87T), relays Due to
33kv cable fault.B-Phase
| 13:34 |  | Khulna (C) S/S TR-1 425T HT Tripped showing 86T lockout Realy relays Due to 33kv cable
fault.B - phase
| 13:37 | 15:44 | Kabirpur -Tongi 132kV Ckt-2 Forced S/D from Kabirpur 132/33kV end Due to Emergency | [7 empty] | 68.0MW load
|  |  | maintenance work | [7 empty] | interrup. Kabirpur
132/33kV end
| 14:28 | 15:28 | Bhaluka 132/33kV S/S BR Powergen Ckt- 01 Project Work S/D Due to N to N test
| 16:47 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 17:10 | 18:33 | Bagerhat 132/33kV S/S 132 kV BUS Scheduled S/D Due to 132 Tr2 bus side red hot | [7 empty] | 65.0MW load
|  |  | maintenance work | [7 empty] | interrup.
| 19:30 |  | Evening Peak Generation: 15016 MW.
|  | 19:50 | Gopalganj 400/132kV S/S 400kV Bus-01 is restored.
| 21:45 | 22:23 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to Red hot for T1 transformer 33KV CT | [7 empty] | 25.0MW load
|  |  | P1 Connector | [7 empty] | interrup.
| 00:15 | 01:20 | Hathazari 230/132/33kV S/S T-01 HT Forced S/D Due to 33 kV XLPE cable fault
| 01:09 |  | Siddhirganj GT-1 was shut down.
| 01:17 |  | Bhola 225 MW CCPP GT-2 Synchronized.
| 06:00 |  | Min. Gen. 11947 MW
| 06:59 |  | Jamalpur-Mymensingh 132kV Ckt-1 Project Work S/D from Mymensingh 132/33kV end Due to
LILO connection of ERS tower at Muktagachha end and from Jamalpur 132/33kV end Due to
Work on mymensingh grid substation
| 07:00 | 07:57 | Gulshan 132/33kV S/S MT-2 LT Scheduled S/D Due to Maintenance Work
| 07:00 |  | Gulshan 132/33kV S/S MT-2 HT Scheduled S/D Due to Maintenance Work
| 07:10 | 07:55 | Mymensingh-Netrokona 132kV Ckt-2 Project Work S/D from Mymensingh 132/33kV end Due to At
Net end
| 07:14 | 07:46 | Mymensingh-Netrokona 132kV Ckt-1 Project Work S/D from Mymensingh 132/33kV end Due to At
Net end.
| 07:39 |  | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
| 07:41 |  | Sirajgonj 225MW CCPP Unit-3, FGMO is OFF with remarks:-
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 325 | 8618400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8899000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 278 | 7046196 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 129506 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 29 | 1388000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6850867 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 60336 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 750240 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 1501920 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 743343 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 301908 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 405600 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 403920 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 288000 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 1816582 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 142 | 2000448 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 701760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 85 | 1038720 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2325600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 134094 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 471240 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 7970454 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 8058182 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1521600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3288 | 63425916
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 40356 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 108000 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 965220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3616756 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 588799 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 48 | 770400 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 409208 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 89 | 1294080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 367680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 93120 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 4797 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 153055 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 568700 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 743040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 237109 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 90 | 170618 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13570908 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 191520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 11730909.09 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1953 | 35624275.09
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 180 | 4350000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 359 | 8545100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 325 | 6932000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 764280 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 32 | 600000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 635636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1138976 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 138 | 1985527 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 46 | 576176 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1052910 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 116 | 2285280 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 78 | 1592640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 217243 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 19 | 385930 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 44 | 570000 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 39 | 459480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 1455360 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 184836 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1636 | 33731374
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12800 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 153 | 2647200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1558800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 231560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 262320 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 249480 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 304 | 4962160
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 899000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3368455 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 715872 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1710720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 174 | 3598430 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 407000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 23 | 487656 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7384500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 349 | 8487000 | Fgmo activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7666300 | Machine Problem
Sylhet Area Total |  |  |  |  | 2368.568 | 1486 | 34724933
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 867 | 21736727 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 347040 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 554400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 380 | 10923640 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1282 | 33561807
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 612 | 14572364 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 0 | 0 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 55 | 1281000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 22465454 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5303960 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5782000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2683 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2094 | 49407461
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 18 | 343767 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 20 | 176470 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 22 | 102739 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 3443727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 153 | 3771191 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 151 | 3641318 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9138109 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 235470 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 400176 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1089312 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 156672 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24540 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1375 | 30621818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 288000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 624550 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2589 | 54057859
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3872000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1098758 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 36968.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1167370 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 153219 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 922320 | -
Rangpur Area Total |  |  |  |  | 950 | 384 | 7250635.64
Eastern Grid Total |  |  |  |  | 16921.242 | 8667 | 172468658.09
Western Grid Total |  |  |  |  | 11614.5 | 6349 | 144277762.64
National Grid Total |  |  |  |  | 28535.742 | 15016 | 316746420.73
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9773.1 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4752.6 | MW
i) Dhaka area |  |  | 5415.1 |  | MW | i) Khulna area |  |  |  | 1760.4 | MW
ii) Chattogram area |  |  | 1318 |  | MW | ii) Barishal area |  |  |  | 376 | MW
iii) Cumilla area |  |  | 1296 |  | MW | iii) Rajshahi area |  |  |  | 1637.2 | MW
iv) Mymensingh area |  |  | 1168 |  | MW | iv) Rangpur area |  |  |  | 979 | MW
v) Sylhet area |  |  | 576 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14525.7 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 88 | 19:00 | 133 | Patuakhali | 79 | 00:00
2 | AKSML | 132 | 11:00 | 68 | Jaldhaka | 80 | 19:00 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 36 | 00:00 | 69 | Jamalpur | 122 | 21:00 | 135 | Postogola | 54 | 00:00
4 | Agargaon | 109 | 13:00 | 70 | Jashore | 152 | 19:30 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 70 | 19:00 | 71 | Jhenaidah | 134 | 19:30 | 137 | Purbasadipur | 128 | 19:00
6 | Amnura | 49 | 21:00 | 72 | Joydebpur | 153 | 19:30 | 138 | Rahanpur | 34 | 23:00
7 | Ashuganj | 103 | 22:00 | 73 | Joypurhat | 72 | 21:00 | 139 | Rahim | 52 | 08:00
8 | BSRM | 196 | 23:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 80 | 00:00
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 15 | 23:00 | 141 | Rajendrapur | 134 | 20:00
10 | Bajitpur | 50 | 00:00 | 76 | Kabirpur | 282 | 08:00 | 142 | Rajshahi | 137 | 20:00
11 | Bakulia | 83 | 19:30 | 77 | Kachua | 80 | 01:00 | 143 | Rajshahi-230 | 98 | 13:00
12 | Banani | 40 | 15:00 | 78 | Kallyanpur | 111 | 00:00 | 144 | Ramganj | 120 | 19:00
13 | Bangabhaban | 15 | 15:00 | 79 | Kalurghat | 38 | 09:00 | 145 | Rampur | 37 | 00:00
14 | Barapukuria | 64 | 21:00 | 80 | Kamrangirchar | 68 | 13:00 | 146 | Rangamati | 13 | 19:30
15 | Barguna | 28 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 162 | 19:30
16 | Barishal | 108 | 11:00 | 82 | Kasba | 34 | 00:00 | 148 | Ruppur | 8 | 16:00
17 | Barishal-230 | 94 | 00:00 | 83 | Kazla | 116 | 18:30 | 149 | SSM | 10 | 01:00
18 | Baroaulia | 62 | 13:00 | 84 | Keranigonj | 76 | 00:00 | 150 | Saidpur | 117 | 19:00
19 | Baroirhat | 59 | 00:00 | 85 | Khagrachori | 28 | 18:30 | 151 | Satkhira | 134 | 21:00
20 | Bashundhara | 188 | 19:00 | 86 | Khulna | 62 | 00:00 | 152 | Satmasjid | 106 | 19:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulshi | 167 | 17:00 | 153 | Savar | 224 | 15:00
22 | Beanibazar | 74 | 19:00 | 88 | Kishoreganj | 128 | 20:00 | 154 | SevenRings | 18.51 | 18:00
23 | Benapole | 68 | 21:00 | 89 | Kodda | 306 | 21:00 | 155 | ShahCement | 36 | 00:00
24 | Bhaluka | 142 | 02:00 | 90 | Kulaura | 44 | 19:30 | 156 | Shahjadpur | 88 | 21:00
25 | Bhandaria | 56 | 22:00 | 91 | Kurigram | 66 | 19:00 | 157 | Shahjibazar | 121 | 19:30
26 | Bhangura | 44 | 00:00 | 92 | Kushtia | 155 | 19:00 | 158 | Shahmirpur | 60 | 16:00
27 | Bheramara(GK) | 70 | 20:00 | 93 | Lalbag | 68 | 12:00 | 159 | Shariatpur | 84 | 00:00
28 | Bhulta | 249 | 21:00 | 94 | Lalmonirhat | 64 | 20:00 | 160 | Sherpur | 142 | 19:00
29 | Bog-Sherpur | 72 | 07:00 | 95 | MI_Cement | 18.2 | 12:00 | 161 | Shikalbaha | 28 | 16:00
30 | Bogura | 180 | 21:00 | 96 | Madanganj | 41 | 19:00 | 162 | Shitalakhya | 78.4 | 16:00
31 | Borhanuddin | 84 | 00:00 | 97 | Madaripur | 108 | 00:00 | 163 | Sholosohor | 31 | 09:00
32 | Brahmanbaria | 132 | 00:00 | 98 | Madartek | 76.39 | 00:00 | 164 | Shyampur | 148 | 00:00
33 | Cantonment | 118 | 13:00 | 99 | Madunaghat | 51 | 22:00 | 165 | Siddhirganj | 117 | 00:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 66 | 00:00 | 166 | Sirajganj | 122 | 20:00
35 | Chandpur | 69 | 19:00 | 101 | Mahasthangarh | 82 | 00:00 | 167 | Sonargaon | 103 | 03:00
36 | Chandraghona | 29 | 00:00 | 102 | Manikganj | 139 | 21:00 | 168 | Sreemongol | 67 | 19:00
37 | Chapai | 76 | 21:00 | 103 | Maniknagar | 72 | 13:00 | 169 | Sreepur | 106 | 19:00
38 | Charsaidpur | 31 | 16:00 | 104 | Matarbari | 41 | 19:00 | 170 | Srinagar | 46.45 | 00:00
39 | Chauddagram | 62 | 00:00 | 105 | Matuail | 66 | 12:00 | 171 | Sunamganj | 57 | 21:00
40 | Chhatak | 33 | 00:00 | 106 | Millgate | 97 | 15:00 | 172 | Sylhet | 43 | 19:30
41 | Chowmuhani | 204 | 21:00 | 107 | Mirpur | 135 | 19:30 | 173 | Sylhet-132 | 116 | 18:30
42 | Chuadanga | 120 | 22:00 | 108 | Mirsorai | 11 | 23:00 | 174 | TK | 30.5 | 00:00
43 | Coxsbazar | 124 | 21:00 | 109 | Mirzapur | 50 | 06:00 | 175 | Tangail | 192 | 06:00
44 | Cumilla(N) | 157 | 01:00 | 110 | Mithapukur | 56 | 19:00 | 176 | Thakurgaon | 111 | 19:30
45 | Cumilla(S) | 163 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 139 | 12:00
46 | Daudkandi | 153 | 19:00 | 112 | Mogbazar | 135.5 | 15:00 | 178 | Ullahpara | 42 | 19:00
47 | Dhaka | 56 | 12:00 | 113 | Mongla | 46 | 23:00 | 179 | Ullon | 47 | 00:00
48 | Dhamrai | 136 | 15:00 | 114 | Motijheel | 37 | 11:00 | 180 | Uttara | 84 | 19:00
49 | Dhanmondi | 140 | 13:00 | 115 | Muktagacha | 35 | 00:00 | 181 | UttaraNew | 49 | 00:00
50 | Dohazari | 90 | 00:00 | 116 | Munshiganj | 109 | 00:00 | 182 | Zigatola | 76 | 01:00
51 | Faridpur | 159 | 00:00 | 117 | Muradnagar | 26 | 00:00
52 | Fatullah | 106 | 12:00 | 118 | Mymensingh | 202 | 19:00
53 | Fenchuganj | 38 | 20:00 | 119 | Naogaon | 144 | 00:00
54 | Feni | 98 | 19:30 | 120 | Narail | 61 | 18:00
55 | GPH | 100 | 09:00 | 121 | Narinda | 73 | 13:00
56 | Ghatail | 84 | 19:30 | 122 | Narshingdi | 181 | 00:00
57 | Ghorashal | 16 | 16:00 | 123 | Natore | 168 | 21:00
58 | Ghorashal-230 | 87 | 00:00 | 124 | Nawabganj | 57 | 00:00
59 | Goalpara | 38 | 19:30 | 125 | Netrakona | 116 | 00:00
60 | Gollamari | 100 | 00:00 | 126 | New | 88.4 | 15:00
61 | Gopalganj | 107.4 | 00:00 | 127 | Niamatpur | 107 | 19:00
62 | Gulshan | 116 | 16:00 | 128 | Noapara | 48 | 19:30
63 | Halishahar | 77.5 | 10:00 | 129 | PHP | 8 | 15:00
64 | HaripurSBU | 191 | 19:00 | 130 | Pabna | 119 | 22:00
65 | Hasnabad | 88 | 19:00 | 131 | Palashbari | 114 | 00:00
66 | Hathazari | 68 | 19:00 | 132 | Panchagarh | 56 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15125.18 | 168 |  | 15300.74
1:00 | 14420.22 | 220 |  | 14650.22
2:00 | 14048.19 | 194 |  | 14251.19
3:00 | 13551.74 | 142 |  | 13699.74
4:00 | 13132.06 | 113 |  | 13250.06
5:00 | 12720.02 | 67 |  | 12790.02
6:00 | 12012.33 | 47 |  | 12061.33
7:00 | 11879.36 | 41 |  | 11922.36
8:00 | 11119.29 | 0 |  | 11119.29
9:00 | 10210.63 | 0 |  | 10210.63
10:00 | 10671.19 | 0 |  | 10671.19
11:00 | 11673.53 | 0 |  | 11673.53
12:00 | 12364.26 | 66 |  | 12433.26
13:00 | 12751.1 | 70 |  | 12824.1
14:00 | 12678.26 | 100 |  | 12782.26
15:00 | 13104.45 | 74 |  | 13181.45
16:00 | 13045.62 | 44 |  | 13091.62
17:00 | 12836.88 | 81 |  | 12921.88
18:00 | 12607.93 | 70 |  | 12680.93
19:00 | 14692 | 74 |  | 14769
19:30 | 15016 | 66 |  | 15085
20:00 | 14902 | 65 |  | 14970
21:00 | 14943 | 45 |  | 14990
22:00 | 14698 | 50 |  | 14750
23:00 | 14438 | 35 |  | 14475
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8332.2 | 6792.98 | 15125.18 | DAILY GENERATION CURVE
00:30 | 8110.2 | 6662.5 | 14772.7
01:00 | 7888.2 | 6532.02 | 14420.22 | 21-04-2025
01:30 | 7767.7 | 6466.505 | 14234.205
02:00 | 7647.2 | 6400.99 | 14048.19
02:30 | 7495.6 | 6304.365 | 13799.965
03:00 | 7344 | 6207.74 | 13551.74
03:30 | 7219 | 6122.9 | 13341.9
04:00 | 7094 | 6038.06 | 13132.06
04:30 | 6916.5 | 6009.54 | 12926.04
05:00 | 6739 | 5981.02 | 12720.02
05:30 | 6494.5 | 5871.675 | 12366.175
06:00 | 6250 | 5762.33 | 12012.33
06:30 | 6166.555 | 5779.29 | 11945.845
07:00 | 6083.11 | 5796.25 | 11879.36
07:30 | 5900.59 | 5598.735 | 11499.325
08:00 | 5718.07 | 5401.22 | 11119.29
08:30 | 5442.355 | 5222.605 | 10664.96
09:00 | 5166.64 | 5043.99 | 10210.63
09:30 | 5374.22 | 5066.69 | 10440.91
10:00 | 5581.8 | 5089.39 | 10671.19
10:30 | 5882.225 | 5290.135 | 11172.36
11:00 | 6182.65 | 5490.88 | 11673.53
11:30 | 6389.9 | 5628.995 | 12018.895
12:00 | 6597.15 | 5767.11 | 12364.26
12:30 | 6713.55 | 5844.13 | 12557.68
13:00 | 6829.95 | 5921.15 | 12751.1
13:30 | 6886.155 | 5828.525 | 12714.68
14:00 | 6942.36 | 5735.9 | 12678.26
14:30 | 7066.81 | 5824.545 | 12891.355
15:00 | 7191.26 | 5913.19 | 13104.45
15:30 | 7247.025 | 5828.01 | 13075.035
16:00 | 7302.79 | 5742.83 | 13045.62
16:30 | 7292.195 | 5649.055 | 12941.25
17:00 | 7281.6 | 5555.28 | 12836.88
17:30 | 7254.525 | 5467.88 | 12722.405
18:00 | 7227.45 | 5380.48 | 12607.93
18:30 | 7892.225 | 5757.74 | 13649.965
19:00 | 8557 | 6135 | 14692
19:30 | 8667 | 6349 | 15016
20:00 | 8529 | 6373 | 14902
20:30 | 8507.5 | 6415 | 14922.5 |  | Executive Engineer
21:00 | 8486 | 6457 | 14943 |  | Network Operation Division
21:30 | 8378.5 | 6442 | 14820.5
22:00 | 8271 | 6427 | 14698
22:30 | 8234 | 6334 | 14568
23:00 | 8197 | 6241 | 14438

## En-Curve
QF-LDC-12
Date | 21-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3315 | 2463 | 916 | 0 | 88 | 1351.98 | 40 | 3985 | 0 | 643 | 2309.2 | 0 | 0 | 14 | 168 | DAILY ENERGY CURVE
00:30 | 3352.5 | 2426 | 915.5 | 0 | 85 | 1331 | 40 | 3956 | 0 | 566 | 2090.7 | 0 | 0 | 10 | 194 | 21-04-2025
01:00 | 3390 | 2389 | 915 | 0 | 82 | 1310.02 | 40 | 3927 | 0 | 489 | 1872.2 | 0 | 0 | 6 | 220
01:30 | 3344.5 | 2390.5 | 915 | 0 | 81 | 1307.505 | 40 | 3924 | 0 | 480.5 | 1743.2 | 0 | 0 | 8 | 207 | Energy Generated | 316.7464 |  | MKWHr
02:00 | 3299 | 2392 | 915 | 0 | 80 | 1304.99 | 40 | 3921 | 0 | 472 | 1614.2 | 0 | 0 | 10 | 194 | Energy not Served | 1.766 |  | MKWHr
02:30 | 3345 | 2347.5 | 915 | 0 | 79 | 1309.865 | 40 | 3917 | 0 | 390.5 | 1443.6 | 0 | 0 | 12.5 | 168 | Total Energy Requirement | 318.5124 |  | MKWHr
03:00 | 3391 | 2303 | 915 | 0 | 78 | 1314.74 | 40 | 3913 | 0 | 309 | 1273 | 0 | 0 | 15 | 142
03:30 | 3424.5 | 2272.5 | 915 | 0 | 77 | 1316.4 | 40 | 3911.5 | 0 | 262 | 1107.5 | 0 | 0 | 15.5 | 127.5
04:00 | 3458 | 2242 | 915 | 0 | 76 | 1318.06 | 40 | 3910 | 0 | 215 | 942 | 0 | 0 | 16 | 113
04:30 | 3438.5 | 2238 | 914.5 | 0 | 75 | 1318.54 | 40 | 3909 | 0 | 168 | 799 | 0 | 0 | 25.5 | 90
05:00 | 3419 | 2234 | 914 | 0 | 74 | 1319.02 | 40 | 3908 | 0 | 121 | 656 | 0 | 0 | 35 | 67
05:30 | 3379.5 | 2147 | 914.5 | 0 | 73 | 1320.385 | 40 | 3769.5 | 3.29 | 105 | 586.5 | 0 | 0 | 27.5 | 57
06:00 | 3340 | 2060 | 915 | 0 | 72 | 1321.75 | 40 | 3631 | 6.58 | 89 | 517 | 0 | 0 | 20 | 47
06:30 | 3330 | 2065 | 914.5 | 0 | 69 | 1323.295 | 40 | 3595 | 46.05 | 89 | 461 | 0 | 0 | 13 | 44
07:00 | 3320 | 2070 | 914 | 0 | 66 | 1324.84 | 40 | 3559 | 85.52 | 89 | 405 | 0 | 0 | 6 | 41
07:30 | 3264 | 1996.5 | 891 | 0 | 50 | 1274.89 | 40 | 3417.5 | 106.435 | 81 | 375 | 0 | 0 | 3 | 20.5
08:00 | 3208 | 1923 | 868 | 0 | 34 | 1224.94 | 40 | 3276 | 127.35 | 73 | 345 | 0 | 0 | 0 | 0
08:30 | 3227 | 1878 | 867.5 | 0 | 30 | 1120.96 | 40 | 3010.5 | 196 | 49 | 244 | 0 | 0 | 2 | 0
09:00 | 3246 | 1833 | 867 | 0 | 26 | 1016.98 | 40 | 2745 | 264.65 | 25 | 143 | 0 | 0 | 4 | 0
09:30 | 3399 | 1924 | 890.5 | 0 | 36 | 969.48 | 40 | 2710 | 271.43 | 33 | 160 | 0 | 0 | 7.5 | 0
10:00 | 3552 | 2015 | 914 | 0 | 46 | 921.98 | 40 | 2675 | 278.21 | 41 | 177 | 0 | 0 | 11 | 0
10:30 | 3613 | 2067 | 914.5 | 0 | 49 | 975.29 | 40 | 2819 | 346.57 | 70.5 | 271 | 0 | 0 | 6.5 | 0
11:00 | 3674 | 2119 | 915 | 0 | 52 | 1028.6 | 40 | 2963 | 414.93 | 100 | 365 | 0 | 0 | 2 | 0
11:30 | 3637 | 2176.5 | 915 | 0 | 59 | 1096.63 | 40 | 3076.5 | 438.265 | 104.5 | 468.5 | 0 | 0 | 7 | 33
12:00 | 3600 | 2234 | 915 | 0 | 66 | 1164.66 | 40 | 3190 | 461.6 | 109 | 572 | 0 | 0 | 12 | 66
12:30 | 3600 | 2234.5 | 915.5 | 0 | 69 | 1220.67 | 40 | 3181.5 | 500.01 | 117.5 | 641 | 0 | 0 | 38 | 68
13:00 | 3600 | 2235 | 916 | 0 | 72 | 1276.68 | 40 | 3173 | 538.42 | 126 | 710 | 0 | 0 | 64 | 70
13:30 | 3590 | 2234.5 | 915.5 | 0 | 72 | 1271.84 | 40 | 3152 | 506.84 | 121 | 778 | 0 | 0 | 33 | 85
14:00 | 3580 | 2234 | 915 | 0 | 72 | 1267 | 40 | 3131 | 475.26 | 116 | 846 | 0 | 0 | 2 | 100
14:30 | 3562 | 2269 | 915 | 0 | 67 | 1308.5 | 40 | 3211.5 | 404.355 | 134.5 | 978.5 | 0 | 0 | 1 | 87
15:00 | 3544 | 2304 | 915 | 0 | 62 | 1350 | 40 | 3292 | 333.45 | 153 | 1111 | 0 | 0 | 0 | 74
15:30 | 3553 | 2252.5 | 915 | 0 | 63 | 1351.5 | 40 | 3243 | 279.535 | 153 | 1224.5 | 0 | 0 | 0 | 59
16:00 | 3562 | 2201 | 915 | 0 | 64 | 1353 | 40 | 3194 | 225.62 | 153 | 1338 | 0 | 0 | 0 | 44
16:30 | 3523 | 2175.5 | 915 | 0 | 62 | 1355 | 40 | 3165 | 158.75 | 178 | 1369 | 0 | 0 | 0 | 62.5
17:00 | 3484 | 2150 | 915 | 0 | 60 | 1357 | 40 | 3136 | 91.88 | 203 | 1400 | 0 | 0 | 0 | 81
17:30 | 3494.5 | 2131.5 | 915 | 0 | 64 | 1313 | 40 | 3039 | 50.905 | 222.5 | 1450 | 0 | 0 | 2 | 75.5
18:00 | 3505 | 2113 | 915 | 0 | 68 | 1269 | 40 | 2942 | 9.93 | 242 | 1500 | 0 | 0 | 4 | 70
18:30 | 3550.5 | 2355.5 | 891 | 0 | 74 | 1318 | 40 | 3224 | 4.965 | 419.5 | 1770.5 | 0 | 0 | 2 | 72
19:00 | 3596 | 2598 | 867 | 0 | 80 | 1367 | 40 | 3506 | 0 | 597 | 2041 | 0 | 0 | 0 | 74
19:30 | 3575 | 2502 | 867 | 0 | 78 | 1375 | 40 | 3542 | 0 | 704 | 2332 | 0 | 0 | 1 | 66
20:00 | 3571 | 2491 | 868 | 0 | 78 | 1366 | 40 | 3465 | 0 | 753 | 2267 | 0 | 0 | 3 | 65
20:30 | 3587.5 | 2488 | 889 | 0 | 74 | 1369 | 40 | 3472 | 0 | 734.5 | 2265 | 0 | 0 | 3.5 | 55
21:00 | 3604 | 2485 | 910 | 0 | 70 | 1372 | 40 | 3479 | 0 | 716 | 2263 | 0 | 0 | 4 | 45
21:30 | 3629 | 2478 | 877.5 | 0 | 71 | 1372 | 40 | 3515.5 | 0 | 690 | 2144 | 0 | 0 | 3.5 | 47.5
22:00 | 3654 | 2471 | 845 | 0 | 72 | 1372 | 40 | 3552 | 0 | 664 | 2025 | 0 | 0 | 3 | 50
22:30 | 3666 | 2474.5 | 845.5 | 0 | 69 | 1362.5 | 40 | 3562.5 | 0 | 617 | 1928.5 | 0 | 0 | 2.5 | 42.5
23:00 | 3678 | 2478 | 846 | 0 | 66 | 1353 | 40 | 3573 | 0 | 570 | 1832 | 0 | 0 | 2 | 35
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 395 | 09:00 | 380 | 00:00 | Payra | 413 | 09:00 | 404 | 00:00
Ashuganj | 406 | 9:00 | 388 | 12:00 | Rahanpur | 417 | 09:00 | 396 | 00:00
Bhulta | 398 | 09:00 | 382 | 12:00 | Rampal | 405 | 09:00 | 386 | 00:00
Bibiana | 394 | 09:00 | 382 | 15:00
BIPTC | 401 | 08:00 | 389 | 00:00
Bogura | 411 | 10:00 | 385 | 00:00
Gopalganj | 401 | 09:00 | 384 | 00:00
Kaliakoir | 367 | 09:00 | 352 | 14:00
Madunaghat | 401 | 21:00 | 392 | 05:00
Meghnaghat | 393 | 09:00 | 385 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 230 | 09:00 | 220 | 12:00 | Keranigonj | 228 | 09:00 | 218 | 12:00
AKSML | 232 | 19:00 | 223 | 02:00 | Khulna(S) | 232 | 09:00 | 216 | 19:00
Aminbazar | 228 | 09:00 | 221 | 10:00 | Madunaghat | 235 | 19:30 | 228 | 00:00
Ashuganj | 233 | 08:00 | 224 | 12:00 | Madunaghat-400 | 234 | 20:00 | 226 | 03:00
Ashuganj-400 | 233 | 08:00 | 224 | 12:00 | Maniknagar | 224 | 09:00 | 216 | 12:00
Baghabari | 235 | 09:00 | 226 | 12:00 | Meghnaghat | 233 | 09:00 | 226 | 12:00
Barapukuria | 219 | 09:00 | 213 | 19:00 | Meghnaghat-400 | 227 | 09:00 | 221 | 12:00
Barapukuria-230 | 219 | 09:00 | 213 | 19:00 | Mirsorai | 235 | 20:00 | 220 | 05:00
Barishal | 234 | 13:00 | 223 | 00:00 | Rajshahi | 232 | 09:00 | 220 | 13:00
Bheramara | 234 | 08:00 | 222 | 14:00 | Rampal | 232 | 09:00 | 218 | 01:00
Bhulta | 226 | 09:00 | 216 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 09:00 | 219 | 13:00 | Rampura | 226 | 09:00 | 214 | 12:00
BIPTC | 236 | 09:00 | 222 | 14:00 | Shikalbaha | 235 | 19:30 | 223 | 02:00
Bogura | 227 | 09:00 | 217 | 00:00 | Shyampur | 229 | 09:00 | 219 | 12:00
Bogura-400 | 228 | 10:00 | 216 | 01:00 | Siddhirganj | 228 | 09:00 | 218 | 12:00
Borhanuddin | 239 | 17:00 | 230 | 00:00 | Sirajgonj | 240 | 09:00 | 234 | 14:00
BSRM | 231 | 19:30 | 220 | 04:00 | Sreepur | 234 | 09:00 | 220 | 16:00
Cumilla(N) | 227 | 09:00 | 217 | 12:00 | Tongi | 225 | 09:00 | 214 | 15:00
Faridpur | 229 | 09:00 | 216 | 00:00
Fenchuganj | 229 | 09:00 | 218 | 23:00
Ghorashal | 230 | 00:00 | 220 | 13:00
Ghorashal-230 | 230 | 09:00 | 216 | 12:00
Gopalganj | 229 | 09:00 | 219 | 00:00
GPH | 232 | 20:00 | 222 | 04:00
Haripur | 228 | 09:00 | 218 | 12:00
Hasnabad | 227 | 09:00 | 219 | 12:00
Hathazari | 234 | 21:00 | 227 | 11:00
Ishurdi | 236 | 09:00 | 225 | 14:00
Jhenaidah | 230 | 09:00 | 213 | 19:00
Kaliakoir | 230 | 09:00 | 219 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 08:00 | 125 | 15:00 | Madartek | 133 | 08:00 | 125 | 13:00
Agargaon | 135 | 09:00 | 128 | 12:00 | Madunaghat | 135 | 19:00 | 130 | 00:00
Agrabad | 135 | 19:30 | 128 | 04:00 | Magura | 132 | 07:00 | 120 | 19:00
AKS | 132 | 20:00 | 126 | 03:00 | Mahasthangarh | 131 | 09:00 | 125 | 00:00
Aminbazar | 128 | 03:00 | 124 | 14:00 | Manikganj | 125 | 09:00 | 120 | 14:00
Amnura | 135 | 21:00 | 124 | 00:00 | Maniknagar | 133 | 09:00 | 125 | 12:00
Ashuganj | 138 | 08:00 | 133 | 00:00 | Matarbari | 127 | 13:00 | 115 | 00:00
Bagerhat | 130 | 09:00 | 117 | 23:00 | Matuail | 132 | 09:00 | 126.4 | 12:00
Bajitpur | 136 | 07:00 | 127 | 12:00 | Millgate | 128 | 01:00 | 122 | 09:00
Bakulia | 136 | 21:00 | 129 | 04:00 | Mirpur | 129 | 09:00 | 123 | 12:00
Banani | 134 | 21:00 | 125 | 15:00 | Mirzapur | 131 | 09:00 | 122 | 06:00
Bangabhaban | 132 | 09:00 | 125 | 11:00 | Mithapukur | 130 | 22:00 | 124 | 13:00
Barapukuria | 132 | 22:00 | 127 | 19:00 | MI_Cement | 132.5 | 09:00 | 126 | 12:00
Barguna | 134 | 09:00 | 129 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 13:00 | 122 | 00:00 | Mogbazar | 134 | 06:00 | 125 | 12:00
Barishal-230 | 131 | 13:00 | 123 | 00:00 | Mongla | 131 | 09:00 | 119 | 00:00
Baroaulia | 134 | 19:30 | 129 | 12:00 | Motijheel | 132 | 09:00 | 125 | 11:00
Baroirhat | 131 | 09:00 | 120 | 00:00 | Muktagacha | 133 | 07:00 | 124 | 00:00
Bashundhara | 133 | 09:00 | 121 | 07:00 | Munshiganj | 131 | 09:00 | 125 | 12:00
BashundharaCement | 131 | 09:00 | 124 | 12:00 | Muradnagar | 131 | 09:00 | 123 | 00:00
Beanibazar | 131 | 07:00 | 126 | 18:30 | Mymensingh | 135 | 07:00 | 118 | 18:30
Benapole | 130 | 09:00 | 116 | 19:00 | Naogaon | 128 | 10:00 | 119 | 00:00
Bhaluka | 135 | 09:00 | 124 | 13:00 | Narail | 133 | 06:00 | 119 | 19:00
Bhandaria | 125 | 13:00 | 112 | 00:00 | Narinda | 133 | 09:00 | 125 | 12:00
Bhangura | 133 | 10:00 | 128 | 14:00 | Narshingdi | 133 | 07:00 | 116 | 12:00
Bheramara | 135 | 09:00 | 126 | 19:00 | Natore | 132 | 09:00 | 125 | 19:30
Bheramara(GK) | 135 | 08:00 | 126 | 19:00 | Nawabganj | 136 | 09:00 | 129 | 00:00
Bhulta | 128 | 09:00 | 120 | 12:00 | Netrakona | 129 | 05:00 | 115 | 18:30
Bog-Sherpur | 131 | 10:00 | 121 | 07:00 | New | 130 | 09:00 | 122 | 11:00
Bogura | 134 | 09:00 | 128 | 00:00 | Niamatpur | 137 | 10:00 | 130 | 00:00
Bogura-230 | 134 | 10:00 | 128 | 00:00 | Noapara | 133 | 18:00 | 121 | 19:00
Brahmanbaria | 135 | 07:00 | 125 | 00:00 | Pabna | 134 | 08:00 | 128 | 15:00
Cantonment | 135 | 09:00 | 128 | 12:00 | Palashbari | 128 | 03:00 | 121 | 13:00
Chandina | 134 | 09:00 | 125 | 12:00 | Panchagarh | 133 | 21:00 | 119 | 07:00
Chandpur | 130 | 09:00 | 119 | 12:00 | Patuakhali | 134 | 15:00 | 129 | 00:00
Chandraghona | 135 | 19:30 | 130 | 00:00 | Payra | 136 | 10:00 | 132 | 00:00
Chapai | 131 | 11:00 | 125 | 00:00 | PHP | 130 | 10:00 | 118 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 09:00 | 126 | 12:00 | Postogola | 134 | 09:00 | 128 | 15:00
Chauddagram | 131 | 09:00 | 119 | 12:00 | Purbachal | 134 | 21:00 | 125 | 12:00
Chhatak | 131 | 07:00 | 124 | 23:00 | Purbasadipur | 129 | 00:00 | 120 | 06:00
Chowmuhani | 126 | 09:00 | 111 | 00:00 | Rahanpur | 138 | 09:00 | 125 | 11:00
Chuadanga | 130 | 08:00 | 116 | 23:00 | Rahanpur-400 | 138 | 09:00 | 132 | 00:00
Coxsbazar | 123 | 13:00 | 114 | 00:00 | Rahim | 133 | 09:00 | 126 | 12:00
Cumilla(N) | 132 | 09:00 | 125 | 12:00 | Rajbari | 134 | 09:00 | 125 | 00:00
Cumilla(S) | 132 | 08:00 | 123 | 11:00 | Rajendrapur | 139 | 09:00 | 121 | 07:00
Daudkandi | 130 | 08:00 | 121 | 12:00 | Rajshahi | 132 | 04:00 | 126 | 14:00
Dhaka | 134 | 09:00 | 126 | 11:00 | Rajshahi-230 | 134 | 09:00 | 117 | 00:00
Dhamrai | 137 | 09:00 | 128 | 06:00 | Ramganj | 127 | 09:00 | 114 | 00:00
Dhanmondi | 134 | 21:00 | 126 | 12:00 | Rampur | 134 | 19:30 | 129 | 00:00
Dohazari | 131 | 19:30 | 124 | 03:00 | Rampura | 134 | 09:00 | 126 | 12:00
Faridpur | 135 | 09:00 | 127 | 01:00 | Rangamati | 134 | 20:00 | 129 | 00:00
Fatullah | 132 | 09:00 | 127 | 01:00 | Rangpur | 128 | 03:00 | 121 | 19:00
Fenchuganj | 136 | 08:00 | 132 | 00:00 | Ruppur | 137 | 08:00 | 131 | 18:30
Feni | 129 | 10:00 | 116 | 00:00 | Saidpur | 131 | 03:00 | 121 | 07:00
Ghatail | 128 | 07:00 | 118 | 15:00 | Satkhira | 132 | 18:00 | 116 | 00:00
Ghorashal | 136 | 09:00 | 131 | 01:00 | Satmasjid | 134 | 09:00 | 128 | 13:00
Goalpara | 135 | 18:00 | 123 | 19:00 | Savar | 128 | 09:00 | 122 | 10:00
Gollamari | 135 | 09:00 | 124 | 01:00 | SevenRings | 139 | 09:00 | 130 | 12:00
Gopalganj | 134 | 09:00 | 125 | 00:00 | ShahCement | 132 | 09:00 | 126 | 12:00
Gopalganj-400 | 136 | 10:00 | 130 | 00:00 | Shahjadpur | 138 | 10:00 | 132 | 00:00
Gulshan | 134 | 09:00 | 125 | 12:00 | Shahjibazar | 136 | 07:00 | 125 | 01:00
Halishahar | 136 | 21:00 | 128 | 08:00 | Shahmirpur | 136 | 18:30 | 130 | 02:00
Haripur | 133 | 09:00 | 126 | 12:00 | Shariatpur | 135 | 09:00 | 125 | 00:00
HaripurSBU | 133 | 09:00 | 126 | 12:00 | Sherpur | 139 | 06:00 | 123 | 01:00
Hasnabad | 132 | 04:00 | 129 | 15:00 | Shikalbaha | 125 | 21:00 | 119 | 00:00
Hathazari | 136 | 21:00 | 132 | 00:00 | Shikalbaha-230 | 137 | 19:30 | 130 | 02:00
Ishurdi | 139 | 09:00 | 131 | 19:00 | Shitalakhya | 132.5 | 09:00 | 126 | 12:00
Jaldhaka | 128 | 22:00 | 118 | 07:00 | Sholosohor | 135 | 20:00 | 129 | 02:00
Jamalpur | 140 | 06:00 | 127 | 01:00 | Shyampur | 131 | 09:00 | 125 | 12:00
Jashore | 131 | 09:00 | 117 | 19:00 | Shyampur-230 | 132 | 09:00 | 127 | 04:00
Jhenaidah | 133 | 08:00 | 122 | 19:00 | Siddhirganj | 133 | 09:00 | 127 | 11:00
Jhenaidah-230 | 135 | 09:00 | 123 | 00:00 | Sirajganj | 130 | 10:00 | 116 | 00:00
Joydebpur | 134 | 08:00 | 124 | 15:00 | Sonargaon | 132 | 09:00 | 124 | 13:00
Joypurhat | 125 | 10:00 | 116 | 00:00 | Sreemongol | 134 | 07:00 | 127 | 18:30
Juldah | 137 | 19:30 | 131 | 00:00 | Sreepur | 138 | 09:00 | 128 | 12:00
Kabirpur | 131 | 09:00 | 120 | 11:00 | Srinagar | 137 | 09:00 | 129 | 18:30
Kachua | 130 | 09:00 | 119 | 13:00 | SSM | 139 | 19:30 | 130 | 07:00
Kaliakoir | 139 | 09:00 | 125 | 14:00 | Sunamganj | 130 | 09:00 | 123 | 00:00
Kallyanpur | 129 | 09:00 | 124 | 12:00 | Sylhet | 132 | 07:00 | 128 | 00:00
Kalurghat | 135 | 20:00 | 131 | 00:00 | Sylhet-132 | 132 | 08:00 | 129 | 00:00
Kamrangirchar | 134 | 08:00 | 128 | 12:00 | Tangail | 132 | 08:00 | 120 | 23:00
Kaptai | 134 | 5:00 | 122 | 12:00 | Thakurgaon | 135 | 21:00 | 121 | 07:00
Kasba | 132 | 09:00 | 122 | 00:00 | TK | 136 | 19:30 | 131 | 00:00
Kazla | 131 | 09:00 | 124 | 13:00 | Tongi | 134 | 09:00 | 125 | 12:00
Keranigonj | 137 | 09:00 | 130 | 12:00 | Ullahpara | 129 | 10:00 | 114 | 07:00
Khagrachori | 133 | 21:00 | 128 | 00:00 | Ullon | 134 | 09:00 | 125 | 11:00
Khulna | 134 | 09:00 | 122 | 00:00 | Uttara | 128 | 05:00 | 122 | 15:00
Khulna(S) | 135 | 09:00 | 124 | 00:00 | UttaraNew | 127 | 03:00 | 122 | 15:00
Khulshi | 134 | 20:00 | 127 | 04:00 | Zigatola | 135 | 10:00 | 129 | 00:00
Kishoreganj | 134 | 09:00 | 125 | 00:00
Kodda | 135 | 09:00 | 119 | 14:00
KSRM | 135 | 10:00 | 130 | 00:00
Kulaura | 135 | 07:00 | 131 | 00:00
Kurigram | 129 | 22:00 | 118 | 13:00
Kushtia | 133 | 08:00 | 123 | 19:00
Lalbag | 136 | 09:00 | 129 | 14:00
Lalmonirhat | 130 | 22:00 | 121 | 00:00
Madanganj | 131 | 09:00 | 124 | 12:00
Madaripur | 135 | 17:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division