## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-04-2025 | during | 23-04-2025 | during | 23-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 400 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 275 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 5 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 100 | 100 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 302 | 320 | 335 | 335 | 315 | 315 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 90 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 144 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 17 | 30 | 30 | 18 | 18 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 19 | 20 | 20 | 20 | 19 | 19 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 17 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 262 | 295 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 51 | 85 | 104 | 104 | 51 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 350 | 450 | 584 | 584 | 450 | 450 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 370 | 500 | 583 | 583 | 450 | 450 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 144 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 3108.5 | 3744 | 5259.9 | 5331.9 | 3779.13 | 3895.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 146 | 144 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 9 | 51 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 47 | 84 | 84 | 64 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 51 | 98 | 98 | 51 | 51 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 60 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 5 | 7 | 12 | 7 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 10 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 72 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 17 | 3 | 42 | 24 | 42 | 24 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 566 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1479 | 1866 | 2851.72 | 2823.72 | 2784.72 | 2776.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 206 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 350 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 330 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 34 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 15 | 55 | 55 | 48 | 48 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 16 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 86 | 130 | 150 | 150 | 140 | 140 | Machine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 87 | 181 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 80 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 68 | 62 | 105.3 | 105.3 | 105.3 | 105.3 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 48 | 73 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 37 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1421 | 1661.2 | 2407.29 | 2357.29 | 2121.85 | 2100.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-04-2025 | during | 23-04-2025 | during | 23-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 1.2 | 0 | 1.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 122 | 150 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 105 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 31.23 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 42 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 275.23 | 321.5 | 600.2 | 549 | 310.7 | 331.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 39 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 143 | 157 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 399 | 348 | 380 | 380 | 352 | 352 | Fgmo activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1499 | 1465 | 1568 | 1568 | 1506 | 1506
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 911 | 867 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 46 | 46 | 46 | 46 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 73.28 | 0 | 95 | 0 | 95 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 607 | 558 | 1234.2 | 1234.2 | 618 | 618 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1591.28 | 1460 | 3611.2 | 3516.2 | 2465.01 | 2370.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 238 | 295 | 290 | 290 | 290 | 290 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 11 | 10.12 | 10.12 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 90 | 90 | 130 | 130 | 95 | 95 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 857 | 1200 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.36 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1643.36 | 2123 | 2462.12 | 2461.12 | 2427 | 2426
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 30 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 5 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 28 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 167 | 156 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 157 | 145 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 165 | 142 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.45 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1353.99 | 1355.87 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 0 | 0 | 4 | 0 | 4 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 98 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2356.44 | 2648.87 | 3058.53 | 2949.53 | 2851.74 | 2742.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 158 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 8 | 0 | 180.02 | 0 | 180.02 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 243.8 | 386 | 638.42 | 422 | 638.42 | 422
System Total |  |  |  |  | 27566.2 | 28535.742 | 13617.61 | 15675.57 | 22457.38 | 21978.76 | 18884.57 | 18570.95
Forecast Scenario (23-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14390 |  | 0 |  | 14390
|  |  |  | 1:00 | 13720 |  | 0 |  | 13720
|  |  |  | 2:00 | 13340 |  | 0 |  | 13340
|  |  |  | 3:00 | 13000 |  | 0 |  | 13000
|  |  |  | 4:00 | 12600 |  | 0 |  | 12600
|  |  |  | 5:00 | 12370 |  | 0 |  | 12370
|  |  |  | 6:00 | 12010 |  | 0 |  | 12010
|  |  |  | 7:00 | 12280 |  | 0 |  | 12280
|  |  |  | 8:00 | 12150 |  | 0 |  | 12150
|  |  |  | 9:00 | 13100 |  | 0 |  | 13100
|  |  |  | 10:00 | 13100 |  | 0 |  | 13100
|  |  |  | 11:00 | 13500 |  | 0 |  | 13500
|  |  |  | 12:00 | 13900 |  | 0 |  | 13900
|  |  |  | 13:00 | 14600 |  | 0 |  | 14600
|  |  |  | 14:00 | 14240 |  | 0 |  | 14240
|  |  |  | 15:00 | 14480 |  | 0 |  | 14480
|  |  |  | 16:00 | 14300 |  | 0 |  | 14300
|  |  |  | 17:00 | 13800 |  | 0 |  | 13800
|  |  |  | 18:00 | 13800 |  | 0 |  | 13800
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15200 |  | 0 |  | 15200
|  |  |  | 19:30 | 15800 |  | 0 |  | 15800
|  |  |  | 20:00 | 15800 |  | 0 |  | 15800
|  |  |  | 21:00 | 15800 |  | 0 |  | 15800
|  |  |  | 22:00 | 15500 |  | 0 |  | 15500
|  |  |  | 23:00 | 15500 |  | 0 |  | 15500
Probable Maximum Temperature: |  |  | 33.60°C
Probable Maximum Demand at Day Peak: |  |  | 13900.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 330.69 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:19 hrs on 23-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-04-2025 | [28 empty] | Date: | 22-04-2025 | [28 empty] | Date: | 22-04-2025 | [28 empty] | Date: | 22-04-2025 | [28 empty] | Date: | 22-04-2025 | [16 empty] | Date: | 22-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 54 | 35 | 96 | 95 | 15 | 0 | 35 | 162 | 0 | 76 | 420 | 291 | 420 | 0 | 17 | 0 | 290 | 30 | 0 | 0 | 108 | 17 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 51 | 79 | 0 | 100 | 60 | 0 | 40 | 75 | 24 | 505 | 0 | 0 | 0 | 0 | 51 | 152 | 0 | 0 | 0 | 612 | 0 | 51 | 140 | 8 | 0 | 360 | 325 | 10 | 198 | 35 | 91 | 50 | 131 | 13 | 20 | 0 | 68 | 0 | 0 | 47 | 305 | 320 | 350 | 39 | 0 | 0 | 154 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 17 | 105 | 154 | 0 | 0 | 0 | 12 | 8094 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 405 | 51 | 1363 | 0 | 50 | 0 | 35 | 21 | 32 | 0 | 0 | 0 | 0 | 30 | 0 | 157 | 0 | 144 | 0 | 145 | 0 | 414 | 0 | 0 | 0 | 162 | 0 | 74 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 613 | 1022 | 0 | 6259 | 14353 | 81.37
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 54 | 17 | 88 | 48 | 0 | 0 | 35 | 126 | 0 | 55 | 420 | 291 | 420 | 0 | 17 | 0 | 280 | 26 | 0 | 0 | 90 | 17.6 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 51 | 48 | 0 | 60 | 20 | 0 | 40 | 34 | 23 | 504 | 0 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 612 | 0 | 51 | 137 | 8 | 0 | 359 | 325 | 10 | 198 | 35 | 90 | 50 | 121 | 10 | 20 | 0 | 66 | 0 | 0 | 47 | 300 | 320 | 386 | 38 | 0 | 0 | 151 | 6 | 0 | 83 | 30 | 0 | 17 | 174 | 17 | 48 | 97 | 0 | 0 | 0 | 8 | 7582.6 | 801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 51 | 1353 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 144 | 0 | 141 | 0 | 414 | 0 | 0 | 0 | 159 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 55 | 220 | 0 | 615 | 1024 | 0 | 5974 | 13556.6 | 81.37
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 54 | 17 | 78 | 48 | 0 | 0 | 35 | 54 | 0 | 16 | 420 | 289 | 420 | 0 | 17 | 0 | 254 | 0 | 0 | 0 | 90 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 60 | 0 | 0 | 40 | 34 | 25 | 500 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 612 | 0 | 51 | 100 | 8 | 0 | 360 | 325 | 10 | 198 | 35 | 91 | 50 | 124 | 9 | 20 | 0 | 66 | 0 | 0 | 47 | 300 | 320 | 352 | 38 | 0 | 0 | 144 | 6 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 7152 | 801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 51 | 1363 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 144 | 0 | 130 | 0 | 414 | 0 | 0 | 0 | 159 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 95 | 220 | 0 | 615 | 1024 | 0 | 6072 | 13224 | 81.36
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 77 | 48 | 0 | 0 | 35 | 54 | 0 | 16 | 420 | 293 | 420 | 0 | 17 | 0 | 268 | 0 | 0 | 0 | 90 | 18 | 18 | 0 | 410 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 60 | 0 | 0 | 40 | 34 | 25 | 502 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 555 | 0 | 51 | 100 | 8 | 0 | 358 | 325 | 10 | 203 | 35 | 68 | 50 | 108 | 9 | 20 | 0 | 64 | 0 | 0 | 47 | 295 | 320 | 350 | 38 | 0 | 0 | 130 | 6 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 7062 | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 51 | 1220 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 144 | 0 | 123 | 0 | 414 | 0 | 0 | 0 | 156 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 90 | 220 | 0 | 607 | 1030 | 0 | 5838 | 12900 | 81.36
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 43 | 17 | 78 | 48 | 0 | 0 | 17 | 17 | 0 | 16 | 420 | 300 | 420 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 18 | 18 | 0 | 410 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 25 | 503 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 504 | 0 | 51 | 50 | 8 | 0 | 359 | 325 | 10 | 203 | 35 | 68 | 50 | 94 | 9 | 20 | 0 | 66 | 0 | 0 | 47 | 305 | 320 | 363 | 38 | 0 | 0 | 134 | 6 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 6789 | 726 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 20 | 1218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 144 | 0 | 124 | 0 | 414 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 90 | 220 | 0 | 603 | 1030 | 0 | 5723 | 12512 | 81.35
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 78 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 306 | 420 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 17 | 18 | 18 | 0 | 410 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 508 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 8 | 0 | 356 | 325 | 10 | 203 | 32 | 34 | 50 | 92 | 9 | 20 | 0 | 66 | 0 | 0 | 0 | 305 | 320 | 490 | 38 | 0 | 0 | 134 | 6 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 6679 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 128 | 0 | 113 | 0 | 350 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 90 | 220 | 0 | 501 | 950 | 0 | 5621 | 12300 | 81.35
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 17 | 79 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 309 | 420 | 0 | 0 | 0 | 293 | 0 | 0 | 1 | 0 | 18 | 18 | 0 | 410 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 503 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 505 | 1 | 51 | 0 | 8 | 0 | 359 | 325 | 10 | 209 | 32 | 0 | 50 | 97 | 9 | 20 | 0 | 62 | 0 | 1 | 0 | 300 | 320 | 385 | 38 | 0 | 0 | 137 | 0 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0.52 | 12 | 6539.52 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.47 | 508 | 0 | 1210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 124 | 0 | 110 | 0 | 350 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 250 | 0 | 90 | 220 | 0 | 400 | 900 | 0 | 5408.48 | 11948 | 81.34
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 17 | 96 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 302 | 420 | 0 | 0 | 0 | 281 | 0 | 0 | 4 | 0 | 18 | 18 | 0 | 410 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 30 | 575 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 555 | 4 | 43 | 0 | 8 | 0 | 359 | 325 | 10 | 206 | 32 | 0 | 50 | 69 | 9 | 12 | 0 | 60 | 0 | 10 | 0 | 300 | 320 | 389 | 38 | 0 | 0 | 146 | 0 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 67 | 126 | 0 | 0 | 3.88 | 12 | 6706.88 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.64 | 552 | 0 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 170 | 0 | 125 | 0 | 110 | 0 | 350 | 0 | 0.39 | 0 | 163 | 0 | 0 | 1 | 0 | 0 | 0 | 0.9 | 3 | 0.12 | 0 | 280 | 8 | 90 | 220 | 0 | 360 | 888 | 0 | 5519.05 | 12225.93 | 81.34
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 96 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 306 | 420 | 0 | 0 | 0 | 315 | 0 | 0 | 9 | 0 | 17 | 0 | 0 | 410 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 14 | 526 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 565 | 9 | 43 | 0 | 8 | 0 | 350 | 325 | 10 | 198 | 31 | 0 | 50 | 60 | 9 | 20 | 0 | 60 | 0 | 21 | 0 | 305 | 320 | 385 | 37 | 0 | 0 | 132 | 0 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 67 | 125 | 0 | 0 | 20.96 | 12 | 6591.96 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.99 | 560 | 0 | 1301.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 170 | 0 | 124 | 0 | 119 | 0 | 300 | 0 | 1.08 | 0 | 157 | 0 | 0 | 2 | 0 | 0 | 0 | 0.8 | 15 | 0.18 | 0 | 280 | 9 | 90 | 220 | 0 | 294 | 897 | 0 | 5475.48 | 12067.44 | 81.33
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 3 | 17 | 110 | 48 | 30 | 0 | 12 | 90 | 0 | 0 | 380 | 283 | 350 | 0 | 0 | 0 | 270 | 0 | 0 | 15 | 17 | 17.5 | 19 | 0 | 410 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 22 | 0 | 3 | 40 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 612 | 14 | 43 | 6 | 8 | 0 | 355 | 325 | 5 | 198 | 33 | 11 | 50 | 64 | 10 | 20 | 0 | 62 | 0 | 38 | 0 | 300 | 320 | 351 | 39 | 0 | 0 | 147 | 0 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 67 | 125 | 0 | 0 | 4.57 | 12 | 6770.07 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.41 | 520 | 0 | 1308.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 170 | 0 | 133 | 0 | 145 | 0 | 350 | 0 | 0.86 | 0 | 163 | 0 | 35 | 12 | 0 | 0 | 0 | 0.9 | 48 | 0.23 | 0 | 280 | 7 | 90 | 220 | 0 | 295 | 931 | 0 | 5647.98 | 12418.05 | 81.33
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 131 | 48 | 30 | 0 | 35 | 90 | 0 | 10 | 340 | 299 | 400 | 0 | 0 | 0 | 295 | 0 | 0 | 17 | 17 | 17.5 | 19 | 0 | 410 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 0 | 2 | 40 | 0 | 2 | 503 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 612 | 18 | 43 | 50 | 8 | 0 | 355 | 325 | 5 | 202 | 33 | 17 | 50 | 63 | 9 | 20 | 0 | 66 | 0 | 44 | 0 | 295 | 320 | 383 | 39 | 0 | 0 | 153 | 0 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 67 | 124 | 0 | 0 | 36.19 | 12 | 7074.69 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.72 | 461 | 0 | 1310.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 170 | 0 | 157 | 0 | 170 | 0 | 414 | 0 | 1 | 0 | 163 | 0 | 35 | 6 | 0 | 0 | 0 | 4.1 | 41 | 0.64 | 0 | 280 | 6 | 90 | 220 | 0 | 296 | 889 | 0 | 5773.11 | 12847.8 | 81.32
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 131 | 48 | 58 | 0 | 35 | 130 | 0 | 46 | 400 | 300 | 400 | 0 | 0 | 0 | 280 | 0 | 0 | 18 | 52 | 17.5 | 19 | 0 | 410 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 24 | 0 | 3 | 40 | 0 | 2 | 503 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 612 | 18 | 43 | 63 | 8 | 0 | 343 | 330 | 5 | 205 | 33 | 24 | 50 | 67 | 0 | 20 | 34 | 68 | 0 | 39 | 0 | 300 | 320 | 368 | 39 | 0 | 0 | 156 | 0 | 0 | 82 | 30 | 0 | 17 | 174 | 16 | 66 | 122 | 0 | 1 | 38.5 | 12 | 7325 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.98 | 490 | 0 | 1324.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 170 | 0 | 160 | 0 | 170 | 0 | 414 | 0 | 0.86 | 0 | 163 | 0 | 35 | 0 | 0 | 0 | 0 | 6 | 42 | 0.31 | 0 | 280 | 9 | 90 | 220 | 0 | 296 | 887 | 0 | 5817.91 | 13142.91 | 81.32
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 131 | 64 | 262 | 5 | 35 | 162 | 0 | 51 | 400 | 295 | 370 | 0 | 17 | 0 | 302 | 0 | 0 | 27 | 52 | 17.5 | 19 | 0 | 350 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 60 | 0 | 4 | 40 | 10 | 3 | 566 | 0 | 0 | 0 | 0 | 9 | 146 | 0 | 0 | 0 | 612 | 12 | 43 | 86 | 8 | 0 | 320 | 330 | 5 | 206 | 33 | 48 | 50 | 87 | 0 | 20 | 68 | 80 | 0 | 37 | 0 | 295 | 320 | 399 | 39 | 0 | 0 | 143 | 0 | 0 | 82 | 30 | 0 | 17 | 174 | 42 | 67 | 122 | 0 | 1 | 31.23 | 12 | 7782.73 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.28 | 607 | 0 | 1353.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 167 | 0 | 157 | 0 | 165 | 0 | 414 | 0 | 1.45 | 0 | 161 | 0 | 35 | 36 | 0 | 0 | 0 | 3.8 | 8 | 0.36 | 0 | 230 | 8 | 90 | 220 | 0 | 238 | 857 | 0 | 5834.88 | 13617.61 | 81.31
13:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 54 | 17 | 131 | 63 | 278 | 52 | 35 | 162 | 0 | 64 | 420 | 294 | 440 | 0 | 17 | 0 | 290 | 0 | 0 | 23 | 52 | 17.5 | 19 | 0 | 400 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 60 | 30 | 4 | 40 | 17 | 0 | 566 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 612 | 17 | 43 | 120 | 8 | 0 | 333 | 330 | 5 | 210 | 32 | 0 | 40 | 140 | 0 | 20 | 65 | 78 | 0 | 38 | 16 | 300 | 320 | 385 | 39 | 0 | 0 | 156 | 0 | 0 | 82 | 30 | 0 | 17 | 175 | 54.3 | 66 | 122 | 0 | 2 | 45.65 | 12 | 8127.45 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.75 | 603 | 0 | 1361.55 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 160 | 0 | 150 | 0 | 151 | 0 | 414 | 0 | 2.03 | 0 | 162 | 0 | 35 | 15 | 26 | 0 | 0 | 3 | 24 | 0.68 | 0 | 270 | 8 | 90 | 220 | 0 | 199 | 937 | 0 | 5918.01 | 14045.46 | 81.31
14:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 54 | 17 | 131 | 62 | 278 | 55 | 35 | 162 | 0 | 67 | 420 | 295 | 440 | 0 | 17 | 0 | 275 | 0 | 0 | 13 | 90 | 17.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 60 | 30 | 4 | 40 | 18 | 5 | 566 | 0 | 0 | 0 | 0 | 22 | 146 | 0 | 0 | 0 | 612 | 14 | 43 | 115 | 8 | 0 | 340 | 330 | 5 | 207 | 32 | 0 | 40 | 171 | 9 | 20 | 58 | 76 | 0 | 36 | 28 | 310 | 320 | 349 | 39 | 0 | 0 | 153 | 8 | 0 | 82 | 30 | 0 | 17 | 175 | 51 | 66 | 121 | 0 | 1 | 25.31 | 12 | 8127.81 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.71 | 610 | 0 | 1362.51 | 0 | 0 | 0 | 55 | 0 | 0 | 10 | 0 | 0 | 73 | 0 | 0 | 156 | 0 | 148 | 0 | 144 | 0 | 414 | 0 | 3.42 | 0 | 164 | 0 | 70 | 4 | 60 | 0 | 0 | 3.1 | 13 | 0.38 | 0 | 307 | 10 | 90 | 220 | 0 | 235 | 987 | 0 | 6119.12 | 14246.93 | 81.3
15:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 54 | 17 | 133 | 62 | 278 | 55 | 35 | 162 | 0 | 67 | 420 | 294 | 440 | 0 | 35 | 0 | 256 | 0 | 0 | 18 | 144 | 17.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 60 | 30 | 3 | 40 | 49 | 2 | 424 | 0 | 0 | 0 | 0 | 51 | 144 | 0 | 0 | 0 | 612 | 10 | 43 | 105 | 8 | 0 | 345 | 330 | 5 | 212 | 29 | 0 | 40 | 161 | 9 | 20 | 65 | 76 | 7 | 39 | 44 | 305 | 320 | 351 | 38 | 0 | 0 | 152 | 8 | 0 | 82 | 30 | 0 | 17 | 172 | 50 | 67 | 121 | 0 | 1 | 33 | 12 | 8117.5 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.3 | 610 | 0 | 1356.91 | 0 | 0 | 0 | 111 | 0 | 0 | 70 | 0 | 0 | 57 | 0 | 0 | 154 | 0 | 145 | 0 | 142 | 0 | 414 | 0 | 3.56 | 0 | 163 | 0 | 115 | 5 | 108 | 0 | 0 | 2 | 18 | 0.22 | 0 | 307 | 10 | 90 | 220 | 0 | 299 | 997 | 0 | 6370.99 | 14488.49 | 81.3
16:00 | 32 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 54 | 17 | 144 | 62 | 295 | 55 | 35 | 162 | 0 | 67 | 420 | 283 | 440 | 0 | 35 | 0 | 258 | 0 | 0 | 14 | 108 | 17.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 75 | 30 | 2 | 40 | 34 | 2 | 421 | 0 | 0 | 0 | 0 | 34 | 147 | 0 | 0 | 0 | 612 | 7 | 43 | 107 | 8 | 0 | 345 | 330 | 5 | 180 | 31 | 0 | 40 | 145 | 23 | 20 | 66 | 78 | 24 | 14 | 43 | 290 | 320 | 352 | 38 | 0 | 0 | 137 | 8 | 0 | 81 | 30 | 0 | 17 | 171 | 49 | 56 | 128 | 0 | 1 | 8.43 | 12 | 7972.93 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.72 | 542 | 0 | 1364.4 | 0 | 0 | 0 | 70 | 0 | 49 | 35 | 0 | 0 | 44 | 0 | 0 | 154 | 0 | 145 | 0 | 141 | 0 | 414 | 0 | 1.75 | 0 | 163 | 0 | 70 | 12 | 70 | 0 | 0 | 1.2 | 83 | 0.15 | 0 | 292 | 9 | 90 | 220 | 0 | 296 | 995 | 0 | 6220.22 | 14193.15 | 81.29
17:00 | 50 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 54 | 17 | 115 | 62 | 295 | 55 | 35 | 162 | 0 | 67 | 420 | 286 | 440 | 0 | 17 | 0 | 259 | 0 | 0 | 6 | 108 | 17 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 75 | 30 | 1 | 40 | 34 | 5 | 422 | 0 | 0 | 0 | 0 | 34 | 146 | 0 | 0 | 0 | 612 | 3 | 43 | 113 | 8 | 0 | 340 | 330 | 5 | 182 | 29 | 2 | 40 | 146 | 36 | 20 | 68 | 76 | 25 | 9 | 44 | 305 | 320 | 350 | 38 | 0 | 0 | 127 | 8 | 0 | 81 | 30 | 0 | 17 | 173 | 0 | 45 | 140 | 0 | 0 | 18.84 | 4 | 7854.84 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.43 | 510 | 1 | 1360.51 | 0 | 0 | 0 | 35 | 0 | 56 | 35 | 0 | 0 | 7 | 0 | 0 | 154 | 0 | 145 | 0 | 140 | 0 | 414 | 0 | 0.08 | 0 | 154 | 0 | 35 | 2 | 34 | 0 | 0 | 0.3 | 34 | 0.75 | 0 | 250 | 7 | 90 | 220 | 0 | 296 | 997 | 0 | 5909.07 | 13763.91 | 81.29
18:00 | 50 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 54 | 17 | 113 | 95 | 295 | 45 | 35 | 162 | 0 | 67 | 370 | 292 | 400 | 0 | 35 | 0 | 265 | 0 | 0 | 0 | 90 | 17 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 9 | 17 | 0 | 0 | 100 | 30 | 0 | 40 | 34 | 6 | 421 | 0 | 0 | 0 | 0 | 34 | 146 | 0 | 0 | 0 | 554 | 0 | 43 | 125 | 8 | 0 | 300 | 330 | 5 | 197 | 32 | 49 | 50 | 145 | 37 | 20 | 44 | 78 | 25 | 1 | 44 | 295 | 320 | 385 | 39 | 0 | 0 | 128 | 8 | 0 | 82 | 30 | 0 | 17 | 173 | 12 | 104 | 150 | 0 | 0 | 1.98 | 8 | 7932.98 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.82 | 505 | 34 | 1324.52 | 0 | 0 | 0 | 35 | 0 | 56 | 35 | 0 | 0 | 0 | 12 | 0 | 156 | 0 | 145 | 0 | 140 | 0 | 330 | 0 | 0.03 | 0 | 157 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 6 | 0.16 | 0 | 200 | 8 | 90 | 220 | 0 | 297 | 951 | 0 | 5687.53 | 13620.51 | 81.29
19:00 | 98 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 115 | 144 | 295 | 48 | 35 | 162 | 0 | 87 | 400 | 300 | 500 | 0 | 55 | 0 | 313 | 0 | 0 | 0 | 102 | 17 | 20 | 0 | 450 | 6 | 15 | 0 | 0 | 3 | 34 | 37 | 0 | 100 | 80 | 0 | 40 | 34 | 3 | 421 | 72 | 0 | 0 | 0 | 34 | 144 | 0 | 0 | 0 | 612 | 0 | 43 | 125 | 8 | 0 | 345 | 330 | 6 | 198 | 33 | 72 | 50 | 171 | 38 | 20 | 62 | 40 | 26 | 0 | 45 | 310 | 320 | 385 | 39 | 0 | 0 | 149 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 20 | 105 | 150 | 0 | 0 | 0 | 12 | 8738 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 35 | 1368.27 | 0 | 0 | 0 | 52 | 5 | 92 | 90 | 15 | 17 | 0 | 30 | 0 | 156 | 0 | 145 | 0 | 141 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 296 | 1042 | 0 | 6339.27 | 15077.27 | 81.28
19:30 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 54 | 17 | 149 | 144 | 295 | 55 | 35 | 162 | 0 | 85 | 400 | 275 | 500 | 0 | 55 | 0 | 320 | 0 | 0 | 0 | 144 | 17 | 20 | 0 | 450 | 17 | 15 | 0 | 0 | 3 | 51 | 47 | 0 | 100 | 100 | 0 | 40 | 34 | 5 | 575 | 72 | 0 | 0 | 0 | 51 | 144 | 0 | 0 | 0 | 612 | 0 | 43 | 130 | 16 | 0 | 350 | 330 | 15 | 181 | 34 | 73 | 50 | 181 | 38 | 20 | 62 | 40 | 52.2 | 0 | 46 | 290 | 320 | 348 | 39 | 0 | 0 | 157 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 54.5 | 105 | 150 | 0 | 0 | 0 | 12 | 9057.7 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 35 | 1355.87 | 0 | 30 | 0 | 113 | 5 | 92 | 113 | 28 | 25 | 0 | 30 | 0 | 156 | 0 | 145 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 158 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 295 | 1200 | 0 | 6617.87 | 15675.57
20:00 | 76 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 20 | 149 | 145 | 295 | 40 | 35 | 162 | 0 | 91 | 400 | 280 | 420 | 0 | 55 | 0 | 321 | 0 | 0 | 0 | 144 | 16 | 20 | 0 | 450 | 17 | 15 | 0 | 0 | 8 | 67 | 47 | 0 | 100 | 100 | 0 | 40 | 37 | 14 | 575 | 17 | 0 | 0 | 0 | 51 | 144 | 0 | 0 | 0 | 612 | 0 | 43 | 127 | 16 | 0 | 353 | 330 | 14 | 180 | 34 | 72 | 50 | 181 | 38 | 20 | 80 | 40 | 52.2 | 0 | 39 | 295 | 320 | 348 | 39 | 0 | 0 | 154 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 54.5 | 105 | 148 | 0 | 0 | 0 | 12 | 8955.7 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 45 | 1360.34 | 0 | 49 | 0 | 113 | 25 | 92 | 113 | 37 | 43 | 0 | 30 | 0 | 156 | 0 | 146 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 158 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 297 | 1200 | 0 | 6698.34 | 15654.04 | 81.28
21:00 | 58 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 33 | 148 | 146 | 295 | 25 | 35 | 162 | 0 | 85 | 400 | 291 | 420 | 0 | 55 | 0 | 323 | 0 | 0 | 0 | 144 | 17 | 5 | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 51 | 47 | 0 | 100 | 100 | 0 | 40 | 56 | 27 | 555 | 0 | 0 | 0 | 4 | 77 | 144 | 0 | 0 | 0 | 613 | 0 | 43 | 125 | 26 | 0 | 356 | 330 | 17 | 180 | 34 | 72 | 50 | 182 | 38 | 20 | 80 | 38 | 52.2 | 0 | 42 | 300 | 320 | 350 | 39 | 0 | 0 | 149 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 54.5 | 106 | 153 | 0 | 0 | 0 | 12 | 8930.7 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 605 | 53 | 1364.35 | 0 | 49 | 0 | 113 | 26 | 92 | 70 | 37 | 43 | 0 | 30 | 0 | 157 | 0 | 148 | 0 | 142 | 0 | 414 | 0 | 0 | 0 | 157 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 296 | 1234 | 0 | 6730.35 | 15661.05 | 81.28
22:00 | 50 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 35 | 149 | 97 | 295 | 25 | 35 | 162 | 0 | 85 | 400 | 289 | 420 | 0 | 55 | 0 | 267 | 0 | 0 | 0 | 142 | 17 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 15 | 51 | 47 | 0 | 100 | 100 | 0 | 40 | 85 | 27 | 556 | 0 | 0 | 0 | 8 | 88 | 150 | 0 | 0 | 0 | 612 | 0 | 43 | 123 | 26 | 0 | 355 | 330 | 18 | 181 | 34 | 74 | 50 | 182 | 38 | 20 | 80 | 42 | 52.2 | 0 | 46 | 300 | 320 | 350 | 39 | 0 | 0 | 146 | 5 | 0 | 83 | 30 | 0 | 17 | 173 | 27 | 106 | 153 | 0 | 0 | 0 | 12 | 8771.2 | 844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 86 | 1359.26 | 0 | 49 | 0 | 113 | 26 | 92 | 70 | 35 | 52.2 | 0 | 30 | 0 | 158 | 0 | 148 | 0 | 143 | 0 | 414 | 0 | 0 | 0 | 159 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 90 | 220 | 0 | 297 | 1232 | 0 | 6781.46 | 15552.66 | 81.27
23:00 | 41 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 35 | 149 | 97 | 300 | 0 | 35 | 162 | 0 | 85 | 400 | 294 | 420 | 0 | 35 | 0 | 285 | 0 | 0 | 0 | 142 | 17.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 17 | 51 | 47 | 0 | 100 | 100 | 0 | 40 | 85 | 28 | 560 | 0 | 0 | 0 | 8 | 88 | 150 | 0 | 0 | 0 | 613 | 0 | 43 | 128 | 8 | 0 | 353 | 330 | 12 | 193 | 34 | 89 | 51 | 182 | 39 | 20 | 80 | 44 | 52.2 | 0 | 46 | 300 | 320 | 321 | 39 | 0 | 0 | 132 | 5 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 105 | 154 | 0 | 0 | 0 | 12 | 8642.7 | 843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 87 | 1364.04 | 0 | 49 | 0 | 113 | 22 | 92 | 35 | 35 | 52.2 | 0 | 30 | 0 | 155 | 0 | 147 | 0 | 146 | 0 | 414 | 0 | 0 | 0 | 163 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 85 | 220 | 0 | 297 | 1240 | 0 | 6755.24 | 15397.94 | 81.27
Total KWH | 482544 | 769920 | 415200 | 0 | 0 | 0 | 0 | 0 | 9007200 | 0 | 0 | 842040 | 508320 | 2826432 | 1679520 | 3684600 | 486126 | 713525 | 2666880 | 0 | 1161600 | 9234000 | 7064262 | 10192727 | 0 | 494545 | 0 | 6902094 | 38000 | 0 | 155347 | 1836000 | 420600 | 426240 | 0 | 10360909 | 30109 | 27600 | 0 | 0 | 282720 | 400915 | 340480 | 0 | 1378560 | 759360 | 29402 | 965880 | 733500 | 380640 | 12305454.55 | 65236 | 0 | 0 | 29113.2 | 710072 | 3509607 | 0 | 0 | 0 | 14127271 | 125010 | 951036 | 2112654 | 250909 | 0 | 8716400 | 7920000 | 217440 | 4837000 | 794520 | 1041600 | 1148700 | 3047040 | 418320 | 444660 | 899460 | 1474560 | 372586 | 393091 | 673488 | 7329000 | 7681000 | 9149000 | 909000 | 0 | 0 | 3432436 | 107232 | 0 | 1984320 | 719712 | 0 | 412000 | 4586950 | 520200 | 1659600 | 2947200 | 0 | 6400 | 245840 | 280080 | 186252994.75 | 21051636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 534240 | 13040000 | 557760 | 31770326.59 | 0 | 394284 | 0 | 1021632 | 117726 | 654976 | 589632 | 157249 | 227611 | 591100 | 193340 | 0 | 3914182 | 0 | 3656909 | 0 | 3582700 | 0 | 9425818 | 0 | 16920 | 0 | 3923000 | 0 | 1220552 | 105486 | 1114195 | 0 | 0 | 28055.64 | 395280 | 3576 | 0 | 6785000 | 167570 | 2113000 | 5407340 | 0 | 8765090 | 25042909 | 0 | 146569095.23 | 332822089.98

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13617.61 | MW | 12:00 Hr. | Energy Generated |  |  | 332.8221 |  | MKWHr.
| Day Peak Demand |  |  | 13682.61 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.771 |  | MKWHr.
| Evening Peak Generation |  |  | 15675.57 | MW | 19:30 Hr. | Energy Demand |  |  | 334.5931 |  | MKWHr.
| Evening Peak Demand |  |  | 15775.57 | MW | 19:30 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 11948 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1042.36 |  | MMCFD
| Maximum Generation of the Day |  |  | 15675.57 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.6555 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 53.646 | 0 | 18.5673 | 0 | 0 | 0.15535 | 0 | 0 | 72.3686 | Gas | 147.3951 | Gas | 518186216.1
| Chattogram Zone |  |  | 3.8902 | 26.4327 | 4.4749 | 0 | 0.96588 | 0.15441 | 0 | 0.28272 | 36.2009 | Coal | 83.9887 | Coal | 537451849.55
| Cumilla Zone |  |  | 25.2807 | 0 | 8.5651 | 0 | 0 | 0.39309 | 1.4746 | 0 | 35.7135 | HFO | 43.2634 | HFO | 808298443.394
| Mymensingh Zone |  |  | 0 | 0 | 5.4071 | 0 | 0 | 0.25224 | 0 | 0 | 5.6593 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.3107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.3107 | Hydro | 0.96588 | Hydro | 96588
| Khulna Zone |  |  | 0 | 13.04 | 0.55776 | 0 | 0 | 0.53424 | 21.0516 | 0 | 35.1836 | Solar | 2.6297 | Solar | 42292716.3704
| Barishal Zone |  |  | 7.6879 | 40.593 | 0 | 0 | 0 | 0.003576 | 0 | 0 | 48.2845 | Import | 54.2965 | Import | 304643992.2506
| Rajshahi Zone |  |  | 20.5796 | 0 | 3.3565 | 0 | 0 | 0.60802 | 31.7703 | 0 | 56.3144 | Wind | 0.28272 | Wind | 4139020.8
| Rangpur Zone |  |  | 0 | 3.923 | 2.3347 | 0 | 0 | 0.52882 | 0 | 0 | 6.7866
| Total |  |  | 147.3951 | 83.9887 | 43.2634 | 0 | 0.96588 | 2.6297 | 54.2965 | 0.28272 | 332.8221
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 518186216.1 |  | Hydro | 96588
|  |  |  | Coal | 537451849.55 |  | Solar | 42292716.3704
|  |  |  | HFO | 808298443.394 |  | Import | 304643992.2506
|  |  |  | HSD | 0 |  | Wind | 4139020.8
[5 empty] | Total: | 221,51,08,826 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.0516 | Peak Hr Flow | 867.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 32364909.14 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.7703 | Peak Hr Flow | 1355.87 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 536 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.4746 | Peak Hr Flow | 40.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 858 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.2965 | Peak Hr Flow | 2262.87 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 50 |  | 5755
|  |  |  | Chattogram |  | 0 |  | 1473
|  |  |  | Cumilla |  | 10 |  | 1410
|  |  |  | Mymensingh |  | 30 |  | 1020
|  |  |  | Sylhet |  | 0 |  | 585
|  |  |  | Khulna |  | 0 |  | 1852
|  |  |  | Barishal |  | 0 |  | 462
|  |  |  | Rajshahi |  | 6 |  | 1721
|  |  |  | Rangpur |  | 0 |  | 923
|  |  |  | Total |  | 96 |  | 15201
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Khulna 330 MW CCPP GT |  |  | 220
|  | 6 | Khulna 330 MW CCPP ST |  |  | 110
|  | 7 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 990 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1425.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 08:38 | BSRM-GPH 230 kV Ckt-2 Tripped from GPH 230/33kV end showing 86.1,86.2,21.1,21.2 relays.
| 08:07 | 18:12 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to Due to IDRNPP project
work.
| 10:34 | 16:51 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning work
| 10:45 | 16:51 | Aminbazar-Meghnaghat 400kV Ckt-1 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance Purpose
| 11:22 | 20:27 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-1 Scheduled S/D Due to Tree cutting
and aviation light setting on Parbatipur Ckt-01
| 11:23 | 20:28 | Bogura 400/230kV S/S Bogura - Parbotipur 230 kV Ckt-2 Scheduled S/D Due to Tree cutting
and aviation light setting on Parbatipur Ckt-02
| 11:50 | 13:55 | Munshiganj 132/33kV S/S Sinha Peoples Energy Limited (SPEL) 52.5 MW IPP Forced S/D Due
to Emergency Shutdown For Tree Trimming
| 13:27 | 16:16 | Haripur-Madanganj 132kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Work on
another side.
|  | 13:42 | Jamalpur-Mymensingh 132kV Ckt-1 is restored.
| 13:44 | 19:15 | Jamalpur-Mymensingh 132kV Ckt-2 Project Work S/D from Mymensingh 132/33kV end Due to
Lilo connection of ERS Tower at Muktagasa ( Jamalpur-2 ckt) and from Jamalpur 132/33kV
end Due to G2G work purpose.
| 14:10 | 16:26 | Chandpur 132/33kV S/S 115MW CPGL Power Plant Incomer (L5) Scheduled S/D Due to CPGL
maintenance work
| 15:08 | 17:54 | Juldah-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end. and from
Juldah 132/33kV end Due to ok
| 16:17 |  | Muktagacha 132/33kV S/S T-2(414T) HT Tripped showing Differential,ph-A,B relays.
| 16:17 |  | Muktagacha 132/33kV S/S T-2(414T) LT Tripped showing Differential,ph-A,B relays.
| 16:30 | 17:52 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to For jumper ing Borpa 33kv feeder load | [7 empty] | 40.0MW load
|  |  | side | [7 empty] | interrup.
|  | 17:52 | Sonargaon 132/33kV S/S Tr-2 LT is restored.
|  | 18:19 | Gopalganj 400/132kV S/S 400kV Bus-01 is restored.
| 18:20 | 19:32 | Kishoreganj 132/33kV S/S Tr-2 (414T) LT Tripped showing Micom relays Due to Due to PBD
33kv feeder fault.
| 18:20 | 19:30 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Tripped showing Micom relays Due to Due to PBD
33kv Feeder fault.
| 23:25 | 02:07 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to High Temperature maintenance | [7 empty] | 75.0MW load
interrup.
| 23:25 | 02:08 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to High temperature maintenance | [7 empty] | 75.0MW load
interrup.
| 02:58 | 03:32 | Fenchuganj-Sreemangal 132kV Ckt-2 Tripped from Sreemongol 132/33kV end showing Distance
Relay relays. and from Fenchuganj 230/132/33kV end showing REL670 relays Due to Bad
Weather
| 03:06 | 03:32 | Fenchuganj-Sreemangal 132kV Ckt-2 Forced S/D from Fenchuganj 230/132/33kV end Due to
After tripped
| 06:00 |  | Minimum Generation: 12675 MW.
| 07:11 |  | Chauddagram 132/33kV S/S 132 kv T-2 HT Scheduled S/D
| 07:26 |  | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D
| 07:32 |  | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D
| 07:35 |  | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 400 | 9007200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9234000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 275 | 7064262 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 486126 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 38000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 6902094 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 482544 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 842040 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 1679520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 713525 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 494545 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 420600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 426240 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 415200 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 3684600 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2826432 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 769920 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 85 | 1161600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2666880 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 155347 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 508320 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 10360909 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 500 | 10192727 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 144 | 1836000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3744 | 72368631
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 29113.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 125010 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 965880 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 144 | 3509607 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 710072 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 47 | 340480 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 51 | 400915 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1378560 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 380640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Machine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 29402 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 27600 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 733500 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 759360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 30109 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 72 | 65236 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 14127271 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 282720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12305454.55 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1866 | 36200929.75
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4837000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 350 | 8716400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 7920000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 794520 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 15 | 217440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 250909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 951036 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 2112654 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 46 | 673488 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1148700 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 181 | 3047040 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 1474560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 372586 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 444660 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 62 | 899460 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 418320 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 1041600 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 393091 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1661.2 | 35713464
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 150 | 2947200 | -
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1659600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 245840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 280080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 520200 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 321.5 | 5659320
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 909000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 157 | 3432436 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 719712 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1984320 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 4586950 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 412000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 107232 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7329000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 9149000 | Fgmo activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7681000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1465 | 36310650
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 867 | 21051636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 557760 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 534240 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 558 | 13040000 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1460 | 35183636
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 295 | 8765090 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 167570 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 90 | 2113000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 25042909 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5407340 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6785000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3576 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2123 | 48284485
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 30 | 394284 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 5 | 117726 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 28 | 157249 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 156 | 3914182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 145 | 3656909 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 142 | 3582700 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9425818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 193340 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 25 | 227611 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 654976 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1021632 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 589632 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 16920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1355.87 | 31770326.59 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 0 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 591100 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2648.87 | 56314405.59
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3923000 | machine problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1114195 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28055.64 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1220552 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 105486 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 395280 | -
Rangpur Area Total |  |  |  |  | 950 | 386 | 6786568.64
Eastern Grid Total |  |  |  |  | 16921.242 | 9057.7 | 186252994.75
Western Grid Total |  |  |  |  | 11614.5 | 6617.87 | 146569095.23
National Grid Total |  |  |  |  | 28535.742 | 15675.57 | 332822089.98
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10153.33 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4952.3 | MW
i) Dhaka area |  |  | 5704.53 |  | MW | i) Khulna area |  |  |  | 1852.4 | MW
ii) Chattogram area |  |  | 1473.3 |  | MW | ii) Barishal area |  |  |  | 461.5 | MW
iii) Cumilla area |  |  | 1400.5 |  | MW | iii) Rajshahi area |  |  |  | 1715.4 | MW
iv) Mymensingh area |  |  | 990 |  | MW | iv) Rangpur area |  |  |  | 923 | MW
v) Sylhet area |  |  | 585 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15105.63 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 91 | 19:30 | 133 | Patuakhali | 81.9 | 23:00
2 | AKSML | 111 | 01:00 | 68 | Jaldhaka | 66 | 18:30 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 38 | 15:00 | 69 | Jamalpur | 116 | 22:00 | 135 | Postogola | 55 | 12:00
4 | Agargaon | 128 | 15:00 | 70 | Jashore | 154 | 22:00 | 136 | Purbachal | 20 | 23:00
5 | Agrabad | 80 | 15:00 | 71 | Jhenaidah | 138 | 19:00 | 137 | Purbasadipur | 126 | 15:00
6 | Amnura | 50 | 21:00 | 72 | Joydebpur | 164 | 18:30 | 138 | Rahanpur | 34 | 00:00
7 | Ashuganj | 123.5 | 21:00 | 73 | Joypurhat | 71 | 19:30 | 139 | Rahim | 52 | 08:00
8 | BSRM | 204 | 02:00 | 74 | Juldah | 12 | 00:00 | 140 | Rajbari | 86 | 19:00
9 | Bagerhat | 92 | 21:00 | 75 | KSRM | 17 | 23:00 | 141 | Rajendrapur | 138 | 22:00
10 | Bajitpur | 55 | 18:30 | 76 | Kabirpur | 256 | 07:00 | 142 | Rajshahi | 142 | 20:00
11 | Bakulia | 95 | 19:30 | 77 | Kachua | 90 | 23:00 | 143 | Rajshahi-230 | 96 | 23:00
12 | Banani | 48 | 14:00 | 78 | Kallyanpur | 114 | 00:00 | 144 | Ramganj | 112 | 19:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 40 | 11:00 | 145 | Rampur | 41 | 23:00
14 | Barapukuria | 67 | 21:00 | 80 | Kamrangirchar | 70.6 | 17:00 | 146 | Rangamati | 17 | 19:00
15 | Barguna | 26 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 153 | 19:30
16 | Barishal | 110 | 22:00 | 82 | Kasba | 37 | 22:00 | 148 | Ruppur | 8 | 16:00
17 | Barishal-230 | 102 | 22:00 | 83 | Kazla | 117 | 16:00 | 149 | SSM | 10 | 06:00
18 | Baroaulia | 60 | 11:00 | 84 | Keranigonj | 83 | 19:00 | 150 | Saidpur | 116 | 19:00
19 | Baroirhat | 63 | 23:00 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 137 | 21:00
20 | Bashundhara | 207 | 14:00 | 86 | Khulna | 60 | 23:00 | 152 | Satmasjid | 114 | 16:00
21 | BashundharaCement | 9 | 10:00 | 87 | Khulshi | 184 | 20:00 | 153 | Savar | 232 | 12:00
22 | Beanibazar | 72 | 18:30 | 88 | Kishoreganj | 123 | 00:00 | 154 | SevenRings | 17.8 | 04:00
23 | Benapole | 71 | 22:00 | 89 | Kodda | 303 | 11:00 | 155 | ShahCement | 36 | 00:00
24 | Bhaluka | 162 | 19:30 | 90 | Kulaura | 46 | 19:30 | 156 | Shahjadpur | 94 | 19:00
25 | Bhandaria | 56 | 22:00 | 91 | Kurigram | 58 | 19:30 | 157 | Shahjibazar | 129 | 21:00
26 | Bhangura | 46 | 19:30 | 92 | Kushtia | 162 | 19:00 | 158 | Shahmirpur | 51 | 18:00
27 | Bheramara(GK) | 72 | 22:00 | 93 | Lalbag | 71 | 13:00 | 159 | Shariatpur | 88 | 22:00
28 | Bhulta | 255 | 23:00 | 94 | Lalmonirhat | 54 | 20:00 | 160 | Sherpur | 130 | 00:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | MI_Cement | 18.5 | 15:00 | 161 | Shikalbaha | 30 | 11:00
30 | Bogura | 190 | 19:30 | 96 | Madanganj | 42 | 13:00 | 162 | Shitalakhya | 86.2 | 12:00
31 | Borhanuddin | 90 | 22:00 | 97 | Madaripur | 113 | 22:00 | 163 | Sholosohor | 44 | 16:00
32 | Brahmanbaria | 135 | 20:00 | 98 | Madartek | 79.38 | 23:00 | 164 | Shyampur | 172 | 01:00
33 | Cantonment | 132 | 15:00 | 99 | Madunaghat | 55 | 19:00 | 165 | Siddhirganj | 130 | 12:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 73 | 19:30 | 166 | Sirajganj | 122 | 21:00
35 | Chandpur | 72 | 22:00 | 101 | Mahasthangarh | 80 | 23:00 | 167 | Sonargaon | 100 | 20:00
36 | Chandraghona | 39 | 19:00 | 102 | Manikganj | 151 | 20:00 | 168 | Sreemongol | 70 | 19:00
37 | Chapai | 78 | 23:00 | 103 | Maniknagar | 77 | 13:00 | 169 | Sreepur | 108 | 19:30
38 | Charsaidpur | 46 | 11:00 | 104 | Matarbari | 49 | 23:00 | 170 | Srinagar | 50.1 | 22:00
39 | Chauddagram | 67 | 18:30 | 105 | Matuail | 68 | 16:00 | 171 | Sunamganj | 55 | 21:00
40 | Chhatak | 33 | 00:00 | 106 | Millgate | 101 | 15:00 | 172 | Sylhet | 45 | 22:00
41 | Chowmuhani | 233 | 22:00 | 107 | Mirpur | 148 | 19:00 | 173 | Sylhet-132 | 126 | 19:30
42 | Chuadanga | 122 | 22:00 | 108 | Mirsorai | 18 | 19:30 | 174 | TK | 33.8 | 22:00
43 | Coxsbazar | 131 | 19:00 | 109 | Mirzapur | 53 | 21:00 | 175 | Tangail | 212 | 19:30
44 | Cumilla(N) | 163 | 22:00 | 110 | Mithapukur | 64 | 18:00 | 176 | Thakurgaon | 110 | 19:30
45 | Cumilla(S) | 176 | 19:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 138 | 19:30
46 | Daudkandi | 156 | 21:00 | 112 | Mogbazar | 143.5 | 16:00 | 178 | Ullahpara | 42 | 19:00
47 | Dhaka | 66 | 13:00 | 113 | Mongla | 46 | 00:00 | 179 | Ullon | 50 | 19:30
48 | Dhamrai | 134 | 17:00 | 114 | Motijheel | 42 | 12:00 | 180 | Uttara | 95 | 15:00
49 | Dhanmondi | 140 | 15:00 | 115 | Muktagacha | 33 | 21:00 | 181 | UttaraNew | 52 | 19:30
50 | Dohazari | 98 | 19:00 | 116 | Munshiganj | 112 | 23:00 | 182 | Zigatola | 83 | 15:00
51 | Faridpur | 174 | 20:00 | 117 | Muradnagar | 29 | 19:00
52 | Fatullah | 113 | 15:00 | 118 | Mymensingh | 191 | 22:00
53 | Fenchuganj | 37 | 19:00 | 119 | Naogaon | 154 | 21:00
54 | Feni | 112 | 22:00 | 120 | Narail | 63 | 20:00
55 | GPH | 95 | 10:00 | 121 | Narinda | 84.5 | 13:00
56 | Ghatail | 86 | 22:00 | 122 | Narshingdi | 181 | 23:00
57 | Ghorashal | 20 | 19:30 | 123 | Natore | 178 | 21:00
58 | Ghorashal-230 | 93 | 23:00 | 124 | Nawabganj | 63.2 | 22:00
59 | Goalpara | 40 | 22:00 | 125 | Netrakona | 135 | 20:00
60 | Gollamari | 102 | 00:00 | 126 | New | 94.2 | 15:00
61 | Gopalganj | 115 | 22:00 | 127 | Niamatpur | 106 | 19:30
62 | Gulshan | 134 | 15:00 | 128 | Noapara | 48 | 19:30
63 | Halishahar | 72.5 | 14:00 | 129 | PHP | 6 | 12:00
64 | HaripurSBU | 190 | 12:00 | 130 | Pabna | 123 | 19:30
65 | Hasnabad | 99 | 21:00 | 131 | Palashbari | 114 | 19:30
66 | Hathazari | 76 | 20:00 | 132 | Panchagarh | 50 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14353 | 35 |  | 14389.58
1:00 | 13556.6 | 157 |  | 13720.6
2:00 | 13224 | 120 |  | 13349
3:00 | 12900 | 96 |  | 13000
4:00 | 12512 | 84 |  | 12600
5:00 | 12300 | 76 |  | 12379
6:00 | 11948 | 65 |  | 12015.93
7:00 | 12225.93 | 58 |  | 12286.54
8:00 | 12067.44 | 87 |  | 12158.44
9:00 | 12418.05 | 65 |  | 12486.05
10:00 | 12847.8 | 53 |  | 12902.8
11:00 | 13142.91 | 94 |  | 13240.91
12:00 | 13617.61 | 62 |  | 13682.61
13:00 | 14045.46 | 62 |  | 14110.46
14:00 | 14246.93 | 73 |  | 14322.93
15:00 | 14488.49 | 71 |  | 14562.49
16:00 | 14193.15 | 61 |  | 14257.15
17:00 | 13763.91 | 66 |  | 13832.91
18:00 | 13620.51 | 50 |  | 13672.51
19:00 | 15077.27 | 70 |  | 15150.27
19:30 | 15675.57 | 96 |  | 15775.57
20:00 | 15654.04 | 93 |  | 15751.04
21:00 | 15661.05 | 67 |  | 15731.05
22:00 | 15552.66 | 65 |  | 15620.66
23:00 | 15397.94 | 41 |  | 15440.94
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8094 | 6259 | 14353 | DAILY GENERATION CURVE
00:30 | 7838.3 | 6116.5 | 13954.8
01:00 | 7582.6 | 5974 | 13556.6 | 22-04-2025
01:30 | 7367.3 | 6023 | 13390.3
02:00 | 7152 | 6072 | 13224
02:30 | 7107 | 5955 | 13062
03:00 | 7062 | 5838 | 12900
03:30 | 6925.5 | 5780.5 | 12706
04:00 | 6789 | 5723 | 12512
04:30 | 6734 | 5672 | 12406
05:00 | 6679 | 5621 | 12300
05:30 | 6609.26 | 5514.74 | 12124
06:00 | 6539.52 | 5408.48 | 11948
06:30 | 6623.2 | 5463.765 | 12086.965
07:00 | 6706.88 | 5519.05 | 12225.93
07:30 | 6649.42 | 5497.265 | 12146.685
08:00 | 6591.96 | 5475.48 | 12067.44
08:30 | 6681.015 | 5561.73 | 12242.745
09:00 | 6770.07 | 5647.98 | 12418.05
09:30 | 6922.38 | 5710.545 | 12632.925
10:00 | 7074.69 | 5773.11 | 12847.8
10:30 | 7199.845 | 5795.51 | 12995.355
11:00 | 7325 | 5817.91 | 13142.91
11:30 | 7553.865 | 5826.395 | 13380.26
12:00 | 7782.73 | 5834.88 | 13617.61
12:30 | 7955.09 | 5876.445 | 13831.535
13:00 | 8127.45 | 5918.01 | 14045.46
13:30 | 8127.63 | 6018.565 | 14146.195
14:00 | 8127.81 | 6119.12 | 14246.93
14:30 | 8122.655 | 6245.055 | 14367.71
15:00 | 8117.5 | 6370.99 | 14488.49
15:30 | 8045.215 | 6295.605 | 14340.82
16:00 | 7972.93 | 6220.22 | 14193.15
16:30 | 7913.885 | 6064.645 | 13978.53
17:00 | 7854.84 | 5909.07 | 13763.91
17:30 | 7893.91 | 5798.3 | 13692.21
18:00 | 7932.98 | 5687.53 | 13620.51
18:30 | 8335.49 | 6013.4 | 14348.89
19:00 | 8738 | 6339.27 | 15077.27
19:30 | 9057.7 | 6617.87 | 15675.57
20:00 | 8955.7 | 6698.34 | 15654.04
20:30 | 8943.2 | 6714.345 | 15657.545 |  | Executive Engineer
21:00 | 8930.7 | 6730.35 | 15661.05 |  | Network Operation Division
21:30 | 8850.95 | 6755.905 | 15606.855
22:00 | 8771.2 | 6781.46 | 15552.66
22:30 | 8706.95 | 6768.35 | 15475.3
23:00 | 8642.7 | 6755.24 | 15397.94

## En-Curve
QF-LDC-12
Date | 22-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3643 | 2499 | 846 | 0 | 68 | 1363 | 40 | 3626 | 0 | 556 | 1712 | 0 | 0 | 0 | 35 | DAILY ENERGY CURVE
00:30 | 3644 | 2493.8 | 823.5 | 0 | 67 | 1358 | 40 | 3628.5 | 0 | 457.5 | 1442 | 0 | 0 | 0.5 | 96 | 22-04-2025
01:00 | 3645 | 2488.6 | 801 | 0 | 66 | 1353 | 40 | 3631 | 0 | 359 | 1172 | 0 | 0 | 1 | 157
01:30 | 3617 | 2460.3 | 801 | 0 | 66 | 1358 | 40 | 3659 | 0 | 318 | 1069 | 0 | 0 | 2 | 138.5 | Energy Generated | 332.8221 |  | MKWHr
02:00 | 3589 | 2432 | 801 | 0 | 66 | 1363 | 40 | 3687 | 0 | 277 | 966 | 0 | 0 | 3 | 120 | Energy not Served | 1.771 |  | MKWHr
02:30 | 3590 | 2429.5 | 763.5 | 0 | 65 | 1291.5 | 40 | 3675 | 0 | 277 | 928.5 | 0 | 0 | 2 | 108 | Total Energy Requirement | 334.5931 |  | MKWHr
03:00 | 3591 | 2427 | 726 | 0 | 64 | 1220 | 40 | 3663 | 0 | 277 | 891 | 0 | 0 | 1 | 96
03:30 | 3613.5 | 2437.5 | 726 | 0 | 65 | 1219 | 40 | 3637.5 | 0 | 216 | 750.5 | 0 | 0 | 1 | 90
04:00 | 3636 | 2448 | 726 | 0 | 66 | 1218 | 40 | 3612 | 0 | 155 | 610 | 0 | 0 | 1 | 84
04:30 | 3665.5 | 2453.5 | 820.5 | 0 | 66 | 1216 | 40 | 3521.5 | 0 | 122.5 | 498.5 | 0 | 0 | 2 | 80
05:00 | 3695 | 2459 | 915 | 0 | 66 | 1214 | 40 | 3431 | 0 | 90 | 387 | 0 | 0 | 3 | 76
05:30 | 3643.5 | 2456.5 | 915 | 0 | 64 | 1212 | 40 | 3328.5 | 2.5 | 81.5 | 373 | 0 | 0 | 7.5 | 70.5
06:00 | 3592 | 2454 | 915 | 0 | 62 | 1210 | 40 | 3226 | 5 | 73 | 359 | 0 | 0 | 12 | 65
06:30 | 3595 | 2451 | 914.5 | 0 | 61 | 1235 | 40 | 3299.5 | 28.465 | 73 | 377.5 | 0 | 0 | 12 | 61.5
07:00 | 3598 | 2448 | 914 | 0 | 60 | 1260 | 40 | 3373 | 51.93 | 73 | 396 | 0 | 0 | 12 | 58
07:30 | 3563.5 | 2412.5 | 886 | 0 | 60 | 1280.715 | 40 | 3326 | 104.97 | 73 | 391 | 0 | 0 | 9 | 72.5
08:00 | 3529 | 2377 | 858 | 0 | 60 | 1301.43 | 40 | 3279 | 158.01 | 73 | 386 | 0 | 0 | 6 | 87
08:30 | 3548.5 | 2335.75 | 861 | 0 | 61 | 1305.005 | 40 | 3290 | 184.49 | 107.5 | 500 | 0 | 0 | 9.5 | 76
09:00 | 3568 | 2294.5 | 864 | 0 | 62 | 1308.58 | 40 | 3301 | 210.97 | 142 | 614 | 0 | 0 | 13 | 65
09:30 | 3670 | 2307.5 | 887.5 | 0 | 64 | 1309.615 | 40 | 3252.5 | 264.31 | 142 | 680.5 | 0 | 0 | 15 | 59
10:00 | 3772 | 2320.5 | 911 | 0 | 66 | 1310.65 | 40 | 3204 | 317.65 | 142 | 747 | 0 | 0 | 17 | 53
10:30 | 3756.5 | 2356 | 911 | 0 | 67 | 1317.705 | 40 | 3217.5 | 316.65 | 159.5 | 831 | 0 | 0 | 22.5 | 73.5
11:00 | 3741 | 2391.5 | 911 | 0 | 68 | 1324.76 | 40 | 3231 | 315.65 | 177 | 915 | 0 | 0 | 28 | 94
11:30 | 3750.5 | 2335 | 911 | 0 | 74 | 1339.375 | 40 | 3251 | 324.385 | 185 | 1147.5 | 0 | 0 | 22.5 | 78
12:00 | 3760 | 2278.5 | 911 | 0 | 80 | 1353.99 | 40 | 3271 | 333.12 | 193 | 1380 | 0 | 0 | 17 | 62
12:30 | 3734.5 | 2355.5 | 913 | 0 | 79 | 1357.77 | 40 | 3310 | 333.115 | 200.5 | 1487.65 | 0 | 0 | 20.5 | 62
13:00 | 3709 | 2432.5 | 915 | 0 | 78 | 1361.55 | 40 | 3349 | 333.11 | 208 | 1595.3 | 0 | 0 | 24 | 62
13:30 | 3680.5 | 2454.5 | 914.5 | 0 | 77 | 1362.03 | 40 | 3415 | 294.515 | 210.5 | 1673.65 | 0 | 0 | 24 | 67.5
14:00 | 3652 | 2476.5 | 914 | 0 | 76 | 1362.51 | 40 | 3481 | 255.92 | 213 | 1752 | 0 | 0 | 24 | 73
14:30 | 3640.5 | 2471.5 | 914.5 | 0 | 76 | 1359.71 | 40 | 3446.5 | 252 | 248 | 1893.5 | 0 | 0 | 25.5 | 72
15:00 | 3629 | 2466.5 | 915 | 0 | 76 | 1356.91 | 40 | 3412 | 248.08 | 283 | 2035 | 0 | 0 | 27 | 71
15:30 | 3604 | 2445 | 915 | 0 | 77 | 1360.655 | 40 | 3366.5 | 240.165 | 289 | 1979.5 | 0 | 0 | 24 | 66
16:00 | 3579 | 2423.5 | 915 | 0 | 78 | 1364.4 | 40 | 3321 | 232.25 | 295 | 1924 | 0 | 0 | 21 | 61
16:30 | 3552 | 2427.75 | 915 | 0 | 77 | 1362.455 | 40 | 3281 | 165.325 | 299 | 1841.5 | 0 | 0 | 17.5 | 63.5
17:00 | 3525 | 2432 | 915 | 0 | 76 | 1360.51 | 40 | 3241 | 98.4 | 303 | 1759 | 0 | 0 | 14 | 66
17:30 | 3508 | 2387 | 914.5 | 0 | 77 | 1342.515 | 40 | 3163 | 55.195 | 342.5 | 1851 | 0 | 0 | 11.5 | 58
18:00 | 3491 | 2342 | 914 | 0 | 78 | 1324.52 | 40 | 3085 | 11.99 | 382 | 1943 | 0 | 0 | 9 | 50
18:30 | 3607.5 | 2445 | 891 | 0 | 59 | 1346.395 | 40 | 3240 | 5.995 | 481.5 | 2226.5 | 0 | 0 | 6 | 60
19:00 | 3724 | 2548 | 868 | 0 | 40 | 1368.27 | 40 | 3395 | 0 | 581 | 2510 | 0 | 0 | 3 | 70
19:30 | 3683 | 2530 | 867 | 0 | 40 | 1355.87 | 40 | 3705 | 0 | 694 | 2757.7 | 0 | 0 | 3 | 96
20:00 | 3688 | 2464 | 867 | 0 | 40 | 1360.34 | 40 | 3704 | 0 | 757 | 2725.7 | 0 | 0 | 8 | 93
20:30 | 3693 | 2475.5 | 855.5 | 0 | 39 | 1362.345 | 40 | 3735.5 | 0 | 753 | 2697.2 | 0 | 0 | 6.5 | 80
21:00 | 3698 | 2487 | 844 | 0 | 38 | 1364.35 | 40 | 3767 | 0 | 749 | 2668.7 | 0 | 0 | 5 | 67
21:30 | 3668 | 2475.5 | 844 | 0 | 40 | 1361.805 | 40 | 3774.5 | 0 | 724.5 | 2668.55 | 0 | 0 | 10 | 66
22:00 | 3638 | 2464 | 844 | 0 | 42 | 1359.26 | 40 | 3782 | 0 | 700 | 2668.4 | 0 | 0 | 15 | 65
22:30 | 3614 | 2448.75 | 843.5 | 0 | 43 | 1361.65 | 40 | 3791 | 0 | 685 | 2632.4 | 0 | 0 | 16 | 53
23:00 | 3590 | 2433.5 | 843 | 0 | 44 | 1364.04 | 40 | 3800 | 0 | 670 | 2596.4 | 0 | 0 | 17 | 41
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 03:00 | 379 | 15:00 | Payra | 413 | 08:00 | 407 | 21:00
Ashuganj | 401 | 2:00 | 383 | 10:00 | Rahanpur | 412 | 04:00 | 402 | 13:00
Bhulta | 395 | 03:00 | 381 | 12:00 | Rampal | 401 | 09:00 | 386 | 19:30
Bibiana | 388 | 19:30 | 382 | 18:30
BIPTC | 404 | 04:00 | 387 | 15:00
Bogura | 404 | 21:00 | 390 | 13:00
Gopalganj | 398 | 09:00 | 387 | 15:00
Kaliakoir | 364 | 18:00 | 355 | 10:00
Madunaghat | 397 | 00:00 | 389 | 13:00
Meghnaghat | 392 | 03:00 | 385 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 03:00 | 218 | 14:00 | Keranigonj | 224 | 03:00 | 217 | 11:00
AKSML | 231 | 09:00 | 221 | 12:00 | Khulna(S) | 230 | 09:00 | 216 | 20:00
Aminbazar | 227 | 06:00 | 218 | 14:00 | Madunaghat | 231 | 00:00 | 225 | 11:00
Ashuganj | 231 | 18:00 | 225 | 10:00 | Madunaghat-400 | 232 | 23:00 | 224 | 11:00
Ashuganj-400 | 231 | 18:00 | 225 | 10:00 | Maniknagar | 223 | 03:00 | 215 | 11:00
Baghabari | 233 | 04:00 | 225 | 12:00 | Meghnaghat | 231 | 01:00 | 223 | 11:00
Barapukuria | 223 | 21:00 | 212 | 13:00 | Meghnaghat-400 | 227 | 03:00 | 220 | 11:00
Barapukuria-230 | 223 | 21:00 | 212 | 13:00 | Mirsorai | 226 | 19:00 | 218 | 13:00
Barishal | 232 | 06:00 | 224 | 23:00 | Rajshahi | 233 | 03:00 | 219 | 13:00
Bheramara | 235 | 03:00 | 219 | 11:00 | Rampal | 230 | 09:00 | 216 | 19:30
Bhulta | 224 | 03:00 | 216 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 222 | 02:00 | 218 | 18:30 | Rampura | 224 | 03:00 | 214 | 11:00
BIPTC | 236 | 03:00 | 221 | 13:00 | Shikalbaha | 228 | 02:00 | 222 | 10:00
Bogura | 226 | 21:00 | 216 | 13:00 | Shyampur | 224 | 02:00 | 217 | 11:00
Bogura-400 | 226 | 21:00 | 217 | 13:00 | Siddhirganj | 224 | 00:00 | 218 | 10:00
Borhanuddin | 238 | 09:00 | 231 | 23:00 | Sirajgonj | 237 | 03:00 | 233 | 13:00
BSRM | 225 | 00:00 | 218 | 13:00 | Sreepur | 228 | 02:00 | 223 | 10:00
Cumilla(N) | 222 | 03:00 | 216 | 12:00 | Tongi | 227 | 17:00 | 216 | 11:00
Faridpur | 228 | 09:00 | 218 | 19:00
Fenchuganj | 226 | 09:00 | 221 | 10:00
Ghorashal | 230 | 00:00 | 225 | 01:00
Ghorashal-230 | 224 | 03:00 | 217 | 11:00
Gopalganj | 228 | 09:00 | 221 | 19:00
GPH | 244 | 15:00 | 231 | 12:00
Haripur | 225 | 03:00 | 217 | 11:00
Hasnabad | 224 | 01:00 | 217 | 11:00
Hathazari | 231 | 00:00 | 224 | 11:00
Ishurdi | 236 | 03:00 | 225 | 13:00
Jhenaidah | 229 | 09:00 | 215 | 00:00
Kaliakoir | 226 | 18:00 | 220 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 02:00 | 126 | 11:00 | Madartek | 135 | 04:00 | 126 | 11:00
Agargaon | 133 | 02:00 | 127 | 11:00 | Madunaghat | 132 | 00:00 | 128 | 11:00
Agrabad | 131 | 00:00 | 125 | 10:00 | Magura | 134 | 09:00 | 120 | 19:00
AKS | 130 | 03:00 | 124 | 12:00 | Mahasthangarh | 131 | 21:00 | 124 | 12:00
Aminbazar | 129 | 01:00 | 122 | 12:00 | Manikganj | 125 | 20:00 | 119 | 11:00
Amnura | 138 | 21:00 | 125 | 13:00 | Maniknagar | 131 | 02:00 | 123 | 11:00
Ashuganj | 136 | 07:00 | 134 | 11:00 | Matarbari | 121 | 00:00 | 110 | 19:00
Bagerhat | 132 | 18:00 | 118 | 00:00 | Matuail | 130 | 04:00 | 124 | 11:00
Bajitpur | 133 | 17:00 | 127 | 12:00 | Millgate | 128 | 01:00 | 122 | 10:00
Bakulia | 133 | 00:00 | 127 | 12:00 | Mirpur | 126 | 00:00 | 121 | 12:00
Banani | 135 | 02:00 | 125 | 12:00 | Mirzapur | 127 | 18:00 | 121 | 14:00
Bangabhaban | 131 | 03:00 | 124 | 11:00 | Mithapukur | 133 | 21:00 | 124 | 13:00
Barapukuria | 136 | 21:00 | 128 | 12:00 | MI_Cement | 130 | 01:00 | 125 | 11:00
Barguna | 134 | 07:00 | 129 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 06:00 | 123 | 23:00 | Mogbazar | 135 | 00:00 | 125 | 11:00
Barishal-230 | 130 | 06:00 | 123 | 19:30 | Mongla | 133 | 18:00 | 119 | 00:00
Baroaulia | 133 | 03:00 | 125 | 10:00 | Motijheel | 131 | 03:00 | 124 | 11:00
Baroirhat | 125 | 18:00 | 118 | 10:00 | Muktagacha | 130 | 08:00 | 120 | 18:30
Bashundhara | 136 | 03:00 | 120 | 10:00 | Munshiganj | 130 | 18:00 | 124 | 11:00
BashundharaCement | 130 | 18:00 | 124 | 11:00 | Muradnagar | 127 | 18:00 | 121 | 11:00
Beanibazar | 132 | 10:00 | 125 | 18:30 | Mymensingh | 131 | 00:00 | 119 | 13:00
Benapole | 130 | 09:00 | 118 | 00:00 | Naogaon | 127 | 21:00 | 120 | 13:00
Bhaluka | 134 | 17:00 | 123 | 08:00 | Narail | 135 | 09:00 | 119 | 19:30
Bhandaria | 126 | 09:00 | 112 | 22:00 | Narinda | 131 | 02:00 | 123 | 11:00
Bhangura | 132 | 18:00 | 128 | 12:00 | Narshingdi | 128 | 01:00 | 117 | 21:00
Bheramara | 135 | 09:00 | 127 | 13:00 | Natore | 131 | 09:00 | 124 | 13:00
Bheramara(GK) | 134 | 09:00 | 127 | 13:00 | Nawabganj | 135 | 04:00 | 127 | 12:00
Bhulta | 124 | 05:00 | 120 | 07:00 | Netrakona | 128 | 16:00 | 117 | 13:00
Bog-Sherpur | 128 | 21:00 | 120 | 12:00 | New | 129 | 22:00 | 123 | 08:00
Bogura | 133 | 00:00 | 126 | 13:00 | Niamatpur | 135 | 09:00 | 131 | 13:00
Bogura-230 | 134 | 21:00 | 126 | 13:00 | Noapara | 133 | 09:00 | 121 | 19:00
Brahmanbaria | 129 | 06:00 | 125 | 23:00 | Pabna | 134 | 04:00 | 128 | 00:00
Cantonment | 134 | 03:00 | 126 | 13:00 | Palashbari | 129 | 15:00 | 118 | 13:00
Chandina | 129 | 18:00 | 124 | 10:00 | Panchagarh | 135 | 15:00 | 122 | 03:00
Chandpur | 131 | 18:00 | 119 | 11:00 | Patuakhali | 134 | 04:00 | 129 | 22:00
Chandraghona | 133 | 00:00 | 127 | 11:00 | Payra | 136 | 09:00 | 132 | 22:00
Chapai | 132 | 17:00 | 126 | 13:00 | PHP | 124 | 18:00 | 117 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 02:00 | 124 | 11:00 | Postogola | 132 | 02:00 | 127 | 11:00
Chauddagram | 125 | 18:00 | 117 | 10:00 | Purbachal | 136 | 02:00 | 126 | 11:00
Chhatak | 131 | 09:00 | 124 | 00:00 | Purbasadipur | 133 | 21:00 | 119 | 08:00
Chowmuhani | 122 | 18:00 | 112 | 23:00 | Rahanpur | 137 | 16:00 | 132 | 13:00
Chuadanga | 131 | 09:00 | 117 | 19:00 | Rahanpur-400 | 137 | 04:00 | 133 | 13:00
Coxsbazar | 118 | 00:00 | 111 | 19:00 | Rahim | 130 | 18:00 | 125 | 11:00
Cumilla(N) | 128 | 17:00 | 123 | 11:00 | Rajbari | 133 | 06:00 | 124 | 22:00
Cumilla(S) | 131 | 21:00 | 121 | 10:00 | Rajendrapur | 132 | 02:00 | 125 | 02:00
Daudkandi | 126 | 18:00 | 119 | 11:00 | Rajshahi | 132 | 09:00 | 124 | 13:00
Dhaka | 136 | 02:00 | 127 | 11:00 | Rajshahi-230 | 133 | 03:00 | 119 | 13:00
Dhamrai | 132 | 21:00 | 128 | 11:00 | Ramganj | 125 | 18:00 | 113 | 11:00
Dhanmondi | 136 | 04:00 | 126.5 | 13:00 | Rampur | 132 | 00:00 | 124 | 11:00
Dohazari | 130 | 00:00 | 122 | 19:00 | Rampura | 136 | 03:00 | 126 | 11:00
Faridpur | 135 | 09:00 | 129 | 21:00 | Rangamati | 132 | 00:00 | 126 | 11:00
Fatullah | 131 | 02:00 | 126 | 11:00 | Rangpur | 132 | 15:00 | 122 | 08:00
Fenchuganj | 135 | 04:00 | 133 | 00:00 | Ruppur | 137 | 09:00 | 130 | 13:00
Feni | 123 | 18:00 | 117 | 15:00 | Saidpur | 131 | 21:00 | 122 | 13:00
Ghatail | 126 | 18:00 | 120 | 18:30 | Satkhira | 132 | 18:00 | 119 | 00:00
Ghorashal | 135 | 00:00 | 132 | 10:00 | Satmasjid | 134 | 03:00 | 126 | 11:00
Goalpara | 136 | 18:00 | 125 | 00:00 | Savar | 128 | 01:00 | 121 | 12:00
Gollamari | 139 | 13:00 | 126 | 00:00 | SevenRings | 135 | 06:00 | 131 | 11:00
Gopalganj | 135 | 18:00 | 126 | 23:00 | ShahCement | 130 | 02:00 | 124 | 11:00
Gopalganj-400 | 136 | 08:00 | 120 | 05:00 | Shahjadpur | 140 | 04:00 | 132 | 13:00
Gulshan | 135 | 05:00 | 126 | 12:00 | Shahjibazar | 138 | 08:00 | 126 | 19:00
Halishahar | 132 | 01:00 | 125 | 16:00 | Shahmirpur | 134 | 00:00 | 128 | 12:00
Haripur | 130 | 01:00 | 125 | 11:00 | Shariatpur | 134 | 08:00 | 126 | 22:00
HaripurSBU | 130 | 00:00 | 125 | 11:00 | Sherpur | 137 | 15:00 | 124 | 01:00
Hasnabad | 132 | 04:00 | 127 | 11:00 | Shikalbaha | 123 | 00:00 | 117 | 12:00
Hathazari | 136 | 01:00 | 129 | 15:00 | Shikalbaha-230 | 133 | 02:00 | 123 | 17:00
Ishurdi | 138 | 03:00 | 132 | 13:00 | Shitalakhya | 130 | 01:00 | 125 | 11:00
Jaldhaka | 135 | 21:00 | 120 | 08:00 | Sholosohor | 132 | 00:00 | 127 | 11:00
Jamalpur | 139 | 08:00 | 127 | 01:00 | Shyampur | 130 | 22:00 | 126 | 13:00
Jashore | 131 | 09:00 | 120 | 00:00 | Shyampur-230 | 130 | 01:00 | 126 | 11:00
Jhenaidah | 133 | 09:00 | 121 | 19:00 | Siddhirganj | 130 | 01:00 | 126 | 11:00
Jhenaidah-230 | 135 | 09:00 | 123 | 00:00 | Sirajganj | 120 | 04:00 | 112 | 12:00
Joydebpur | 132 | 19:30 | 117 | 12:00 | Sonargaon | 132 | 04:00 | 124 | 10:00
Joypurhat | 123 | 18:00 | 116 | 13:00 | Sreemongol | 130 | 07:00 | 127 | 00:00
Juldah | 134 | 00:00 | 128 | 10:00 | Sreepur | 135 | 17:00 | 129 | 09:00
Kabirpur | 130 | 20:00 | 120 | 10:00 | Srinagar | 134 | 02:00 | 128 | 11:00
Kachua | 129 | 18:00 | 118 | 10:00 | SSM | 136 | 00:00 | 127 | 17:00
Kaliakoir | 134 | 01:00 | 126 | 14:00 | Sunamganj | 131 | 09:00 | 122 | 21:00
Kallyanpur | 128 | 01:00 | 122 | 12:00 | Sylhet | 132 | 07:00 | 127 | 19:00
Kalurghat | 132 | 00:00 | 127 | 11:00 | Sylhet-132 | 132 | 07:00 | 128 | 00:00
Kamrangirchar | 134 | 05:00 | 127 | 11:00 | Tangail | 125 | 18:00 | 120 | 18:30
Kaptai | 136 | 1:00 | 130 | 11:00 | Thakurgaon | 138 | 21:00 | 123 | 08:00
Kasba | 127 | 18:00 | 121 | 10:00 | TK | 134 | 00:00 | 128 | 11:00
Kazla | 131 | 02:00 | 123 | 13:00 | Tongi | 131 | 17:00 | 126 | 11:00
Keranigonj | 134 | 02:00 | 128 | 13:00 | Ullahpara | 122 | 03:00 | 111 | 13:00
Khagrachori | 131 | 00:00 | 125 | 12:00 | Ullon | 135 | 01:00 | 126 | 11:00
Khulna | 135 | 18:00 | 124 | 00:00 | Uttara | 127 | 02:00 | 121 | 11:00
Khulna(S) | 137 | 18:00 | 126 | 00:00 | UttaraNew | 127 | 00:00 | 120 | 12:00
Khulshi | 131 | 00:00 | 124 | 11:00 | Zigatola | 134 | 02:00 | 128 | 11:00
Kishoreganj | 132 | 04:00 | 126 | 00:00
Kodda | 133 | 21:00 | 120 | 14:00
KSRM | 134 | 20:00 | 127 | 10:00
Kulaura | 133 | 04:00 | 130 | 19:00
Kurigram | 132 | 15:00 | 122 | 08:00
Kushtia | 133 | 09:00 | 124 | 19:00
Lalbag | 134 | 03:00 | 127 | 14:00
Lalmonirhat | 132 | 21:00 | 121 | 18:00
Madanganj | 130 | 18:00 | 124 | 11:00
Madaripur | 133 | 05:00 | 129 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division