## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 23-04-2025 | [28 empty] | Date: | 23-04-2025 | [28 empty] | Date: | 23-04-2025 | [28 empty] | Date: | 23-04-2025 | [28 empty] | Date: | 23-04-2025 | [16 empty] | Date: | 23-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 40 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 35 | 149 | 97 | 300 | 0 | 35 | 162 | 0 | 68 | 400 | 279 | 420 | 0 | 35 | 0 | 266 | 0 | 0 | 0 | 142 | 17.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 14 | 51 | 47 | 0 | 100 | 88 | 0 | 40 | 85 | 28 | 555 | 0 | 0 | 0 | 8 | 88 | 150 | 0 | 0 | 0 | 612 | 0 | 43 | 123 | 8 | 0 | 360 | 330 | 5 | 205 | 34 | 90 | 51 | 182 | 12 | 20 | 80 | 40 | 52.2 | 0 | 47 | 305 | 320 | 287 | 39 | 0 | 0 | 131 | 5 | 0 | 83 | 30 | 0 | 17 | 174 | 17 | 48 | 105 | 0 | 0 | 0 | 12 | 8401.7 | 843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 87 | 1371.71 | 0 | 49 | 0 | 113 | 21 | 92 | 10 | 33 | 52.2 | 0 | 30 | 0 | 155 | 0 | 148 | 0 | 143 | 0 | 414 | 0 | 0 | 0 | 164 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 85 | 220 | 0 | 296 | 1240 | 0 | 6732.91 | 15134.61 | 81.27
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 93 | 64 | 45 | 0 | 35 | 162 | 0 | 68 | 400 | 293 | 420 | 0 | 35 | 0 | 278 | 0 | 0 | 0 | 108 | 17.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 8 | 51 | 47 | 0 | 100 | 88 | 0 | 40 | 85 | 31 | 556 | 0 | 0 | 0 | 0 | 88 | 150 | 0 | 0 | 0 | 612 | 0 | 43 | 120 | 8 | 0 | 356 | 330 | 6 | 204 | 34 | 90 | 51 | 181 | 8 | 20 | 80 | 40 | 52.2 | 0 | 47 | 300 | 320 | 299 | 38 | 0 | 0 | 129 | 5 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7950.7 | 788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 53 | 1368.78 | 0 | 49 | 0 | 113 | 0 | 0 | 0 | 33 | 0 | 0 | 30 | 0 | 155 | 0 | 148 | 0 | 139 | 0 | 414 | 0 | 0 | 0 | 166 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 85 | 220 | 0 | 297 | 1240 | 0 | 6463.78 | 14414.48 | 81.26
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 17 | 77 | 48 | 15 | 0 | 35 | 162 | 0 | 50 | 400 | 296 | 420 | 0 | 55 | 0 | 280 | 0 | 0 | 0 | 52 | 17.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 14 | 17 | 24 | 0 | 100 | 10 | 0 | 40 | 85 | 30 | 555 | 0 | 0 | 0 | 0 | 88 | 150 | 0 | 0 | 0 | 612 | 0 | 43 | 125 | 8 | 0 | 353 | 330 | 6 | 207 | 34 | 89 | 51 | 182 | 9 | 20 | 72 | 40 | 52.2 | 0 | 47 | 310 | 320 | 291 | 38 | 0 | 0 | 129 | 5 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 7693.7 | 788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 17 | 1351.81 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 147 | 0 | 137 | 0 | 414 | 0 | 0 | 0 | 163 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 297 | 1244 | 0 | 6223.81 | 13917.51 | 81.26
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 17 | 77 | 48 | 15 | 0 | 35 | 162 | 0 | 50 | 400 | 291 | 420 | 0 | 55 | 0 | 275 | 0 | 0 | 0 | 52 | 18 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 24 | 17 | 0 | 0 | 100 | 10 | 0 | 40 | 85 | 31 | 556 | 0 | 0 | 0 | 0 | 87 | 150 | 0 | 0 | 0 | 612 | 0 | 43 | 130 | 8 | 0 | 357 | 330 | 6 | 208 | 34 | 91 | 51 | 155 | 9 | 12 | 63 | 40 | 8 | 0 | 0 | 300 | 320 | 296 | 37 | 0 | 0 | 127 | 5 | 0 | 83 | 30 | 0 | 17 | 172 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 7532 | 788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 17 | 1357.17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 147 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 164 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 297 | 1244 | 0 | 6093.17 | 13625.17 | 81.26
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 17 | 77 | 48 | 0 | 0 | 17 | 126 | 0 | 16 | 400 | 292 | 420 | 0 | 17 | 0 | 273 | 0 | 0 | 0 | 52 | 18 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 0 | 42 | 10 | 0 | 40 | 85 | 31 | 556 | 0 | 0 | 0 | 0 | 88 | 151 | 0 | 0 | 0 | 612 | 0 | 43 | 130 | 8 | 0 | 357 | 330 | 6 | 213 | 34 | 89 | 50 | 155 | 9 | 12 | 63 | 36 | 8 | 0 | 0 | 310 | 320 | 287 | 37 | 0 | 0 | 130 | 5 | 0 | 83 | 30 | 0 | 17 | 172 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 7336 | 787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1377.61 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 147 | 0 | 147 | 0 | 414 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 296 | 1244 | 0 | 6014.61 | 13350.61 | 81.25
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 77 | 48 | 0 | 0 | 17 | 126 | 0 | 16 | 400 | 297 | 420 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 52 | 19 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 20 | 17 | 0 | 0 | 20 | 0 | 0 | 40 | 51 | 31 | 557 | 0 | 0 | 0 | 0 | 51 | 151 | 0 | 0 | 0 | 612 | 0 | 43 | 20 | 8 | 0 | 354 | 330 | 6 | 214 | 31 | 90 | 50 | 155 | 9 | 12 | 63 | 36 | 8 | 0 | 0 | 310 | 320 | 315 | 37 | 0 | 0 | 131 | 5 | 0 | 83 | 30 | 0 | 17 | 172 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 7162 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 1364.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 140 | 0 | 135 | 0 | 414 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 296 | 1244 | 0 | 5995.23 | 13157.23 | 81.25
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 17 | 77 | 48 | 0 | 0 | 17 | 126 | 0 | 16 | 400 | 304 | 420 | 0 | 0 | 0 | 305 | 0 | 0 | 1 | 52 | 18.8 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 10 | 0 | 0 | 40 | 17 | 0 | 558 | 0 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 612 | 1 | 43 | 20 | 8 | 0 | 347 | 330 | 5 | 214 | 34 | 90 | 50 | 120 | 8 | 12 | 63 | 34 | 8 | 0 | 0 | 305 | 320 | 343 | 37 | 0 | 0 | 135 | 5 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 49 | 96 | 0 | 0 | 0.39 | 12 | 7065.19 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.83 | 510 | 0 | 1226.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 133 | 0 | 127 | 0 | 350 | 0 | 0.05 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | 0 | 307 | 10 | 90 | 220 | 0 | 296 | 1120 | 0 | 5612.77 | 12677.96 | 81.25
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 17 | 17 | 82 | 48 | 0 | 0 | 17 | 126 | 0 | 16 | 400 | 292 | 420 | 0 | 0 | 0 | 285 | 0 | 0 | 3 | 52 | 17 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 10 | 0 | 1 | 40 | 17 | 18 | 556 | 0 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 612 | 5 | 43 | 20 | 8 | 0 | 352 | 330 | 5 | 215 | 34 | 90 | 50 | 120 | 9 | 12 | 63 | 26 | 8 | 14 | 0 | 310 | 320 | 289 | 37 | 0 | 0 | 141 | 0 | 0 | 83 | 30 | 0 | 17 | 172 | 0 | 68 | 124 | 0 | 0 | 4.23 | 12 | 7080.23 | 909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 510 | 0 | 1219.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 165 | 0 | 137 | 0 | 125 | 0 | 414 | 0 | 0.12 | 0 | 154 | 0 | 0 | 3 | 0 | 0 | 0 | 0.5 | 27 | 0.5 | 0 | 307 | 9 | 90 | 220 | 0 | 298 | 1115 | 0 | 5728.74 | 12808.97 | 81.24
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 17 | 17 | 95 | 48 | 0 | 0 | 17 | 126 | 0 | 16 | 400 | 304 | 420 | 0 | 0 | 0 | 300 | 0 | 0 | 3 | 35 | 18 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 10 | 0 | 1 | 40 | 17 | 2 | 555 | 0 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 600 | 10 | 43 | 0 | 8 | 0 | 345 | 325 | 5 | 210 | 34 | 90 | 50 | 34 | 9 | 11 | 17 | 34 | 8 | 17 | 0 | 305 | 320 | 320 | 37 | 0 | 0 | 130 | 0 | 0 | 83 | 30 | 0 | 17 | 172 | 0 | 68 | 124 | 0 | 0 | 8.62 | 12 | 6896.62 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.97 | 511 | 0 | 1219.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 165 | 0 | 145 | 0 | 142 | 0 | 350 | 0 | 1.33 | 0 | 115 | 0 | 30 | 9 | 28 | 0 | 0 | 1 | 47 | 0.13 | 0 | 307 | 7 | 90 | 220 | 0 | 297 | 1115 | 0 | 5717.35 | 12613.97 | 81.24
09:00 | 0 | 52 | 10 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 17 | 17 | 98 | 48 | 15 | 2 | 17 | 126 | 0 | 16 | 370 | 294 | 380 | 0 | 0 | 0 | 285 | 0 | 0 | 20 | 52 | 5 | 15 | 0 | 380 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 10 | 30 | 3 | 40 | 0 | 2 | 508 | 0 | 0 | 0 | 0 | 17 | 147 | 0 | 0 | 0 | 550 | 15 | 43 | 13 | 8 | 0 | 345 | 325 | 5 | 210 | 31 | 90 | 50 | 52 | 9 | 11 | 31 | 32 | 8 | 15 | 0 | 310 | 320 | 380 | 37 | 0 | 0 | 154 | 0 | 0 | 80 | 30 | 0 | 17 | 174 | 0 | 68 | 123 | 0 | 1 | 8.5 | 12 | 6922.5 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.57 | 510 | 0 | 1224.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 165 | 0 | 147 | 0 | 162 | 0 | 350 | 0 | 1.79 | 0 | 110 | 0 | 35 | 11 | 34 | 0 | 0 | 0.9 | 72 | 0.34 | 0 | 307 | 6 | 90 | 220 | 0 | 296 | 1109 | 0 | 5816.36 | 12738.86 | 81.24
10:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 17 | 119 | 62 | 45 | 30 | 35 | 126 | 0 | 20 | 370 | 301 | 380 | 0 | 25 | 0 | 288 | 0 | 0 | 24 | 52 | 17 | 15 | 0 | 380 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 10 | 30 | 2 | 40 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 17 | 146 | 0 | 0 | 0 | 500 | 11 | 43 | 50 | 8 | 0 | 340 | 330 | 5 | 207 | 31 | 90 | 50 | 63 | 8 | 11 | 34 | 30 | 8 | 29 | 0 | 310 | 320 | 395 | 39 | 0 | 0 | 155 | 0 | 0 | 80 | 30 | 0 | 17 | 174 | 0 | 68 | 122 | 0 | 2 | 18.82 | 12 | 6992.82 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.17 | 458 | 0 | 1287.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 165 | 0 | 154 | 0 | 164 | 0 | 414 | 0 | 3.97 | 0 | 156 | 0 | 35 | 11 | 0 | 0 | 0 | 2.8 | 145 | 0.46 | 0 | 250 | 6 | 90 | 220 | 0 | 298 | 1108 | 0 | 6022.97 | 13015.79 | 81.23
11:00 | 8 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 17 | 131 | 63 | 95 | 40 | 35 | 126 | 0 | 42 | 370 | 286 | 380 | 0 | 35 | 0 | 265 | 0 | 0 | 27 | 60 | 17 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 10 | 50 | 4 | 40 | 0 | 2 | 507 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 500 | 16 | 43 | 76 | 8 | 0 | 346 | 330 | 5 | 207 | 31 | 72 | 50 | 65 | 9 | 11 | 31 | 32 | 8 | 67 | 43 | 305 | 320 | 356 | 39 | 0 | 0 | 156 | 0 | 0 | 80 | 30 | 0 | 17 | 175 | 10 | 67 | 122 | 0 | 2 | 44.75 | 12 | 7373.75 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.54 | 457 | 0 | 1358.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0 | 165 | 0 | 150 | 0 | 159 | 0 | 414 | 0 | 5.82 | 0 | 157 | 0 | 35 | 28 | 0 | 0 | 0 | 4.3 | 100 | 0.3 | 0 | 250 | 6 | 90 | 220 | 0 | 297 | 1050 | 0 | 6038.24 | 13411.99 | 81.23
12:00 | 8 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 17 | 131 | 63 | 145 | 45 | 35 | 140 | 0 | 50 | 400 | 291 | 400 | 0 | 35 | 0 | 284 | 0 | 0 | 33 | 90 | 17 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 44 | 22 | 38 | 0 | 21 | 50 | 5 | 40 | 0 | 3 | 565 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 500 | 18 | 43 | 97 | 8 | 0 | 340 | 330 | 5 | 211 | 31 | 77 | 40 | 61 | 11 | 11 | 32 | 34 | 8 | 30 | 45 | 300 | 320 | 374 | 39 | 0 | 0 | 151 | 0 | 0 | 80 | 30 | 0 | 17 | 174 | 54 | 66 | 121 | 0 | 2 | 38.14 | 12 | 7715.14 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4 | 458 | 0 | 1363.75 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 164 | 0 | 147 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 35 | 32 | 24 | 0 | 0 | 6 | 120 | 0.36 | 0 | 250 | 6 | 90 | 220 | 0 | 298 | 1000 | 0 | 6068.51 | 13783.65 | 81.23
13:00 | 8 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 17 | 131 | 63 | 175 | 55 | 35 | 144 | 0 | 50 | 360 | 286 | 400 | 0 | 35 | 0 | 265 | 0 | 0 | 31 | 90 | 17 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 46 | 15 | 38 | 0 | 22 | 50 | 5 | 40 | 0 | 6 | 557 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 540 | 18 | 43 | 112 | 8 | 0 | 338 | 330 | 5 | 209 | 31 | 83 | 40 | 65 | 14 | 0 | 29 | 38 | 8 | 45 | 45 | 305 | 320 | 350 | 39 | 0 | 0 | 154 | 0 | 0 | 82 | 30 | 0 | 17 | 173 | 51 | 65 | 121 | 0 | 2 | 50.4 | 12 | 7748.4 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.61 | 458 | 0 | 1367.4 | 0 | 0 | 0 | 61 | 0 | 0 | 35 | 0 | 0 | 109 | 0 | 0 | 161 | 0 | 143 | 0 | 149 | 0 | 414 | 0 | 5.09 | 0 | 164 | 0 | 65 | 32 | 50 | 0 | 0 | 7.2 | 186 | 0.77 | 0 | 307 | 0 | 90 | 220 | 0 | 298 | 1002 | 0 | 6326.07 | 14074.47 | 81.22
14:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 17 | 131 | 63 | 175 | 55 | 35 | 144 | 0 | 50 | 360 | 293 | 400 | 0 | 35 | 0 | 270 | 0 | 0 | 28 | 90 | 18 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 49 | 34 | 38 | 0 | 10 | 50 | 3 | 40 | 0 | 5 | 556 | 17 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 525 | 14 | 43 | 115 | 8 | 0 | 338 | 330 | 5 | 206 | 31 | 75 | 40 | 63 | 9 | 0 | 31 | 38 | 8 | 52 | 45 | 305 | 320 | 360 | 39 | 0 | 0 | 150 | 0 | 0 | 81 | 30 | 0 | 17 | 173 | 23 | 66 | 121 | 0 | 2 | 40.4 | 12 | 7670.4 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3 | 459 | 0 | 1362 | 0 | 0 | 0 | 105 | 0 | 0 | 109 | 0 | 0 | 100 | 0 | 0 | 159 | 0 | 140 | 0 | 144 | 0 | 350 | 0 | 4.57 | 0 | 164 | 0 | 113 | 27 | 66 | 0 | 0 | 5.8 | 162 | 0.7 | 0 | 307 | 7 | 90 | 220 | 0 | 298 | 1025 | 0 | 6411.37 | 14081.77 | 81.22
15:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 131 | 62 | 201 | 55 | 35 | 144 | 0 | 50 | 360 | 296 | 400 | 0 | 55 | 0 | 270 | 0 | 0 | 22 | 104 | 18 | 13 | 0 | 420 | 0 | 0 | 0 | 0 | 33 | 34 | 41 | 0 | 10 | 75 | 2 | 40 | 0 | 2 | 556 | 53 | 0 | 0 | 0 | 4 | 145 | 0 | 0 | 0 | 500 | 12 | 43 | 110 | 8 | 0 | 339 | 330 | 5 | 210 | 31 | 72 | 40 | 77 | 9 | 0 | 49 | 40 | 8 | 45 | 44 | 305 | 320 | 366 | 36 | 0 | 0 | 151 | 0 | 0 | 77 | 30 | 0 | 17 | 173 | 18 | 66 | 121 | 0 | 2 | 27.58 | 12 | 7763.58 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.94 | 458 | 0 | 1365 | 0 | 0 | 0 | 113 | 0 | 12 | 113 | 6 | 0 | 75 | 0 | 0 | 157 | 0 | 140 | 0 | 145 | 0 | 414 | 0 | 3.57 | 0 | 114 | 0 | 114 | 21 | 105 | 0 | 0 | 4.9 | 127 | 0.47 | 0 | 307 | 0 | 90 | 220 | 0 | 297 | 1050 | 0 | 6434.88 | 14198.46 | 81.22
16:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 17 | 147 | 62 | 295 | 55 | 35 | 144 | 0 | 51 | 360 | 300 | 400 | 0 | 55 | 0 | 270 | 0 | 0 | 14 | 125 | 18 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 24 | 34 | 46 | 0 | 50 | 50 | 2 | 40 | 16 | 2 | 515 | 53 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 500 | 8 | 43 | 113 | 8 | 0 | 336 | 330 | 5 | 201 | 31 | 74 | 40 | 103 | 24 | 20 | 46 | 36 | 8 | 29 | 44 | 310 | 320 | 366 | 38 | 0 | 0 | 143 | 0 | 0 | 77 | 30 | 0 | 17 | 173 | 17 | 66 | 121 | 0 | 1 | 17.66 | 12 | 7882.66 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.53 | 455 | 0 | 1361 | 0 | 47 | 0 | 113 | 0 | 52 | 113 | 13 | 0 | 48 | 0 | 0 | 157 | 0 | 140 | 0 | 145 | 0 | 360 | 0 | 2.32 | 0 | 164 | 0 | 114 | 15 | 105 | 0 | 0 | 3.1 | 81 | 0.26 | 0 | 307 | 9 | 90 | 220 | 0 | 316 | 1050 | 0 | 6443.21 | 14325.87 | 81.21
17:00 | 32 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 17 | 148 | 62 | 295 | 55 | 35 | 144 | 0 | 56 | 360 | 291 | 400 | 0 | 55 | 0 | 261 | 0 | 0 | 6 | 125 | 17 | 21 | 0 | 420 | 0 | 0 | 0 | 0 | 16 | 34 | 46 | 0 | 100 | 50 | 1 | 40 | 17 | 5 | 545 | 53 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 450 | 2 | 43 | 123 | 8 | 0 | 339 | 330 | 5 | 203 | 31 | 81 | 40 | 104 | 35 | 20 | 46 | 38 | 8 | 11 | 44 | 295 | 320 | 349 | 38 | 0 | 0 | 128 | 0 | 0 | 55 | 30 | 0 | 17 | 173 | 22 | 66 | 128 | 0 | 0 | 8.8 | 12 | 7854.8 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.94 | 454 | 0 | 1354 | 0 | 46 | 0 | 113 | 0 | 78 | 50 | 33 | 0 | 20 | 0 | 0 | 159 | 0 | 145 | 0 | 148 | 0 | 360 | 0 | 0.9 | 0 | 167 | 0 | 50 | 6 | 111 | 0 | 0 | 1.3 | 38 | 0.15 | 0 | 260 | 9 | 90 | 220 | 0 | 300 | 1000 | 0 | 6145.29 | 14000.09 | 81.21
18:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 54 | 17 | 149 | 95 | 260 | 55 | 35 | 144 | 0 | 60 | 320 | 293 | 300 | 0 | 55 | 0 | 271 | 0 | 0 | 0 | 125 | 17 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 13 | 34 | 38 | 0 | 55 | 30 | 0 | 40 | 17 | 0 | 555 | 53 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 450 | 0 | 43 | 123 | 8 | 0 | 300 | 330 | 5 | 212 | 31 | 72 | 40 | 105 | 47 | 20 | 52 | 36 | 8 | 1 | 44 | 300 | 320 | 358 | 38 | 0 | 0 | 138 | 8 | 0 | 78 | 30 | 0 | 17 | 173 | 53 | 101 | 148 | 0 | 0 | 1.16 | 12 | 7826.16 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 457 | 14 | 1367 | 0 | 46 | 0 | 70 | 5 | 80 | 35 | 34 | 0 | 3 | 30 | 0 | 159 | 0 | 147 | 0 | 151 | 0 | 414 | 0 | 0.15 | 0 | 169 | 0 | 50 | 1 | 110 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 250 | 8 | 90 | 220 | 0 | 306 | 970 | 0 | 6110.77 | 13936.93 | 81.21
19:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 17 | 149 | 144 | 295 | 55 | 35 | 144 | 0 | 65 | 450 | 281 | 420 | 0 | 55 | 0 | 273 | 0 | 0 | 0 | 160 | 17.5 | 21 | 0 | 500 | 2 | 10 | 1 | 0 | 20 | 51 | 50 | 0 | 100 | 100 | 0 | 40 | 31 | 4 | 556 | 160 | 0 | 0 | 0 | 46 | 145 | 0 | 0 | 0 | 612 | 0 | 43 | 127 | 8 | 0 | 344 | 330 | 5 | 210 | 32 | 72 | 50 | 126 | 43 | 20 | 88 | 42 | 10 | 0 | 45 | 305 | 320 | 374 | 38 | 0 | 0 | 150 | 8 | 0 | 79 | 30 | 0 | 17 | 173 | 54 | 101 | 146 | 0 | 0 | 0 | 12 | 8988.5 | 893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 569 | 61 | 1354 | 0 | 49 | 0 | 90 | 18 | 81 | 100 | 34 | 42 | 0 | 30 | 0 | 159 | 0 | 147 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 168 | 0 | 115 | 0 | 113 | 15 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 321 | 1000 | 0 | 6550 | 15538.5 | 81.21
19:30 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 149 | 145 | 295 | 55 | 35 | 144 | 0 | 67 | 400 | 274 | 420 | 0 | 55 | 0 | 260 | 0 | 0 | 0 | 160 | 17.5 | 20 | 0 | 400 | 17 | 15 | 25 | 0 | 17 | 95 | 70 | 17 | 100 | 100 | 0 | 40 | 51 | 2 | 556 | 160 | 0 | 15 | 0 | 87 | 145 | 0 | 0 | 0 | 612 | 0 | 43 | 116 | 8 | 0 | 349 | 330 | 5 | 201 | 32 | 94 | 50 | 130 | 38 | 20 | 86 | 38 | 43 | 0 | 45 | 300 | 320 | 349 | 38 | 0 | 0 | 149 | 8 | 0 | 79 | 30 | 0 | 17 | 173 | 54.5 | 102 | 147 | 0 | 0 | 0 | 12 | 8998 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 70 | 1353 | 0 | 50 | 0 | 90 | 18 | 81 | 113 | 34 | 52.2 | 0 | 30 | 0 | 159 | 0 | 147 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 169 | 0 | 115 | 0 | 113 | 15 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 321 | 1130 | 0 | 6730.2 | 15728.2 | 81.21
20:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 19 | 148 | 145 | 295 | 55 | 35 | 144 | 0 | 67 | 400 | 286 | 350 | 0 | 55 | 0 | 258 | 0 | 0 | 0 | 160 | 17.5 | 20 | 0 | 400 | 17 | 15 | 19 | 0 | 15 | 102 | 70 | 17 | 100 | 100 | 0 | 40 | 92 | 9 | 557 | 160 | 0 | 15 | 0 | 88 | 147 | 0 | 0 | 0 | 612 | 0 | 43 | 120 | 8 | 0 | 351 | 330 | 5 | 196 | 33 | 80 | 50 | 136 | 37 | 20 | 83 | 42 | 40 | 0 | 46 | 295 | 320 | 376 | 39 | 0 | 0 | 140 | 8 | 0 | 80 | 30 | 0 | 17 | 173 | 54.5 | 95 | 148 | 0 | 0 | 0 | 12 | 9022 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 81 | 1356 | 0 | 49 | 0 | 113 | 24 | 81 | 113 | 36 | 52.2 | 0 | 30 | 0 | 159 | 0 | 147 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 167 | 0 | 115 | 0 | 113 | 15 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 365 | 1135 | 0 | 6818.2 | 15840.2 | 81.2
21:00 | 98 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 54 | 35 | 149 | 145 | 295 | 55 | 35 | 144 | 0 | 67 | 400 | 281 | 350 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 160 | 18 | 20 | 0 | 400 | 17 | 15 | 25 | 0 | 20 | 102 | 70 | 0 | 100 | 50 | 0 | 40 | 51 | 10 | 558 | 53 | 0 | 0 | 0 | 88 | 147 | 0 | 0 | 0 | 612 | 0 | 43 | 122 | 8 | 0 | 348 | 330 | 5 | 196 | 33 | 93 | 50 | 132 | 38 | 20 | 83 | 38 | 52.2 | 0 | 46 | 290 | 320 | 361 | 39 | 0 | 0 | 142 | 0 | 0 | 83 | 30 | 0 | 17 | 173 | 54.5 | 95 | 148 | 0 | 0 | 0 | 12 | 8924.7 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 85 | 1366 | 0 | 49 | 0 | 113 | 24 | 81 | 113 | 36 | 52.2 | 0 | 30 | 0 | 158 | 0 | 147 | 0 | 149 | 0 | 373 | 0 | 0 | 0 | 167 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 467 | 1150 | 0 | 6943.2 | 15867.9 | 81.19
22:00 | 50 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 35 | 149 | 112 | 295 | 55 | 35 | 144 | 0 | 67 | 400 | 290 | 350 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 160 | 17 | 15 | 0 | 400 | 17 | 15 | 25 | 0 | 25 | 68 | 70 | 0 | 100 | 10 | 0 | 40 | 51 | 15 | 556 | 53 | 0 | 0 | 0 | 88 | 147 | 0 | 0 | 0 | 613 | 0 | 43 | 132 | 8 | 0 | 349 | 330 | 5 | 192 | 33 | 106 | 50 | 144 | 38 | 20 | 84 | 44 | 52.2 | 0 | 47 | 305 | 320 | 371 | 39 | 0 | 0 | 154 | 0 | 0 | 83 | 30 | 0 | 17 | 173 | 23 | 95 | 151 | 0 | 0 | 0 | 12 | 8790.2 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 69 | 1369 | 0 | 47 | 0 | 113 | 19 | 84 | 113 | 36 | 52.2 | 0 | 30 | 0 | 158 | 0 | 150 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 166 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 465 | 1150 | 0 | 6971.2 | 15761.4 | 81.19
23:00 | 32 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 35 | 149 | 96 | 285 | 55 | 35 | 126 | 0 | 67 | 400 | 288 | 350 | 0 | 55 | 0 | 321 | 0 | 0 | 0 | 160 | 17 | 20 | 0 | 400 | 17 | 15 | 24 | 0 | 12 | 68 | 62 | 0 | 100 | 10 | 0 | 40 | 51 | 20 | 560 | 53 | 0 | 0 | 0 | 70 | 147 | 0 | 0 | 0 | 612 | 0 | 43 | 132 | 8 | 0 | 346 | 330 | 5 | 192 | 31 | 115 | 50 | 147 | 38 | 20 | 91 | 46 | 52.2 | 0 | 47 | 305 | 320 | 400 | 39 | 0 | 0 | 157 | 8 | 0 | 83 | 30 | 0 | 17 | 172 | 17 | 87 | 151 | 0 | 0 | 0 | 12 | 8688.2 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 69 | 1366 | 0 | 47 | 0 | 113 | 19 | 84 | 113 | 36 | 52.2 | 0 | 30 | 0 | 159 | 0 | 148 | 0 | 148 | 0 | 414 | 0 | 0 | 0 | 165 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 80 | 220 | 0 | 464 | 1150 | 0 | 6958.2 | 15646.4 | 81.19
Total KWH | 535392 | 771840 | 309600 | 0 | 0 | 0 | 0 | 0 | 8798400 | 0 | 0 | 518400 | 508680 | 2895264 | 1768320 | 3537316 | 790104 | 756827 | 3355200 | 0 | 1124160 | 9097500 | 7026124 | 9506818 | 0 | 879729 | 0 | 6884948 | 0 | 0 | 200380 | 2326800 | 412200 | 420480 | 0 | 10034545 | 90327 | 82800 | 120960 | 0 | 574080 | 760056 | 747216 | 28252 | 1241280 | 930240 | 25102 | 962700 | 1005309 | 323520 | 13098181.82 | 730982 | 0 | 31680 | 2052 | 1142472 | 3446342 | 0 | 0 | 0 | 13625453 | 127035 | 905300 | 2366909 | 217455 | 0 | 8630100 | 7960000 | 134400 | 5021000 | 787680 | 2094720 | 1130410 | 2783520 | 459480 | 330080 | 1405620 | 889920 | 521760 | 348555 | 732608 | 7398500 | 7680700 | 8720000 | 898000 | 0 | 0 | 3438082 | 73776 | 0 | 1891200 | 705216 | 0 | 409000 | 3573520 | 510120 | 1635600 | 2918400 | 0 | 12450 | 248160 | 296160 | 188683467.82 | 20929454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 582480 | 12923640 | 574080 | 32148971 | 0 | 482478 | 0 | 1629120 | 117504 | 726368 | 1110816 | 302450 | 277531 | 794470 | 255300 | 0 | 3891182 | 0 | 3699927 | 0 | 3702044 | 0 | 9554618 | 0 | 25920 | 0 | 3814000 | 0 | 1577217 | 192005 | 1596172 | 20500 | 0 | 34989.36 | 1103760 | 3765 | 0 | 7070000 | 208031 | 2132000 | 5392530 | 0 | 7820363 | 27335272 | 0 | 152028957.36 | 340712425.18

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 24-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-04-2025 | during | 24-04-2025 | during | 24-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 351 | 405 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 291 | 281 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 208.13 | 208.13 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 284 | 322 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 98 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 63 | 145 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 55 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 18 | 30 | 30 | 18 | 18 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 20 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 295 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 50 | 67 | 104 | 104 | 51 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 140 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 22 | 0 | 22 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 400 | 584 | 584 | 450 | 450 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 400 | 350 | 583 | 583 | 500 | 500 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 3055 | 3565 | 5193.9 | 5265.9 | 3961.26 | 4105.26
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 145 | 147 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 88 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 38 | 70 | 84 | 84 | 60 | 60 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 22 | 102 | 98 | 98 | 51 | 51 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 21 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 10 | 7 | 22 | 7 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 25 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 3.79 | 0 | 3.79 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 51 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 500 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 44 | 20 | 54 | 16 | 54 | 16 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 565 | 558 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1468 | 1958 | 2865.51 | 2825.72 | 2794.51 | 2754.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 211 | 196 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 348 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 330 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 31 | 33 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 18 | 18 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 97 | 122 | 150 | 150 | 130 | 130 | Machine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 45 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 50 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 61 | 132 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 24.5 | 24.5 | 24.5 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 32 | 83 | 105.3 | 105.3 | 105.3 | 105.3 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 11 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 77 | 93 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 30 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1414 | 1637.2 | 2407.29 | 2357.29 | 2198.35 | 2177.35
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 23-04-2025 | during | 24-04-2025 | during | 24-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 121 | 148 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 66 | 95 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 38.14 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 54 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 293.14 | 309.5 | 597.2 | 549 | 307.7 | 331.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 39 | 39 | 39 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 142 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20 | 17 | 17 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 374 | 361 | 365 | 365 | 337 | 337 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1485 | 1455 | 1556 | 1556 | 1463 | 1463
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 916 | 915 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 46 | 46 | 46 | 46 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 85 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 94.4 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 458 | 612 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1468.4 | 1612 | 3586.2 | 3516.2 | 2439.01 | 2369.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 298 | 467 | 295 | 295 | 290 | 290 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 11 | 10.12 | 10.12 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 90 | 90 | 130 | 130 | 95 | 95 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1000 | 1150 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.36 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1864.36 | 2245 | 2467.12 | 2466.12 | 2427 | 2426
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 49 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 24 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 36 | 40 | 40 | 40 | 40 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 164 | 158 | 214 | 214 | 170 | 170 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 147 | 147 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 154 | 149 | 220 | 220 | 170 | 170 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 373 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 81 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 4 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.05 | 0 | 5.05 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1363.75 | 1366 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 0 | 0 | 3 | 0 | 3 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 112 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2358.75 | 2691.2 | 3056.58 | 2948.53 | 2849.79 | 2741.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 167 | 160 | 160 | 160 | 160 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 24 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 120 | 0 | 173.39 | 0 | 173.39 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 377 | 395 | 631.79 | 422 | 631.79 | 422
System Total |  |  |  |  | 27566.2 | 28535.742 | 13783.65 | 15867.9 | 22361.59 | 21906.76 | 19072.41 | 18790.58
Forecast Scenario (24-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15220 |  | 0 |  | 15220
|  |  |  | 1:00 | 14500 |  | 0 |  | 14500
|  |  |  | 2:00 | 14000 |  | 0 |  | 14000
|  |  |  | 3:00 | 13740 |  | 0 |  | 13740
|  |  |  | 4:00 | 13460 |  | 0 |  | 13460
|  |  |  | 5:00 | 13270 |  | 0 |  | 13270
|  |  |  | 6:00 | 12780 |  | 0 |  | 12780
|  |  |  | 7:00 | 12880 |  | 0 |  | 12880
|  |  |  | 8:00 | 12640 |  | 0 |  | 12640
|  |  |  | 9:00 | 12780 |  | 0 |  | 12780
|  |  |  | 10:00 | 13060 |  | 0 |  | 13060
|  |  |  | 11:00 | 13450 |  | 0 |  | 13450
|  |  |  | 12:00 | 13830 |  | 0 |  | 13830
|  |  |  | 13:00 | 14120 |  | 0 |  | 14120
|  |  |  | 14:00 | 14130 |  | 0 |  | 14130
|  |  |  | 15:00 | 14280 |  | 0 |  | 14280
|  |  |  | 16:00 | 14500 |  | 0 |  | 14500
|  |  |  | 17:00 | 14150 |  | 0 |  | 14150
|  |  |  | 18:00 | 14000 |  | 0 |  | 14000
|  |  |  | 18:30 | 14900 |  | 0 |  | 14900
|  |  |  | 19:00 | 15800 |  | 0 |  | 15800
|  |  |  | 19:30 | 16000 |  | 0 |  | 16000
|  |  |  | 20:00 | 16020 |  | 0 |  | 16020
|  |  |  | 21:00 | 16050 |  | 0 |  | 16050
|  |  |  | 22:00 | 15760 |  | 0 |  | 15760
|  |  |  | 23:00 | 15500 |  | 0 |  | 15500
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 13830.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 16050.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16050.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 339.92 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:25 hrs on 24-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 23-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13783.65 | MW | 12:00 Hr. | Energy Generated |  |  | 340.7124 |  | MKWHr.
| Day Peak Demand |  |  | 13836.65 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.532 |  | MKWHr.
| Evening Peak Generation |  |  | 15867.9 | MW | 21:00 Hr. | Energy Demand |  |  | 343.2444 |  | MKWHr.
| Evening Peak Demand |  |  | 16050.9 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.6 |  | °C
| Minimum Generation of the Day |  |  | 12613.97 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1034.81 |  | MMCFD
| Maximum Generation of the Day |  |  | 15867.9 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.0344 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 52.181 | 0 | 20.0776 | 0 | 0 | 0.20038 | 0 | 0 | 72.459 | Gas | 144.4356 | Gas | 508307427.6
| Chattogram Zone |  |  | 3.7699 | 26.7236 | 6.9136 | 0 | 0.9627 | 0.15214 | 0 | 0.57408 | 39.096 | Coal | 85.6869 | Coal | 555720270.09
| Cumilla Zone |  |  | 25.1164 | 0 | 10.3646 | 0 | 0 | 0.34856 | 0.88992 | 0 | 36.7195 | HFO | 51.3652 | HFO | 960066058.24
| Mymensingh Zone |  |  | 0 | 0 | 5.3603 | 0 | 0 | 0.26061 | 0 | 0 | 5.6209 | HSD | 0.0205 | HSD | 1137545
| Sylhet Zone |  |  | 34.788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.788 | Hydro | 0.9627 | Hydro | 96270
| Khulna Zone |  |  | 0 | 12.9236 | 0.57408 | 0 | 0 | 0.58248 | 20.9295 | 0 | 35.0097 | Solar | 3.6991 | Solar | 61429687.8596
| Barishal Zone |  |  | 7.7326 | 42.2256 | 0 | 0 | 0 | 0.003765 | 0 | 0 | 49.962 | Import | 53.9683 | Import | 301547298.16
| Rajshahi Zone |  |  | 20.8478 | 0 | 4.9016 | 0 | 0 | 0.82039 | 32.149 | 0 | 58.7187 | Wind | 0.57408 | Wind | 8404531.2
| Rangpur Zone |  |  | 0 | 3.814 | 3.1734 | 0.0205 | 0 | 1.3308 | 0 | 0 | 8.3386
| Total |  |  | 144.4356 | 85.6869 | 51.3652 | 0.0205 | 0.9627 | 3.6991 | 53.9683 | 0.57408 | 340.7124
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 508307427.6 |  | Hydro | 96270
|  |  |  | Coal | 555720270.09 |  | Solar | 61429687.8596
|  |  |  | HFO | 960066058.24 |  | Import | 301547298.16
|  |  |  | HSD | 1137545 |  | Wind | 8404531.2
[5 empty] | Total: | 239,67,09,088 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9295 | Peak Hr Flow | 915.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 29641181.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.149 | Peak Hr Flow | 1366.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 648 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.88992 | Peak Hr Flow | 38.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 952 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.9683 | Peak Hr Flow | 2319.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 100 |  | 5872
|  |  |  | Chattogram |  | 0 |  | 1453
|  |  |  | Cumilla |  | 0 |  | 1446
|  |  |  | Mymensingh |  | 50 |  | 1250
|  |  |  | Sylhet |  | 0 |  | 428
|  |  |  | Khulna |  | 0 |  | 1891
|  |  |  | Barishal |  | 0 |  | 482
|  |  |  | Rajshahi |  | 25 |  | 1747
|  |  |  | Rangpur |  | 0 |  | 974
|  |  |  | Total |  | 175 |  | 15543
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:34 |  | Bheramara 230/132kV S/S Bus-A (132) Project Work S/D Due to ishurdi ckt 1&2 Reconducting
| 08:49 | 17:25 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to Project Work
| 09:24 | 09:52 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Over Current protection (Micom
P-142) relays Due to 33 kv incomer T1 CB trip of Over Current / Earth Fault for 33 kv
Amtoli feeder (BPBS-1) trip.
| 10:01 | 18:02 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning works. and from Meghnaghat 400/230kV end Due to Requested by LDC
| 10:33 | 17:46 | Chandina 132/33kV S/S TR-3 HT Project Work S/D Due to 33KV switchyard work br BREB
| 10:34 | 17:41 | Chandina 132/33kV S/S TR-2 HT Project Work S/D Due to 33 KV switchyard work br BREB
| 11:29 | 11:33 | Keranigonj 230/132/33kV S/S 33kV Bus Section-1 Tripped showing 51 Non directional
overcurrent relays.
|  | 12:05 | Chauddagram 132/33kV S/S 132 kv T-2 HT is restored.
| 12:46 | 17:00 | BSRM 230/33kV S/S GPH Ispat Ckt. -01 Forced S/D Due to Kite is hanged in span of
conductor 230kV GPH-BSRM Ckt-01.
| 12:48 |  | GPH 230/33kV S/S BSRM CKT-1 Forced S/D Due to Emergency shutdown
| 13:10 | 19:25 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to High temperature maintenance. | [7 empty] | 85.0MW load
interrup.
| 13:10 | 19:25 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to High temperature maintenance | [7 empty] | 85.0MW load
interrup.
| 13:40 | 14:27 | Thakurgaon 132/33kV S/S T-1(422T) LT Scheduled S/D Due to Red hot at Incoming CT Clamp | [7 empty] | 14.0MW load
interrup.
| 13:40 | 14:27 | Thakurgaon 132/33kV S/S T-1(422T) HT Scheduled S/D Due to Red hot at Incoming CT Clamp | [7 empty] | 14.0MW load
interrup.
|  | 14:31 | Khulna (C) S/S TR-1 425T HT is restored.
|  | 14:32 | Khulna (C) S/S TR-1 425T LT is restored.
| 15:05 |  | Chhatak 132/33kV S/S Bus A Forced S/D Due to Y phase PT loop out
| 15:52 | 15:56 | Shahjadpur 132/33kV S/S T-2(415T) LT Forced S/D Due to 33 kV bus PT problem solve by PBS
and Energy Audit
| 15:55 | 15:55 | Shahjadpur 132/33kV S/S T-2(415T) HT Forced S/D Due to 33 kV bus PT work by energy Audit
and PBS
| 16:30 | 16:34 | Shahjibazar 132/33kV S/S SPCL 86 MW Tripped showing MiCOM relays Due to O/C Trip
|  | 16:51 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 is restored.
|  | 16:51 | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-1 is restored.
| 19:06 | 20:10 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Forced S/D Due to from other end.
|  | 20:20 | Rangpur-Saidpur 132kV Ckt-2 is restored.
|  | 21:21 | Gopalganj 400/132kV S/S 400kV Bus-02 is restored.
| 05:50 |  | Tangail 132/33kV S/S Tr-2 LT Tripped showing REF-615 relays Due to 33kv kachuadanga | [7 empty] | 60.0MW load
|  |  | Feeder B phase out. | [7 empty] | interrup.
| 05:50 |  | Tangail 132/33kV S/S Tr-2 HT Tripped showing K-50 relays Due to 33 Kv kachuadanga fedder | [7 empty] | 60.0MW load
|  |  | B phase out | [7 empty] | interrup.
| 05:50 | 06:27 | Tangail 132/33kV S/S Tr-1 HT Tripped showing K-50 relays Due to 33 KV kachuadanga feeder | [7 empty] | 60.0MW load
|  |  | B phase out. | [7 empty] | interrup.
| 05:50 | 06:28 | Tangail 132/33kV S/S Tr-1 LT Tripped showing REF-615 relays Due to 33kv kachuadanga | [7 empty] | 60.0MW load
|  |  | feeder. | [7 empty] | interrup.
| 06:48 |  | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Shutdown taken by PBS
| 06:48 |  | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Shutdown taken by PBS
| 07:00 |  | Minimum Generation is 12966 MW
| 07:05 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to Shutdown taken by PBS
| 07:05 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to Shutdown taken by PBS
| 07:30 |  | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
| 07:32 |  | Chandraghona 132/33kV S/S TR-01(406T) HT Scheduled S/D Due to BPDB work. | [7 empty] | 18.0MW load
interrup.
| 07:32 |  | Chandraghona 132/33kV S/S TR-01(406T) LT Scheduled S/D | [7 empty] | 18.0MW load
interrup.
| 07:50 |  | Chauddagram 132/33kV S/S 132 kv T-1 HT Scheduled S/D Due to Red hot maintenance
| 07:50 |  | Chauddagram 132/33kV S/S 132 kv T-1 LT Scheduled S/D Due to Red hot maintenance
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 23-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 405 | 8798400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9097500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 281 | 7026124 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 790104 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 322 | 6884948 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 98 | 535392 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 518400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 1768320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 756827 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 879729 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 412200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 420480 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 309600 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 3537316 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 2895264 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 771840 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 1124160 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3355200 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 200380 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 508680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10034545 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 350 | 9506818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2326800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3565 | 72459027
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Under Maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 2052 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 127035 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 31680 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 962700 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 147 | 3446342 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 88 | 1142472 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 70 | 747216 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 760056 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1241280 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 10 | 323520 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 25 | 120960 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25102 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 82800 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 28252 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 51 | 1005309 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 930240 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 90327 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 730982 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13625453 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 20 | 574080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 558 | 13098181.82 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1958 | 39096039.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 196 | 5021000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 348 | 8630100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 7960000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 787680 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 134400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 905300 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 122 | 2366909 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 46 | 732608 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1130410 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 132 | 2783520 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 889920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 521760 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 330080 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 83 | 1405620 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 459480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 2094720 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 348555 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1637.2 | 36719517
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 148 | 2918400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 95 | 1635600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 248160 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 296160 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 510120 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 309.5 | 5620890
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 898000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3438082 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 705216 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1891200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 3573520 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 409000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 73776 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7398500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8720000 | Fgmo activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7680700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1455 | 34787994
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 20929454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 85 | 574080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 582480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 612 | 12923640 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1612 | 35009654
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 467 | 7820363 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 208031 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 90 | 2132000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1150 | 27335272 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5392530 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7070000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3765 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2245 | 49961961
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 49 | 482478 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 24 | 117504 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 36 | 302450 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 158 | 3891182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 147 | 3699927 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 149 | 3702044 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 373 | 9554618 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 255300 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 52.2 | 277531 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 81 | 726368 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1629120 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1110816 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25920 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1366 | 32148971 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 0 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 794470 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2691.2 | 58718699
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 167 | 3814000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 20500 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1596172 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 34989.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1577217 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 192005 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1103760 | -
Rangpur Area Total |  |  |  |  | 950 | 395 | 8338643.36
Eastern Grid Total |  |  |  |  | 16921.242 | 8924.7 | 188683467.82
Western Grid Total |  |  |  |  | 11614.5 | 6943.2 | 152028957.36
National Grid Total |  |  |  |  | 28535.742 | 15867.9 | 340712425.18
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 23-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10299.62 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5069 | MW
i) Dhaka area |  |  | 5772.12 |  | MW | i) Khulna area |  |  |  | 1891 | MW
ii) Chattogram area |  |  | 1453 |  | MW | ii) Barishal area |  |  |  | 482 | MW
iii) Cumilla area |  |  | 1446.5 |  | MW | iii) Rajshahi area |  |  |  | 1722 | MW
iv) Mymensingh area |  |  | 1200 |  | MW | iv) Rangpur area |  |  |  | 974 | MW
v) Sylhet area |  |  | 428 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15368.62 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 86 | 19:30 | 133 | Patuakhali | 80 | 21:00
2 | AKSML | 127 | 00:00 | 68 | Jaldhaka | 86 | 19:30 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 40 | 15:00 | 69 | Jamalpur | 119 | 19:00 | 135 | Postogola | 57 | 13:00
4 | Agargaon | 138 | 16:00 | 70 | Jashore | 160 | 19:00 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 84 | 18:30 | 71 | Jhenaidah | 143 | 19:30 | 137 | Purbasadipur | 132 | 19:30
6 | Amnura | 54 | 22:00 | 72 | Joydebpur | 158 | 12:00 | 138 | Rahanpur | 33 | 21:00
7 | Ashuganj | 100 | 00:00 | 73 | Joypurhat | 76 | 21:00 | 139 | Rahim | 54 | 11:00
8 | BSRM | 200 | 02:00 | 74 | Juldah | 12 | 00:00 | 140 | Rajbari | 90 | 19:00
9 | Bagerhat | 92 | 00:00 | 75 | KSRM | 11 | 10:00 | 141 | Rajendrapur | 148 | 19:30
10 | Bajitpur | 53 | 19:00 | 76 | Kabirpur | 277 | 08:00 | 142 | Rajshahi | 138 | 00:00
11 | Bakulia | 95 | 20:00 | 77 | Kachua | 93 | 22:00 | 143 | Rajshahi-230 | 99 | 23:00
12 | Banani | 50 | 13:00 | 78 | Kallyanpur | 123 | 18:00 | 144 | Ramganj | 122 | 23:00
13 | Bangabhaban | 18 | 11:00 | 79 | Kalurghat | 40 | 15:00 | 145 | Rampur | 42 | 23:00
14 | Barapukuria | 67 | 19:30 | 80 | Kamrangirchar | 73.1 | 13:00 | 146 | Rangamati | 17 | 19:00
15 | Barguna | 24 | 23:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 164 | 19:00
16 | Barishal | 112 | 19:00 | 82 | Kasba | 38 | 20:00 | 148 | Ruppur | 8.4 | 16:00
17 | Barishal-230 | 108 | 22:00 | 83 | Kazla | 122 | 19:30 | 149 | SSM | 12 | 01:00
18 | Baroaulia | 60 | 10:00 | 84 | Keranigonj | 84 | 20:00 | 150 | Saidpur | 118 | 19:30
19 | Baroirhat | 64 | 22:00 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 136 | 00:00
20 | Bashundhara | 207 | 19:00 | 86 | Khulna | 64 | 13:00 | 152 | Satmasjid | 123 | 16:00
21 | BashundharaCement | 15 | 12:00 | 87 | Khulshi | 183 | 14:00 | 153 | Savar | 230 | 18:30
22 | Beanibazar | 62 | 18:30 | 88 | Kishoreganj | 134 | 23:00 | 154 | SevenRings | 18.4 | 12:00
23 | Benapole | 71 | 19:30 | 89 | Kodda | 309 | 21:00 | 155 | ShahCement | 36 | 01:00
24 | Bhaluka | 183 | 19:00 | 90 | Kulaura | 41 | 00:00 | 156 | Shahjadpur | 97 | 21:00
25 | Bhandaria | 56 | 22:00 | 91 | Kurigram | 66 | 20:00 | 157 | Shahjibazar | 117 | 04:00
26 | Bhangura | 50 | 19:00 | 92 | Kushtia | 150 | 19:00 | 158 | Shahmirpur | 56 | 18:00
27 | Bheramara(GK) | 68 | 20:00 | 93 | Lalbag | 72 | 13:00 | 159 | Shariatpur | 90 | 22:00
28 | Bhulta | 234 | 22:00 | 94 | Lalmonirhat | 66 | 19:00 | 160 | Sherpur | 156 | 21:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | MI_Cement | 14.2 | 13:00 | 161 | Shikalbaha | 27 | 00:00
30 | Bogura | 184 | 00:00 | 96 | Madanganj | 48 | 18:30 | 162 | Shitalakhya | 89.8 | 16:00
31 | Borhanuddin | 93 | 22:00 | 97 | Madaripur | 120 | 23:00 | 163 | Sholosohor | 47 | 18:30
32 | Brahmanbaria | 130 | 23:00 | 98 | Madartek | 84.59 | 23:00 | 164 | Shyampur | 172 | 12:00
33 | Cantonment | 142 | 19:30 | 99 | Madunaghat | 52 | 19:30 | 165 | Siddhirganj | 132 | 18:30
34 | Chandina | 0 | 00:00 | 100 | Magura | 73 | 19:00 | 166 | Sirajganj | 128 | 19:00
35 | Chandpur | 79 | 22:00 | 101 | Mahasthangarh | 86 | 20:00 | 167 | Sonargaon | 120 | 23:00
36 | Chandraghona | 35 | 19:00 | 102 | Manikganj | 152 | 20:00 | 168 | Sreemongol | 68 | 00:00
37 | Chapai | 77 | 00:00 | 103 | Maniknagar | 90 | 17:00 | 169 | Sreepur | 109 | 19:30
38 | Charsaidpur | 80 | 11:00 | 104 | Matarbari | 49 | 21:00 | 170 | Srinagar | 50.7 | 22:00
39 | Chauddagram | 74 | 19:30 | 105 | Matuail | 66 | 15:00 | 171 | Sunamganj | 42 | 00:00
40 | Chhatak | 28 | 19:30 | 106 | Millgate | 102 | 15:00 | 172 | Sylhet | 43 | 00:00
41 | Chowmuhani | 227 | 20:00 | 107 | Mirpur | 160.5 | 19:00 | 173 | Sylhet-132 | 119 | 19:30
42 | Chuadanga | 125 | 22:00 | 108 | Mirsorai | 18 | 19:00 | 174 | TK | 33.5 | 19:30
43 | Coxsbazar | 132 | 20:00 | 109 | Mirzapur | 49 | 15:00 | 175 | Tangail | 188 | 19:00
44 | Cumilla(N) | 169 | 03:00 | 110 | Mithapukur | 60 | 19:30 | 176 | Thakurgaon | 107 | 19:30
45 | Cumilla(S) | 177 | 23:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 145 | 15:00
46 | Daudkandi | 161 | 21:00 | 112 | Mogbazar | 173.2 | 14:00 | 178 | Ullahpara | 46 | 19:00
47 | Dhaka | 70 | 13:00 | 113 | Mongla | 36 | 00:00 | 179 | Ullon | 49 | 00:00
48 | Dhamrai | 134 | 18:00 | 114 | Motijheel | 45 | 18:30 | 180 | Uttara | 101 | 16:00
49 | Dhanmondi | 171 | 12:00 | 115 | Muktagacha | 40 | 22:00 | 181 | UttaraNew | 55 | 15:00
50 | Dohazari | 101 | 21:00 | 116 | Munshiganj | 114 | 23:00 | 182 | Zigatola | 81 | 12:00
51 | Faridpur | 176 | 20:00 | 117 | Muradnagar | 29 | 19:30
52 | Fatullah | 112 | 17:00 | 118 | Mymensingh | 209 | 21:00
53 | Fenchuganj | 36 | 00:00 | 119 | Naogaon | 152 | 23:00
54 | Feni | 109 | 20:00 | 120 | Narail | 61 | 21:00
55 | GPH | 82 | 06:00 | 121 | Narinda | 84.5 | 13:00
56 | Ghatail | 86 | 19:00 | 122 | Narshingdi | 193 | 23:00
57 | Ghorashal | 17 | 18:30 | 123 | Natore | 172 | 20:00
58 | Ghorashal-230 | 92 | 19:00 | 124 | Nawabganj | 68.1 | 20:00
59 | Goalpara | 40 | 00:00 | 125 | Netrakona | 124 | 18:30
60 | Gollamari | 102 | 00:00 | 126 | New | 94 | 15:00
61 | Gopalganj | 116 | 19:30 | 127 | Niamatpur | 116 | 22:00
62 | Gulshan | 142 | 16:00 | 128 | Noapara | 51 | 19:30
63 | Halishahar | 71.5 | 09:00 | 129 | PHP | 5 | 13:00
64 | HaripurSBU | 188 | 21:00 | 130 | Pabna | 121 | 00:00
65 | Hasnabad | 101 | 22:00 | 131 | Palashbari | 125 | 19:30
66 | Hathazari | 85 | 20:00 | 132 | Panchagarh | 55 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 23-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15134.61 | 83 |  | 15221.35
1:00 | 14414.48 | 83 |  | 14501.48
2:00 | 13917.51 | 80 |  | 14001.51
3:00 | 13625.17 | 110 |  | 13740.17
4:00 | 13350.61 | 105 |  | 13460.61
5:00 | 13157.23 | 108 |  | 13270.23
6:00 | 12677.96 | 100 |  | 12782.46
7:00 | 12808.97 | 71 |  | 12882.97
8:00 | 12613.97 | 28 |  | 12642.97
9:00 | 12738.86 | 43 |  | 12783.86
10:00 | 13015.79 | 51 |  | 13068.79
11:00 | 13411.99 | 44 |  | 13457.99
12:00 | 13783.65 | 51 |  | 13836.65
13:00 | 14074.47 | 46 |  | 14122.47
14:00 | 14081.77 | 47 |  | 14130.77
15:00 | 14198.46 | 81 |  | 14283.46
16:00 | 14325.87 | 168 |  | 14501.87
17:00 | 14000.09 | 146 |  | 14153.09
18:00 | 13936.93 | 61 |  | 14000.93
19:00 | 15538.5 | 250 |  | 15799.5
19:30 | 15728.2 | 261 |  | 16001.2
20:00 | 15840.2 | 178 |  | 16026.2
21:00 | 15867.9 | 175 |  | 16050.9
22:00 | 15761.4 | 209 |  | 15979.4
23:00 | 15646.4 | 214 |  | 15870.4
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 23-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8401.7 | 6732.91 | 15134.61 | DAILY GENERATION CURVE
00:30 | 8176.2 | 6598.345 | 14774.545
01:00 | 7950.7 | 6463.78 | 14414.48 | 23-04-2025
01:30 | 7822.2 | 6343.795 | 14165.995
02:00 | 7693.7 | 6223.81 | 13917.51
02:30 | 7612.85 | 6158.49 | 13771.34
03:00 | 7532 | 6093.17 | 13625.17
03:30 | 7434 | 6053.89 | 13487.89
04:00 | 7336 | 6014.61 | 13350.61
04:30 | 7249 | 6004.92 | 13253.92
05:00 | 7162 | 5995.23 | 13157.23
05:30 | 7113.595 | 5804 | 12917.595
06:00 | 7065.19 | 5612.77 | 12677.96
06:30 | 7072.71 | 5670.755 | 12743.465
07:00 | 7080.23 | 5728.74 | 12808.97
07:30 | 6988.425 | 5723.045 | 12711.47
08:00 | 6896.62 | 5717.35 | 12613.97
08:30 | 6909.56 | 5766.855 | 12676.415
09:00 | 6922.5 | 5816.36 | 12738.86
09:30 | 6957.66 | 5919.665 | 12877.325
10:00 | 6992.82 | 6022.97 | 13015.79
10:30 | 7183.285 | 6030.605 | 13213.89
11:00 | 7373.75 | 6038.24 | 13411.99
11:30 | 7544.445 | 6053.375 | 13597.82
12:00 | 7715.14 | 6068.51 | 13783.65
12:30 | 7731.77 | 6197.29 | 13929.06
13:00 | 7748.4 | 6326.07 | 14074.47
13:30 | 7709.4 | 6368.72 | 14078.12
14:00 | 7670.4 | 6411.37 | 14081.77
14:30 | 7716.99 | 6423.125 | 14140.115
15:00 | 7763.58 | 6434.88 | 14198.46
15:30 | 7823.12 | 6439.045 | 14262.165
16:00 | 7882.66 | 6443.21 | 14325.87
16:30 | 7868.73 | 6294.25 | 14162.98
17:00 | 7854.8 | 6145.29 | 14000.09
17:30 | 7840.48 | 6128.03 | 13968.51
18:00 | 7826.16 | 6110.77 | 13936.93
18:30 | 8407.33 | 6330.385 | 14737.715
19:00 | 8988.5 | 6550 | 15538.5
19:30 | 8998 | 6730.2 | 15728.2
20:00 | 9022 | 6818.2 | 15840.2
20:30 | 8973.35 | 6880.7 | 15854.05 |  | Executive Engineer
21:00 | 8924.7 | 6943.2 | 15867.9 |  | Network Operation Division
21:30 | 8857.45 | 6957.2 | 15814.65
22:00 | 8790.2 | 6971.2 | 15761.4
22:30 | 8739.2 | 6964.7 | 15703.9
23:00 | 8688.2 | 6958.2 | 15646.4

## En-Curve
QF-LDC-12
Date | 23-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3560 | 2415.5 | 843 | 0 | 40 | 1371.71 | 40 | 3794 | 0 | 652 | 2404.4 | 0 | 0 | 14 | 83 | DAILY ENERGY CURVE
00:30 | 3560.5 | 2421 | 815.5 | 0 | 40 | 1370.245 | 40 | 3795.5 | 0 | 553 | 2167.8 | 0 | 0 | 11 | 83 | 23-04-2025
01:00 | 3561 | 2426.5 | 788 | 0 | 40 | 1368.78 | 40 | 3797 | 0 | 454 | 1931.2 | 0 | 0 | 8 | 83
01:30 | 3560.5 | 2432.5 | 788 | 0 | 40 | 1360.295 | 40 | 3797.5 | 0 | 333.5 | 1802.7 | 0 | 0 | 11 | 81.5 | Energy Generated | 340.7124 |  | MKWHr
02:00 | 3560 | 2438.5 | 788 | 0 | 40 | 1351.81 | 40 | 3798 | 0 | 213 | 1674.2 | 0 | 0 | 14 | 80 | Energy not Served | 2.532 |  | MKWHr
02:30 | 3559.5 | 2426.75 | 788 | 0 | 40 | 1354.49 | 40 | 3799.5 | 0 | 177.5 | 1566.6 | 0 | 0 | 19 | 95 | Total Energy Requirement | 343.2444 |  | MKWHr
03:00 | 3559 | 2415 | 788 | 0 | 40 | 1357.17 | 40 | 3801 | 0 | 142 | 1459 | 0 | 0 | 24 | 110
03:30 | 3566 | 2422 | 787.5 | 0 | 38 | 1367.39 | 40 | 3798.5 | 0 | 142 | 1308.5 | 0 | 0 | 18 | 107.5
04:00 | 3573 | 2429 | 787 | 0 | 36 | 1377.61 | 40 | 3796 | 0 | 142 | 1158 | 0 | 0 | 12 | 105
04:30 | 3582.5 | 2432.5 | 848 | 0 | 36 | 1370.92 | 40 | 3760 | 0 | 142 | 1026 | 0 | 0 | 16 | 106.5
05:00 | 3592 | 2436 | 909 | 0 | 36 | 1364.23 | 40 | 3724 | 0 | 142 | 894 | 0 | 0 | 20 | 108
05:30 | 3579.5 | 2422.9 | 909 | 0 | 35 | 1295.53 | 40 | 3638.5 | 2.165 | 133.5 | 837 | 0 | 0 | 24.5 | 104
06:00 | 3567 | 2409.8 | 909 | 0 | 34 | 1226.83 | 40 | 3553 | 4.33 | 125 | 780 | 0 | 0 | 29 | 100
06:30 | 3575 | 2414.4 | 909 | 0 | 30 | 1223.225 | 40 | 3552.5 | 43.84 | 125 | 806.5 | 0 | 0 | 24 | 85.5
07:00 | 3583 | 2419 | 909 | 0 | 26 | 1219.62 | 40 | 3552 | 83.35 | 125 | 833 | 0 | 0 | 19 | 71
07:30 | 3562.5 | 2405 | 887 | 0 | 30 | 1219.77 | 40 | 3526 | 116.7 | 116.5 | 792.5 | 0 | 0 | 15.5 | 49.5
08:00 | 3542 | 2391 | 865 | 0 | 34 | 1219.92 | 40 | 3500 | 150.05 | 108 | 752 | 0 | 0 | 12 | 28
08:30 | 3584 | 2337 | 864.5 | 0 | 33 | 1222.34 | 40 | 3445 | 199.575 | 135 | 796 | 0 | 0 | 20 | 35.5
09:00 | 3626 | 2283 | 864 | 0 | 32 | 1224.76 | 40 | 3390 | 249.1 | 162 | 840 | 0 | 0 | 28 | 43
09:30 | 3670 | 2293 | 889.5 | 0 | 31 | 1256.165 | 40 | 3260 | 319.16 | 172 | 910.5 | 0 | 0 | 36 | 47
10:00 | 3714 | 2303 | 915 | 0 | 30 | 1287.57 | 40 | 3130 | 389.22 | 182 | 981 | 0 | 0 | 44 | 51
10:30 | 3684.5 | 2313.5 | 915.5 | 0 | 31 | 1322.925 | 40 | 3174 | 431.965 | 208 | 1055.5 | 0 | 0 | 37 | 47.5
11:00 | 3655 | 2324 | 916 | 0 | 32 | 1358.28 | 40 | 3218 | 474.71 | 234 | 1130 | 0 | 0 | 30 | 44
11:30 | 3655 | 2347 | 916 | 0 | 33 | 1361.015 | 40 | 3224.5 | 482.805 | 280 | 1221.5 | 0 | 0 | 37 | 47.5
12:00 | 3655 | 2370 | 916 | 0 | 34 | 1363.75 | 40 | 3231 | 490.9 | 326 | 1313 | 0 | 0 | 44 | 51
12:30 | 3633.5 | 2338 | 916 | 0 | 36 | 1365.575 | 40 | 3278.5 | 533.985 | 322.5 | 1420 | 0 | 0 | 45 | 48.5
13:00 | 3612 | 2306 | 916 | 0 | 38 | 1367.4 | 40 | 3326 | 577.07 | 319 | 1527 | 0 | 0 | 46 | 46
13:30 | 3573.5 | 2321 | 916 | 0 | 38 | 1364.7 | 40 | 3330 | 546.92 | 307 | 1593.5 | 0 | 0 | 47.5 | 46.5
14:00 | 3535 | 2336 | 916 | 0 | 38 | 1362 | 40 | 3334 | 516.77 | 295 | 1660 | 0 | 0 | 49 | 47
14:30 | 3580 | 2327 | 916 | 0 | 39 | 1363.5 | 40 | 3308 | 463.115 | 311.5 | 1751 | 0 | 0 | 41 | 64
15:00 | 3625 | 2318 | 916 | 0 | 40 | 1365 | 40 | 3282 | 409.46 | 328 | 1842 | 0 | 0 | 33 | 81
15:30 | 3578 | 2337 | 915.5 | 0 | 38 | 1363 | 40 | 3294.5 | 339.165 | 388 | 1940.5 | 0 | 0 | 28.5 | 124.5
16:00 | 3531 | 2356 | 915 | 0 | 36 | 1361 | 40 | 3307 | 268.87 | 448 | 2039 | 0 | 0 | 24 | 168
16:30 | 3525 | 2326.5 | 915.5 | 0 | 37 | 1357.5 | 40 | 3241.5 | 189.98 | 470.5 | 2039.5 | 0 | 0 | 20 | 157
17:00 | 3519 | 2297 | 916 | 0 | 38 | 1354 | 40 | 3176 | 111.09 | 493 | 2040 | 0 | 0 | 16 | 146
17:30 | 3542 | 2213 | 915.5 | 0 | 37 | 1360.5 | 40 | 3166.5 | 63.51 | 550.5 | 2065.5 | 0 | 0 | 14.5 | 103.5
18:00 | 3565 | 2129 | 915 | 0 | 36 | 1367 | 40 | 3157 | 15.93 | 608 | 2091 | 0 | 0 | 13 | 61
18:30 | 3608 | 2335.75 | 904 | 0 | 39 | 1360.5 | 40 | 3345 | 7.965 | 673.5 | 2400 | 7.5 | 0 | 16.5 | 155.5
19:00 | 3651 | 2542.5 | 893 | 0 | 42 | 1354 | 40 | 3533 | 0 | 739 | 2709 | 15 | 0 | 20 | 250
19:30 | 3586 | 2376.5 | 867 | 0 | 38 | 1353 | 40 | 3707 | 0 | 805 | 2923.7 | 15 | 0 | 17 | 261
20:00 | 3643 | 2312.5 | 868 | 0 | 42 | 1356 | 40 | 3751 | 0 | 820 | 2977.7 | 15 | 0 | 15 | 178
20:30 | 3665.5 | 2306.75 | 891.5 | 0 | 40 | 1361 | 40 | 3812 | 0 | 820 | 2892.3 | 7.5 | 0 | 17.5 | 176.5
21:00 | 3688 | 2301 | 915 | 0 | 38 | 1366 | 40 | 3873 | 0 | 820 | 2806.9 | 0 | 0 | 20 | 175
21:30 | 3712 | 2318.5 | 915.5 | 0 | 41 | 1367.5 | 40 | 3872.5 | 0 | 785 | 2740.15 | 0 | 0 | 22.5 | 192
22:00 | 3736 | 2336 | 916 | 0 | 44 | 1369 | 40 | 3872 | 0 | 750 | 2673.4 | 0 | 0 | 25 | 209
22:30 | 3741 | 2345.5 | 915.5 | 0 | 45 | 1367.5 | 40 | 3875 | 0 | 721 | 2634.9 | 0 | 0 | 18.5 | 211.5
23:00 | 3746 | 2355 | 915 | 0 | 46 | 1366 | 40 | 3878 | 0 | 692 | 2596.4 | 0 | 0 | 12 | 214
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 23-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 06:00 | 378 | 13:00 | Payra | 412 | 18:00 | 406 | 22:00
Ashuganj | 395 | 7:00 | 379 | 14:00 | Rahanpur | 417 | 18:00 | 404 | 12:00
Bhulta | 391 | 07:00 | 381 | 14:00 | Rampal | 397 | 09:00 | 383 | 22:00
Bibiana | 388 | 19:30 | 382 | 15:00
BIPTC | 404 | 04:00 | 391 | 16:00
Bogura | 409 | 17:00 | 393 | 11:00
Gopalganj | 395 | 18:00 | 382 | 23:00
Kaliakoir | 365 | 19:30 | 350 | 9:00
Madunaghat | 397 | 20:00 | 390 | 13:00
Meghnaghat | 390 | 06:00 | 383 | 14:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 03:00 | 216 | 15:00 | Keranigonj | 222 | 03:00 | 214 | 15:00
AKSML | 234 | 19:30 | 221 | 14:00 | Khulna(S) | 227 | 09:00 | 212 | 23:00
Aminbazar | 226 | 06:00 | 217 | 11:00 | Madunaghat | 232 | 19:00 | 225 | 10:00
Ashuganj | 229 | 18:00 | 223 | 15:00 | Madunaghat-400 | 232 | 20:00 | 225 | 09:00
Ashuganj-400 | 229 | 18:00 | 223 | 15:00 | Maniknagar | 221 | 04:00 | 213 | 14:00
Baghabari | 234 | 18:00 | 226 | 12:00 | Meghnaghat | 230 | 03:00 | 222 | 14:00
Barapukuria | 222 | 15:00 | 211 | 07:00 | Meghnaghat-400 | 224 | 02:00 | 217 | 14:00
Barapukuria-230 | 222 | 15:00 | 211 | 07:00 | Mirsorai | 233 | 20:00 | 220 | 13:00
Barishal | 232 | 18:00 | 222 | 22:00 | Rajshahi | 233 | 09:00 | 221 | 23:00
Bheramara | 234 | 09:00 | 222 | 22:00 | Rampal | 227 | 09:00 | 215 | 22:00
Bhulta | 222 | 07:00 | 215 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 222 | 01:00 | 219 | 16:00 | Rampura | 221 | 03:00 | 211 | 15:00
BIPTC | 236 | 09:00 | 221 | 23:00 | Shikalbaha | 232 | 19:00 | 222 | 14:00
Bogura | 227 | 17:00 | 218 | 07:00 | Shyampur | 222 | 03:00 | 215 | 15:00
Bogura-400 | 227 | 15:00 | 218 | 07:00 | Siddhirganj | 224 | 05:00 | 219 | 21:00
Borhanuddin | 239 | 15:00 | 231 | 00:00 | Sirajgonj | 238 | 18:00 | 234 | 02:00
BSRM | 229 | 19:30 | 219 | 13:00 | Sreepur | 227 | 18:00 | 221 | 15:00
Cumilla(N) | 221 | 18:00 | 217 | 13:00 | Tongi | 225 | 04:00 | 214 | 09:00
Faridpur | 225 | 09:00 | 215 | 23:00
Fenchuganj | 224 | 11:00 | 218 | 00:00
Ghorashal | 230 | 00:00 | 224 | 15:00
Ghorashal-230 | 221 | 00:00 | 214 | 15:00
Gopalganj | 255 | 18:00 | 218 | 22:00
GPH | 232 | 08:00 | 222 | 10:00
Haripur | 222 | 04:00 | 215 | 15:00
Hasnabad | 223 | 05:00 | 216 | 15:00
Hathazari | 233 | 19:30 | 223 | 22:00
Ishurdi | 235 | 18:00 | 224 | 23:00
Jhenaidah | 228 | 09:00 | 211 | 22:00
Kaliakoir | 226 | 19:30 | 218 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 02:00 | 125 | 14:00 | Madartek | 133 | 03:00 | 125 | 13:00
Agargaon | 132 | 07:00 | 125 | 12:00 | Madunaghat | 133 | 19:00 | 128 | 14:00
Agrabad | 133 | 20:00 | 126 | 10:00 | Magura | 133 | 09:00 | 118 | 22:00
AKS | 130 | 19:30 | 125 | 06:00 | Mahasthangarh | 131 | 15:00 | 123 | 07:00
Aminbazar | 130 | 19:00 | 121 | 10:00 | Manikganj | 126 | 19:30 | 119 | 8:00
Amnura | 138 | 18:00 | 125 | 12:00 | Maniknagar | 130 | 04:00 | 123 | 13:00
Ashuganj | 135 | 00:00 | 134 | 01:00 | Matarbari | 119 | 09:00 | 112 | 22:00
Bagerhat | 131 | 09:00 | 118 | 23:00 | Matuail | 129 | 19:30 | 125 | 10:00
Bajitpur | 131 | 09:00 | 125 | 22:00 | Millgate | 127 | 00:00 | 121 | 10:00
Bakulia | 134 | 19:30 | 127 | 13:00 | Mirpur | 128 | 19:30 | 121 | 12:00
Banani | 133 | 02:00 | 124 | 13:00 | Mirzapur | 128 | 19:30 | 120 | 15:00
Bangabhaban | 130 | 05:00 | 123 | 12:00 | Mithapukur | 133 | 05:00 | 122 | 05:00
Barapukuria | 135 | 15:00 | 125 | 07:00 | MI_Cement | 130 | 20:00 | 125 | 12:00
Barguna | 134 | 18:00 | 129 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 18:00 | 121 | 23:00 | Mogbazar | 135 | 07:00 | 125 | 13:00
Barishal-230 | 130 | 18:00 | 121 | 22:00 | Mongla | 132 | 18:00 | 119 | 23:00
Baroaulia | 130 | 00:00 | 127 | 11:00 | Motijheel | 130 | 05:00 | 123 | 12:00
Baroirhat | 124 | 18:00 | 119 | 14:00 | Muktagacha | 132 | 09:00 | 118 | 19:00
Bashundhara | 134 | 07:00 | 121 | 08:00 | Munshiganj | 129 | 19:30 | 124 | 06:00
BashundharaCement | 130 | 19:30 | 116 | 08:00 | Muradnagar | 125 | 18:00 | 121 | 03:00
Beanibazar | 134 | 08:00 | 126 | 19:30 | Mymensingh | 133 | 11:00 | 114 | 23:00
Benapole | 130 | 09:00 | 114 | 23:00 | Naogaon | 128 | 15:00 | 119 | 07:00
Bhaluka | 131 | 12:00 | 125 | 15:00 | Narail | 134 | 09:00 | 116 | 22:00
Bhandaria | 125 | 18:00 | 110 | 22:00 | Narinda | 129 | 7:00 | 123 | 14:00
Bhangura | 132 | 18:00 | 129 | 04:00 | Narshingdi | 129 | 13:00 | 114 | 23:00
Bheramara | 135 | 09:00 | 125 | 23:00 | Natore | 132 | 18:00 | 125 | 13:00
Bheramara(GK) | 134 | 08:00 | 125 | 22:00 | Nawabganj | 133 | 06:00 | 127 | 12:00
Bhulta | 124 | 05:00 | 120 | 07:00 | Netrakona | 126 | 11:00 | 113 | 22:00
Bog-Sherpur | 127 | 16:00 | 120 | 07:00 | New | 128 | 18:30 | 122 | 10:00
Bogura | 134 | 15:00 | 126 | 07:00 | Niamatpur | 136 | 17:00 | 131 | 12:00
Bogura-230 | 134 | 15:00 | 126 | 07:00 | Noapara | 132 | 09:00 | 121 | 22:00
Brahmanbaria | 129 | 13:00 | 121 | 23:00 | Pabna | 135 | 09:00 | 127 | 22:00
Cantonment | 132 | 03:00 | 124 | 15:00 | Palashbari | 130 | 15:00 | 120 | 11:00
Chandina | 127 | 07:00 | 124 | 02:00 | Panchagarh | 134 | 15:00 | 118 | 06:00
Chandpur | 126 | 17:00 | 120 | 14:00 | Patuakhali | 133 | 09:00 | 130 | 00:00
Chandraghona | 133 | 20:00 | 128 | 05:00 | Payra | 135 | 10:00 | 132 | 22:00
Chapai | 133 | 18:00 | 127 | 12:00 | PHP | 123 | 18:30 | 117 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 19:30 | 125 | 10:00 | Postogola | 131 | 01:00 | 126 | 12:00
Chauddagram | 124 | 18:00 | 118 | 13:00 | Purbachal | 134 | 05:00 | 123 | 15:00
Chhatak | 134 | 07:00 | 126 | 00:00 | Purbasadipur | 131 | 00:00 | 115 | 07:00
Chowmuhani | 120 | 18:00 | 111 | 00:00 | Rahanpur | 138 | 17:00 | 133 | 12:00
Chuadanga | 129 | 09:00 | 116 | 22:00 | Rahanpur-400 | 138 | 15:00 | 134 | 12:00
Coxsbazar | 119 | 15:00 | 113 | 22:00 | Rahim | 128 | 02:00 | 124 | 15:00
Cumilla(N) | 127 | 07:00 | 124 | 00:00 | Rajbari | 132 | 18:00 | 124 | 23:00
Cumilla(S) | 134 | 05:00 | 121 | 13:00 | Rajendrapur | 131 | 18:00 | 123 | 06:00
Daudkandi | 124 | 17:00 | 119 | 03:00 | Rajshahi | 133 | 18:00 | 126 | 12:00
Dhaka | 134 | 03:00 | 124 | 13:00 | Rajshahi-230 | 135 | 18:00 | 118 | 12:00
Dhamrai | 133 | 19:30 | 127 | 08:00 | Ramganj | 120 | 07:00 | 114 | 00:00
Dhanmondi | 134 | 04:00 | 124 | 15:00 | Rampur | 132 | 19:30 | 125 | 14:00
Dohazari | 130 | 19:30 | 123 | 06:00 | Rampura | 134 | 04:00 | 123 | 15:00
Faridpur | 133 | 08:00 | 126 | 23:00 | Rangamati | 132 | 20:00 | 127 | 13:00
Fatullah | 130 | 19:30 | 125 | 13:00 | Rangpur | 131 | 04:00 | 120 | 06:00
Fenchuganj | 135 | 09:00 | 133 | 00:00 | Ruppur | 137 | 09:00 | 130 | 22:00
Feni | 123 | 07:00 | 115 | 14:00 | Saidpur | 130 | 02:00 | 118 | 12:00
Ghatail | 128 | 19:30 | 117 | 19:00 | Satkhira | 132 | 09:00 | 117 | 22:00
Ghorashal | 135 | 18:00 | 131 | 12:00 | Satmasjid | 132 | 06:00 | 124 | 13:00
Goalpara | 136 | 18:00 | 124 | 22:00 | Savar | 129 | 19:30 | 121 | 12:00
Gollamari | 134 | 08:00 | 124 | 23:00 | SevenRings | 136 | 19:30 | 130 | 15:00
Gopalganj | 134 | 09:00 | 124 | 23:00 | ShahCement | 130 | 19:30 | 25 | 10:00
Gopalganj-400 | 135 | 09:00 | 129 | 22:00 | Shahjadpur | 138 | 03:00 | 130 | 12:00
Gulshan | 134 | 05:00 | 124 | 15:00 | Shahjibazar | 130 | 08:00 | 125 | 23:00
Halishahar | 131 | 00:00 | 125 | 14:00 | Shahmirpur | 133 | 00:00 | 128 | 08:00
Haripur | 129 | 19:30 | 125 | 15:00 | Shariatpur | 136 | 19:00 | 124 | 23:00
HaripurSBU | 128 | 00:00 | 126 | 10:00 | Sherpur | 136 | 09:00 | 121 | 19:00
Hasnabad | 131 | 05:00 | 126 | 00:00 | Shikalbaha | 124 | 19:30 | 117 | 11:00
Hathazari | 135 | 00:00 | 129 | 15:00 | Shikalbaha-230 | 135 | 21:00 | 129 | 11:00
Ishurdi | 137 | 08:00 | 131 | 23:00 | Shitalakhya | 131 | 19:30 | 125 | 12:00
Jaldhaka | 129 | 01:00 | 116 | 07:00 | Sholosohor | 133 | 19:30 | 127 | 14:00
Jamalpur | 137 | 09:00 | 125 | 19:00 | Shyampur | 130 | 22:00 | 126 | 11:00
Jashore | 131 | 09:00 | 116 | 23:00 | Shyampur-230 | 129 | 05:00 | 124 | 15:00
Jhenaidah | 133 | 09:00 | 120 | 22:00 | Siddhirganj | 129 | 07:00 | 126 | 10:00
Jhenaidah-230 | 134 | 09:00 | 120 | 23:00 | Sirajganj | 121 | 03:00 | 112 | 07:00
Joydebpur | 135 | 17:00 | 125 | 08:00 | Sonargaon | 128 | 04:00 | 123 | 12:00
Joypurhat | 125 | 19:00 | 114 | 12:00 | Sreemongol | 131 | 09:00 | 126 | 15:00
Juldah | 135 | 19:30 | 128 | 10:00 | Sreepur | 132 | 07:00 | 128 | 15:00
Kabirpur | 132 | 19:30 | 118 | 15:00 | Srinagar | 133 | 07:00 | 126 | 15:00
Kachua | 125 | 18:30 | 120 | 00:00 | SSM | 136 | 23:00 | 132 | 00:00
Kaliakoir | 136 | 19:30 | 124 | 08:00 | Sunamganj | 132 | 07:00 | 125 | 00:00
Kallyanpur | 128 | 03:00 | 122 | 12:00 | Sylhet | 134 | 08:00 | 128 | 00:00
Kalurghat | 133 | 19:30 | 128 | 10:00 | Sylhet-132 | 134 | 07:00 | 129 | 00:00
Kamrangirchar | 133 | 04:00 | 126 | 13:00 | Tangail | 126 | 11:00 | 117 | 15:00
Kaptai | 134 | 19:00 | 130 | 13:00 | Thakurgaon | 136 | 00:00 | 120 | 07:00
Kasba | 125 | 17:00 | 120 | 22:00 | TK | 134 | 19:30 | 129 | 07:00
Kazla | 129 | 03:00 | 122 | 13:00 | Tongi | 132 | 04:00 | 125 | 08:00
Keranigonj | 133 | 04:00 | 127 | 15:00 | Ullahpara | 120 | 00:00 | 112 | 12:00
Khagrachori | 130 | 20:00 | 125 | 14:00 | Ullon | 133 | 04:00 | 124 | 13:00
Khulna | 134 | 09:00 | 122 | 22:00 | Uttara | 127 | 06:00 | 120 | 12:00
Khulna(S) | 136 | 18:00 | 124 | 23:00 | UttaraNew | 127 | 05:00 | 120 | 12:00
Khulshi | 132 | 20:00 | 125 | 14:00 | Zigatola | 133 | 05:00 | 127 | 15:00
Kishoreganj | 130 | 11:00 | 122 | 23:00
Kodda | 132 | 18:00 | 120 | 08:00
KSRM | 135 | 18:30 | 127 | 08:00
Kulaura | 135 | 08:00 | 131 | 00:00
Kurigram | 131 | 14:00 | 114 | 07:00
Kushtia | 133 | 09:00 | 121 | 23:00
Lalbag | 133 | 06:00 | 126 | 13:00
Lalmonirhat | 131 | 15:00 | 121 | 19:30
Madanganj | 130 | 19:30 | 123 | 15:00
Madaripur | 134 | 18:00 | 126 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division