## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-04-2025 | during | 25-04-2025 | during | 25-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 360 | 398 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 293 | 295 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 278 | 272 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 90 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 96 | 146 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 17.5 | 30 | 30 | 19 | 19 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 21 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 32 | 25 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 295 | 295 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 125 | 149 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 34 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 48 | 67 | 104 | 104 | 51 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 33 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 400 | 584 | 584 | 700 | 700 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 430 | 583 | 583 | 700 | 700 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 108 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 3289 | 3627.5 | 5009.9 | 5071.9 | 4434.12 | 4558.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 19 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 147 | 144 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 30 | 70 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 34 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 22 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 5 | 7 | 22 | 7 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 40 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 5.08 | 0 | 5.08 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 68 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 77 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 75 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 555 | 614 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 44 | 21 | 18 | 12 | 18 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 556 | 557 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1606 | 2214.5 | 2810.8 | 2819.72 | 2810.8 | 2819.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 336 | 347 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 330 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 31 | 31 | 46.94 | 46.94 | 34 | 34 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55 | 6 | 6 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 45 | 170 | 170 | 170 | 170 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 80 | 125 | 150 | 150 | 130 | 130 | Machine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 37 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 50 | 163 | 163 | 51 | 51 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 128 | 152 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 48 | 82 | 105.3 | 105.3 | 105.3 | 105.3 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 37 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 64 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 60 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1470 | 1725.2 | 2407.29 | 2357.29 | 2060.85 | 2039.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-04-2025 | during | 25-04-2025 | during | 25-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 121 | 145 | 200 | 200 | 125 | 150 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 93 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 49.09 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 52 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 268.09 | 302 | 597.2 | 549 | 307.7 | 321.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 38 | 38 | 38 | 36 | 36 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 29 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 138 | 151 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 170 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 359 | 360 | 380 | 380 | 337 | 337 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1468 | 1521 | 1568 | 1568 | 1462 | 1462
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 870 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 12 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 32 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 85 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 47 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 460 | 614 | 1234.2 | 1234.2 | 617.2 | 617.2 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1430 | 1613 | 3597.2 | 3512.2 | 2450.21 | 2365.21
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 559 | 626 | 600 | 600 | 290 | 290 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 80 | 80 | 130 | 130 | 90 | 90 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 778 | 1060 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 230 | 260 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.48 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1874.48 | 2273 | 2772.12 | 2771.12 | 2422 | 2421
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 47 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 25 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 13 | 40 | 40 | 40 | 40 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 162 | 158 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 152 | 158 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 149 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 397 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 42 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.51 | 0 | 5.05 | 0 | 5.05 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1365 | 1351.6 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.39 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 109 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2554.9 | 2703.6 | 3114.58 | 2948.53 | 3061.79 | 2895.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 164 | 158 | 160 | 160 | 160 | 160 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 105 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.2 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 207 | 0 | 173.39 | 0 | 173.39 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 634.2 | 386 | 631.79 | 422 | 631.79 | 422
System Total |  |  |  |  | 27566.2 | 28535.742 | 14594.67 | 16365.8 | 22508.88 | 22019.76 | 19641.26 | 19305.14
Forecast Scenario (25-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15700 |  | 0 |  | 15700
|  |  |  | 1:00 | 15140 |  | 0 |  | 15140
|  |  |  | 2:00 | 14580 |  | 0 |  | 14580
|  |  |  | 3:00 | 14040 |  | 0 |  | 14040
|  |  |  | 4:00 | 13610 |  | 0 |  | 13610
|  |  |  | 5:00 | 13280 |  | 0 |  | 13280
|  |  |  | 6:00 | 12770 |  | 0 |  | 12770
|  |  |  | 7:00 | 12850 |  | 0 |  | 12850
|  |  |  | 8:00 | 12730 |  | 0 |  | 12730
|  |  |  | 9:00 | 12700 |  | 0 |  | 12700
|  |  |  | 10:00 | 12640 |  | 0 |  | 12640
|  |  |  | 11:00 | 12860 |  | 0 |  | 12860
|  |  |  | 12:00 | 13480 |  | 0 |  | 13480
|  |  |  | 13:00 | 13800 |  | 0 |  | 13800
|  |  |  | 14:00 | 12760 |  | 0 |  | 12760
|  |  |  | 15:00 | 12740 |  | 0 |  | 12740
|  |  |  | 16:00 | 12230 |  | 0 |  | 12230
|  |  |  | 17:00 | 12180 |  | 0 |  | 12180
|  |  |  | 18:00 | 12600 |  | 0 |  | 12600
|  |  |  | 18:30 | 13500 |  | 0 |  | 13500
|  |  |  | 19:00 | 14370 |  | 0 |  | 14370
|  |  |  | 19:30 | 14710 |  | 0 |  | 14710
|  |  |  | 20:00 | 14660 |  | 0 |  | 14660
|  |  |  | 21:00 | 14800 |  | 0 |  | 14800
|  |  |  | 22:00 | 14800 |  | 0 |  | 14800
|  |  |  | 23:00 | 14710 |  | 0 |  | 14710
Probable Maximum Temperature: |  |  | 34.80°C
Probable Maximum Demand at Day Peak: |  |  | 13480.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 326.03 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:15 hrs on 25-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-04-2025 | [28 empty] | Date: | 24-04-2025 | [28 empty] | Date: | 24-04-2025 | [28 empty] | Date: | 24-04-2025 | [28 empty] | Date: | 24-04-2025 | [16 empty] | Date: | 24-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 35 | 149 | 98 | 297 | 55 | 35 | 126 | 0 | 67 | 400 | 287 | 350 | 0 | 55 | 0 | 325 | 0 | 0 | 0 | 160 | 17.5 | 20 | 0 | 400 | 17 | 15 | 25 | 0 | 12 | 68 | 62 | 0 | 100 | 50 | 0 | 40 | 75 | 21 | 557 | 53 | 0 | 0 | 0 | 81 | 149 | 0 | 0 | 0 | 612 | 0 | 43 | 130 | 8 | 0 | 354 | 330 | 5 | 195 | 33 | 115 | 51 | 145 | 12 | 20 | 83 | 48 | 52.2 | 0 | 47 | 300 | 320 | 290 | 39 | 0 | 0 | 152 | 8 | 0 | 83 | 30 | 0 | 17 | 172 | 17 | 50 | 123 | 0 | 0 | 0 | 12 | 8574.7 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 69 | 1360 | 0 | 47 | 0 | 113 | 19 | 84 | 113 | 36 | 52.2 | 0 | 30 | 0 | 159 | 0 | 146 | 0 | 148 | 0 | 414 | 0 | 0 | 0 | 163 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 80 | 220 | 0 | 461 | 1150 | 0 | 6943.2 | 15517.9 | 81.18
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 | 17 | 17 | 149 | 64 | 245 | 30 | 35 | 144 | 0 | 57 | 400 | 294 | 350 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 160 | 17.5 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 10 | 68 | 62 | 0 | 85 | 50 | 0 | 40 | 110 | 22 | 560 | 0 | 0 | 0 | 0 | 88 | 150 | 0 | 0 | 0 | 612 | 0 | 43 | 125 | 8 | 0 | 352 | 330 | 5 | 198 | 33 | 104 | 50 | 132 | 9 | 20 | 86 | 40 | 52.2 | 0 | 47 | 295 | 320 | 309 | 39 | 0 | 0 | 129 | 8 | 0 | 83 | 30 | 0 | 17 | 172 | 17 | 49 | 97 | 0 | 0 | 0 | 12 | 8283.7 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 53 | 1365 | 0 | 47 | 0 | 113 | 13 | 65 | 5 | 36 | 0 | 0 | 30 | 0 | 159 | 0 | 141 | 0 | 147 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 80 | 220 | 0 | 460 | 1150 | 0 | 6731 | 15014.7 | 81.17
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 149 | 48 | 145 | 0 | 17 | 144 | 0 | 52 | 400 | 289 | 350 | 0 | 55 | 0 | 324 | 0 | 0 | 0 | 160 | 17.5 | 20 | 0 | 400 | 0 | 0 | 0 | 0 | 12 | 68 | 62 | 0 | 55 | 50 | 0 | 40 | 110 | 13 | 557 | 0 | 0 | 0 | 0 | 67 | 150 | 0 | 0 | 0 | 612 | 0 | 43 | 127 | 8 | 0 | 355 | 330 | 5 | 205 | 33 | 93 | 51 | 141 | 9 | 20 | 80 | 40 | 52.2 | 0 | 38 | 310 | 320 | 289 | 39 | 0 | 0 | 134 | 8 | 0 | 83 | 30 | 0 | 17 | 172 | 17 | 49 | 95 | 0 | 0 | 0 | 12 | 8042.7 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 53 | 1364 | 0 | 47 | 0 | 113 | 0 | 0 | 0 | 15 | 0 | 0 | 30 | 0 | 159 | 0 | 139 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 80 | 220 | 0 | 414 | 1150 | 0 | 6579 | 14621.7 | 81.17
03:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 149 | 48 | 145 | 0 | 19 | 144 | 0 | 50 | 400 | 287 | 350 | 0 | 35 | 0 | 324 | 0 | 0 | 0 | 160 | 17.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 23 | 51 | 62 | 0 | 35 | 30 | 0 | 40 | 110 | 18 | 556 | 0 | 0 | 0 | 0 | 70 | 150 | 0 | 0 | 0 | 551 | 0 | 43 | 128 | 8 | 0 | 355 | 330 | 5 | 206 | 33 | 90 | 51 | 143 | 9 | 20 | 81 | 40 | 52.2 | 0 | 16 | 310 | 320 | 295 | 39 | 0 | 0 | 136 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 49 | 95 | 0 | 0 | 0 | 12 | 7910.7 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 53 | 1365 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 159 | 0 | 136 | 0 | 134 | 0 | 414 | 0 | 0 | 0 | 165 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 80 | 220 | 0 | 413 | 1122 | 0 | 6365 | 14275.7 | 81.16
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 17 | 108 | 48 | 45 | 0 | 35 | 144 | 0 | 48 | 400 | 290 | 350 | 0 | 35 | 0 | 325 | 0 | 0 | 0 | 125 | 17.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 25 | 34 | 62 | 0 | 35 | 10 | 0 | 40 | 110 | 23 | 557 | 0 | 0 | 0 | 0 | 70 | 150 | 0 | 0 | 0 | 550 | 0 | 43 | 123 | 8 | 0 | 354 | 330 | 5 | 210 | 33 | 89 | 51 | 137 | 9 | 20 | 80 | 38 | 52.2 | 0 | 16 | 305 | 320 | 288 | 37 | 0 | 0 | 130 | 8 | 0 | 83 | 30 | 0 | 17 | 172 | 0 | 49 | 95 | 0 | 0 | 0 | 12 | 7665.7 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 53 | 1358 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 137 | 0 | 132 | 0 | 414 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 80 | 220 | 0 | 413 | 1120 | 0 | 6290 | 13955.7 | 81.16
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 70 | 48 | 0 | 0 | 35 | 144 | 0 | 21 | 400 | 296 | 350 | 0 | 35 | 0 | 322 | 0 | 0 | 0 | 125 | 17.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 21 | 10 | 0 | 40 | 34 | 24 | 557 | 0 | 0 | 0 | 0 | 70 | 150 | 0 | 0 | 0 | 551 | 0 | 43 | 122 | 8 | 0 | 345 | 330 | 5 | 211 | 33 | 90 | 51 | 142 | 9 | 20 | 98 | 36 | 0 | 0 | 16 | 305 | 320 | 329 | 37 | 0 | 0 | 137 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 49 | 95 | 0 | 0 | 0 | 12 | 7381.5 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 17 | 1365 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 137 | 0 | 135 | 0 | 414 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 80 | 220 | 0 | 413 | 1120 | 0 | 6226 | 13607.5 | 81.15
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 70 | 48 | 0 | 0 | 35 | 144 | 0 | 16 | 370 | 282 | 350 | 0 | 35 | 0 | 324 | 0 | 0 | 1 | 108 | 18 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 21 | 10 | 0 | 40 | 0 | 26 | 560 | 0 | 0 | 0 | 0 | 34 | 150 | 0 | 0 | 0 | 552 | 0 | 43 | 100 | 8 | 0 | 354 | 330 | 5 | 215 | 33 | 90 | 50 | 128 | 9 | 20 | 38 | 36 | 0 | 3 | 16 | 310 | 320 | 288 | 37 | 0 | 0 | 133 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 49 | 95 | 0 | 0 | 1.38 | 0 | 7089.38 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 622 | 0 | 1367 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 137 | 0 | 142 | 0 | 300 | 0 | 0.11 | 0 | 164 | 0 | 0 | 1 | 34 | 0 | 0 | 0 | 0 | 0.02 | 0 | 307 | 10 | 80 | 220 | 0 | 413 | 1120 | 0 | 6030.33 | 13119.71 | 81.15
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 80 | 48 | 0 | 0 | 35 | 144 | 0 | 16 | 420 | 304 | 350 | 0 | 35 | 0 | 323 | 0 | 0 | 6 | 108 | 17 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 20 | 10 | 0 | 40 | 0 | 23 | 556 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 550 | 4 | 43 | 70 | 8 | 0 | 355 | 330 | 5 | 215 | 30 | 82 | 50 | 85 | 9 | 20 | 15 | 34 | 0 | 12 | 16 | 305 | 320 | 380 | 37 | 0 | 0 | 139 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 68 | 124 | 0 | 0 | 7.08 | 0 | 7126.08 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7 | 555 | 0 | 1362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 165 | 0 | 137 | 0 | 156 | 0 | 300 | 0 | 0.6 | 0 | 163 | 0 | 0 | 4 | 34 | 0 | 0 | 1.3 | 30 | 0.88 | 0 | 270 | 10 | 80 | 220 | 0 | 414 | 1005 | 0 | 5842.48 | 12968.56 | 81.15
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 17 | 17 | 85 | 48 | 0 | 0 | 35 | 144 | 0 | 16 | 420 | 294 | 350 | 0 | 0 | 0 | 320 | 0 | 0 | 13 | 90 | 15 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 20 | 10 | 2 | 40 | 0 | 6 | 557 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 550 | 12 | 43 | 70 | 8 | 0 | 349 | 325 | 5 | 211 | 29 | 68 | 50 | 77 | 9 | 20 | 15 | 34 | 0 | 8 | 38 | 305 | 320 | 370 | 37 | 0 | 0 | 151 | 8 | 0 | 80 | 30 | 0 | 17 | 174 | 0 | 70 | 124 | 0 | 1 | 13.54 | 0 | 7129.54 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 440 | 0 | 1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 171 | 0 | 150 | 0 | 159 | 0 | 414 | 0 | 1.22 | 0 | 163 | 0 | 0 | 10 | 34 | 0 | 0 | 3.1 | 69 | 0.16 | 0 | 270 | 7 | 80 | 220 | 0 | 475 | 950 | 0 | 5907.48 | 13037.02 | 81.14
09:00 | 0 | 52 | 11 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 86 | 48 | 0 | 0 | 35 | 144 | 0 | 16 | 420 | 292 | 350 | 0 | 0 | 0 | 315 | 0 | 0 | 16 | 90 | 17 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 20 | 30 | 2 | 40 | 0 | 2 | 556 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 550 | 9 | 43 | 70 | 8 | 0 | 345 | 325 | 5 | 207 | 28 | 57 | 50 | 77 | 9 | 20 | 16 | 34 | 0 | 30 | 37 | 305 | 320 | 350 | 38 | 0 | 0 | 141 | 8 | 0 | 80 | 30 | 0 | 17 | 175 | 0 | 68 | 124 | 0 | 1 | 27.13 | 0 | 7191.13 | 876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 415 | 0 | 1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 172 | 0 | 157 | 0 | 166 | 0 | 414 | 0 | 2.66 | 0 | 162 | 0 | 0 | 13 | 34 | 0 | 0 | 4.8 | 138 | 0.49 | 0 | 270 | 6 | 80 | 220 | 0 | 558 | 951 | 0 | 6079.95 | 13271.08 | 81.13
10:00 | 8 | 52 | 21 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 92 | 128 | 95 | 0 | 35 | 144 | 0 | 16 | 420 | 305 | 350 | 0 | 35 | 0 | 316 | 0 | 0 | 13 | 108 | 17 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 42 | 0 | 2 | 0 | 20 | 30 | 0 | 40 | 0 | 2 | 556 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 555 | 16 | 43 | 76 | 8 | 0 | 337 | 330 | 5 | 210 | 30 | 63 | 50 | 91 | 9 | 11 | 41 | 32 | 0 | 61 | 37 | 300 | 320 | 388 | 38 | 0 | 0 | 150 | 8 | 0 | 80 | 30 | 0 | 17 | 173 | 5 | 64 | 124 | 0 | 1 | 46.57 | 9 | 7608.57 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 376 | 0 | 1367 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 167 | 0 | 157 | 0 | 164 | 0 | 380 | 0 | 4.85 | 0 | 160 | 0 | 30 | 24 | 60 | 0 | 0 | 6.1 | 165 | 0.41 | 0 | 233 | 6 | 80 | 220 | 0 | 559 | 850 | 0 | 6104.36 | 13712.93 | 81.13
11:00 | 8 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 17 | 108 | 128 | 282 | 50 | 35 | 144 | 0 | 48 | 450 | 280 | 350 | 0 | 35 | 0 | 261 | 0 | 0 | 32 | 108 | 17 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 43 | 26 | 24 | 0 | 22 | 88 | 5 | 40 | 0 | 2 | 556 | 53 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 558 | 18 | 43 | 81 | 8 | 0 | 344 | 330 | 5 | 212 | 30 | 69 | 50 | 132 | 9 | 11 | 43 | 34 | 0 | 49 | 37 | 310 | 372 | 326 | 38 | 0 | 0 | 146 | 8 | 0 | 80 | 30 | 0 | 17 | 174 | 17 | 63 | 123 | 0 | 2 | 45.74 | 12 | 8070.74 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 413 | 0 | 1358 | 0 | 0 | 0 | 83 | 0 | 0 | 25 | 0 | 0 | 106 | 0 | 0 | 163 | 0 | 153 | 0 | 161 | 0 | 340 | 0 | 5.44 | 0 | 158 | 0 | 100 | 33 | 72 | 0 | 0 | 7.1 | 195 | 0.73 | 0 | 230 | 7 | 80 | 220 | 0 | 559 | 835 | 0 | 6311.27 | 14382.01 | 81.12
12:00 | 8 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 17 | 125 | 96 | 295 | 55 | 35 | 144 | 0 | 48 | 450 | 293 | 350 | 0 | 55 | 0 | 278 | 0 | 0 | 33 | 108 | 17 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 44 | 34 | 30 | 0 | 22 | 77 | 4 | 40 | 0 | 3 | 556 | 75 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 555 | 19 | 43 | 80 | 8 | 0 | 336 | 330 | 5 | 199 | 31 | 64 | 45 | 128 | 9 | 11 | 48 | 36 | 0 | 60 | 37 | 305 | 320 | 359 | 38 | 0 | 0 | 138 | 8 | 0 | 80 | 30 | 0 | 17 | 173 | 17 | 67 | 121 | 0 | 2 | 49.09 | 12 | 8101.09 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 460 | 0 | 1365 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 0 | 0 | 109 | 0 | 58.39 | 162 | 0 | 152 | 0 | 160 | 0 | 397 | 0 | 3.51 | 0 | 164 | 0 | 115 | 36 | 105 | 0 | 0 | 7.2 | 207 | 0.48 | 0 | 230 | 7 | 80 | 220 | 0 | 559 | 778 | 0 | 6493.58 | 14594.67 | 81.12
13:00 | 8 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 17 | 131 | 110 | 295 | 55 | 35 | 144 | 0 | 51 | 450 | 285 | 350 | 0 | 55 | 0 | 270 | 0 | 0 | 32 | 108 | 17 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 41 | 31 | 48 | 0 | 22 | 88 | 5 | 40 | 0 | 5 | 555 | 125 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 612 | 17 | 43 | 83 | 8 | 0 | 334 | 330 | 5 | 191 | 31 | 53 | 40 | 131 | 9 | 11 | 59 | 40 | 0 | 33 | 37 | 310 | 320 | 355 | 38 | 0 | 0 | 152 | 8 | 0 | 80 | 30 | 0 | 17 | 173 | 17 | 67 | 120 | 0 | 2 | 44.69 | 12 | 8259.69 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 505 | 0 | 1362 | 0 | 0 | 0 | 113 | 0 | 0 | 90 | 0 | 0 | 93 | 0 | 49.4 | 162 | 0 | 147 | 0 | 158 | 0 | 414 | 0 | 4.98 | 0 | 165 | 0 | 115 | 32 | 113 | 0 | 0 | 7.1 | 197 | 0.32 | 0 | 230 | 6 | 80 | 220 | 0 | 559 | 770 | 0 | 6558.8 | 14818.49 | 81.11
14:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 0 | 130 | 124 | 295 | 55 | 35 | 144 | 0 | 50 | 450 | 295 | 350 | 0 | 55 | 0 | 278 | 0 | 0 | 27 | 108 | 17.5 | 21 | 0 | 450 | 11 | 0 | 0 | 0 | 33 | 31 | 48 | 0 | 22 | 88 | 4 | 40 | 14 | 4 | 556 | 160 | 0 | 0 | 0 | 33 | 145 | 0 | 0 | 0 | 612 | 16 | 51 | 92 | 8 | 0 | 335 | 330 | 5 | 196 | 30 | 67 | 40 | 146 | 9 | 11 | 58 | 38 | 0 | 27 | 37 | 305 | 320 | 386 | 38 | 0 | 0 | 146 | 8 | 0 | 77 | 30 | 0 | 17 | 170 | 17 | 66 | 121 | 0 | 2 | 29.72 | 12 | 8330.22 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 510 | 0 | 1370.66 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 0 | 93 | 0 | 53.04 | 159 | 0 | 145 | 0 | 145 | 0 | 350 | 0 | 4.77 | 0 | 163 | 0 | 115 | 29 | 112 | 0 | 0 | 6.2 | 166 | 0.46 | 0 | 230 | 8 | 80 | 220 | 0 | 622 | 750 | 0 | 6522.13 | 14852.35 | 81.11
15:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 17 | 0 | 133 | 125 | 294 | 55 | 35 | 144 | 0 | 50 | 450 | 298 | 350 | 0 | 55 | 0 | 281 | 0 | 0 | 21 | 108 | 17.5 | 21 | 0 | 450 | 17 | 0 | 0 | 0 | 33 | 44 | 47 | 0 | 22 | 73 | 2 | 40 | 17 | 2 | 556 | 160 | 0 | 0 | 1 | 29 | 144 | 0 | 0 | 0 | 600 | 12 | 51 | 88 | 26 | 0 | 335 | 330 | 5 | 201 | 27 | 72 | 40 | 150 | 9 | 11 | 84 | 38 | 1 | 26 | 36 | 305 | 320 | 380 | 38 | 0 | 0 | 147 | 8 | 0 | 77 | 30 | 0 | 17 | 170 | 17 | 66 | 112 | 0 | 1 | 24.05 | 12 | 8375.55 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 507 | 0 | 1363.13 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 0 | 72 | 0 | 40.21 | 159 | 0 | 143 | 0 | 143 | 0 | 414 | 0 | 3.75 | 0 | 160 | 0 | 115 | 22 | 111 | 0 | 0 | 4.8 | 134 | 0.35 | 0 | 230 | 9 | 80 | 220 | 0 | 616 | 760 | 0 | 6512.24 | 14887.79 | 81.1
16:00 | 32 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 0 | 149 | 125 | 294 | 55 | 35 | 144 | 0 | 50 | 450 | 288 | 350 | 0 | 55 | 0 | 261 | 0 | 0 | 14 | 108 | 17.5 | 21 | 0 | 420 | 17 | 0 | 4 | 0 | 27 | 48 | 46 | 0 | 85 | 82 | 2 | 40 | 29 | 2 | 556 | 160 | 0 | 11 | 8 | 49 | 144 | 0 | 0 | 0 | 565 | 8 | 51 | 92 | 45 | 0 | 340 | 330 | 5 | 183 | 30 | 72 | 40 | 152 | 25 | 11 | 79 | 38 | 30 | 16 | 36 | 300 | 320 | 350 | 37 | 20 | 0 | 148 | 8 | 0 | 77 | 30 | 0 | 17 | 171 | 17 | 66 | 120 | 0 | 1 | 21.07 | 12 | 8483.57 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 510 | 0 | 1356.7 | 0 | 0 | 0 | 113 | 0 | 55 | 113 | 0 | 0 | 46 | 0 | 25.23 | 159 | 0 | 144 | 0 | 141 | 0 | 414 | 0 | 2.29 | 0 | 160 | 0 | 113 | 16 | 104 | 0 | 0 | 3.1 | 81 | 0.31 | 0 | 230 | 8 | 80 | 220 | 0 | 618 | 797 | 0 | 6463.63 | 14947.2 | 81.1
17:00 | 42 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 17 | 0 | 149 | 134 | 294 | 55 | 35 | 144 | 0 | 50 | 400 | 292 | 350 | 0 | 55 | 0 | 261 | 0 | 0 | 5 | 108 | 17.5 | 21 | 0 | 420 | 0 | 0 | 12 | 0 | 18 | 48 | 51 | 0 | 90 | 50 | 1 | 40 | 34 | 5 | 522 | 90 | 0 | 19 | 25.5 | 34 | 144 | 0 | 0 | 0 | 500 | 3 | 51 | 107 | 45 | 0 | 340 | 330 | 5 | 197 | 31 | 79 | 40 | 144 | 34 | 20 | 86 | 40 | 52.2 | 8 | 44 | 300 | 320 | 372 | 37 | 30 | 0 | 149 | 8 | 0 | 77 | 30 | 0 | 17 | 171 | 17 | 84 | 120 | 0 | 0 | 7.3 | 12 | 8356.5 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 508 | 0 | 1358.72 | 0 | 48 | 0 | 35 | 0 | 55 | 35 | 0 | 0 | 19 | 30 | 4.19 | 158 | 0 | 148 | 0 | 143 | 0 | 370 | 0 | 0.94 | 0 | 161 | 0 | 70 | 7 | 111 | 0 | 0 | 1.3 | 34 | 0.12 | 0 | 230 | 6 | 80 | 220 | 0 | 614 | 796 | 0 | 6181.27 | 14537.77 | 81.09
18:00 | 49 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 54 | 2 | 149 | 143 | 295 | 55 | 35 | 144 | 0 | 50 | 320 | 288 | 350 | 0 | 55 | 0 | 260 | 0 | 0 | 0 | 108 | 5 | 21 | 0 | 370 | 0 | 0 | 12 | 0 | 17 | 48 | 64 | 0 | 55 | 50 | 0 | 40 | 34 | 6 | 523 | 90 | 0 | 19 | 25.5 | 34 | 144 | 0 | 0 | 0 | 500 | 0 | 51 | 108 | 45 | 0 | 330 | 330 | 5 | 185 | 31 | 75 | 50 | 150 | 37 | 20 | 79 | 38 | 52.2 | 1 | 44 | 305 | 320 | 356 | 37 | 30 | 0 | 140 | 8 | 0 | 80 | 30 | 0 | 17 | 171 | 52 | 101 | 154 | 0 | 0 | 1.09 | 12 | 8244.79 | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88 | 509 | 7 | 1263.92 | 0 | 47 | 0 | 35 | 5 | 55 | 35 | 13 | 0 | 3 | 30 | 0.56 | 159 | 0 | 149 | 0 | 144 | 0 | 300 | 0 | 0.13 | 0 | 122 | 0 | 70 | 1 | 70 | 0 | 0 | 0.3 | 6 | 0.02 | 0 | 230 | 7 | 80 | 220 | 0 | 611 | 810 | 0 | 5921.81 | 14166.6 | 81.09
19:00 | 82 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 17 | 149 | 144 | 295 | 55 | 35 | 144 | 0 | 67 | 450 | 300 | 430 | 0 | 55 | 0 | 283 | 0 | 0 | 0 | 160 | 17.5 | 21 | 0 | 450 | 14 | 15 | 18 | 0 | 22 | 82 | 64 | 0 | 100 | 100 | 0 | 40 | 45 | 9 | 556 | 160 | 0 | 23 | 25.5 | 60 | 144 | 0 | 0 | 0 | 577 | 0 | 51 | 117 | 45 | 0 | 343 | 330 | 5 | 202 | 31 | 100 | 50 | 157 | 37 | 20 | 89 | 44 | 52.2 | 0 | 46 | 310 | 320 | 390 | 38 | 30 | 0 | 139 | 8 | 0 | 83 | 30 | 0 | 17 | 170 | 52 | 93 | 155 | 0 | 0 | 0 | 12 | 9276.2 | 879 | 0 | 0 | 11 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 30 | 1359.72 | 0 | 47 | 0 | 80 | 6 | 90 | 100 | 13 | 20 | 0 | 30 | 0 | 158 | 0 | 154 | 0 | 148 | 0 | 414 | 0 | 0 | 0 | 155 | 0 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 32 | 260 | 11 | 80 | 220 | 0 | 612 | 980 | 17 | 6733.72 | 16009.92 | 81.08
19:30 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 54 | 17 | 149 | 146 | 295 | 55 | 35 | 144 | 0 | 67 | 450 | 295 | 430 | 0 | 55 | 0 | 272 | 0 | 0 | 0 | 160 | 17.5 | 21 | 0 | 400 | 35 | 15 | 40 | 0 | 21 | 102 | 70 | 0 | 100 | 100 | 0 | 40 | 68 | 5 | 557 | 160 | 0 | 33 | 25.5 | 85 | 144 | 0 | 0 | 0 | 614 | 0 | 51 | 125 | 45 | 0 | 347 | 330 | 5 | 193 | 31 | 115 | 50 | 152 | 37 | 20 | 82 | 44 | 52.2 | 0 | 46 | 315 | 320 | 360 | 38 | 29 | 0 | 151 | 8 | 0 | 83 | 30 | 0 | 17 | 170 | 52 | 93 | 145 | 0 | 0 | 0 | 12 | 9390.2 | 870 | 0 | 0 | 12 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 85 | 1351.6 | 0 | 47 | 0 | 113 | 25 | 90 | 113 | 13 | 42 | 0 | 30 | 0 | 158 | 0 | 158 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 158 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 260 | 11 | 80 | 220 | 0 | 626 | 1060 | 0 | 6975.6 | 16365.8
20:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 54 | 17 | 149 | 146 | 295 | 55 | 35 | 144 | 0 | 67 | 450 | 294 | 430 | 0 | 55 | 0 | 275 | 0 | 0 | 0 | 160 | 17.5 | 21 | 0 | 400 | 35 | 15 | 40 | 0 | 13 | 102 | 70 | 0 | 100 | 100 | 0 | 40 | 90 | 7 | 556 | 160 | 0 | 30 | 25.5 | 68 | 145 | 0 | 0 | 0 | 612 | 0 | 51 | 124 | 45 | 0 | 351 | 330 | 5 | 188 | 32 | 115 | 50 | 149 | 37 | 20 | 81 | 44 | 52.2 | 0 | 46 | 305 | 320 | 348 | 38 | 29 | 0 | 149 | 8 | 0 | 83 | 30 | 0 | 17 | 170 | 54 | 93 | 145 | 0 | 0 | 0 | 12 | 9346.2 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 85 | 1359.05 | 0 | 47 | 0 | 113 | 25 | 90 | 113 | 37 | 52.2 | 0 | 30 | 0 | 158 | 0 | 157 | 0 | 148 | 0 | 414 | 0 | 0 | 0 | 155 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 11 | 80 | 220 | 0 | 616 | 1063 | 0 | 6876.25 | 16222.45 | 81.08
21:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 17 | 149 | 146 | 295 | 55 | 35 | 144 | 0 | 70 | 450 | 278 | 460 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 160 | 17.5 | 21 | 0 | 450 | 17 | 0 | 12 | 0 | 15 | 102 | 70 | 0 | 100 | 60 | 0 | 40 | 68 | 12 | 556 | 160 | 0 | 19 | 25.5 | 34 | 149 | 0 | 0 | 0 | 612 | 0 | 51 | 129 | 16 | 0 | 355 | 330 | 5 | 215 | 33 | 99 | 50 | 133 | 38 | 20 | 79 | 44 | 52.2 | 0 | 47 | 285 | 320 | 384 | 38 | 29 | 0 | 147 | 8 | 0 | 83 | 30 | 0 | 17 | 170 | 52 | 94 | 145 | 0 | 0 | 0 | 12 | 9309.2 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 588 | 53 | 1362.18 | 0 | 47 | 0 | 113 | 25 | 85 | 70 | 37 | 52.2 | 0 | 30 | 0 | 158 | 0 | 157 | 0 | 148 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 80 | 220 | 0 | 610 | 1091 | 0 | 6846.38 | 16155.58 | 81.07
22:00 | 50 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 149 | 146 | 295 | 55 | 35 | 144 | 0 | 71 | 450 | 289 | 450 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 160 | 17.7 | 21 | 0 | 450 | 17 | 0 | 0 | 0 | 18 | 102 | 70 | 0 | 100 | 100 | 0 | 40 | 34 | 23 | 556 | 160 | 0 | 19 | 25.5 | 34 | 147 | 0 | 0 | 0 | 613 | 0 | 51 | 129 | 8 | 0 | 349 | 330 | 5 | 196 | 33 | 111 | 50 | 152 | 38 | 20 | 84 | 46 | 52.2 | 0 | 47 | 300 | 320 | 375 | 38 | 30 | 0 | 152 | 8 | 0 | 83 | 30 | 0 | 17 | 170 | 52 | 94 | 136 | 0 | 0 | 0 | 12 | 9248.4 | 799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 51 | 1350.37 | 0 | 47 | 0 | 113 | 25 | 86 | 113 | 37 | 52.2 | 0 | 30 | 0 | 158 | 0 | 157 | 0 | 148 | 0 | 370 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 11 | 80 | 220 | 0 | 612 | 1092 | 0 | 6823.57 | 16071.97 | 81.07
23:00 | 32 | 35 | 18 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 149 | 129 | 295 | 55 | 35 | 144 | 0 | 72 | 450 | 293 | 450 | 0 | 55 | 0 | 320 | 0 | 0 | 0 | 160 | 17.7 | 21 | 0 | 450 | 17 | 0 | 0 | 0 | 18 | 85 | 70 | 0 | 100 | 100 | 0 | 40 | 34 | 26 | 556 | 160 | 0 | 19 | 25.5 | 34 | 146 | 0 | 0 | 0 | 613 | 0 | 51 | 123 | 8 | 0 | 344 | 330 | 5 | 212 | 33 | 97 | 50 | 169 | 38 | 20 | 100 | 46 | 52.2 | 0 | 47 | 305 | 320 | 392 | 38 | 30 | 0 | 156 | 6 | 0 | 80 | 28 | 0 | 17 | 174 | 23 | 94 | 136 | 0 | 0 | 0 | 12 | 9161.4 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 51 | 1356.38 | 0 | 47 | 0 | 113 | 25 | 87 | 113 | 37 | 52.2 | 0 | 30 | 0 | 158 | 0 | 154 | 0 | 150 | 0 | 414 | 0 | 0 | 0 | 163 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 11 | 0 | 220 | 0 | 614 | 1095 | 0 | 6803.58 | 15964.98 | 81.06
Total KWH | 545760 | 794880 | 378720 | 0 | 0 | 0 | 0 | 0 | 9331200 | 0 | 0 | 518400 | 314280 | 3025584 | 2356320 | 4764513 | 838676 | 844913 | 3484800 | 0 | 1096320 | 9606500 | 7006720 | 9006364 | 0 | 1065768 | 0 | 7309821 | 0 | 0 | 216377 | 3051600 | 411000 | 502200 | 0 | 10175000 | 209509 | 50182 | 120000 | 0 | 576000 | 1027561 | 983040 | 0 | 1276800 | 1427520 | 26641 | 956160 | 1024545 | 314400 | 13287272.73 | 1855055 | 0 | 182400 | 209952 | 996109 | 3522538 | 0 | 0 | 0 | 13767271 | 119745 | 933752 | 2549236 | 418182 | 0 | 8630100 | 7960000 | 132000 | 4948000 | 762912 | 2016000 | 1130560 | 3236160 | 446040 | 417020 | 1619940 | 936960 | 667051 | 345209 | 876736 | 7384000 | 7648600 | 8819000 | 890000 | 207120 | 0 | 3456900 | 181392 | 0 | 1946880 | 708864 | 0 | 411000 | 4557310 | 509400 | 1666800 | 2877600 | 0 | 14000 | 309560 | 254160 | 198446860.73 | 22035636 | 0 | 0 | 8640 | 46464 | 0 | 0 | 0 | 0 | 0 | 0 | 509040 | 13178180 | 589440 | 32589533.64 | 0 | 455351 | 0 | 2091552 | 131650 | 731024 | 1260000 | 219850 | 293458 | 738370 | 312200 | 231744 | 3878636 | 0 | 3738109 | 0 | 3800540 | 0 | 9407418 | 0 | 32580 | 0 | 3932000 | 0 | 1795109 | 232935 | 2089363 | 0 | 0 | 52606.56 | 1422720 | 3177 | 42048 | 6458000 | 220212 | 1814000 | 5386140 | 0 | 12829817 | 24081455 | 14400 | 156653398.2 | 355100258.93

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14594.67 | MW | 12:00 Hr. | Energy Generated |  |  | 355.1003 |  | MKWHr.
| Day Peak Demand |  |  | 14731.67 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.52 |  | MKWHr.
| Evening Peak Generation |  |  | 16365.8 | MW | 19:30 Hr. | Energy Demand |  |  | 358.6203 |  | MKWHr.
| Evening Peak Demand |  |  | 16510.8 | MW | 19:30 Hr. | Maximum Temperature |  |  | 35.6 |  | °C
| Minimum Generation of the Day |  |  | 12968.56 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1045.99 |  | MMCFD
| Maximum Generation of the Day |  |  | 16365.8 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.1812 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 53.3488 | 0 | 23.0805 | 0 | 0 | 0.21638 | 0 | 0 | 76.6457 | Gas | 146.9744 | Gas | 516900905.73
| Chattogram Zone |  |  | 3.8369 | 27.0545 | 9.3627 | 0 | 0.95616 | 0.14639 | 0 | 0.576 | 41.9327 | Coal | 87.534 | Coal | 534122045.11
| Cumilla Zone |  |  | 25.3325 | 0 | 11.4112 | 0 | 0 | 0.34521 | 0.93696 | 0 | 38.0259 | HFO | 59.2429 | HFO | 1111512899.66
| Mymensingh Zone |  |  | 0 | 0 | 5.308 | 0 | 0 | 0.32356 | 0 | 0 | 5.6315 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.2111 | Hydro | 0.95616 | Hydro | 95616
| Khulna Zone |  |  | 0 | 13.1782 | 0.64454 | 0 | 0 | 0.50904 | 22.0356 | 0 | 36.3674 | Solar | 4.2547 | Solar | 70720956.8216
| Barishal Zone |  |  | 7.4204 | 43.3693 | 0.056448 | 0 | 0 | 0.003177 | 0 | 0 | 50.8492 | Import | 55.5621 | Import | 308246843.9976
| Rajshahi Zone |  |  | 20.8247 | 0 | 5.4951 | 0 | 0 | 1.0027 | 32.5895 | 0 | 59.912 | Wind | 0.576 | Wind | 8432640
| Rangpur Zone |  |  | 0 | 3.932 | 3.8845 | 0 | 0 | 1.7083 | 0 | 0 | 9.5247
| Total |  |  | 146.9744 | 87.534 | 59.2429 | 0 | 0.95616 | 4.2547 | 55.5621 | 0.576 | 355.1003
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 516900905.73 |  | Hydro | 95616
|  |  |  | Coal | 534122045.11 |  | Solar | 70720956.8216
|  |  |  | HFO | 1111512899.66 |  | Import | 308246843.9976
|  |  |  | HSD | 0 |  | Wind | 8432640
[5 empty] | Total: | 255,00,31,907 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0356 | Peak Hr Flow | 870.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9926181.88 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.5895 | Peak Hr Flow | 1351.60 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 474 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.93696 | Peak Hr Flow | 44.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 914 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.5621 | Peak Hr Flow | 2265.60 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 55 |  | 5877
|  |  |  | Chattogram |  | 0 |  | 1522
|  |  |  | Cumilla |  | 0 |  | 1396
|  |  |  | Mymensingh |  | 60 |  | 1245
|  |  |  | Sylhet |  | 0 |  | 578
|  |  |  | Khulna |  | 0 |  | 1924
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 11 |  | 1740
|  |  |  | Rangpur |  | 13 |  | 1024
|  |  |  | Total |  | 139 |  | 15784
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1095.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:31 | 18:27 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D
| 08:35 | 09:58 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Forced S/D Due to For red hot in 33KV | [7 empty] | 20.0MW load
|  |  | Beanibazar and Golapgonj feeder | [7 empty] | interrup.
| 08:35 | 10:00 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Forced S/D Due to For red hot in 33KV | [7 empty] | 20.0MW load
|  |  | Beanibazar and Golapgonj feeder | [7 empty] | interrup.
|  | 08:37 | Tangail 132/33kV S/S Tr-2 LT is restored.
|  | 08:37 | Tangail 132/33kV S/S Tr-2 HT is restored.
|  | 09:34 | Chandraghona 132/33kV S/S TR-01(406T) HT is restored.
|  | 09:35 | Chandraghona 132/33kV S/S TR-01(406T) LT is restored.
|  | 09:40 | Shahjibazar 132/33kV S/S TR-06 HT is restored.
|  | 09:46 | Shahjibazar 132/33kV S/S TR-04 HT is restored.
| 09:48 |  | Bhulta 400/230kV S/S 230kV Bus-02 Project Work S/D
|  | 09:48 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
|  | 09:48 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
|  | 10:22 | Chauddagram 132/33kV S/S 132 kv T-1 LT is restored.
|  | 10:22 | Chauddagram 132/33kV S/S 132 kv T-1 HT is restored.
| 10:43 | 17:05 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Disc cleaning work
| 11:14 | 17:06 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance Purpose
| 11:35 | 14:42 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to Shutdown taken by Dhaka PBS -1 due | [7 empty] | 80.0MW load
|  |  | to High temperature maintenance work at 33KV BUS | [7 empty] | interrup.
| 12:00 |  | Day Peak Gen. 14594 MW
| 15:10 | 15:17 | Joydebpur 132/33kV S/S GT-4 HT Tripped showing Lock out Realy relays Due to Trip | [7 empty] | 39.0MW load
interrup.
| 15:17 |  | Rajbari 132/33kV S/S Transformer-3 LT Project Work S/D Due to SAS INTRIGATION WORKS.
| 15:18 |  | Rajbari 132/33kV S/S Transformer-3 HT Project Work S/D Due to SAS Integration works.
| 16:34 | 18:42 | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Forced S/D Due to 33 kv Bus conductor and Amtoli | [7 empty] | 35.0MW load
|  |  | feeder 33kv bus loop Maintenance of PBS. | [7 empty] | interrup.
| 16:35 | 18:41 | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Forced S/D Due to 33 kv Bus conductor and Amtoli | [7 empty] | 35.0MW load
|  |  | feeder 33kv bus loop Maintenance of PBS. | [7 empty] | interrup.
|  | 16:43 | Bheramara 230/132kV S/S Bus-A (132) is restored.
|  | 19:54 | Gopalganj 400/132kV S/S 400kV Bus-02 is restored.
| 06:30 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D Due to Red hot maintenance and CT to CB
conductor change.
| 06:30 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D Due to Red hot maintenance and CT to CB
conductor change
| 06:42 |  | Kodda-Rajendrapur 132kV Ckt-1 Project Work S/D from Rajendrapur 132/33kV end Due to
Kodda end bus shutdown purpose.
| 07:03 |  | Rampura 230/132kV S/S 230kV Busbar-1 Project Work S/D Due to Connect of Auto tx-2 to
jackbus
| 07:11 |  | Bhaluka 132/33kV S/S Transformer- 02 HT Forced S/D Due to T2 33 kv bushing temperature | [7 empty] | 10.0MW load
|  |  | minimize | [7 empty] | interrup.
| 07:12 |  | Bhaluka 132/33kV S/S Transformer- 02 LT Forced S/D Due to T2 33 kv bushing temperature | [7 empty] | 10.0MW load
|  |  | minimize | [7 empty] | interrup.
| 07:47 |  | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 398 | 9331200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9606500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 295 | 7006720 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 838676 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 272 | 7309821 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 545760 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 518400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 146 | 2356320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 844913 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 1065768 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17.5 | 411000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 21 | 502200 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 378720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 4764513 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 3025584 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 794880 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 1096320 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3484800 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 216377 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 314280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10175000 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 430 | 9006364 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 3051600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3627.5 | 76645716
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 209952 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 119745 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 182400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 956160 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 144 | 3522538 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 996109 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 70 | 983040 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 1027561 | Machine Problem
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1276800 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 314400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 40 | 120000 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26641 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 50182 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 68 | 1024545 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1427520 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 209509 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 1855055 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 614 | 13767271 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 21 | 576000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 557 | 13287272.73 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2214.5 | 41932700.73
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 193 | 4948000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 347 | 8630100 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 7960000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 31 | 762912 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 132000 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 418182 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 933752 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 2549236 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 46 | 876736 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1130560 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 152 | 3236160 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 44 | 936960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 667051 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 417020 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 82 | 1619940 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 446040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2016000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 345209 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1725.2 | 38025858
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 145 | 2877600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 93 | 1666800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 309560 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 254160 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 52 | 509400 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 302 | 5631520
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 890000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 207120 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3456900 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 708864 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1946880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 170 | 4557310 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 411000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 181392 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7384000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 360 | 8819000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7648600 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1521 | 36211066
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 870 | 22035636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 12 | 8640 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 32 | 46464 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 85 | 589440 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 509040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 614 | 13178180 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1613 | 36367400
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 626 | 12829817 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 42048 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 220212 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 80 | 1814000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1060 | 24081455 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5386140 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 14400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 260 | 6458000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3177 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2273 | 50849249
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 47 | 455351 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 25 | 131650 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 13 | 219850 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 158 | 3878636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 158 | 3738109 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 149 | 3800540 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9407418 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 312200 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 42 | 293458 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 731024 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2091552 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1260000 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1351.6 | 32589533.64 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 231744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 738370 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2703.6 | 59912015.64
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3932000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 2089363 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52606.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1795109 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 232935 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1422720 | -
Rangpur Area Total |  |  |  |  | 950 | 386 | 9524733.56
Eastern Grid Total |  |  |  |  | 16921.242 | 9390.2 | 198446860.73
Western Grid Total |  |  |  |  | 11614.5 | 6975.6 | 156653398.2
National Grid Total |  |  |  |  | 28535.742 | 16365.8 | 355100258.93
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10503.24 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5141.7 | MW
i) Dhaka area |  |  | 5822.04 |  | MW | i) Khulna area |  |  |  | 1924 | MW
ii) Chattogram area |  |  | 1522.2 |  | MW | ii) Barishal area |  |  |  | 477.5 | MW
iii) Cumilla area |  |  | 1396 |  | MW | iii) Rajshahi area |  |  |  | 1729.2 | MW
iv) Mymensingh area |  |  | 1185 |  | MW | iv) Rangpur area |  |  |  | 1011 | MW
v) Sylhet area |  |  | 578 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15644.94 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 91 | 19:30 | 133 | Patuakhali | 81.5 | 22:00
2 | AKSML | 26.5 | 15:00 | 68 | Jaldhaka | 85 | 19:30 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 40 | 13:00 | 69 | Jamalpur | 115 | 10:00 | 135 | Postogola | 61 | 16:00
4 | Agargaon | 141 | 15:00 | 70 | Jashore | 156 | 19:30 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 96 | 18:30 | 71 | Jhenaidah | 143 | 19:00 | 137 | Purbasadipur | 137 | 19:30
6 | Amnura | 58 | 22:00 | 72 | Joydebpur | 165 | 16:00 | 138 | Rahanpur | 34 | 22:00
7 | Ashuganj | 109 | 23:00 | 73 | Joypurhat | 78 | 21:00 | 139 | Rahim | 51 | 12:00
8 | BSRM | 191 | 05:00 | 74 | Juldah | 12 | 00:00 | 140 | Rajbari | 86 | 00:00
9 | Bagerhat | 92 | 00:00 | 75 | KSRM | 11 | 17:00 | 141 | Rajendrapur | 152 | 19:00
10 | Bajitpur | 54 | 21:00 | 76 | Kabirpur | 277 | 18:00 | 142 | Rajshahi | 146 | 21:00
11 | Bakulia | 98 | 18:30 | 77 | Kachua | 93 | 20:00 | 143 | Rajshahi-230 | 102 | 00:00
12 | Banani | 52 | 13:00 | 78 | Kallyanpur | 120 | 00:00 | 144 | Ramganj | 118 | 00:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kalurghat | 40 | 12:00 | 145 | Rampur | 43 | 23:00
14 | Barapukuria | 72 | 19:00 | 80 | Kamrangirchar | 70.2 | 18:00 | 146 | Rangamati | 17 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 161 | 20:00
16 | Barishal | 117 | 19:00 | 82 | Kasba | 38 | 00:00 | 148 | Ruppur | 8.2 | 11:00
17 | Barishal-230 | 108 | 22:00 | 83 | Kazla | 121 | 17:00 | 149 | SSM | 10 | 01:00
18 | Baroaulia | 64 | 10:00 | 84 | Keranigonj | 83 | 19:00 | 150 | Saidpur | 120 | 19:00
19 | Baroirhat | 64 | 19:00 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 138 | 19:30
20 | Bashundhara | 216 | 14:00 | 86 | Khulna | 68 | 19:00 | 152 | Satmasjid | 118 | 19:00
21 | BashundharaCement | 8 | 16:00 | 87 | Khulshi | 185 | 19:00 | 153 | Savar | 230 | 17:00
22 | Beanibazar | 62 | 18:30 | 88 | Kishoreganj | 144 | 22:00 | 154 | SevenRings | 16.92 | 12:00
23 | Benapole | 70 | 21:00 | 89 | Kodda | 307 | 13:00 | 155 | ShahCement | 36 | 01:00
24 | Bhaluka | 173 | 19:00 | 90 | Kulaura | 45 | 20:00 | 156 | Shahjadpur | 98 | 22:00
25 | Bhandaria | 56 | 22:00 | 91 | Kurigram | 68 | 19:00 | 157 | Shahjibazar | 117 | 21:00
26 | Bhangura | 51 | 19:30 | 92 | Kushtia | 160 | 19:00 | 158 | Shahmirpur | 56 | 18:00
27 | Bheramara(GK) | 75 | 20:00 | 93 | Lalbag | 70 | 16:00 | 159 | Shariatpur | 92 | 22:00
28 | Bhulta | 232 | 19:00 | 94 | Lalmonirhat | 71 | 19:30 | 160 | Sherpur | 144 | 21:00
29 | Bog-Sherpur | 72 | 22:00 | 95 | MI_Cement | 18.2 | 21:00 | 161 | Shikalbaha | 22 | 00:00
30 | Bogura | 194 | 19:30 | 96 | Madanganj | 48 | 00:00 | 162 | Shitalakhya | 93.2 | 16:00
31 | Borhanuddin | 93 | 22:00 | 97 | Madaripur | 122 | 22:00 | 163 | Sholosohor | 48 | 16:00
32 | Brahmanbaria | 134 | 21:00 | 98 | Madartek | 84.73 | 23:00 | 164 | Shyampur | 182 | 12:00
33 | Cantonment | 150 | 13:00 | 99 | Madunaghat | 57 | 18:00 | 165 | Siddhirganj | 134 | 12:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 72 | 19:30 | 166 | Sirajganj | 120 | 00:00
35 | Chandpur | 74 | 21:00 | 101 | Mahasthangarh | 96 | 22:00 | 167 | Sonargaon | 134 | 23:00
36 | Chandraghona | 37 | 19:30 | 102 | Manikganj | 141 | 19:30 | 168 | Sreemongol | 82 | 23:00
37 | Chapai | 81 | 21:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 105 | 20:00
38 | Charsaidpur | 81 | 01:00 | 104 | Matarbari | 50 | 21:00 | 170 | Srinagar | 52 | 22:00
39 | Chauddagram | 75 | 00:00 | 105 | Matuail | 67 | 15:00 | 171 | Sunamganj | 54 | 21:00
40 | Chhatak | 31 | 19:00 | 106 | Millgate | 105 | 16:00 | 172 | Sylhet | 39 | 20:00
41 | Chowmuhani | 231 | 20:00 | 107 | Mirpur | 152 | 18:30 | 173 | Sylhet-132 | 135 | 19:00
42 | Chuadanga | 127 | 22:00 | 108 | Mirsorai | 18 | 15:00 | 174 | TK | 35 | 19:00
43 | Coxsbazar | 134 | 19:30 | 109 | Mirzapur | 52 | 12:00 | 175 | Tangail | 188 | 12:00
44 | Cumilla(N) | 169 | 00:00 | 110 | Mithapukur | 67 | 23:00 | 176 | Thakurgaon | 114 | 19:30
45 | Cumilla(S) | 176 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 152 | 18:30
46 | Daudkandi | 151 | 00:00 | 112 | Mogbazar | 164.7 | 16:00 | 178 | Ullahpara | 46 | 13:00
47 | Dhaka | 70 | 13:00 | 113 | Mongla | 37 | 15:00 | 179 | Ullon | 42 | 00:00
48 | Dhamrai | 136 | 18:30 | 114 | Motijheel | 44 | 13:00 | 180 | Uttara | 104 | 16:00
49 | Dhanmondi | 170.6 | 13:00 | 115 | Muktagacha | 40 | 19:30 | 181 | UttaraNew | 54 | 00:00
50 | Dohazari | 111 | 22:00 | 116 | Munshiganj | 118 | 23:00 | 182 | Zigatola | 86 | 16:00
51 | Faridpur | 187 | 23:00 | 117 | Muradnagar | 29 | 19:30
52 | Fatullah | 110 | 15:00 | 118 | Mymensingh | 219 | 19:00
53 | Fenchuganj | 39 | 19:00 | 119 | Naogaon | 157 | 22:00
54 | Feni | 110 | 23:00 | 120 | Narail | 62 | 19:30
55 | GPH | 20 | 19:00 | 121 | Narinda | 81 | 12:00
56 | Ghatail | 80 | 13:00 | 122 | Narshingdi | 189 | 00:00
57 | Ghorashal | 18 | 09:00 | 123 | Natore | 183 | 22:00
58 | Ghorashal-230 | 100 | 23:00 | 124 | Nawabganj | 66.6 | 22:00
59 | Goalpara | 42 | 13:00 | 125 | Netrakona | 120 | 00:00
60 | Gollamari | 104 | 00:00 | 126 | New | 92.8 | 16:00
61 | Gopalganj | 113 | 19:30 | 127 | Niamatpur | 119 | 20:00
62 | Gulshan | 144 | 15:00 | 128 | Noapara | 50 | 19:30
63 | Halishahar | 76 | 11:00 | 129 | PHP | 5 | 01:00
64 | HaripurSBU | 177 | 10:00 | 130 | Pabna | 122 | 18:30
65 | Hasnabad | 94 | 23:00 | 131 | Palashbari | 128 | 22:00
66 | Hathazari | 83 | 00:00 | 132 | Panchagarh | 60 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15517.9 | 251 |  | 15780.2
1:00 | 15014.7 | 235 |  | 15260.7
2:00 | 14621.7 | 219 |  | 14850.7
3:00 | 14275.7 | 196 |  | 14480.7
4:00 | 13955.7 | 186 |  | 14149.7
5:00 | 13607.5 | 156 |  | 13770.5
6:00 | 13119.71 | 116 |  | 13240.93
7:00 | 12968.56 | 80 |  | 13052.56
8:00 | 13037.02 | 118 |  | 13160.02
9:00 | 13271.08 | 130 |  | 13407.08
10:00 | 13712.93 | 104 |  | 13821.93
11:00 | 14382.01 | 129 |  | 14517.01
12:00 | 14594.67 | 131 |  | 14731.67
13:00 | 14818.49 | 133 |  | 14957.49
14:00 | 14852.35 | 125 |  | 14983.35
15:00 | 14887.79 | 158 |  | 15052.79
16:00 | 14947.2 | 172 |  | 15127.2
17:00 | 14537.77 | 111 |  | 14653.77
18:00 | 14166.6 | 107 |  | 14278.6
19:00 | 16009.92 | 136 |  | 16151.92
19:30 | 16365.8 | 139 |  | 16510.8
20:00 | 16222.45 | 123 |  | 16351.45
21:00 | 16155.58 | 111 |  | 16271.58
22:00 | 16071.97 | 153 |  | 16231.97
23:00 | 15964.98 | 140 |  | 16110.98
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8574.7 | 6943.2 | 15517.9 | DAILY GENERATION CURVE
00:30 | 8429.2 | 6837.1 | 15266.3
01:00 | 8283.7 | 6731 | 15014.7 | 24-04-2025
01:30 | 8163.2 | 6655 | 14818.2
02:00 | 8042.7 | 6579 | 14621.7
02:30 | 7976.7 | 6472 | 14448.7
03:00 | 7910.7 | 6365 | 14275.7
03:30 | 7788.2 | 6327.5 | 14115.7
04:00 | 7665.7 | 6290 | 13955.7
04:30 | 7523.6 | 6258 | 13781.6
05:00 | 7381.5 | 6226 | 13607.5
05:30 | 7235.44 | 6128.165 | 13363.605
06:00 | 7089.38 | 6030.33 | 13119.71
06:30 | 7107.73 | 5936.405 | 13044.135
07:00 | 7126.08 | 5842.48 | 12968.56
07:30 | 7127.81 | 5874.98 | 13002.79
08:00 | 7129.54 | 5907.48 | 13037.02
08:30 | 7160.335 | 5993.715 | 13154.05
09:00 | 7191.13 | 6079.95 | 13271.08
09:30 | 7399.85 | 6092.155 | 13492.005
10:00 | 7608.57 | 6104.36 | 13712.93
10:30 | 7839.655 | 6207.815 | 14047.47
11:00 | 8070.74 | 6311.27 | 14382.01
11:30 | 8085.915 | 6402.425 | 14488.34
12:00 | 8101.09 | 6493.58 | 14594.67
12:30 | 8180.39 | 6526.19 | 14706.58
13:00 | 8259.69 | 6558.8 | 14818.49
13:30 | 8294.955 | 6540.465 | 14835.42
14:00 | 8330.22 | 6522.13 | 14852.35
14:30 | 8352.885 | 6517.185 | 14870.07
15:00 | 8375.55 | 6512.24 | 14887.79
15:30 | 8429.56 | 6487.935 | 14917.495
16:00 | 8483.57 | 6463.63 | 14947.2
16:30 | 8420.035 | 6322.45 | 14742.485
17:00 | 8356.5 | 6181.27 | 14537.77
17:30 | 8300.645 | 6051.54 | 14352.185
18:00 | 8244.79 | 5921.81 | 14166.6
18:30 | 8760.495 | 6327.765 | 15088.26
19:00 | 9276.2 | 6733.72 | 16009.92
19:30 | 9390.2 | 6975.6 | 16365.8
20:00 | 9346.2 | 6876.25 | 16222.45
20:30 | 9327.7 | 6861.315 | 16189.015 |  | Executive Engineer
21:00 | 9309.2 | 6846.38 | 16155.58 |  | Network Operation Division
21:30 | 9278.8 | 6834.975 | 16113.775
22:00 | 9248.4 | 6823.57 | 16071.97
22:30 | 9204.9 | 6813.575 | 16018.475
23:00 | 9161.4 | 6803.58 | 15964.98

## En-Curve
QF-LDC-12
Date | 24-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3655 | 2345.5 | 915 | 0 | 48 | 1360 | 40 | 3868 | 0 | 693 | 2581.4 | 0 | 0 | 12 | 251 | DAILY ENERGY CURVE
00:30 | 3662 | 2335.5 | 915.5 | 0 | 44 | 1362.5 | 40 | 3867.5 | 0 | 655 | 2373.3 | 0 | 0 | 11 | 243 | 24-04-2025
01:00 | 3669 | 2325.5 | 916 | 0 | 40 | 1365 | 40 | 3867 | 0 | 617 | 2165.2 | 0 | 0 | 10 | 235
01:30 | 3660 | 2328.5 | 916 | 0 | 40 | 1364.5 | 40 | 3843 | 0 | 555 | 2060.2 | 0 | 0 | 11 | 227 | Energy Generated | 355.1003 |  | MKWHr
02:00 | 3651 | 2331.5 | 916 | 0 | 40 | 1364 | 40 | 3819 | 0 | 493 | 1955.2 | 0 | 0 | 12 | 219 | Energy not Served | 3.52 |  | MKWHr
02:30 | 3650.5 | 2334.5 | 916 | 0 | 40 | 1364.5 | 40 | 3777.5 | 0 | 442.5 | 1865.7 | 0 | 0 | 17.5 | 207.5 | Total Energy Requirement | 358.6203 |  | MKWHr
03:00 | 3650 | 2337.5 | 916 | 0 | 40 | 1365 | 40 | 3736 | 0 | 392 | 1776.2 | 0 | 0 | 23 | 196
03:30 | 3647 | 2335.5 | 916.5 | 0 | 39 | 1361.5 | 40 | 3735 | 0 | 351 | 1666.2 | 0 | 0 | 24 | 191
04:00 | 3644 | 2333.5 | 917 | 0 | 38 | 1358 | 40 | 3734 | 0 | 310 | 1556.2 | 0 | 0 | 25 | 186
04:30 | 3660.5 | 2340.5 | 917 | 0 | 37 | 1361.5 | 40 | 3733.5 | 0 | 262 | 1405.6 | 0 | 0 | 24 | 171
05:00 | 3677 | 2347.5 | 917 | 0 | 36 | 1365 | 40 | 3733 | 0 | 214 | 1255 | 0 | 0 | 23 | 156
05:30 | 3594.5 | 2327.25 | 917 | 0 | 36 | 1366 | 40 | 3735.5 | 3.855 | 205.5 | 1116 | 0 | 0 | 22 | 136
06:00 | 3512 | 2307 | 917 | 0 | 36 | 1367 | 40 | 3738 | 7.71 | 197 | 977 | 0 | 0 | 21 | 116
06:30 | 3566.5 | 2316.5 | 916.5 | 0 | 35 | 1364.5 | 40 | 3625.5 | 46.135 | 197 | 919 | 0 | 0 | 17.5 | 98
07:00 | 3621 | 2326 | 916 | 0 | 34 | 1362 | 40 | 3513 | 84.56 | 197 | 861 | 0 | 0 | 14 | 80
07:30 | 3690 | 2339.5 | 896.5 | 0 | 34 | 1363 | 40 | 3459 | 133.79 | 199 | 836 | 0 | 0 | 12 | 99
08:00 | 3759 | 2353 | 877 | 0 | 34 | 1364 | 40 | 3405 | 183.02 | 201 | 811 | 0 | 0 | 10 | 118
08:30 | 3748.5 | 2345.5 | 876.5 | 0 | 34 | 1357.5 | 40 | 3433.5 | 258.05 | 219.5 | 815.5 | 0 | 0 | 25.5 | 124
09:00 | 3738 | 2338 | 876 | 0 | 34 | 1351 | 40 | 3462 | 333.08 | 238 | 820 | 0 | 0 | 41 | 130
09:30 | 3736.5 | 2342 | 899.5 | 0 | 33 | 1359 | 40 | 3375.5 | 416.005 | 293 | 956 | 0 | 0 | 41.5 | 117
10:00 | 3735 | 2346 | 923 | 0 | 32 | 1367 | 40 | 3289 | 498.93 | 348 | 1092 | 0 | 0 | 42 | 104
10:30 | 3663 | 2352 | 923 | 0 | 33 | 1362.5 | 40 | 3299 | 540.97 | 377.5 | 1414 | 0 | 0 | 42.5 | 116.5
11:00 | 3591 | 2358 | 923 | 0 | 34 | 1358 | 40 | 3309 | 583.01 | 407 | 1736 | 0 | 0 | 43 | 129
11:30 | 3602.5 | 2358.5 | 923 | 0 | 35 | 1361.5 | 40 | 3305.5 | 609.34 | 398 | 1811.5 | 0 | 0 | 43.5 | 130
12:00 | 3614 | 2359 | 923 | 0 | 36 | 1365 | 40 | 3302 | 635.67 | 389 | 1887 | 0 | 0 | 44 | 131
12:30 | 3607 | 2390 | 923.5 | 0 | 38 | 1363.5 | 40 | 3349 | 597.58 | 399.5 | 1956 | 0 | 0 | 42.5 | 132
13:00 | 3600 | 2421 | 924 | 0 | 40 | 1362 | 40 | 3396 | 559.49 | 410 | 2025 | 0 | 0 | 41 | 133
13:30 | 3570 | 2423.75 | 921.5 | 0 | 39 | 1366.33 | 40 | 3419.5 | 531.34 | 395.5 | 2091.5 | 0 | 0 | 37 | 129
14:00 | 3540 | 2426.5 | 919 | 0 | 38 | 1370.66 | 40 | 3443 | 503.19 | 381 | 2158 | 0 | 0 | 33 | 125
14:30 | 3588.5 | 2437 | 919 | 0 | 38 | 1366.895 | 40 | 3436 | 463.175 | 383 | 2165.5 | 0 | 0 | 33 | 141.5
15:00 | 3637 | 2447.5 | 919 | 0 | 38 | 1363.13 | 40 | 3429 | 423.16 | 385 | 2173 | 0 | 0 | 33 | 158
15:30 | 3624 | 2434.5 | 919 | 0 | 38 | 1359.915 | 40 | 3432.5 | 347.08 | 414 | 2278.5 | 0 | 0 | 30 | 165
16:00 | 3611 | 2421.5 | 919 | 0 | 38 | 1356.7 | 40 | 3436 | 271 | 443 | 2384 | 0 | 0 | 27 | 172
16:30 | 3598 | 2404 | 919.5 | 0 | 39 | 1357.71 | 40 | 3383.5 | 189.925 | 505.5 | 2282.85 | 0 | 0 | 22.5 | 141.5
17:00 | 3585 | 2386.5 | 920 | 0 | 40 | 1358.72 | 40 | 3331 | 108.85 | 568 | 2181.7 | 0 | 0 | 18 | 111
17:30 | 3508 | 2313.75 | 920 | 0 | 39 | 1311.32 | 40 | 3318 | 62.415 | 609 | 2213.2 | 0 | 0 | 17.5 | 109
18:00 | 3431 | 2241 | 920 | 0 | 38 | 1263.92 | 40 | 3305 | 15.98 | 650 | 2244.7 | 0 | 0 | 17 | 107
18:30 | 3566.5 | 2405.25 | 899.5 | 0 | 41 | 1311.82 | 40 | 3512.5 | 7.99 | 723.5 | 2560.7 | 0 | 0 | 19.5 | 121.5
19:00 | 3702 | 2569.5 | 879 | 0 | 44 | 1359.72 | 40 | 3720 | 0 | 797 | 2876.7 | 0 | 0 | 22 | 136
19:30 | 3688 | 2527.5 | 870 | 0 | 44 | 1351.6 | 40 | 3889 | 0 | 850 | 3084.7 | 0 | 0 | 21 | 139
20:00 | 3665 | 2516.5 | 800 | 0 | 44 | 1359.05 | 40 | 3877 | 0 | 830 | 3077.9 | 0 | 0 | 13 | 123
20:30 | 3733 | 2525.5 | 800 | 0 | 44 | 1360.615 | 40 | 3900.5 | 0 | 828 | 2943.4 | 0 | 0 | 14 | 117
21:00 | 3801 | 2534.5 | 800 | 0 | 44 | 1362.18 | 40 | 3924 | 0 | 826 | 2808.9 | 0 | 0 | 15 | 111
21:30 | 3761 | 2546.6 | 799.5 | 0 | 45 | 1356.275 | 40 | 3920.5 | 0 | 826.5 | 2801.9 | 0 | 0 | 16.5 | 132
22:00 | 3721 | 2558.7 | 799 | 0 | 46 | 1350.37 | 40 | 3917 | 0 | 827 | 2794.9 | 0 | 0 | 18 | 153
22:30 | 3716 | 2564.2 | 799.5 | 0 | 46 | 1353.375 | 40 | 3921.5 | 0 | 798.5 | 2761.4 | 0 | 0 | 18 | 146.5
23:00 | 3711 | 2569.7 | 800 | 0 | 46 | 1356.38 | 40 | 3926 | 0 | 770 | 2727.9 | 0 | 0 | 18 | 140
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 07:00 | 377 | 23:00 | Payra | 412 | 08:00 | 404 | 23:00
Ashuganj | 397 | 7:00 | 382 | 12:00 | Rahanpur | 418 | 14:00 | 401 | 19:00
Bhulta | 392 | 03:00 | 379 | 12:00 | Rampal | 399 | 08:00 | 379 | 23:00
Bibiana | 387 | 00:00 | 382 | 19:00
BIPTC | 401 | 09:00 | 387 | 16:00
Bogura | 412 | 14:00 | 392 | 19:00
Gopalganj | 395 | 07:00 | 381 | 23:00
Kaliakoir | 385 | 19:00 | 350 | 09:00
Madunaghat | 397 | 20:00 | 379 | 10:00
Meghnaghat | 390 | 06:00 | 383 | 09:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 07:00 | 216 | 12:00 | Keranigonj | 223 | 06:00 | 215 | 12:00
AKSML | 232 | 18:00 | 221 | 10:00 | Khulna(S) | 228 | 08:00 | 212 | 23:00
Aminbazar | 226 | 05:00 | 217 | 12:00 | Madunaghat | 233 | 18:30 | 224 | 08:00
Ashuganj | 229 | 06:00 | 224 | 09:00 | Madunaghat-400 | 232 | 20:00 | 224 | 10:00
Ashuganj-400 | 229 | 06:00 | 224 | 09:00 | Maniknagar | 221 | 03:00 | 213 | 12:00
Baghabari | 232 | 04:00 | 226 | 18:30 | Meghnaghat | 230 | 05:00 | 220 | 14:00
Barapukuria | 223 | 11:00 | 211 | 19:00 | Meghnaghat-400 | 225 | 07:00 | 218 | 12:00
Barapukuria-230 | 223 | 11:00 | 211 | 19:00 | Mirsorai | 234 | 20:00 | 218 | 10:00
Barishal | 231 | 08:00 | 218 | 23:00 | Rajshahi | 232 | 08:00 | 221 | 19:00
Bheramara | 234 | 08:00 | 226 | 17:00 | Rampal | 228 | 08:00 | 212 | 23:00
Bhulta | 222 | 03:00 | 214 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 222 | 11:00 | 218 | 23:00 | Rampura | 222 | 06:00 | 211 | 12:00
BIPTC | 236 | 08:00 | 222 | 19:00 | Shikalbaha | 231 | 18:00 | 221 | 09:00
Bogura | 229 | 14:00 | 218 | 19:00 | Shyampur | 223 | 06:00 | 216 | 12:00
Bogura-400 | 230 | 14:00 | 218 | 19:00 | Siddhirganj | 224 | 05:00 | 216 | 12:00
Borhanuddin | 237 | 08:00 | 224 | 23:00 | Sirajgonj | 240 | 14:00 | 220 | 19:00
BSRM | 230 | 18:30 | 219 | 10:00 | Sreepur | 226 | 06:00 | 221 | 19:00
Cumilla(N) | 223 | 18:00 | 216 | 10:00 | Tongi | 221 | 04:00 | 215 | 09:00
Faridpur | 225 | 08:00 | 213 | 23:00
Fenchuganj | 225 | 07:00 | 218 | 12:00
Ghorashal | 230 | 18:00 | 225 | 00:00
Ghorashal-230 | 222 | 02:00 | 215 | 12:00
Gopalganj | 226 | 07:00 | 217 | 23:00
GPH | 232 | 00:00 | 223 | 09:00
Haripur | 223 | 07:00 | 215 | 12:00
Hasnabad | 226 | 02:00 | 215 | 11:00
Hathazari | 232 | 18:30 | 224 | 08:00
Ishurdi | 236 | 11:00 | 225 | 19:00
Jhenaidah | 228 | 09:00 | 213 | 23:00
Kaliakoir | 224 | 03:00 | 216 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 05:00 | 124 | 12:00 | Madartek | 134 | 06:00 | 124 | 12:00
Agargaon | 133 | 06:00 | 125 | 12:00 | Madunaghat | 134 | 18:00 | 128 | 08:00
Agrabad | 132 | 19:30 | 126 | 09:00 | Magura | 132 | 08:00 | 117 | 19:00
AKS | 130 | 19:00 | 125 | 08:00 | Mahasthangarh | 132 | 11:00 | 123 | 19:00
Aminbazar | 131 | 03:00 | 126 | 13:00 | Manikganj | 125 | 11:00 | 119 | 16:00
Amnura | 139 | 22:00 | 124 | 23:00 | Maniknagar | 129 | 03:00 | 122 | 12:00
Ashuganj | 135 | 03:00 | 133 | 12:00 | Matarbari | 119 | 16:00 | 113 | 07:00
Bagerhat | 131 | 09:00 | 116 | 23:00 | Matuail | 128.5 | 07:00 | 124 | 10:00
Bajitpur | 128 | 05:00 | 123 | 19:00 | Millgate | 127 | 21:00 | 120 | 10:00
Bakulia | 136 | 16:00 | 127 | 09:00 | Mirpur | 131 | 06:00 | 122 | 15:00
Banani | 134 | 05:00 | 123 | 12:00 | Mirzapur | 127 | 22:00 | 121 | 13:00
Bangabhaban | 129 | 04:00 | 122 | 12:00 | Mithapukur | 132 | 03:00 | 119 | 19:00
Barapukuria | 135 | 11:00 | 126 | 19:00 | MI_Cement | 133 | 00:00 | 124 | 12:00
Barguna | 133 | 07:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 129 | 07:00 | 119 | 23:00 | Mogbazar | 135 | 06:00 | 124 | 13:00
Barishal-230 | 129 | 08:00 | 120 | 23:00 | Mongla | 132 | 08:00 | 118 | 23:00
Baroaulia | 133 | 18:00 | 129 | 11:00 | Motijheel | 129 | 04:00 | 122 | 12:00
Baroirhat | 127 | 18:00 | 119 | 02:00 | Muktagacha | 129 | 18:00 | 117 | 14:00
Bashundhara | 134 | 04:00 | 120 | 15:00 | Munshiganj | 129 | 06:00 | 124 | 10:00
BashundharaCement | 129 | 20:00 | 124 | 10:00 | Muradnagar | 127 | 18:00 | 118 | 23:00
Beanibazar | 130 | 06:00 | 125 | 19:00 | Mymensingh | 130 | 00:00 | 113 | 21:00
Benapole | 130 | 07:00 | 114 | 23:00 | Naogaon | 127 | 16:00 | 119 | 19:00
Bhaluka | 129 | 04:00 | 124 | 19:00 | Narail | 132 | 08:00 | 116 | 19:00
Bhandaria | 123 | 10:00 | 109 | 23:00 | Narinda | 129 | 03:00 | 122 | 12:00
Bhangura | 131 | 05:00 | 127 | 19:00 | Narshingdi | 126 | 07:00 | 115 | 19:00
Bheramara | 134 | 06:00 | 126 | 19:00 | Natore | 131 | 11:00 | 125 | 19:00
Bheramara(GK) | 134 | 08:00 | 125 | 19:00 | Nawabganj | 132 | 06:00 | 126 | 12:00
Bhulta | 124 | 21:00 | 119 | 12:00 | Netrakona | 122 | 07:00 | 113 | 19:00
Bog-Sherpur | 131 | 14:00 | 122 | 07:00 | New | 128 | 03:00 | 122 | 08:00
Bogura | 135 | 16:00 | 128 | 07:00 | Niamatpur | 137 | 01:00 | 130 | 19:30
Bogura-230 | 135 | 14:00 | 127 | 19:00 | Noapara | 132 | 08:00 | 120 | 23:00
Brahmanbaria | 129 | 08:00 | 121 | 19:00 | Pabna | 134 | 09:00 | 127 | 19:00
Cantonment | 132 | 04:00 | 124 | 15:00 | Palashbari | 128 | 01:00 | 117 | 19:00
Chandina | 129 | 18:00 | 123 | 12:00 | Panchagarh | 137 | 02:00 | 120 | 07:00
Chandpur | 130 | 18:00 | 122 | 06:00 | Patuakhali | 133 | 16:00 | 129 | 22:00
Chandraghona | 133 | 19:30 | 127 | 10:00 | Payra | 135 | 18:00 | 131 | 23:00
Chapai | 132 | 11:00 | 126 | 19:00 | PHP | 125 | 18:00 | 117 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 20:00 | 124 | 12:00 | Postogola | 131 | 04:00 | 126 | 12:00
Chauddagram | 126 | 18:00 | 119 | 06:00 | Purbachal | 134 | 05:00 | 123 | 11:00
Chhatak | 130 | 06:00 | 124 | 18:00 | Purbasadipur | 134 | 12:00 | 118 | 07:00
Chowmuhani | 118 | 17:00 | 113 | 00:00 | Rahanpur | 138 | 12:00 | 132 | 19:00
Chuadanga | 130 | 08:00 | 114 | 19:00 | Rahanpur-400 | 138 | 02:00 | 132 | 19:00
Coxsbazar | 117 | 14:00 | 113 | 01:00 | Rahim | 129 | 07:00 | 124 | 10:00
Cumilla(N) | 129 | 18:00 | 123 | 10:00 | Rajbari | 132 | 08:00 | 123 | 23:00
Cumilla(S) | 133 | 02:00 | 121 | 12:00 | Rajendrapur | 132 | 02:00 | 123 | 10:00
Daudkandi | 125 | 18:00 | 114 | 21:00 | Rajshahi | 132 | 18:30 | 126 | 12:00
Dhaka | 133 | 02:00 | 124 | 12:00 | Rajshahi-230 | 133 | 09:00 | 118 | 19:00
Dhamrai | 130 | 00:00 | 124 | 09:00 | Ramganj | 124 | 18:00 | 112 | 02:00
Dhanmondi | 134.5 | 06:00 | 124 | 12:00 | Rampur | 132 | 18:00 | 125 | 10:00
Dohazari | 129 | 17:00 | 123 | 10:00 | Rampura | 134 | 06:00 | 123 | 13:00
Faridpur | 133 | 08:00 | 127 | 23:00 | Rangamati | 131 | 18:00 | 127 | 10:00
Fatullah | 130 | 06:00 | 125 | 10:00 | Rangpur | 131 | 11:00 | 119 | 19:00
Fenchuganj | 135 | 08:00 | 131 | 14:00 | Ruppur | 137 | 03:00 | 131 | 19:00
Feni | 125 | 18:00 | 116 | 01:00 | Saidpur | 131 | 02:00 | 120 | 08:00
Ghatail | 126 | 15:00 | 116 | 14:00 | Satkhira | 131 | 08:00 | 116 | 23:00
Ghorashal | 134 | 20:00 | 131 | 09:00 | Satmasjid | 132 | 06:00 | 124 | 12:00
Goalpara | 136 | 09:00 | 122 | 23:00 | Savar | 132 | 04:00 | 123 | 12:00
Gollamari | 135 | 08:00 | 124 | 23:00 | SevenRings | 134 | 00:00 | 130 | 12:00
Gopalganj | 133 | 08:00 | 124 | 23:00 | ShahCement | 130 | 20:00 | 124 | 12:00
Gopalganj-400 | 135 | 07:00 | 128 | 23:00 | Shahjadpur | 136 | 05:00 | 130 | 19:00
Gulshan | 133 | 04:00 | 124 | 12:00 | Shahjibazar | 133 | 08:00 | 124 | 19:00
Halishahar | 133 | 20:00 | 125 | 10:00 | Shahmirpur | 134 | 19:00 | 128 | 08:00
Haripur | 129 | 04:00 | 125 | 10:00 | Shariatpur | 132 | 07:00 | 123 | 23:00
HaripurSBU | 129 | 08:00 | 125 | 10:00 | Sherpur | 132 | 18:00 | 120 | 14:00
Hasnabad | 131 | 18:00 | 126 | 12:00 | Shikalbaha | 123 | 03:00 | 116 | 10:00
Hathazari | 135 | 19:00 | 128 | 08:00 | Shikalbaha-230 | 136 | 19:00 | 128 | 09:00
Ishurdi | 138 | 08:00 | 131 | 19:00 | Shitalakhya | 133 | 00:00 | 124 | 12:00
Jaldhaka | 130 | 11:00 | 115 | 19:00 | Sholosohor | 132 | 18:00 | 128 | 09:00
Jamalpur | 137 | 18:00 | 122 | 13:00 | Shyampur | 130 | 00:00 | 124 | 12:00
Jashore | 139 | 10:00 | 116 | 23:00 | Shyampur-230 | 129 | 03:00 | 124 | 12:00
Jhenaidah | 133 | 07:00 | 120 | 19:00 | Siddhirganj | 129 | 06:00 | 125 | 09:00
Jhenaidah-230 | 133 | 08:00 | 121 | 19:00 | Sirajganj | 127 | 14:00 | 113 | 08:00
Joydebpur | 135 | 00:00 | 127 | 09:00 | Sonargaon | 129 | 18:00 | 122 | 07:00
Joypurhat | 122 | 16:00 | 113 | 19:00 | Sreemongol | 133 | 08:00 | 124 | 23:00
Juldah | 136 | 19:30 | 127 | 07:00 | Sreepur | 132 | 06:00 | 127 | 19:00
Kabirpur | 130 | 14:00 | 119 | 12:00 | Srinagar | 133 | 07:00 | 126 | 12:00
Kachua | 129 | 18:00 | 120 | 02:00 | SSM | 136 | 00:00 | 130 | 02:00
Kaliakoir | 133 | 19:00 | 124 | 18:30 | Sunamganj | 128 | 00:00 | 122 | 19:30
Kallyanpur | 130 | 05:00 | 123 | 15:00 | Sylhet | 131 | 07:00 | 127 | 16:00
Kalurghat | 133 | 18:00 | 128 | 10:00 | Sylhet-132 | 131 | 05:00 | 128 | 15:00
Kamrangirchar | 132 | 05:00 | 126 | 12:00 | Tangail | 125 | 18:00 | 115 | 14:00
Kaptai | 133 | 6:00 | 122 | 12:00 | Thakurgaon | 138 | 02:00 | 121 | 07:00
Kasba | 127 | 18:00 | 118 | 22:00 | TK | 135 | 19:30 | 128 | 10:00
Kazla | 129 | 04:00 | 121 | 13:00 | Tongi | 129 | 01:00 | 125 | 09:00
Keranigonj | 134 | 07:00 | 127 | 12:00 | Ullahpara | 127 | 14:00 | 113 | 07:00
Khagrachori | 130 | 18:00 | 125 | 10:00 | Ullon | 133 | 03:00 | 123 | 13:00
Khulna | 133 | 08:00 | 122 | 23:00 | Uttara | 130 | 06:00 | 122 | 12:00
Khulna(S) | 135 | 08:00 | 124 | 23:00 | UttaraNew | 130 | 03:00 | 122 | 12:00
Khulshi | 132 | 19:30 | 124 | 10:00 | Zigatola | 133 | 04:00 | 126 | 13:00
Kishoreganj | 129 | 06:00 | 120 | 18:30
Kodda | 132 | 02:00 | 122 | 09:00
KSRM | 133 | 18:30 | 127 | 09:00
Kulaura | 134 | 07:00 | 130 | 18:30
Kurigram | 132 | 10:00 | 112 | 19:00
Kushtia | 132 | 06:00 | 121 | 19:00
Lalbag | 160 | 19:00 | 126 | 12:00
Lalmonirhat | 129 | 11:00 | 114 | 19:00
Madanganj | 129 | 20:00 | 124 | 10:00
Madaripur | 133 | 18:00 | 125 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division