## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-04-2025 | during | 27-04-2025 | during | 27-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 365 | 345 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 286 | 335 | 335 | 302 | 302 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 313 | 286 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 90 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 144 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 25 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 18 | 18 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 18 | 20 | 20 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 34 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 295 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 104 | 131 | 149 | 149 | 149 | 149 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 55 | 105 | 105 | 34 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 45 | 67 | 104 | 104 | 51 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 500 | 500 | 584 | 584 | 500 | 500 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 500 | 583 | 583 | 583 | 540 | 540 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 84 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 3267 | 3772 | 5269.9 | 5331.9 | 3826.37 | 3950.37
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 40 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 149 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 87 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 78 | 48 | 72 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 24 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 11 | 7 | 12 | 7 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 59 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 1.33 | 0 | 1.33 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 100 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 54 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 106 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 3 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 108 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 805 | 1218 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 14 | 4 | 3 | 6 | 3 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 268 | 557 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1324 | 3098.5 | 3389.05 | 3405.72 | 3405.05 | 3415.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 190 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 335 | 352 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 330 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 29 | 29 | 46.94 | 46.94 | 33 | 33 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 13 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 175 | 175 | 175 | 175 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 36 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 50 | 108 | 150 | 150 | 130 | 130 | Machine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 38 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 48 | 168 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 32 | 98 | 105.3 | 105.3 | 105.3 | 105.3 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 36 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 58 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1369 | 1705.2 | 2422.29 | 2362.29 | 2150.85 | 2119.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-04-2025 | during | 27-04-2025 | during | 27-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.2 | 0 | 2.2 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 102 | 139 | 200 | 200 | 125 | 150 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 83 | 102 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 45.42 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 21 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 261.42 | 274 | 601.2 | 549 | 311.7 | 321.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 36 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 39 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 104 | 94 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 175 | 174 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 0 | 0 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 375 | 334 | 385 | 385 | 337 | 337 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 0 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1488 | 1110 | 1595 | 1595 | 1521 | 1521
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 544 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 2 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 92.54 | 0 | 91 | 0 | 91 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 380 | 0 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1385.54 | 563 | 3603.2 | 3512.2 | 2456.01 | 2365.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 439 | 0 | 660 | 660 | 660 | 660 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 32 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 11 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 40 | 0 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 602 | 680 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 17 | 220 | 220 | 198 | 198 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 0 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.75 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1462.75 | 775 | 2832.12 | 2831.12 | 2810.12 | 2809.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 33 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 20 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 36 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 183 | 170 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 172 | 166 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 171 | 165 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 380 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.05 | 0 | 5.05 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1368 | 1347.73 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 42.04 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2452.04 | 2706.73 | 3114.58 | 2948.53 | 2991.79 | 2825.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 48 | 0 | 0 | 62 | 62 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 161 | 160 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.1 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 121 | 0 | 68.07 | 0 | 68.07 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 482.1 | 436 | 492.47 | 398 | 554.47 | 460
System Total |  |  |  |  | 27566.2 | 28535.742 | 13491.85 | 14440.43 | 23319.81 | 22933.76 | 20027.36 | 19788.31
Forecast Scenario (27-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15280 |  | 0 |  | 15280
|  |  |  | 1:00 | 14760 |  | 0 |  | 14760
|  |  |  | 2:00 | 14350 |  | 0 |  | 14350
|  |  |  | 3:00 | 13980 |  | 0 |  | 13980
|  |  |  | 4:00 | 13650 |  | 0 |  | 13650
|  |  |  | 5:00 | 13270 |  | 0 |  | 13270
|  |  |  | 6:00 | 12740 |  | 0 |  | 12740
|  |  |  | 7:00 | 12550 |  | 0 |  | 12550
|  |  |  | 8:00 | 12660 |  | 0 |  | 12660
|  |  |  | 9:00 | 12900 |  | 0 |  | 12900
|  |  |  | 10:00 | 13320 |  | 0 |  | 13320
|  |  |  | 11:00 | 14010 |  | 0 |  | 14010
|  |  |  | 12:00 | 14230 |  | 0 |  | 14230
|  |  |  | 13:00 | 14450 |  | 0 |  | 14450
|  |  |  | 14:00 | 14480 |  | 0 |  | 14480
|  |  |  | 15:00 | 14550 |  | 0 |  | 14550
|  |  |  | 16:00 | 14620 |  | 0 |  | 14620
|  |  |  | 17:00 | 14150 |  | 0 |  | 14150
|  |  |  | 18:00 | 13770 |  | 0 |  | 13770
|  |  |  | 18:30 | 14600 |  | 0 |  | 14600
|  |  |  | 19:00 | 15650 |  | 0 |  | 15650
|  |  |  | 19:30 | 16010 |  | 0 |  | 16010
|  |  |  | 20:00 | 15850 |  | 0 |  | 15850
|  |  |  | 21:00 | 15770 |  | 0 |  | 15770
|  |  |  | 22:00 | 15730 |  | 0 |  | 15730
|  |  |  | 23:00 | 15610 |  | 0 |  | 15610
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 14230.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16010.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16010.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 342.33 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:44 hrs on 27-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-04-2025 | [28 empty] | Date: | 26-04-2025 | [28 empty] | Date: | 26-04-2025 | [28 empty] | Date: | 26-04-2025 | [28 empty] | Date: | 26-04-2025 | [16 empty] | Date: | 26-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 33 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 0 | 95 | 31 | 295 | 55 | 35 | 72 | 0 | 84 | 450 | 295 | 500 | 0 | 55 | 0 | 285 | 0 | 0 | 0 | 160 | 22 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 5 | 51 | 24 | 0 | 100 | 100 | 0 | 40 | 0 | 32 | 556 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 613 | 0 | 51 | 112 | 45 | 0 | 352 | 270 | 47 | 197 | 33 | 115 | 50 | 178 | 11 | 20 | 98 | 46 | 52.2 | 0 | 47 | 305 | 320 | 360 | 39 | 38 | 0 | 25 | 6 | 0 | 80 | 30 | 0 | 17 | 174 | 54.3 | 84 | 111 | 0 | 0 | 0 | 6 | 8403.5 | 794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 52 | 1372.5 | 0 | 0 | 0 | 113 | 12 | 94 | 50 | 35 | 52.2 | 0 | 30 | 0 | 177 | 0 | 165 | 0 | 165 | 0 | 414 | 0 | 0 | 0 | 167 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 0 | 220 | 0 | 616 | 1244 | 0 | 6939.7 | 15343.2 | 80.91
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 17 | 0 | 92 | 32 | 245 | 55 | 35 | 17 | 0 | 84 | 450 | 290 | 500 | 0 | 55 | 0 | 272 | 0 | 0 | 0 | 160 | 22 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 10 | 51 | 0 | 0 | 55 | 88 | 0 | 40 | 0 | 28 | 556 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 613 | 0 | 51 | 122 | 16 | 0 | 353 | 320 | 39 | 201 | 33 | 115 | 50 | 178 | 9 | 20 | 98 | 42 | 52.2 | 0 | 40 | 305 | 320 | 350 | 39 | 39 | 0 | 25 | 6 | 0 | 80 | 28 | 0 | 17 | 174 | 23 | 47 | 93 | 0 | 0 | 0 | 12 | 8077.2 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 52 | 1374.7 | 0 | 0 | 0 | 113 | 0 | 60 | 50 | 35 | 34 | 0 | 30 | 0 | 177 | 0 | 162 | 0 | 162 | 0 | 414 | 0 | 0 | 0 | 164 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 0 | 220 | 0 | 616 | 1244 | 0 | 6863.7 | 14940.9 | 80.9
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 17 | 0 | 69 | 32 | 245 | 55 | 35 | 17 | 0 | 50 | 420 | 285 | 500 | 0 | 55 | 0 | 282 | 0 | 0 | 0 | 125 | 22 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 7 | 51 | 0 | 0 | 55 | 50 | 0 | 40 | 0 | 32 | 556 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 555 | 0 | 51 | 122 | 16 | 0 | 354 | 330 | 30 | 201 | 33 | 101 | 50 | 170 | 9 | 20 | 98 | 42 | 52.2 | 0 | 47 | 305 | 320 | 380 | 39 | 39 | 0 | 35 | 0 | 0 | 80 | 28 | 0 | 17 | 174 | 17 | 47 | 93 | 0 | 0 | 0 | 12 | 7870.2 | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 52 | 1369.58 | 0 | 0 | 0 | 113 | 0 | 0 | 50 | 33 | 0 | 0 | 30 | 0 | 177 | 0 | 166 | 0 | 162 | 0 | 380 | 0 | 0 | 0 | 162 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 0 | 220 | 0 | 619 | 1140 | 0 | 6570.58 | 14440.78 | 80.89
03:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 17 | 0 | 69 | 32 | 245 | 55 | 17 | 17 | 0 | 50 | 420 | 300 | 500 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 90 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 4 | 51 | 0 | 0 | 33 | 50 | 0 | 40 | 0 | 32 | 556 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 555 | 0 | 51 | 117 | 8 | 0 | 350 | 330 | 30 | 209 | 33 | 96 | 50 | 172 | 9 | 20 | 98 | 40 | 52.2 | 0 | 47 | 300 | 320 | 385 | 39 | 39 | 0 | 85 | 0 | 0 | 80 | 28 | 0 | 17 | 174 | 17 | 47 | 93 | 0 | 0 | 0 | 12 | 7810.2 | 789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 559 | 52 | 1316.16 | 0 | 0 | 0 | 113 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 168 | 0 | 162 | 0 | 380 | 0 | 0 | 0 | 162 | 0 | 35 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 0 | 220 | 0 | 617 | 1102 | 0 | 6253.16 | 14063.36 | 80.88
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 0 | 69 | 32 | 145 | 15 | 17 | 17 | 0 | 50 | 420 | 303 | 450 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 90 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 13 | 51 | 0 | 0 | 33 | 10 | 0 | 40 | 0 | 32 | 557 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 555 | 0 | 51 | 117 | 8 | 0 | 350 | 330 | 30 | 209 | 33 | 97 | 50 | 176 | 9 | 20 | 88 | 40 | 52.2 | 0 | 47 | 300 | 320 | 385 | 39 | 39 | 0 | 83 | 0 | 0 | 80 | 28 | 0 | 17 | 174 | 17 | 47 | 94 | 0 | 0 | 0 | 12 | 7586.2 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 515 | 17 | 1320.55 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 171 | 0 | 165 | 0 | 380 | 0 | 0 | 0 | 159 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 0 | 220 | 0 | 617 | 1102 | 0 | 6147.55 | 13733.75 | 80.87
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 69 | 32 | 95 | 0 | 17 | 17 | 0 | 16 | 380 | 300 | 450 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 90 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 18 | 51 | 0 | 0 | 22 | 10 | 0 | 40 | 0 | 38 | 556 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 555 | 0 | 51 | 110 | 8 | 0 | 353 | 330 | 30 | 209 | 33 | 95 | 50 | 189 | 9 | 20 | 67 | 38 | 52.2 | 0 | 47 | 300 | 320 | 382 | 39 | 39 | 0 | 90 | 0 | 0 | 80 | 28 | 0 | 17 | 174 | 17 | 47 | 94 | 0 | 0 | 0 | 12 | 7419.2 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516 | 17 | 1319.58 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 171 | 0 | 180 | 0 | 380 | 0 | 0 | 0 | 161 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 0 | 220 | 0 | 615 | 1100 | 0 | 6204.58 | 13623.78 | 80.86
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 0 | 69 | 32 | 95 | 0 | 17 | 17 | 0 | 16 | 380 | 300 | 450 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 52 | 23 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 22 | 10 | 0 | 30 | 0 | 36 | 556 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 552 | 1 | 0 | 90 | 8 | 0 | 354 | 330 | 29 | 201 | 33 | 95 | 50 | 159 | 9 | 20 | 49 | 36 | 52.2 | 3 | 47 | 295 | 320 | 382 | 39 | 39 | 0 | 85 | 0 | 0 | 81 | 28 | 0 | 17 | 175 | 17 | 48 | 96 | 0 | 0 | 1.93 | 12 | 7190.13 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.95 | 408 | 17 | 1318.11 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 174 | 0 | 180 | 0 | 380 | 0 | 0.09 | 0 | 160 | 0 | 35 | 1 | 35 | 0 | 0 | 0 | 3 | 0.24 | 0 | 250 | 10 | 0 | 220 | 0 | 615 | 1064 | 0 | 6003.39 | 13193.52 | 80.85
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 69 | 48 | 95 | 0 | 17 | 17 | 0 | 16 | 340 | 281 | 450 | 0 | 0 | 0 | 272 | 0 | 0 | 4 | 35 | 21 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 20 | 34 | 0 | 0 | 22 | 10 | 1 | 30 | 0 | 30 | 530 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 552 | 4 | 10 | 3 | 8 | 0 | 354 | 330 | 20 | 215 | 33 | 96 | 50 | 109 | 9 | 20 | 28 | 34 | 25 | 19 | 46 | 305 | 320 | 351 | 39 | 39 | 0 | 105 | 0 | 0 | 80 | 30 | 0 | 17 | 174 | 17 | 87 | 105 | 0 | 0 | 10.46 | 12 | 6988.46 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 409 | 35 | 1321.46 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 187 | 0 | 174 | 0 | 177 | 0 | 380 | 0 | 0.3 | 0 | 161 | 0 | 35 | 5 | 34 | 0 | 0 | 0.8 | 22 | 0.14 | 0 | 250 | 8 | 0 | 220 | 0 | 618 | 1000 | 0 | 6006.7 | 12995.16 | 80.84
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 69 | 48 | 95 | 0 | 17 | 17 | 0 | 16 | 340 | 293 | 420 | 0 | 0 | 0 | 287 | 0 | 0 | 9 | 48 | 20 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 9 | 34 | 0 | 0 | 22 | 10 | 2 | 40 | 0 | 8 | 500 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 602 | 9 | 39 | 50 | 8 | 0 | 349 | 330 | 20 | 211 | 31 | 90 | 50 | 89 | 9 | 20 | 29 | 32 | 25 | 28 | 38 | 300 | 320 | 357 | 39 | 40 | 0 | 108 | 0 | 0 | 81 | 30 | 0 | 17 | 175 | 17 | 87 | 106 | 0 | 1 | 13.52 | 12 | 6976.52 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 409 | 17 | 1276 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 4.47 | 187 | 0 | 178 | 0 | 177 | 0 | 350 | 0 | 1.89 | 0 | 161 | 0 | 35 | 13 | 34 | 0 | 0 | 0 | 82 | 0.18 | 0 | 200 | 7 | 0 | 220 | 0 | 616 | 920 | 0 | 5837.54 | 12814.06 | 80.83
09:00 | 0 | 34 | 10 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 11 | 86 | 48 | 130 | 0 | 35 | 17 | 0 | 16 | 400 | 271 | 420 | 0 | 0 | 0 | 270 | 0 | 0 | 20 | 52 | 19.5 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 22 | 17 | 0 | 0 | 22 | 0 | 4 | 40 | 0 | 2 | 405 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 694 | 0 | 51 | 50 | 8 | 0 | 346 | 330 | 13 | 213 | 30 | 93 | 50 | 91 | 9 | 20 | 13 | 32 | 8 | 26 | 38 | 305 | 320 | 349 | 39 | 39 | 0 | 106 | 0 | 0 | 80 | 30 | 0 | 17 | 175 | 17 | 87 | 105 | 0 | 1 | 24.86 | 12 | 7067.36 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.3 | 379 | 0 | 1256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 6.98 | 188 | 0 | 186 | 0 | 181 | 0 | 350 | 0 | 3.34 | 0 | 162 | 0 | 35 | 14 | 34 | 0 | 0 | 4 | 117 | 0.25 | 0 | 150 | 7 | 0 | 220 | 0 | 616 | 690 | 0 | 5600.87 | 12668.23 | 80.82
10:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 104 | 48 | 260 | 0 | 35 | 17 | 0 | 30 | 400 | 296 | 350 | 0 | 0 | 0 | 280 | 0 | 0 | 14 | 70 | 18 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 12 | 0 | 2 | 40 | 0 | 3 | 405 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 744 | 8 | 36 | 50 | 8 | 0 | 347 | 330 | 10 | 182 | 30 | 93 | 50 | 67 | 9 | 18 | 0 | 30 | 8 | 62 | 38 | 300 | 320 | 359 | 39 | 39 | 0 | 105 | 0 | 0 | 80 | 30 | 0 | 17 | 175 | 17 | 77 | 104 | 0 | 2 | 39.7 | 12 | 7231.7 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.71 | 377 | 0 | 1262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 34.21 | 140 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 158 | 0 | 0 | 28 | 34 | 0 | 0 | 4.7 | 85 | 0.65 | 0 | 150 | 11 | 0 | 220 | 0 | 600 | 620 | 0 | 5434.27 | 12665.97 | 80.81
11:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 104 | 48 | 278 | 0 | 35 | 86 | 0 | 40 | 420 | 291 | 400 | 0 | 0 | 0 | 271 | 0 | 0 | 32 | 70 | 18 | 22 | 0 | 450 | 0 | 0 | 0 | 0 | 28 | 17 | 0 | 0 | 12 | 0 | 5 | 40 | 0 | 3 | 362 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 700 | 0 | 36 | 50 | 8 | 0 | 342 | 330 | 10 | 184 | 30 | 72 | 50 | 51 | 8 | 18 | 0 | 34 | 8 | 72 | 38 | 305 | 320 | 387 | 38 | 38 | 0 | 104 | 6 | 0 | 80 | 30 | 0 | 17 | 175 | 17 | 84 | 104 | 0 | 2 | 40.13 | 12 | 7410.13 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.21 | 380 | 0 | 1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 48.68 | 154 | 0 | 168 | 0 | 168 | 0 | 350 | 0 | 4.51 | 0 | 160 | 6 | 0 | 33 | 34 | 0 | 0 | 7.5 | 111 | 0.71 | 0 | 150 | 11 | 0 | 220 | 0 | 495 | 600 | 0 | 5512.61 | 12922.74 | 80.8
12:00 | 0 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 17 | 104 | 48 | 295 | 0 | 35 | 90 | 0 | 45 | 420 | 296 | 500 | 0 | 25 | 0 | 313 | 0 | 0 | 32 | 84 | 18 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 14 | 17 | 0 | 0 | 24 | 3 | 5 | 40 | 0 | 4 | 268 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 805 | 0 | 36 | 50 | 8 | 0 | 335 | 330 | 13 | 199 | 29 | 72 | 50 | 48 | 9 | 18 | 32 | 36 | 8 | 58 | 38 | 300 | 320 | 375 | 38 | 40 | 0 | 104 | 6 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 83 | 102 | 0 | 2 | 45.42 | 12 | 7709.42 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.54 | 380 | 0 | 1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 42.04 | 183 | 0 | 172 | 0 | 171 | 0 | 414 | 0 | 0 | 0 | 161 | 55 | 70 | 34 | 34 | 0 | 0 | 7.1 | 121 | 0.75 | 0 | 150 | 11 | 40 | 220 | 0 | 439 | 602 | 0 | 5782.43 | 13491.85 | 80.79
13:00 | 8 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 0 | 17 | 108 | 48 | 295 | 4 | 35 | 90 | 0 | 48 | 420 | 285 | 540 | 0 | 55 | 0 | 313 | 0 | 0 | 30 | 144 | 18 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 8 | 17 | 0 | 0 | 23 | 100 | 2 | 40 | 0 | 6 | 360 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 800 | 0 | 36 | 50 | 45 | 0 | 336 | 330 | 20 | 184 | 29 | 97 | 70 | 103 | 9 | 18 | 47 | 42 | 17 | 74 | 44 | 305 | 320 | 391 | 38 | 40 | 0 | 100 | 6 | 0 | 82 | 30 | 0 | 17 | 172 | 17 | 74 | 102 | 0 | 2 | 45.64 | 12 | 8186.64 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.15 | 379 | 0 | 1360 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 51.12 | 179 | 0 | 165 | 0 | 168 | 0 | 414 | 0 | 0 | 0 | 165 | 50 | 85 | 12 | 85 | 0 | 0 | 5.5 | 134 | 0.55 | 0 | 150 | 0 | 60 | 220 | 0 | 355 | 601 | 0 | 5746.32 | 13932.96 | 80.78
14:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 18 | 17 | 115 | 48 | 294 | 55 | 35 | 126 | 0 | 50 | 420 | 296 | 540 | 0 | 55 | 0 | 290 | 0 | 0 | 26 | 160 | 18 | 18 | 0 | 500 | 1 | 0 | 0 | 0 | 6 | 17 | 0 | 0 | 23 | 96 | 4 | 37 | 11 | 4 | 360 | 0 | 0 | 0 | 0 | 16 | 145 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | 61 | 0 | 336 | 330 | 20 | 185 | 29 | 114 | 70 | 141 | 9 | 18 | 97 | 42 | 52.2 | 26 | 44 | 300 | 0 | 362 | 36 | 38 | 0 | 96 | 6 | 0 | 81 | 30 | 0 | 17 | 172 | 17 | 74 | 110 | 0 | 2 | 21.81 | 12 | 7997.01 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.67 | 380 | 0 | 1369.48 | 0 | 0 | 0 | 95 | 0 | 0 | 20 | 0 | 0 | 80 | 0 | 48.72 | 174 | 0 | 160 | 0 | 162 | 0 | 414 | 0 | 0 | 0 | 161 | 50 | 114 | 21 | 113 | 0 | 0 | 6.7 | 120 | 0.62 | 0 | 160 | 0 | 60 | 220 | 0 | 355 | 600 | 0 | 5881.19 | 13878.2 | 80.77
15:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 35 | 17 | 130 | 48 | 294 | 55 | 35 | 144 | 0 | 50 | 450 | 291 | 500 | 0 | 55 | 0 | 308 | 0 | 0 | 20 | 160 | 18 | 18 | 0 | 500 | 0 | 0 | 0 | 0 | 4 | 17 | 24 | 0 | 23 | 96 | 3 | 40 | 17 | 2 | 360 | 25 | 0 | 0 | 0 | 17 | 142 | 0 | 0 | 0 | 900 | 0 | 36 | 20 | 61 | 0 | 325 | 330 | 20 | 205 | 29 | 115 | 70 | 179 | 8 | 18 | 97 | 42 | 52.2 | 29 | 42 | 320 | 0 | 365 | 37 | 38 | 0 | 99 | 6 | 0 | 78 | 30 | 0 | 14 | 172 | 17 | 73 | 111 | 0 | 2 | 32.17 | 12 | 8304.37 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.34 | 380 | 0 | 1363.36 | 0 | 0 | 0 | 113 | 0 | 21 | 90 | 0 | 0 | 69 | 0 | 37.08 | 172 | 0 | 160 | 0 | 160 | 0 | 414 | 0 | 0 | 0 | 161 | 47 | 115 | 8 | 106 | 0 | 0 | 3.3 | 85 | 0.48 | 0 | 180 | 2 | 60 | 220 | 0 | 356 | 635 | 0 | 5936.56 | 14240.93 | 80.76
16:00 | 32 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 0 | 130 | 48 | 294 | 55 | 35 | 144 | 0 | 50 | 450 | 295 | 500 | 0 | 55 | 0 | 311 | 0 | 0 | 13 | 160 | 18 | 18 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 102 | 40 | 0 | 84 | 86 | 2 | 40 | 17 | 2 | 360 | 17 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 900 | 0 | 51 | 71 | 63 | 0 | 334 | 330 | 20 | 198 | 29 | 115 | 50 | 168 | 31 | 18 | 88 | 42 | 43 | 30 | 42 | 300 | 0 | 365 | 37 | 40 | 0 | 90 | 6 | 0 | 78 | 30 | 0 | 15 | 170 | 17 | 73 | 119 | 0 | 1 | 23.89 | 12 | 8487.89 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.79 | 430 | 0 | 1362.78 | 0 | 18 | 0 | 113 | 0 | 53 | 113 | 0 | 8 | 43 | 0 | 23.49 | 169 | 0 | 160 | 0 | 159 | 0 | 414 | 0 | 0.41 | 0 | 160 | 47 | 115 | 12 | 113 | 0 | 0 | 2.4 | 65 | 0.32 | 0 | 220 | 11 | 113 | 200 | 0 | 333 | 600 | 0 | 6016.19 | 14504.08 | 80.75
17:00 | 50 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 35 | 0 | 130 | 52 | 294 | 55 | 35 | 144 | 0 | 50 | 420 | 297 | 500 | 0 | 55 | 0 | 315 | 0 | 0 | 6 | 160 | 17.8 | 18 | 0 | 500 | 0 | 0 | 0 | 0 | 2 | 99 | 78 | 0 | 89 | 96 | 1 | 40 | 17 | 5 | 360 | 17 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 900 | 3 | 51 | 95 | 63 | 0 | 338 | 330 | 20 | 209 | 29 | 115 | 50 | 175 | 33 | 18 | 88 | 40 | 48 | 11 | 35 | 310 | 0 | 350 | 36 | 38 | 0 | 92 | 6 | 0 | 81 | 30 | 0 | 15 | 171 | 17 | 82 | 119 | 0 | 0 | 7.47 | 12 | 8550.27 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.23 | 430 | 0 | 1353.76 | 0 | 35 | 0 | 113 | 0 | 53 | 113 | 0 | 8 | 18 | 24 | 9.67 | 169 | 0 | 160 | 0 | 159 | 0 | 414 | 0 | 0.8 | 0 | 162 | 46 | 115 | 6 | 113 | 0 | 0 | 0.9 | 37 | 0.14 | 0 | 220 | 10 | 113 | 220 | 0 | 334 | 600 | 0 | 5969.5 | 14519.77 | 80.74
18:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 35 | 1 | 130 | 63 | 294 | 55 | 35 | 144 | 0 | 68 | 420 | 296 | 450 | 0 | 55 | 0 | 295 | 0 | 0 | 1 | 160 | 17.8 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 4 | 102 | 78 | 0 | 100 | 100 | 0 | 40 | 0 | 5 | 394 | 0 | 0 | 0 | 6 | 0 | 146 | 0 | 0 | 0 | 1070 | 0 | 51 | 100 | 8 | 0 | 334 | 330 | 14 | 210 | 29 | 115 | 50 | 161 | 36 | 20 | 97 | 38 | 52.2 | 1 | 36 | 300 | 0 | 390 | 36 | 40 | 0 | 85 | 6 | 0 | 82 | 30 | 0 | 15 | 170 | 17 | 100 | 128 | 0 | 0 | 1.27 | 12 | 8655.27 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.82 | 0 | 25 | 0 | 113 | 4 | 90 | 50 | 3 | 0 | 1 | 30 | 1.36 | 169 | 0 | 159 | 0 | 159 | 0 | 340 | 0 | 0.12 | 0 | 159 | 47 | 115 | 1 | 113 | 0 | 0 | 0.2 | 5 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 3894.5 | 12549.77 | 80.73
19:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 17 | 130 | 144 | 294 | 55 | 35 | 144 | 0 | 68 | 450 | 262 | 500 | 0 | 55 | 0 | 270 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 530 | 11 | 30 | 0 | 0 | 2 | 102 | 78 | 4 | 100 | 100 | 0 | 40 | 13 | 7 | 556 | 72 | 0 | 1 | 10 | 34 | 150 | 0 | 0 | 0 | 1160 | 0 | 51 | 107 | 8 | 0 | 340 | 330 | 10 | 210 | 29 | 107 | 50 | 174 | 36 | 8 | 97 | 46 | 52.2 | 0 | 38 | 300 | 0 | 350 | 36 | 40 | 0 | 93 | 8 | 0 | 83 | 30 | 0 | 15 | 170 | 21 | 101 | 130 | 0 | 0 | 0 | 12 | 9235.2 | 554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.18 | 0 | 33 | 0 | 113 | 4 | 90 | 100 | 23 | 25 | 0 | 30 | 0 | 169 | 0 | 160 | 0 | 159 | 0 | 320 | 0 | 0 | 0 | 161 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 3587.18 | 12822.38 | 80.72
19:30 | 98 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 17 | 130 | 142 | 294 | 55 | 35 | 144 | 0 | 67 | 420 | 270 | 500 | 0 | 55 | 0 | 268 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 450 | 80 | 49 | 3 | 0 | 0 | 102 | 78 | 17 | 100 | 100 | 0 | 40 | 40 | 9 | 556 | 160 | 0 | 25 | 25.5 | 80 | 150 | 0 | 0 | 0 | 1195 | 0 | 51 | 106 | 8 | 0 | 356 | 330 | 10 | 216 | 29 | 115 | 50 | 158 | 36 | 20 | 97 | 46 | 52.2 | 0 | 44 | 270 | 0 | 350 | 36 | 39 | 0 | 95 | 8 | 0 | 83 | 30 | 0 | 15 | 170 | 54.5 | 101 | 130 | 0 | 0 | 0 | 12 | 9511.2 | 546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.34 | 0 | 33 | 0 | 113 | 11 | 90 | 113 | 32 | 34 | 0 | 30 | 0 | 170 | 0 | 165 | 0 | 159 | 0 | 350 | 0 | 0 | 0 | 161 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 220 | 0 | 3876.34 | 13387.54
20:00 | 98 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 35 | 17 | 131 | 142 | 294 | 55 | 35 | 144 | 0 | 67 | 420 | 265 | 583 | 0 | 55 | 0 | 272 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 480 | 67 | 49 | 18 | 0 | 2 | 102 | 78 | 26 | 100 | 100 | 0 | 40 | 81 | 0 | 557 | 160 | 0 | 27 | 25.5 | 87 | 150 | 0 | 0 | 0 | 1212 | 0 | 51 | 105 | 16 | 0 | 354 | 330 | 10 | 214 | 29 | 115 | 50 | 168 | 36 | 20 | 97 | 46 | 52.2 | 0 | 45 | 300 | 0 | 384 | 36 | 39 | 0 | 95 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 54.5 | 101 | 130 | 0 | 0 | 0 | 12 | 9796.2 | 543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.72 | 0 | 33 | 0 | 113 | 18 | 90 | 113 | 37 | 43 | 0 | 30 | 0 | 170 | 0 | 165 | 0 | 162 | 0 | 414 | 0 | 0 | 0 | 162 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 11 | 0 | 0 | 0 | 0 | 250 | 3 | 4003.72 | 13799.92 | 80.71
21:00 | 90 | 55 | 34 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 35 | 17 | 131 | 144 | 294 | 55 | 35 | 144 | 0 | 67 | 420 | 286 | 583 | 0 | 55 | 0 | 286 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 500 | 108 | 100 | 59 | 0 | 4 | 102 | 78 | 54 | 100 | 100 | 0 | 40 | 106 | 11 | 557 | 160 | 0 | 40 | 25.5 | 87 | 149 | 0 | 0 | 0 | 1218 | 0 | 51 | 108 | 8 | 0 | 352 | 330 | 10 | 190 | 29 | 115 | 50 | 168 | 36 | 20 | 98 | 42 | 52.2 | 0 | 46 | 295 | 0 | 334 | 36 | 39 | 0 | 94 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 21 | 102 | 139 | 0 | 0 | 0 | 12 | 9959.7 | 544 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1347.73 | 0 | 33 | 0 | 113 | 20 | 90 | 113 | 36 | 43 | 0 | 30 | 0 | 170 | 0 | 166 | 0 | 165 | 0 | 380 | 0 | 0 | 0 | 160 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 11 | 0 | 17 | 0 | 0 | 680 | 35 | 4480.73 | 14440.43 | 80.7
22:00 | 50 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 17 | 130 | 47 | 294 | 55 | 35 | 144 | 0 | 67 | 420 | 286 | 583 | 0 | 55 | 0 | 282 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 500 | 108 | 163 | 57 | 0 | 10 | 102 | 62 | 54 | 100 | 100 | 0 | 40 | 106 | 16 | 450 | 160 | 0 | 46 | 25.5 | 87 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 113 | 8 | 0 | 352 | 330 | 10 | 194 | 33 | 115 | 50 | 177 | 38 | 20 | 98 | 44 | 52.2 | 0 | 46 | 320 | 25 | 304 | 36 | 40 | 0 | 88 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 102 | 140 | 0 | 0 | 0 | 12 | 9849.7 | 545 | 0 | 0 | 5 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1359.25 | 0 | 33 | 0 | 113 | 25 | 92 | 113 | 36 | 52.2 | 0 | 30 | 0 | 171 | 0 | 166 | 0 | 165 | 0 | 380 | 0 | 0 | 0 | 161 | 48 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 11 | 0 | 19 | 0 | 0 | 910 | 100 | 4923.45 | 14773.15 | 80.69
23:00 | 32 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 130 | 32 | 294 | 55 | 35 | 144 | 0 | 67 | 350 | 290 | 400 | 0 | 55 | 0 | 290 | 0 | 0 | 0 | 160 | 19 | 18 | 0 | 450 | 108 | 222 | 53 | 0 | 11 | 102 | 54 | 54.36 | 100 | 100 | 0 | 40 | 107 | 21 | 450 | 160 | 0 | 28 | 25.5 | 87 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 113 | 8 | 0 | 300 | 330 | 10 | 198 | 33 | 115 | 50 | 171 | 37 | 20 | 98 | 48 | 52.2 | 0 | 46 | 300 | 40 | 356 | 38 | 40 | 0 | 90 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 102 | 138 | 0 | 0 | 0 | 12 | 9512.06 | 745 | 0 | 0 | 15 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 1362.95 | 0 | 33 | 0 | 113 | 25 | 92 | 113 | 36 | 43 | 0 | 30 | 0 | 171 | 0 | 165 | 0 | 167 | 0 | 414 | 0 | 0 | 0 | 143 | 50 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 8 | 0 | 40 | 0 | 0 | 1160 | 100 | 5327.95 | 14840.01 | 80.68
Total KWH | 560592 | 762240 | 412800 | 0 | 0 | 0 | 0 | 0 | 8812800 | 0 | 0 | 388440 | 233280 | 2529648 | 1336320 | 5782451 | 833615 | 767490 | 1964160 | 0 | 1118400 | 9538000 | 7036829 | 11446965 | 0 | 805966 | 0 | 7073967 | 0 | 0 | 208305 | 2918400 | 472800 | 428040 | 0 | 11239090.91 | 510600 | 692509 | 201600 | 0 | 238080 | 1365467 | 611808 | 223526 | 1281600 | 1415040 | 29863 | 934040 | 613055 | 377760 | 11047272.73 | 851418 | 0 | 180000 | 128406.6 | 562036 | 3434182 | 0 | 0 | 0 | 19756362 | 38745 | 939060 | 2012291 | 501818 | 0 | 8592500 | 7986000 | 458880 | 4894000 | 753192 | 2482560 | 1253970 | 3476160 | 434280 | 441580 | 1687200 | 947520 | 990350 | 450800 | 1012768 | 7407000 | 4393100 | 9116000 | 893000 | 903600 | 0 | 2167855 | 105240 | 0 | 1953600 | 703584 | 0 | 398000 | 3570820 | 476640 | 1851600 | 2676000 | 0 | 13350 | 288410 | 294240 | 197690937.24 | 17901090 | 0 | 0 | 30720 | 64384 | 0 | 0 | 0 | 0 | 0 | 0 | 699840 | 8109091 | 432960 | 32181145 | 0 | 252192 | 0 | 1949664 | 91208 | 814016 | 1265280 | 244925 | 281837 | 692420 | 282000 | 326248 | 4219455 | 0 | 4200364 | 0 | 4225782 | 0 | 9266909 | 0 | 11340 | 0 | 3903000 | 562036 | 1894172 | 186829 | 1890470 | 0 | 0 | 47543.16 | 961920 | 4825 | 304224 | 3861000 | 222125 | 484000 | 4053100 | 0 | 9249984 | 19777454 | 291600 | 135237152.16 | 332928089.4

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13491.85 | MW | 12:00 Hr. | Energy Generated |  |  | 332.9281 |  | MKWHr.
| Day Peak Demand |  |  | 13551.85 | MW | 12:00 Hr. | Energy Unserverd |  |  | 11.64 |  | MKWHr.
| Evening Peak Generation |  |  | 14440.43 | MW | 21:00 Hr. | Energy Demand |  |  | 344.5681 |  | MKWHr.
| Evening Peak Demand |  |  | 15998.43 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.6 |  | °C
| Minimum Generation of the Day |  |  | 12665.97 | MW | 10:00 Hr. | Total Gas Supplied |  |  | 1027.48 |  | MMCFD
| Maximum Generation of the Day |  |  | 15343.2 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.247 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 56.0485 | 0 | 20.4138 | 0 | 0 | 0.2083 | 0 | 0 | 76.6706 | Gas | 143.965 | Gas | 507294394.8047
| Chattogram Zone |  |  | 3.8119 | 30.8036 | 8.6371 | 0 | 0.93404 | 0.068608 | 0 | 0.23808 | 44.4934 | Coal | 76.2662 | Coal | 480151610.36
| Cumilla Zone |  |  | 25.821 | 0 | 12.0956 | 0 | 0 | 0.4508 | 0.94752 | 0 | 39.3149 | HFO | 56.5346 | HFO | 1063749496.162
| Mymensingh Zone |  |  | 0 | 0 | 5.2985 | 0 | 0 | 0.30176 | 0 | 0 | 5.6002 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.6118 | Hydro | 0.93404 | Hydro | 93404
| Khulna Zone |  |  | 0 | 8.1091 | 0.52806 | 0 | 0 | 0.69984 | 17.9011 | 0 | 27.2381 | Solar | 3.9604 | Solar | 63902694.6576
| Barishal Zone |  |  | 4.7592 | 32.8884 | 0.59582 | 0 | 0 | 0.004825 | 0 | 0 | 38.2483 | Import | 51.0298 | Import | 294062069.6
| Rajshahi Zone |  |  | 21.9125 | 0 | 5.1811 | 0 | 0 | 1.03 | 32.1811 | 0 | 60.3048 | Wind | 0.23808 | Wind | 3485491.2
| Rangpur Zone |  |  | 0 | 4.465 | 3.7846 | 0 | 0 | 1.1963 | 0 | 0 | 9.446
| Total |  |  | 143.965 | 76.2662 | 56.5346 | 0 | 0.93404 | 3.9604 | 51.0298 | 0.23808 | 332.9281
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 507294394.8047 |  | Hydro | 93404
|  |  |  | Coal | 480151610.36 |  | Solar | 63902694.6576
|  |  |  | HFO | 1063749496.162 |  | Import | 294062069.6
|  |  |  | HSD | 0 |  | Wind | 3485491.2
[5 empty] | Total: | 241,27,39,160 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 50181.82 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.9011 | Peak Hr Flow | 544.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 26332163.69 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.1811 | Peak Hr Flow | 1347.73 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 274 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.94752 | Peak Hr Flow | 42.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 940 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.0298 | Peak Hr Flow | 1933.73 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 310 |  | 5573
|  |  |  | Chattogram |  | 0 |  | 1498
|  |  |  | Cumilla |  | 250 |  | 1425
|  |  |  | Mymensingh |  | 210 |  | 1303
|  |  |  | Sylhet |  | 80 |  | 589
|  |  |  | Khulna |  | 416 |  | 1855
|  |  |  | Barishal |  | 80 |  | 519
|  |  |  | Rajshahi |  | 75 |  | 1630
|  |  |  | Rangpur |  | 70 |  | 1000
|  |  |  | Total |  | 1491 |  | 15392
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:52 | 16:20 | Chowmuhani 132/33kV S/S TR3-435T HT Scheduled S/D Due to 33KV Bus section of T-03 | [7 empty] | 20.0MW load
|  |  | shutdown taken by BPDB and LPBS & NPBS. | [7 empty] | interrup.
| 08:52 | 16:20 | Chowmuhani 132/33kV S/S TR3-435T LT Scheduled S/D Due to 33KV Bus section of T-03 | [7 empty] | 20.0MW load
|  |  | shutdown taken by BPDB and LPBS & NPBS for maintenance. | [7 empty] | interrup.
| 09:00 |  | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to 33 kv bay extension work.
| 09:00 |  | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to 33 kv bay extension work.
| 09:00 |  | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to 33 kv bay extension work.
| 09:00 |  | Narail 132/33kV S/S TR1 (403-T) LT Scheduled S/D Due to 33 kv bay extension work.
| 09:11 | 21:02 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Scheduled S/D Due to Maintenance
work.
| 09:12 | 21:00 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Scheduled S/D Due to Maintenance
work.
| 09:14 | 21:37 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Project Work S/D Due to 400KV bay extension
work
| 09:14 | 21:37 | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Scheduled S/D Due to Development work
| 09:29 | 16:16 | Pabna 132/33kV S/S T-3 LT Scheduled S/D Due to Oil Leakage Maintenance | [7 empty] | 8.0MW load
interrup.
| 09:30 | 16:15 | Pabna 132/33kV S/S T-3 HT Scheduled S/D Due to Oil Leakage Maintenance | [7 empty] | 8.0MW load
interrup.
| 09:41 | 14:14 | Jamalpur-Mymensingh 132kV Ckt-1 Project Work S/D from Jamalpur 132/33kV end Due to G2g
| 10:05 | 19:28 | Rajbari 132/33kV S/S Bheramara-1 Project Work S/D Due to SAS INTEGRATION WORK.
|  | 10:10 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) HT is restored.
|  | 10:10 | Purbasadipur 132/33kV S/S T-1 Transformer (403T) LT is restored.
|  | 11:26 | Shahjadpur-Ullahpara 132kV Ckt-1 is restored.
| 11:26 | 13:32 | Sirajganj-Ullahpara 132KV Ckt-1 Forced S/D from Ullahpara 132/33kV end Due to Instruction
by ALDC Bogura
| 11:27 | 13:32 | Sirajganj-Ullahpara 132KV Ckt-2 Forced S/D from Ullahpara 132/33kV end Due to Instruction
by ALDC Bogura
| 11:33 | 12:39 | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 Forced S/D from Bogura 230/132kV end Due to Red
Hot Maintenance and from Bog-Sherpur 132/33kVend.
| 12:00 |  | Day peak generation: 13490 MW
| 12:05 | 16:31 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to Emergency maintenance work of 33 kV | [7 empty] | 15.0MW load
|  |  | side. | [7 empty] | interrup.
| 12:07 | 16:30 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to Emergency Maintenance Work of 33 kV | [7 empty] | 15.0MW load
|  |  | side. | [7 empty] | interrup.
| 12:12 | 12:24 | Barishal 132/33kV S/S T-1 (405T) LT Tripped showing Instt.O/C, Instt. E/F relays Due to | [7 empty] | 40.0MW load
|  |  | WZPDCL 33 kV Dopdopia feeder 2 line side loop disconnect | [7 empty] | interrup.
|  | 12:48 | Muktagacha 132/33kV S/S T-2(414T) HT is restored.
|  | 12:53 | Muktagacha 132/33kV S/S T-2(414T) LT is restored.
|  | 12:55 | Barishal-Bhandaria 132 kV Ckt-1 is restored.
|  | 13:05 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
|  | 13:06 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
|  | 13:09 | Bhandaria 132/33kV S/S Transformer-2 HT is restored.
|  | 13:10 | Bhandaria 132/33kV S/S Transformer-2 LT is restored.
|  | 13:10 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 13:11 | 15:13 | Kasba 132/33kV S/S TR-1 LT Scheduled S/D Due to Shutdown taken by PBS
| 13:14 | 15:12 | Kasba 132/33kV S/S TR-1 HT Scheduled S/D Due to Shutdown taken by PBS for Redhot
Maintanace.
| 13:23 |  | Bibiyana South 400 MW Tripped
| 13:25 |  | Bibiyana South 400 MW Tripped with remarks:- gt
| 13:33 |  | Shahjadpur-Ullahpara 132kV Ckt-1 Forced S/D from Ullahpara 132/33kV end Due to
Instruction By ALDC Bogra.
|  | 14:54 | Jhenaidah-Khulna 230kV Ckt-2 is restored.
|  | 14:54 | Jhenaidah-Khulna 230kV Ckt-1 is restored.
| 15:32 | 16:38 | Kasba 132/33kV S/S TR-2 LT Scheduled S/D Due to Shutdown taken by redhot maintenance
| 15:33 | 16:37 | Kasba 132/33kV S/S TR-2 HT Scheduled S/D Due to Shutdown taken by redhot maintenance
|  | 15:49 | Magura 132/33kV S/S T-3 (425T) HT is restored.
| 16:50 | 18:36 | Jaldhaka 132/33kV S/S 416T-2 LT Forced S/D Due to Emergency maintenance work. | [7 empty] | 35.0MW load
interrup.
| 16:51 | 18:35 | Jaldhaka 132/33kV S/S 416T-2 HT Forced S/D Due to Emergency maintenance work | [7 empty] | 35.0MW load
interrup.
| 17:03 | 17:50 | Narshingdi 132/33kV S/S T-4 LT Tripped showing dF/dt, Lockout Relay relays Due to N/A | [7 empty] | 7.0MW load
interrup.
| 17:44 |  | Bhola Nutan Biddut BD LTD Tripped with remarks:- unit-11,unit-12
| 17:45 | 18:19 | Aminbazar 400/230/132kV S/S Gopalganj-1 Tripped showing SEL-421 relays Due to Unknown
| 17:45 | 18:17 | Jashore 132/33kV S/S JH-2(L1) Tripped showing Z1 & Trip ABC relays. | [7 empty] | 107.0MW load
interrup.
| 17:45 | 18:17 | Jashore 132/33kV S/S JH-1(L2) Tripped showing Z1 & Trip ABC relays. | [7 empty] | 107.0MW load
interrup.
| 17:45 |  | Barisal 307 MW Tripped
| 17:45 | 18:25 | Aminbazar 400/230/132kV S/S Gopalganj-2 Tripped showing SEL-421 relays Due to Unknown
| 17:46 |  | Payra 1320 MW Tripped with remarks:- unit-2
| 17:46 | 19:02 | Benapole 132/33kV S/S Transformer-2(416T) LT Tripped showing REF630 relays Due to Under | [7 empty] | 24.0MW load
|  |  | Frequency | [7 empty] | interrup.
| 17:46 | 19:07 | Jashore 132/33kV S/S Cap. Bank-1 Tripped showing Trip ABC relays. | [7 empty] | 107.0MW load
interrup.
| 17:46 | 19:03 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing REF 630 relays Due to Under | [7 empty] | 30.0MW load
|  |  | Frequency | [7 empty] | interrup.
| 17:47 | 18:27 | Madaripur 132/33kV S/S Gopaganj North CKT-04 Tripped showing Distance relays. | [7 empty] | 80.0MW load
interrup.
| 17:48 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
| 17:48 |  | Payra 1320 MW Tripped with remarks:- unit-1
| 17:49 | 20:18 | Barishal 132/33kV S/S 132 kV Capacitor Bank Tripped showing O/V relays Due to O/V
| 17:51 |  | Bhola Nutan Biddut BD LTD Tripped with remarks:- GT--11,GT-12,ST
| 17:58 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
| 18:06 | 18:50 | Rajbari 132/33kV S/S Faridpur -1 Forced S/D Due to Grid fail so ordered by NLDC SD
| 18:06 | 18:49 | Rajbari 132/33kV S/S Faridpur - 2 Forced S/D Due to Ordered by NLDC SD for Grid fail
| 18:10 | 19:36 | Barishal-Barishal(N) 132 kV Ckt-2 Tripped from Barishal 132/33kV end showing O/V , SOTF
relays Due to O/V ,
| 18:12 | 18:26 | Gopalganj(N)-Madaripur 132kV Ckt-2 Tripped from Madaripur 132/33kV end showing Distance
Relay relays Due to None
| 18:12 | 18:27 | Gopalganj(N)-Madaripur 132kV Ckt-3 Tripped from Madaripur 132/33kV end showing Distance
Relay relays.
| 18:12 | 18:26 | Gopalganj(N)-Madaripur 132kV Ckt-1 Tripped from Madaripur 132/33kV end showing Distance
relay relays.
| 18:15 | 19:39 | Gopalganj- Gopalganj(N) 132kV Ckt-2 Tripped from Gopalganj 132/33kV end showing O/V relay
relays.
| 18:15 | 18:39 | Gopalganj 132/33kV S/S Gallamari-1 Tripped showing O/V relay relays Due to None
| 18:15 | 19:39 | Gopalganj (O) - Gopalgan (N) Ckt-1 Tripped from Gopalganj 132/33kV end showing O/V Relay
relays Due to None
| 18:28 | 18:56 | Gopalganj 132/33kV S/S T1 LT Tripped showing O/V relay relays.
| 18:28 | 18:34 | Gopalganj 132/33kV S/S T2 LT Tripped showing O/v relay relays.
| 18:28 | 19:15 | Gollamari 132/33kV S/S E07 Gollamari-Gopalgonj Line - 2 Tripped showing Main-2 Distance
Protection Relay relays Due to Over Voltage
| 18:28 | 18:56 | Gopalganj 132/33kV S/S T1 HT Tripped showing O/v relay relays.
| 18:28 | 18:31 | Gollamari 132/33kV S/S E01 Gollamari-Gopalgonj Line - 1 Tripped showing Main-2 Distance
Protection Relay relays Due to Over Voltage
| 18:28 | 19:48 | Gopalganj 132/33kV S/S Gallamari-2 Tripped showing O/v relay relays.
| 18:28 | 18:48 | Gopalganj 132/33kV S/S Gopalganj 100 MW PS Tripped showing O/v relay relays.
| 18:28 | 18:34 | Gopalganj 132/33kV S/S T2 HT Tripped showing O/v relay relays.
| 18:40 | 19:02 | Madaripur 132/33kV S/S Gopaganj North CKT-04 Tripped showing Distance Relay relays.
| 18:55 |  | Goalpara- Khulna (C) 132kV Ckt-2 Tripped from Khulna (C) end showing 21, (Distance Relay | [7 empty] | 120.0MW load
|  |  | Trip) relays Due to Goal para End fault and from Goalpara 132/33kVend. | [7 empty] | interrup. Khulna
(C) end
| 19:01 |  | Payra 1320 MW Synchronized with remarks:- unit-1
| 19:08 |  | Payra 1320 MW Synchronized with remarks:- unit-2
|  | 20:06 | Baghabari-Ullahpara 132 kV Ckt-1 is restored.
| 20:54 |  | Bhola Nutan Biddut BD LTD Synchronized with remarks:- GT12
| 21:38 |  | Bibiyana South 400 MW Synchronized with remarks:- gt
| 22:32 |  | Rangpur-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing Distance
Relay- TRIP R,Y,B ZM 1 TRIP, ZM 2 TRIP, ZM 3 TRIP, CARRIER RECEV. CARRIER SEND. AR
COMMAND relays Due to Due to Rain and lightning
| 22:44 |  | Rangpur-Saidpur 132kV Ckt-1 Tripped from Saidpur 132/33kV end showing Distance
Relay- Trip R,Y,B PHSEL R,Y,B SOTF ZM 1,2,3 TRIP CARR.SEND relays.
| 22:52 | 23:13 | Barapukuria-Rangpur 132 kV Ckt-1 Tripped from Barapukuria 230/132/33kV end showing
REL-511 relays Due to Thunder storm of Rangpur end
| 22:52 | 23:13 | Barapukuria-Rangpur 132 kV Ckt-2 Tripped from Barapukuria 230/132/33kV end showing
Siprotec 7SA87 relays Due to Thunder storm of Rangpur end
| 22:52 | 23:42 | Lalmonirhat 132/33kV S/S T-1 (425T) LT Forced S/D Due to 132 KV Rangpur - Lalmonirhat | [7 empty] | 22.0MW load
|  |  | Line Trip( From Rangpur Side) | [7 empty] | interrup.
| 22:52 | 23:42 | Lalmonirhat 132/33kV S/S T-2 (415T) LT Forced S/D Due to 132 KV Rangpur - Lalmonirhat | [7 empty] | 22.0MW load
|  |  | Line Trip(From Rangpur Side) | [7 empty] | interrup.
| 22:54 | 23:44 | Kurigram 132/33kV S/S Transformer T-1 (Tr-403T) HT Tripped showing Overcurrent protection
relays.
| 22:54 | 23:44 | Kurigram 132/33kV S/S Transformer T-2 (Tr-413T) HT Tripped showing overcurrent
protection. relays.
| 01:03 |  | Bhola Notun Bidyut ST was sync.
| 01:17 |  | Bhola Notun Bidyut GT-11 was sync.
| 01:54 |  | Bhola 225 MW CCPP GT-1 was sync.
| 02:47 |  | Bhola 225 MW CCPP GT-2 was sync.
| 06:00 |  | Minimum Generation: 12532 MW.
| 06:00 |  | Min. Gen.12534 MW
| 06:35 |  | Bibiyana South 400 MW Synchronized with remarks:- st
| 06:35 |  | Bibiyana South 400MW CCPP ST was sync.
| 07:22 |  | Aminbazar 400/230/132kV S/S Bus-1 (400kV) Scheduled S/D Due to Project Development work
| 07:29 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to Project Work
| 08:00 |  | Rangpur-Saidpur 132kV Ckt-2 Forced S/D from Rangpur 132/33kV end.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | -
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 345 | 8812800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9538000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 286 | 7036829 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 833615 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 286 | 7073967 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 560592 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 388440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 1336320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 767490 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 805966 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 472800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 428040 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 412800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 5782451 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2529648 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 55 | 762240 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 1118400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1964160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 208305 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 233280 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 500 | 11239090.91 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 11446965 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2918400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3772 | 76670598.91
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 128406.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 38745 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 180000 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 934040 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 149 | 3434182 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 562036 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 611808 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 1365467 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1281600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 11 | 377760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 59 | 201600 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 29863 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 100 | 692509 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54 | 223526 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 106 | 613055 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1415040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 510600 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 851418 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1218 | 19756362 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 4 | 238080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 557 | 11047272.73 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 3098.5 | 44493370.33
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 190 | 4894000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 352 | 8592500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 7986000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 29 | 753192 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 458880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 501818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 939060 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 108 | 2012291 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 46 | 1012768 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1253970 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 168 | 3476160 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 42 | 947520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 990350 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 441580 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1687200 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 36 | 434280 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2482560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 450800 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1705.2 | 39314929
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13350 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 139 | 2676000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1851600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 288410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 21 | 476640 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 274 | 5600240
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 893000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 39 | 903600 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 94 | 2167855 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 703584 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1953600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 174 | 3570820 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 398000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 105240 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7407000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 334 | 9116000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 4393100 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1110 | 31611799
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 544 | 17901090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 2 | 30720 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 64384 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 432960 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 699840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 8109091 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 563 | 27238085
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 0 | 9249984 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 32 | 304224 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 222125 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 0 | 484000 | Maintenance
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 680 | 19777454 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 17 | 4053100 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 291600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 0 | 3861000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4825 | -
Barishal Area Total |  |  |  |  | 3585.1 | 775 | 38248312
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 33 | 252192 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 20 | 91208 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 36 | 244925 | Machine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 170 | 4219455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 166 | 4200364 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 165 | 4225782 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 380 | 9266909 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 282000 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 281837 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 814016 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1949664 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1265280 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 11340 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1347.73 | 32181145 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 326248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 692420 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2706.73 | 60304785
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 562036 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3903000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1890470 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 47543.16 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1894172 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 186829 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 961920 | -
Rangpur Area Total |  |  |  |  | 950 | 436 | 9445970.16
Eastern Grid Total |  |  |  |  | 16921.242 | 9959.7 | 197690937.24
Western Grid Total |  |  |  |  | 11614.5 | 4480.73 | 135237152.16
National Grid Total |  |  |  |  | 28535.742 | 14440.43 | 332928089.4
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-04-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9537.7 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4363 | MW
i) Dhaka area |  |  | 5262.6 |  | MW | i) Khulna area |  |  |  | 1439 | MW
ii) Chattogram area |  |  | 1498.1 |  | MW | ii) Barishal area |  |  |  | 439 | MW
iii) Cumilla area |  |  | 1175 |  | MW | iii) Rajshahi area |  |  |  | 1555 | MW
iv) Mymensingh area |  |  | 1093 |  | MW | iv) Rangpur area |  |  |  | 930 | MW
v) Sylhet area |  |  | 509 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13900.7 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 87 | 15:00 | 133 | Patuakhali | 91 | 22:00
2 | AKSML | 24 | 22:00 | 68 | Jaldhaka | 76 | 20:00 | 134 | Payra | 36 | 22:00
3 | Aftabnagar | 42 | 19:00 | 69 | Jamalpur | 117 | 15:00 | 135 | Postogola | 59 | 19:00
4 | Agargaon | 140 | 15:00 | 70 | Jashore | 156 | 22:00 | 136 | Purbachal | 22 | 19:30
5 | Agrabad | 98 | 20:00 | 71 | Jhenaidah | 142 | 20:00 | 137 | Purbasadipur | 145 | 13:00
6 | Amnura | 57 | 00:00 | 72 | Joydebpur | 164 | 21:00 | 138 | Rahanpur | 36 | 00:00
7 | Ashuganj | 130.5 | 20:00 | 73 | Joypurhat | 86 | 01:00 | 139 | Rahim | 47 | 13:00
8 | BSRM | 200 | 08:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 84 | 00:00
9 | Bagerhat | 95 | 23:00 | 75 | KSRM | 14 | 14:00 | 141 | Rajendrapur | 132 | 22:00
10 | Bajitpur | 55 | 22:00 | 76 | Kabirpur | 273 | 09:00 | 142 | Rajshahi | 161 | 20:00
11 | Bakulia | 97 | 20:00 | 77 | Kachua | 92 | 23:00 | 143 | Rajshahi-230 | 100 | 00:00
12 | Banani | 41.4 | 15:00 | 78 | Kallyanpur | 120 | 19:30 | 144 | Ramganj | 112 | 01:00
13 | Bangabhaban | 8 | 11:00 | 79 | Kalurghat | 40 | 12:00 | 145 | Rampur | 45 | 23:00
14 | Barapukuria | 76 | 19:30 | 80 | Kamrangirchar | 71.4 | 19:30 | 146 | Rangamati | 18 | 20:00
15 | Barguna | 26 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 161 | 20:00
16 | Barishal | 123 | 21:00 | 82 | Kasba | 36 | 17:00 | 148 | Ruppur | 6.2 | 15:00
17 | Barishal-230 | 96 | 00:00 | 83 | Kazla | 132 | 18:30 | 149 | SSM | 9 | 23:00
18 | Baroaulia | 63 | 15:00 | 84 | Keranigonj | 84 | 23:00 | 150 | Saidpur | 125 | 20:00
19 | Baroirhat | 74 | 18:30 | 85 | Khagrachori | 36 | 20:00 | 151 | Satkhira | 135 | 01:00
20 | Bashundhara | 215 | 19:00 | 86 | Khulna | 84 | 13:00 | 152 | Satmasjid | 118 | 19:00
21 | BashundharaCement | 8 | 12:00 | 87 | Khulshi | 177 | 16:00 | 153 | Savar | 232 | 12:00
22 | Beanibazar | 82 | 23:00 | 88 | Kishoreganj | 143 | 22:00 | 154 | SevenRings | 18.59 | 17:00
23 | Benapole | 68 | 00:00 | 89 | Kodda | 282 | 21:00 | 155 | ShahCement | 32 | 00:00
24 | Bhaluka | 162 | 22:00 | 90 | Kulaura | 52 | 23:00 | 156 | Shahjadpur | 96 | 19:00
25 | Bhandaria | 60 | 22:00 | 91 | Kurigram | 68 | 20:00 | 157 | Shahjibazar | 115 | 00:00
26 | Bhangura | 52 | 19:30 | 92 | Kushtia | 163 | 19:30 | 158 | Shahmirpur | 63 | 16:00
27 | Bheramara(GK) | 70 | 22:00 | 93 | Lalbag | 70 | 13:00 | 159 | Shariatpur | 86 | 01:00
28 | Bhulta | 235 | 12:00 | 94 | Lalmonirhat | 74 | 19:30 | 160 | Sherpur | 138 | 23:00
29 | Bog-Sherpur | 80 | 23:00 | 95 | MI_Cement | 18.4 | 19:00 | 161 | Shikalbaha | 30 | 20:00
30 | Bogura | 192 | 19:30 | 96 | Madanganj | 44 | 12:00 | 162 | Shitalakhya | 91.9 | 16:00
31 | Borhanuddin | 89 | 00:00 | 97 | Madaripur | 123 | 00:00 | 163 | Sholosohor | 45 | 16:00
32 | Brahmanbaria | 125 | 00:00 | 98 | Madartek | 98.26 | 23:00 | 164 | Shyampur | 172 | 15:00
33 | Cantonment | 144 | 13:00 | 99 | Madunaghat | 54 | 20:00 | 165 | Siddhirganj | 140 | 12:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 76 | 19:00 | 166 | Sirajganj | 138 | 21:00
35 | Chandpur | 83 | 23:00 | 101 | Mahasthangarh | 96 | 23:00 | 167 | Sonargaon | 134 | 11:00
36 | Chandraghona | 38 | 21:00 | 102 | Manikganj | 128 | 00:00 | 168 | Sreemongol | 84 | 23:00
37 | Chapai | 91 | 13:00 | 103 | Maniknagar | 84 | 13:00 | 169 | Sreepur | 107 | 15:00
38 | Charsaidpur | 44 | 01:00 | 104 | Matarbari | 53 | 20:00 | 170 | Srinagar | 54.06 | 23:00
39 | Chauddagram | 76 | 23:00 | 105 | Matuail | 64 | 23:00 | 171 | Sunamganj | 59 | 23:00
40 | Chhatak | 39 | 23:00 | 106 | Millgate | 105 | 15:00 | 172 | Sylhet | 45 | 23:00
41 | Chowmuhani | 216 | 02:00 | 107 | Mirpur | 159 | 18:30 | 173 | Sylhet-132 | 124 | 14:00
42 | Chuadanga | 122 | 00:00 | 108 | Mirsorai | 19 | 11:00 | 174 | TK | 37 | 20:00
43 | Coxsbazar | 136 | 20:00 | 109 | Mirzapur | 50 | 12:00 | 175 | Tangail | 188 | 21:00
44 | Cumilla(N) | 178 | 23:00 | 110 | Mithapukur | 66 | 00:00 | 176 | Thakurgaon | 115 | 19:30
45 | Cumilla(S) | 187 | 23:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 140 | 15:00
46 | Daudkandi | 160 | 23:00 | 112 | Mogbazar | 153.4 | 16:00 | 178 | Ullahpara | 51 | 23:00
47 | Dhaka | 54 | 13:00 | 113 | Mongla | 40 | 15:00 | 179 | Ullon | 44 | 00:00
48 | Dhamrai | 134 | 18:00 | 114 | Motijheel | 44 | 13:00 | 180 | Uttara | 101 | 19:00
49 | Dhanmondi | 159 | 13:00 | 115 | Muktagacha | 38 | 23:00 | 181 | UttaraNew | 53 | 14:00
50 | Dohazari | 104 | 22:00 | 116 | Munshiganj | 117 | 00:00 | 182 | Zigatola | 83 | 15:00
51 | Faridpur | 168 | 00:00 | 117 | Muradnagar | 28 | 00:00
52 | Fatullah | 104 | 12:00 | 118 | Mymensingh | 215 | 23:00
53 | Fenchuganj | 40 | 23:00 | 119 | Naogaon | 167 | 19:30
54 | Feni | 107 | 15:00 | 120 | Narail | 68 | 19:00
55 | GPH | 24 | 10:00 | 121 | Narinda | 83.5 | 13:00
56 | Ghatail | 86 | 13:00 | 122 | Narshingdi | 179 | 01:00
57 | Ghorashal | 17 | 19:00 | 123 | Natore | 191 | 20:00
58 | Ghorashal-230 | 94 | 00:00 | 124 | Nawabganj | 69.6 | 23:00
59 | Goalpara | 80 | 18:30 | 125 | Netrakona | 132 | 00:00
60 | Gollamari | 104 | 22:00 | 126 | New | 93.6 | 15:00
61 | Gopalganj | 122 | 21:00 | 127 | Niamatpur | 119 | 23:00
62 | Gulshan | 120 | 13:00 | 128 | Noapara | 56 | 20:00
63 | Halishahar | 79.5 | 15:00 | 129 | PHP | 3 | 08:00
64 | HaripurSBU | 158 | 09:00 | 130 | Pabna | 121 | 01:00
65 | Hasnabad | 94 | 18:30 | 131 | Palashbari | 138 | 00:00
66 | Hathazari | 90 | 20:00 | 132 | Panchagarh | 64 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15343.2 | 151 |  | 15501
1:00 | 14940.9 | 201 |  | 15150.9
2:00 | 14440.78 | 172 |  | 14620.78
3:00 | 14063.36 | 150 |  | 14220.36
4:00 | 13733.75 | 140 |  | 13879.75
5:00 | 13623.78 | 121 |  | 13749.78
6:00 | 13193.52 | 142 |  | 13341.52
7:00 | 12995.16 | 140 |  | 13141.16
8:00 | 12814.06 | 189 |  | 13012.06
9:00 | 12668.23 | 177 |  | 12853.23
10:00 | 12665.97 | 102 |  | 12772.97
11:00 | 12922.74 | 38 |  | 12962.74
12:00 | 13491.85 | 57 |  | 13551.85
13:00 | 13932.96 | 47 |  | 13981.96
14:00 | 13878.2 | 159 |  | 14044.2
15:00 | 14240.93 | 173 |  | 14421.93
16:00 | 14504.08 | 201 |  | 14714.08
17:00 | 14519.77 | 253 |  | 14783.77
18:00 | 12549.77 | 1579 |  | 14199.77
19:00 | 12822.38 | 2223 |  | 15145.38
19:30 | 13387.54 | 2353 |  | 15846.54
20:00 | 13799.92 | 2009 |  | 15898.92
21:00 | 14440.43 | 1491 |  | 15998.43
22:00 | 14773.15 | 1125 |  | 15949.15
23:00 | 14840.01 | 600 |  | 15467.01
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8403.5 | 6939.7 | 15343.2 | DAILY GENERATION CURVE
00:30 | 8240.35 | 6901.7 | 15142.05
01:00 | 8077.2 | 6863.7 | 14940.9 | 26-04-2025
01:30 | 7973.7 | 6717.14 | 14690.84
02:00 | 7870.2 | 6570.58 | 14440.78
02:30 | 7840.2 | 6411.87 | 14252.07
03:00 | 7810.2 | 6253.16 | 14063.36
03:30 | 7698.2 | 6200.355 | 13898.555
04:00 | 7586.2 | 6147.55 | 13733.75
04:30 | 7502.7 | 6176.065 | 13678.765
05:00 | 7419.2 | 6204.58 | 13623.78
05:30 | 7304.665 | 6103.985 | 13408.65
06:00 | 7190.13 | 6003.39 | 13193.52
06:30 | 7089.295 | 6005.045 | 13094.34
07:00 | 6988.46 | 6006.7 | 12995.16
07:30 | 6982.49 | 5922.12 | 12904.61
08:00 | 6976.52 | 5837.54 | 12814.06
08:30 | 7021.94 | 5719.205 | 12741.145
09:00 | 7067.36 | 5600.87 | 12668.23
09:30 | 7149.53 | 5517.57 | 12667.1
10:00 | 7231.7 | 5434.27 | 12665.97
10:30 | 7320.915 | 5473.44 | 12794.355
11:00 | 7410.13 | 5512.61 | 12922.74
11:30 | 7559.775 | 5647.52 | 13207.295
12:00 | 7709.42 | 5782.43 | 13491.85
12:30 | 7948.03 | 5764.375 | 13712.405
13:00 | 8186.64 | 5746.32 | 13932.96
13:30 | 8091.825 | 5813.755 | 13905.58
14:00 | 7997.01 | 5881.19 | 13878.2
14:30 | 8150.69 | 5908.875 | 14059.565
15:00 | 8304.37 | 5936.56 | 14240.93
15:30 | 8396.13 | 5976.375 | 14372.505
16:00 | 8487.89 | 6016.19 | 14504.08
16:30 | 8519.08 | 5992.845 | 14511.925
17:00 | 8550.27 | 5969.5 | 14519.77
17:30 | 8602.77 | 4932 | 13534.77
18:00 | 8655.27 | 3894.5 | 12549.77
18:30 | 8945.235 | 3740.84 | 12686.075
19:00 | 9235.2 | 3587.18 | 12822.38
19:30 | 9511.2 | 3876.34 | 13387.54
20:00 | 9796.2 | 4003.72 | 13799.92
20:30 | 9877.95 | 4242.225 | 14120.175 |  | Executive Engineer
21:00 | 9959.7 | 4480.73 | 14440.43 |  | Network Operation Division
21:30 | 9904.7 | 4702.09 | 14606.79
22:00 | 9849.7 | 4923.45 | 14773.15
22:30 | 9680.88 | 5125.7 | 14806.58
23:00 | 9512.06 | 5327.95 | 14840.01

## En-Curve
QF-LDC-12
Date | 26-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3597 | 2581 | 794 | 0 | 46 | 1372.5 | 40 | 4124 | 0 | 526 | 2257.7 | 0 | 0 | 5 | 151 | DAILY ENERGY CURVE
00:30 | 3608 | 2558 | 792 | 0 | 44 | 1373.6 | 40 | 4122 | 0 | 479.5 | 2117.45 | 0 | 0 | 7.5 | 176 | 26-04-2025
01:00 | 3619 | 2535 | 790 | 0 | 42 | 1374.7 | 40 | 4120 | 0 | 433 | 1977.2 | 0 | 0 | 10 | 201
01:30 | 3624.5 | 2517 | 789.5 | 0 | 42 | 1372.14 | 40 | 4010.5 | 0 | 388 | 1898.7 | 0 | 0 | 8.5 | 186.5 | Energy Generated | 332.9281 |  | MKWHr
02:00 | 3630 | 2499 | 789 | 0 | 42 | 1369.58 | 40 | 3901 | 0 | 343 | 1820.2 | 0 | 0 | 7 | 172 | Energy not Served | 11.64 |  | MKWHr
02:30 | 3646 | 2525.5 | 789 | 0 | 41 | 1342.87 | 40 | 3851 | 0 | 294 | 1717.2 | 0 | 0 | 5.5 | 161 | Total Energy Requirement | 344.5681 |  | MKWHr
03:00 | 3662 | 2552 | 789 | 0 | 40 | 1316.16 | 40 | 3801 | 0 | 245 | 1614.2 | 0 | 0 | 4 | 150
03:30 | 3668.5 | 2527.5 | 789.5 | 0 | 40 | 1318.355 | 40 | 3778 | 0 | 245 | 1483.2 | 0 | 0 | 8.5 | 145
04:00 | 3675 | 2503 | 790 | 0 | 40 | 1320.55 | 40 | 3755 | 0 | 245 | 1352.2 | 0 | 0 | 13 | 140
04:30 | 3685 | 2488 | 851 | 0 | 39 | 1320.065 | 40 | 3754 | 0 | 245 | 1241.2 | 0 | 0 | 15.5 | 130.5
05:00 | 3695 | 2473 | 912 | 0 | 38 | 1319.58 | 40 | 3753 | 0 | 245 | 1130.2 | 0 | 0 | 18 | 121
05:30 | 3682 | 2441 | 912 | 0 | 37 | 1318.845 | 35 | 3679 | 6.605 | 217.5 | 1062.7 | 0 | 0 | 17 | 131.5
06:00 | 3669 | 2409 | 912 | 0 | 36 | 1318.11 | 30 | 3605 | 13.21 | 190 | 995.2 | 0 | 0 | 16 | 142
06:30 | 3652 | 2389.5 | 912.5 | 0 | 35 | 1319.785 | 30 | 3562.5 | 50.455 | 189 | 935.6 | 0 | 0 | 18 | 141
07:00 | 3635 | 2370 | 913 | 0 | 34 | 1321.46 | 30 | 3520 | 87.7 | 188 | 876 | 0 | 0 | 20 | 140
07:30 | 3624 | 2327 | 889 | 0 | 33 | 1298.73 | 35 | 3464 | 150.38 | 190.5 | 878.5 | 0 | 0 | 14.5 | 164.5
08:00 | 3613 | 2284 | 865 | 0 | 32 | 1276 | 40 | 3408 | 213.06 | 193 | 881 | 0 | 0 | 9 | 189
08:30 | 3610 | 2303.25 | 865 | 0 | 32 | 1266 | 40 | 3252 | 285.395 | 196 | 876 | 0 | 0 | 15.5 | 183
09:00 | 3607 | 2322.5 | 865 | 0 | 32 | 1256 | 40 | 3096 | 357.73 | 199 | 871 | 0 | 0 | 22 | 177
09:30 | 3531 | 2299.75 | 888.5 | 0 | 31 | 1259 | 40 | 3075 | 402.85 | 215.5 | 908.5 | 0 | 0 | 16 | 139.5
10:00 | 3455 | 2277 | 912 | 0 | 30 | 1262 | 40 | 3054 | 447.97 | 232 | 946 | 0 | 0 | 10 | 102
10:30 | 3505 | 2339.5 | 912 | 0 | 32 | 1285 | 40 | 2953.5 | 497.855 | 231.5 | 979 | 0 | 0 | 19 | 70
11:00 | 3555 | 2402 | 912 | 0 | 34 | 1308 | 40 | 2853 | 547.74 | 231 | 1012 | 0 | 0 | 28 | 38
11:30 | 3647.5 | 2480.5 | 912.5 | 0 | 35 | 1338 | 40 | 2856.5 | 544.795 | 238 | 1093.5 | 0 | 0 | 21 | 47.5
12:00 | 3740 | 2559 | 913 | 0 | 36 | 1368 | 40 | 2860 | 541.85 | 245 | 1175 | 0 | 0 | 14 | 57
12:30 | 3769 | 2564 | 912.5 | 0 | 39 | 1364 | 40 | 2860 | 540.405 | 278 | 1334.5 | 0 | 0 | 11 | 52
13:00 | 3798 | 2569 | 912 | 0 | 42 | 1360 | 40 | 2860 | 538.96 | 311 | 1494 | 0 | 0 | 8 | 47
13:30 | 3582 | 2583.5 | 912 | 0 | 42 | 1364.74 | 38.5 | 2888 | 490.24 | 306.5 | 1691.1 | 0 | 0 | 7 | 103
14:00 | 3366 | 2598 | 912 | 0 | 42 | 1369.48 | 37 | 2916 | 441.52 | 302 | 1888.2 | 0 | 0 | 6 | 159
14:30 | 3389 | 2618.5 | 912 | 0 | 42 | 1366.42 | 38.5 | 2967.5 | 398.445 | 323.5 | 1998.7 | 0 | 0 | 5 | 166
15:00 | 3412 | 2639 | 912 | 0 | 42 | 1363.36 | 40 | 3019 | 355.37 | 345 | 2109.2 | 0 | 0 | 4 | 173
15:30 | 3440 | 2629.5 | 912.5 | 0 | 42 | 1363.07 | 40 | 3034.5 | 308.335 | 420.5 | 2179.6 | 0 | 0 | 2.5 | 187
16:00 | 3468 | 2620 | 913 | 0 | 42 | 1362.78 | 40 | 3050 | 261.3 | 496 | 2250 | 0 | 0 | 1 | 201
16:30 | 3469.5 | 2624.4 | 913 | 0 | 41 | 1358.27 | 40 | 3051 | 190.755 | 532.5 | 2290 | 0 | 0 | 1.5 | 227
17:00 | 3471 | 2628.8 | 913 | 0 | 40 | 1353.76 | 40 | 3052 | 120.21 | 569 | 2330 | 0 | 0 | 2 | 253
17:30 | 3367 | 2429.8 | 913 | 0 | 39 | 1371.29 | 40 | 2361 | 66.08 | 618.5 | 2326.1 | 0 | 0 | 3 | 916
18:00 | 3263 | 2230.8 | 913 | 0 | 38 | 1388.82 | 40 | 1670 | 11.95 | 668 | 2322.2 | 0 | 0 | 4 | 1579
18:30 | 3211 | 2293.4 | 733.5 | 0 | 42 | 1375 | 40 | 1797 | 5.975 | 723.5 | 2461.7 | 0 | 0 | 3 | 1901
19:00 | 3159 | 2356 | 554 | 0 | 46 | 1361.18 | 40 | 1924 | 0 | 779 | 2601.2 | 0 | 0 | 2 | 2223
19:30 | 3214 | 2241 | 546 | 0 | 46 | 1362.34 | 40 | 2180 | 0 | 799 | 2959.2 | 0 | 0 | 0 | 2353
20:00 | 3337 | 2378 | 543 | 0 | 46 | 1362.72 | 40 | 2229 | 0 | 812 | 3050.2 | 0 | 0 | 2 | 2009
20:30 | 3289.5 | 2405.5 | 543.5 | 0 | 44 | 1355.225 | 40 | 2446 | 0 | 821 | 3172.45 | 0 | 0 | 3 | 1750
21:00 | 3242 | 2433 | 544 | 0 | 42 | 1347.73 | 40 | 2663 | 0 | 830 | 3294.7 | 0 | 0 | 4 | 1491
21:30 | 3251.5 | 2446 | 544.5 | 0 | 43 | 1353.49 | 40 | 2728 | 0 | 793.5 | 3399.8 | 0 | 0 | 7 | 1308
22:00 | 3261 | 2459 | 545 | 0 | 44 | 1359.25 | 40 | 2793 | 0 | 757 | 3504.9 | 0 | 0 | 10 | 1125
22:30 | 3286 | 2312.5 | 645 | 0 | 46 | 1361.1 | 40 | 2910 | 0 | 762 | 3433.48 | 0 | 0 | 10.5 | 862.5
23:00 | 3311 | 2166 | 745 | 0 | 48 | 1362.95 | 40 | 3027 | 0 | 767 | 3362.06 | 0 | 0 | 11 | 600
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 19:00 | 377 | 18:00 | Payra | 413 | 10:00 | 404 | 00:00
Ashuganj | 409 | 19:00 | 378 | 17:00 | Rahanpur | 416 | 18:30 | 402 | 00:00
Bhulta | 400 | 19:30 | 378 | 12:00 | Rampal | 402 | 19:30 | 383 | 00:00
Bibiana | 395 | 19:00 | 382 | 12:00
BIPTC | 406 | 18:30 | 387 | 15:00
Bogura | 409 | 21:00 | 393 | 07:00
Gopalganj | 403 | 19:00 | 383 | 00:00
Kaliakoir | 374 | 19:00 | 353 | 12:00
Madunaghat | 403 | 21:00 | 389 | 01:00
Meghnaghat | 397 | 19:00 | 384 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 19:00 | 218 | 12:00 | Keranigonj | 228 | 19:00 | 216 | 12:00
AKSML | 240 | 19:30 | 221 | 11:00 | Khulna(S) | 232 | 18:30 | 215 | 00:00
Aminbazar | 229 | 19:00 | 218 | 12:00 | Madunaghat | 238 | 22:00 | 225 | 02:00
Ashuganj | 236 | 19:30 | 223 | 12:00 | Madunaghat-400 | 237 | 20:00 | 225 | 01:00
Ashuganj-400 | 236 | 19:30 | 223 | 12:00 | Maniknagar | 225 | 19:30 | 213 | 12:00
Baghabari | 235 | 17:00 | 225 | 12:00 | Meghnaghat | 236 | 20:00 | 222 | 11:00
Barapukuria | 224 | 18:30 | 211 | 07:00 | Meghnaghat-400 | 230 | 19:30 | 219 | 12:00
Barapukuria-230 | 224 | 18:30 | 211 | 07:00 | Mirsorai | 236 | 19:30 | 220 | 01:00
Barishal | 232 | 09:00 | 220 | 00:00 | Rajshahi | 240 | 18:30 | 220 | 12:00
Bheramara | 240 | 18:00 | 223 | 12:00 | Rampal | 230 | 19:30 | 214 | 00:00
Bhulta | 227 | 19:30 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 19:30 | 218 | 00:00 | Rampura | 226 | 20:00 | 212 | 12:00
BIPTC | 240 | 18:00 | 223 | 12:00 | Shikalbaha | 237 | 22:00 | 221 | 12:00
Bogura | 230 | 18:30 | 218 | 07:00 | Shyampur | 228 | 19:30 | 216 | 12:00
Bogura-400 | 229 | 21:00 | 218 | 07:00 | Siddhirganj | 228 | 19:30 | 216 | 12:00
Borhanuddin | 235 | 06:00 | 218 | 21:00 | Sirajgonj | 239 | 18:00 | 235 | 00:00
BSRM | 236 | 19:30 | 219 | 12:00 | Sreepur | 233 | 19:00 | 221 | 12:00
Cumilla(N) | 228 | 19:30 | 216 | 11:00 | Tongi | 230 | 20:00 | 215 | 12:00
Faridpur | 230 | 19:00 | 215 | 00:00
Fenchuganj | 227 | 08:00 | 218 | 00:00
Ghorashal | 230 | 02:00 | 220 | 09:00
Ghorashal-230 | 229 | 19:30 | 214 | 12:00
Gopalganj | 228 | 09:00 | 218 | 00:00
GPH | 237 | 19:30 | 222 | 12:00
Haripur | 227 | 19:30 | 217 | 11:00
Hasnabad | 228 | 19:00 | 215 | 12:00
Hathazari | 238 | 19:30 | 224 | 04:00
Ishurdi | 241 | 18:00 | 225 | 12:00
Jhenaidah | 237 | 18:00 | 214 | 22:00
Kaliakoir | 233 | 19:30 | 219 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 20:00 | 125 | 12:00 | Madartek | 134 | 04:00 | 124 | 12:00
Agargaon | 133 | 19:00 | 126 | 12:00 | Madunaghat | 137 | 18:30 | 128 | 03:00
Agrabad | 138 | 19:30 | 125 | 12:00 | Magura | 135 | 18:00 | 121 | 00:00
AKS | 134 | 19:00 | 125 | 12:00 | Mahasthangarh | 134 | 18:30 | 123 | 07:00
Aminbazar | 132 | 18:00 | 121 | 10:00 | Manikganj | 134 | 19:00 | 116 | 08:00
Amnura | 140 | 18:00 | 124 | 00:00 | Maniknagar | 131 | 20:00 | 123 | 12:00
Ashuganj | 139 | 19:30 | 134 | 00:00 | Matarbari | 130 | 19:00 | 113 | 05:00
Bagerhat | 134 | 19:30 | 120 | 00:00 | Matuail | 133 | 20:00 | 124 | 12:00
Bajitpur | 133 | 18:30 | 126 | 00:00 | Millgate | 159 | 22:00 | 122 | 12:00
Bakulia | 139 | 19:00 | 128 | 10:00 | Mirpur | 131 | 19:00 | 123 | 12:00
Banani | 134 | 03:00 | 125 | 12:00 | Mirzapur | 134 | 19:00 | 120 | 12:00
Bangabhaban | 131 | 19:30 | 123 | 12:00 | Mithapukur | 133 | 18:30 | 122 | 07:00
Barapukuria | 137 | 18:30 | 125 | 07:00 | MI_Cement | 134 | 19:30 | 124 | 12:00
Barguna | 137 | 19:00 | 127 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 139 | 19:00 | 120 | 00:00 | Mogbazar | 135 | 03:00 | 125 | 12:00
Barishal-230 | 134 | 21:00 | 120 | 00:00 | Mongla | 136 | 19:30 | 121 | 22:00
Baroaulia | 140 | 19:30 | 126 | 11:00 | Motijheel | 131 | 19:30 | 123 | 12:00
Baroirhat | 133 | 19:30 | 119 | 12:00 | Muktagacha | 134 | 20:00 | 120 | 04:00
Bashundhara | 134 | 03:00 | 120 | 17:00 | Munshiganj | 133 | 19:00 | 122 | 12:00
BashundharaCement | 131 | 22:00 | 123 | 12:00 | Muradnagar | 133 | 19:30 | 121 | 12:00
Beanibazar | 130 | 03:00 | 124 | 18:30 | Mymensingh | 132 | 19:00 | 115 | 23:00
Benapole | 133 | 20:00 | 118 | 00:00 | Naogaon | 129 | 18:30 | 117 | 07:00
Bhaluka | 135 | 19:00 | 125 | 12:00 | Narail | 136 | 09:00 | 121 | 00:00
Bhandaria | 127 | 13:00 | 112 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 135 | 18:00 | 128 | 00:00 | Narshingdi | 133 | 19:00 | 116 | 00:00
Bheramara | 138 | 18:00 | 127 | 00:00 | Natore | 135 | 18:30 | 127 | 12:00
Bheramara(GK) | 136 | 18:00 | 127 | 12:00 | Nawabganj | 136 | 20:00 | 127 | 12:00
Bhulta | 127 | 19:30 | 118 | 12:00 | Netrakona | 126 | 18:00 | 113 | 22:00
Bog-Sherpur | 132 | 18:30 | 121 | 07:00 | New | 132 | 19:30 | 123 | 12:00
Bogura | 136 | 18:30 | 126 | 07:00 | Niamatpur | 136 | 18:30 | 130 | 00:00
Bogura-230 | 136 | 18:30 | 127 | 07:00 | Noapara | 135 | 09:00 | 121 | 19:00
Brahmanbaria | 133 | 18:30 | 121 | 00:00 | Pabna | 138 | 18:30 | 129 | 22:00
Cantonment | 133 | 19:30 | 126 | 12:00 | Palashbari | 129 | 14:00 | 119 | 07:00
Chandina | 134 | 21:00 | 123 | 12:00 | Panchagarh | 138 | 14:00 | 117 | 11:00
Chandpur | 138 | 19:00 | 120 | 12:00 | Patuakhali | 135 | 22:00 | 129 | 00:00
Chandraghona | 137 | 19:00 | 128 | 00:00 | Payra | 135 | 10:00 | 132 | 00:00
Chapai | 131 | 21:00 | 125 | 00:00 | PHP | 133 | 19:30 | 116 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 19:00 | 123 | 12:00 | Postogola | 135 | 19:30 | 126 | 12:00
Chauddagram | 133 | 19:00 | 118 | 11:00 | Purbachal | 134 | 04:00 | 124 | 12:00
Chhatak | 131 | 02:00 | 122 | 23:00 | Purbasadipur | 137 | 22:00 | 114 | 11:00
Chowmuhani | 130 | 19:00 | 113 | 00:00 | Rahanpur | 137 | 18:30 | 132 | 00:00
Chuadanga | 134 | 09:00 | 115 | 19:00 | Rahanpur-400 | 138 | 18:30 | 132 | 00:00
Coxsbazar | 127 | 18:30 | 114 | 00:00 | Rahim | 132 | 19:00 | 124 | 12:00
Cumilla(N) | 134 | 19:30 | 123 | 11:00 | Rajbari | 138 | 19:00 | 124 | 00:00
Cumilla(S) | 136 | 19:30 | 120 | 12:00 | Rajendrapur | 135 | 19:30 | 122 | 13:00
Daudkandi | 131 | 19:30 | 118 | 12:00 | Rajshahi | 135 | 18:00 | 127 | 13:00
Dhaka | 135 | 03:00 | 126 | 12:00 | Rajshahi-230 | 138 | 18:30 | 116 | 00:00
Dhamrai | 138 | 19:00 | 127 | 12:00 | Ramganj | 133 | 19:00 | 114 | 12:00
Dhanmondi | 135 | 05:00 | 126 | 12:00 | Rampur | 137 | 19:00 | 126 | 11:00
Dohazari | 138 | 19:00 | 124 | 04:00 | Rampura | 134 | 03:00 | 126 | 12:00
Faridpur | 137 | 19:00 | 127 | 00:00 | Rangamati | 137 | 19:30 | 127 | 01:00
Fatullah | 134 | 19:30 | 124 | 12:00 | Rangpur | 132 | 18:30 | 118 | 07:00
Fenchuganj | 135 | 12:00 | 130 | 00:00 | Ruppur | 141 | 18:00 | 132 | 12:00
Feni | 130 | 19:00 | 120 | 11:00 | Saidpur | 132 | 22:00 | 118 | 11:00
Ghatail | 132 | 19:00 | 118 | 00:00 | Satkhira | 141 | 18:30 | 118 | 00:00
Ghorashal | 139 | 19:30 | 130 | 09:00 | Satmasjid | 133 | 19:00 | 125 | 18:00
Goalpara | 139 | 18:30 | 125 | 01:00 | Savar | 133 | 19:00 | 123 | 12:00
Gollamari | 137 | 09:00 | 126 | 00:00 | SevenRings | 139 | 19:00 | 129 | 12:00
Gopalganj | 135 | 09:00 | 123 | 19:00 | ShahCement | 134 | 19:00 | 123 | 12:00
Gopalganj-400 | 138 | 19:30 | 129 | 01:00 | Shahjadpur | 140 | 18:00 | 133 | 00:00
Gulshan | 134 | 03:00 | 125 | 12:00 | Shahjibazar | 134 | 19:30 | 123 | 00:00
Halishahar | 139 | 19:30 | 125 | 12:00 | Shahmirpur | 141 | 19:30 | 128 | 12:00
Haripur | 133 | 19:30 | 126 | 11:00 | Shariatpur | 137 | 19:00 | 124 | 00:00
HaripurSBU | 133 | 19:30 | 126 | 12:00 | Sherpur | 136 | 19:00 | 121 | 01:00
Hasnabad | 135 | 19:30 | 127 | 12:00 | Shikalbaha | 129 | 19:30 | 119 | 01:00
Hathazari | 139 | 19:30 | 124 | 12:00 | Shikalbaha-230 | 139 | 19:00 | 129 | 11:00
Ishurdi | 141 | 18:00 | 133 | 12:00 | Shitalakhya | 134 | 19:30 | 124 | 12:00
Jaldhaka | 133 | 22:00 | 116 | 19:00 | Sholosohor | 136 | 19:00 | 128 | 11:00
Jamalpur | 139 | 20:00 | 123 | 01:00 | Shyampur | 133 | 20:00 | 125 | 12:00
Jashore | 135 | 18:30 | 119 | 00:00 | Shyampur-230 | 133 | 19:00 | 125 | 12:00
Jhenaidah | 136 | 18:00 | 112 | 7:00 | Siddhirganj | 133 | 19:30 | 124 | 12:00
Jhenaidah-230 | 137 | 18:00 | 123 | 22:00 | Sirajganj | 129 | 21:00 | 114 | 07:00
Joydebpur | 138 | 20:00 | 124 | 12:00 | Sonargaon | 133 | 19:00 | 122 | 12:00
Joypurhat | 124 | 18:30 | 112 | 07:00 | Sreemongol | 133 | 19:00 | 124 | 00:00
Juldah | 140 | 19:00 | 128 | 11:00 | Sreepur | 137 | 18:30 | 128 | 16:00
Kabirpur | 137 | 19:00 | 120 | 12:00 | Srinagar | 136 | 19:00 | 128 | 12:00
Kachua | 136 | 19:30 | 119 | 12:00 | SSM | 141 | 19:30 | 130 | 01:00
Kaliakoir | 140 | 20:00 | 125 | 13:00 | Sunamganj | 129 | 06:00 | 121 | 00:00
Kallyanpur | 133 | 18:30 | 125 | 11:00 | Sylhet | 131 | 07:00 | 126 | 23:00
Kalurghat | 136 | 19:00 | 128 | 01:00 | Sylhet-132 | 131 | 19:00 | 127 | 23:00
Kamrangirchar | 136 | 19:30 | 127 | 12:00 | Tangail | 132 | 19:00 | 117 | 12:00
Kaptai | 139 | 19:00 | 131 | 1:00 | Thakurgaon | 141 | 18:30 | 117 | 11:00
Kasba | 132 | 19:30 | 120 | 12:00 | TK | 140 | 19:30 | 129 | 10:00
Kazla | 131 | 21:00 | 122 | 13:00 | Tongi | 134 | 20:00 | 125 | 12:00
Keranigonj | 136 | 19:00 | 128 | 12:00 | Ullahpara | 130 | 21:00 | 115 | 06:00
Khagrachori | 137 | 19:30 | 126 | 01:00 | Ullon | 134 | 05:00 | 125 | 12:00
Khulna | 151 | 18:30 | 123 | 22:00 | Uttara | 131 | 19:30 | 123 | 12:00
Khulna(S) | 144 | 18:30 | 126 | 00:00 | UttaraNew | 132 | 19:30 | 124 | 12:00
Khulshi | 137 | 19:30 | 126 | 10:00 | Zigatola | 136 | 20:00 | 128 | 13:00
Kishoreganj | 132 | 18:30 | 121 | 00:00
Kodda | 136 | 19:00 | 120 | 12:00
KSRM | 137 | 19:00 | 127 | 11:00
Kulaura | 134 | 19:00 | 129 | 00:00
Kurigram | 136 | 00:00 | 117 | 07:00
Kushtia | 138 | 18:30 | 121 | 19:00
Lalbag | 135 | 20:00 | 126 | 12:00
Lalmonirhat | 130 | 14:00 | 120 | 19:30
Madanganj | 131 | 22:00 | 123 | 12:00
Madaripur | 138 | 19:00 | 125 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division