## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-04-2025 | during | 28-04-2025 | during | 28-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 405 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 288 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 310 | 323 | 335 | 335 | 310 | 310 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 81 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 35 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 128 | 144 | 149.36 | 149.36 | 48 | 149 | Liquid fuel shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17 | 18 | 30 | 30 | 23 | 23 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 18 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 295 | 295 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 113 | 149 | 149 | 130 | 130 | Machine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 67 | 67 | 104 | 104 | 67 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 54 | 162 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 400 | 584 | 584 | 500 | 500 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 400 | 350 | 583 | 583 | 540 | 540 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 44 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 3248 | 3518 | 5272.9 | 5333.9 | 3636.79 | 3978.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 147 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 68 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 30 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 51 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 8 | 7 | 22 | 7 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.94 | 0 | 4.94 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 100 | 100 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 20 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 108 | 108 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 53 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 3 | 12 | 1 | 12 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 576 | 575 | 150 | 150 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2244 | 2434 | 2991.66 | 2995.72 | 3208.66 | 3212.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 201 | 207 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 330 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 33 | 32 | 46.94 | 46.94 | 33 | 33 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 76 | 8 | 190 | 190 | 63 | 63 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 92 | 118 | 150 | 150 | 135 | 135 | Machine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 14 | 38 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 50 | 50 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 132 | 163 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20.83 | 24.5 | 20.83 | 24.5 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 50 | 98 | 105.3 | 105.3 | 105.3 | 105.3 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 89 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 35 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1576 | 1728.2 | 2443.62 | 2377.29 | 2034.68 | 1997.35
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-04-2025 | during | 28-04-2025 | during | 28-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 112 | 157 | 200 | 200 | 125 | 150 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 75 | 104 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.36 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 54 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 254.36 | 290 | 601.1 | 549 | 274.1 | 321
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 38 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 0 | 0 | 40 | 40 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 97 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 175 | 175 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 20 | 20 | 17 | 17 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 6 | 8 | 8 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 396 | 350 | 385 | 385 | 337 | 337 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1463 | 1446 | 1558 | 1558 | 1503 | 1503
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 875 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 52 | 105 | 105 | 84 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 92 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 0 | 512 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1015 | 1439 | 3577.2 | 3512.2 | 2424.01 | 2345.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 0 | 250 | 660 | 660 | 660 | 660 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 950 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 203 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.43 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1650.43 | 1858 | 2832.12 | 2831.12 | 2832.12 | 2831.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 41 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 12 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 30 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 171 | 166 | 214 | 214 | 188 | 188 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 166 | 154 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 155 | 154 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 94 | 93 | 93 | 93 | 93 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.53 | 0 | 5.05 | 0 | 5.05 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1282 | 1368.38 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 44.24 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 105 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2453.77 | 2732.38 | 3112.58 | 2946.53 | 3033.79 | 2867.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 52 | 58 | 58 | 62 | 62 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 167 | 167 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 204 | 0 | 180 | 0 | 180 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 456.9 | 447 | 674.4 | 470 | 678.4 | 474
System Total |  |  |  |  | 27566.2 | 28535.742 | 14361.46 | 15892.58 | 23063.58 | 22573.76 | 19625.55 | 19530.73
Forecast Scenario (28-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15270 |  | 0 |  | 15270
|  |  |  | 1:00 | 14850 |  | 0 |  | 14850
|  |  |  | 2:00 | 14300 |  | 0 |  | 14300
|  |  |  | 3:00 | 13380 |  | 0 |  | 13380
|  |  |  | 4:00 | 12800 |  | 0 |  | 12800
|  |  |  | 5:00 | 12580 |  | 0 |  | 12580
|  |  |  | 6:00 | 12330 |  | 0 |  | 12330
|  |  |  | 7:00 | 12370 |  | 0 |  | 12370
|  |  |  | 8:00 | 12280 |  | 0 |  | 12280
|  |  |  | 9:00 | 12800 |  | 0 |  | 12800
|  |  |  | 10:00 | 13170 |  | 0 |  | 13170
|  |  |  | 11:00 | 13730 |  | 0 |  | 13730
|  |  |  | 12:00 | 14280 |  | 0 |  | 14280
|  |  |  | 13:00 | 14610 |  | 0 |  | 14610
|  |  |  | 14:00 | 14620 |  | 0 |  | 14620
|  |  |  | 15:00 | 14850 |  | 0 |  | 14850
|  |  |  | 16:00 | 14550 |  | 0 |  | 14550
|  |  |  | 17:00 | 14130 |  | 0 |  | 14130
|  |  |  | 18:00 | 13980 |  | 0 |  | 13980
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15320 |  | 0 |  | 15320
|  |  |  | 19:30 | 15690 |  | 0 |  | 15690
|  |  |  | 20:00 | 15670 |  | 0 |  | 15670
|  |  |  | 21:00 | 15800 |  | 0 |  | 15800
|  |  |  | 22:00 | 15750 |  | 0 |  | 15750
|  |  |  | 23:00 | 15250 |  | 0 |  | 15250
Probable Maximum Temperature: |  |  | 30.00°C
Probable Maximum Demand at Day Peak: |  |  | 14280.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 338.67 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:31 hrs on 28-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-04-2025 | [28 empty] | Date: | 27-04-2025 | [28 empty] | Date: | 27-04-2025 | [28 empty] | Date: | 27-04-2025 | [28 empty] | Date: | 27-04-2025 | [16 empty] | Date: | 27-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 132 | 64 | 295 | 55 | 35 | 144 | 0 | 52 | 400 | 290 | 400 | 0 | 55 | 0 | 277 | 0 | 0 | 0 | 160 | 19 | 18 | 0 | 450 | 53 | 223 | 12 | 0 | 14 | 102 | 54 | 17 | 100 | 100 | 0 | 40 | 110 | 22 | 450 | 160 | 0 | 0 | 8 | 87 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 8 | 0 | 352 | 330 | 10 | 195 | 34 | 115 | 50 | 180 | 12 | 20 | 98 | 46 | 52.2 | 0 | 46 | 315 | 60 | 358 | 38 | 39 | 0 | 101 | 8 | 0 | 83 | 28 | 0 | 17 | 173 | 17 | 102 | 139 | 0 | 0 | 0 | 12 | 9495.2 | 913 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1359.84 | 0 | 33 | 0 | 113 | 12 | 92 | 113 | 34 | 52.2 | 0 | 30 | 0 | 171 | 0 | 165 | 0 | 166 | 0 | 414 | 0 | 0 | 0 | 165 | 56 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 11 | 0 | 40 | 0 | 0 | 1210 | 100 | 5565.04 | 15060.24 | 80.67
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 0 | 17 | 115 | 64 | 295 | 55 | 35 | 17 | 0 | 50 | 450 | 284 | 450 | 0 | 55 | 0 | 285 | 0 | 0 | 0 | 160 | 19 | 18 | 0 | 450 | 53 | 223 | 12 | 0 | 16 | 102 | 54 | 17 | 100 | 100 | 0 | 40 | 110 | 22 | 360 | 160 | 0 | 19 | 8 | 87 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 8 | 0 | 353 | 330 | 10 | 190 | 34 | 108 | 50 | 181 | 8 | 20 | 98 | 44 | 52.2 | 0 | 46 | 310 | 60 | 368 | 38 | 40 | 0 | 100 | 8 | 0 | 83 | 28 | 0 | 17 | 173 | 17 | 24 | 94 | 0 | 0 | 0 | 12 | 9185.2 | 913 | 0 | 0 | 27 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 1359.38 | 0 | 33 | 0 | 113 | 0 | 92 | 113 | 34 | 52.2 | 0 | 30 | 0 | 171 | 0 | 162 | 0 | 164 | 0 | 414 | 0 | 0 | 0 | 163 | 57 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 11 | 0 | 40 | 0 | 0 | 1244 | 136 | 5765.58 | 14950.78 | 80.66
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 0 | 17 | 113 | 64 | 280 | 55 | 35 | 17 | 0 | 48 | 450 | 288 | 450 | 0 | 55 | 0 | 285 | 0 | 0 | 0 | 108 | 19 | 18 | 0 | 450 | 53 | 185 | 0 | 0 | 9 | 68 | 54 | 0 | 100 | 50 | 0 | 40 | 110 | 22 | 250 | 160 | 0 | 0 | 8 | 87 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 8 | 0 | 354 | 330 | 10 | 194 | 31 | 96 | 50 | 166 | 9 | 20 | 98 | 44 | 52.2 | 0 | 46 | 305 | 60 | 365 | 38 | 40 | 0 | 90 | 8 | 0 | 83 | 28 | 0 | 17 | 173 | 17 | 28 | 96 | 0 | 0 | 0 | 12 | 8799.2 | 912 | 0 | 0 | 25 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 1355.41 | 0 | 25 | 0 | 113 | 0 | 0 | 50 | 34 | 52.2 | 0 | 30 | 0 | 170 | 0 | 164 | 0 | 165 | 0 | 350 | 0 | 0 | 0 | 164 | 57 | 115 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 11 | 20 | 126 | 0 | 0 | 1244 | 150 | 5641.61 | 14440.81 | 80.65
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 113 | 64 | 15 | 0 | 35 | 17 | 0 | 51 | 450 | 270 | 450 | 0 | 55 | 0 | 267 | 0 | 0 | 0 | 34 | 19.5 | 18 | 0 | 450 | 53 | 15 | 0 | 0 | 1 | 51 | 54 | 0 | 100 | 10 | 0 | 40 | 110 | 22 | 425 | 0 | 0 | 0 | 0 | 87 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 8 | 0 | 359 | 330 | 10 | 180 | 31 | 94 | 50 | 165 | 9 | 20 | 98 | 42 | 52.2 | 0 | 45 | 295 | 60 | 346 | 38 | 40 | 0 | 80 | 0 | 0 | 83 | 28 | 0 | 17 | 173 | 17 | 49 | 96 | 0 | 0 | 0 | 2 | 8082.7 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 1359.1 | 0 | 25 | 0 | 113 | 0 | 0 | 0 | 34 | 0 | 0 | 30 | 0 | 170 | 0 | 165 | 0 | 169 | 0 | 350 | 0 | 0 | 0 | 165 | 57 | 50 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 11 | 110 | 220 | 0 | 0 | 1244 | 100 | 5500.1 | 13582.8 | 80.64
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 113 | 64 | 0 | 0 | 17 | 17 | 0 | 16 | 450 | 294 | 400 | 0 | 17 | 0 | 277 | 0 | 0 | 0 | 0 | 19.5 | 18 | 0 | 400 | 17 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 100 | 10 | 0 | 40 | 68 | 29 | 566 | 0 | 0 | 0 | 0 | 87 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 8 | 0 | 359 | 330 | 10 | 181 | 31 | 93 | 50 | 162 | 9 | 20 | 98 | 40 | 52.2 | 0 | 45 | 305 | 60 | 348 | 38 | 40 | 0 | 80 | 0 | 0 | 83 | 28 | 0 | 17 | 174 | 17 | 49 | 96 | 0 | 0 | 0 | 10 | 7849.7 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1366.01 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 170 | 0 | 170 | 0 | 168 | 0 | 414 | 0 | 0 | 0 | 167 | 57 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 130 | 220 | 0 | 0 | 1244 | 17 | 5155.01 | 13004.71 | 80.63
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 105 | 64 | 0 | 0 | 17 | 17 | 0 | 0 | 450 | 305 | 400 | 0 | 17 | 0 | 296 | 0 | 0 | 0 | 0 | 19.5 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 34 | 24 | 0 | 66 | 0 | 0 | 40 | 0 | 22 | 575 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 70 | 8 | 0 | 359 | 330 | 10 | 204 | 31 | 93 | 50 | 167 | 9 | 20 | 98 | 40 | 52.2 | 0 | 45 | 305 | 65 | 386 | 38 | 40 | 0 | 84 | 0 | 0 | 83 | 28 | 0 | 17 | 172 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 7705.7 | 913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.66 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 168 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 168 | 58 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 125 | 220 | 0 | 0 | 1244 | 0 | 5076.66 | 12782.36 | 80.62
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 95 | 64 | 0 | 0 | 17 | 0 | 0 | 0 | 450 | 300 | 400 | 0 | 0 | 0 | 286 | 0 | 0 | 1 | 0 | 19.5 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 13 | 34 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 25 | 575 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1224 | 1 | 51 | 40 | 8 | 0 | 359 | 330 | 10 | 191 | 34 | 34 | 50 | 169 | 9 | 20 | 98 | 38 | 8 | 3 | 45 | 310 | 65 | 347 | 38 | 40 | 0 | 82 | 0 | 0 | 84 | 30 | 0 | 17 | 173 | 0 | 49 | 96 | 0 | 0 | 2.43 | 12 | 7446.93 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.43 | 0 | 0 | 1361.9 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 172 | 0 | 171 | 0 | 165 | 0 | 414 | 0 | 0.14 | 0 | 172 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0.02 | 0 | 0 | 10 | 120 | 220 | 0 | 0 | 1244 | 0 | 5087.49 | 12534.42 | 80.61
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 11 | 95 | 64 | 0 | 0 | 17 | 0 | 0 | 0 | 450 | 286 | 400 | 0 | 0 | 0 | 266 | 0 | 0 | 4 | 0 | 19 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 15 | 34 | 0 | 0 | 48 | 0 | 1 | 40 | 0 | 17 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1224 | 5 | 51 | 40 | 8 | 0 | 359 | 330 | 10 | 179 | 34 | 34 | 50 | 149 | 8 | 20 | 98 | 36 | 8 | 8 | 45 | 300 | 120 | 364 | 38 | 40 | 0 | 81 | 0 | 0 | 84 | 30 | 0 | 17 | 173 | 0 | 78 | 115 | 0 | 0 | 11.41 | 12 | 7496.41 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.22 | 0 | 0 | 1358.89 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 5.24 | 173 | 0 | 168 | 0 | 168 | 0 | 300 | 0 | 0.5 | 0 | 172 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0.02 | 0 | 0 | 9 | 120 | 220 | 0 | 0 | 1244 | 0 | 5073.87 | 12570.28 | 80.6
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 17 | 95 | 64 | 0 | 0 | 17 | 0 | 0 | 0 | 400 | 307 | 400 | 0 | 0 | 0 | 296 | 0 | 0 | 9 | 0 | 18.6 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 48 | 0 | 2 | 40 | 0 | 5 | 575 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1224 | 5 | 51 | 10 | 8 | 0 | 358 | 330 | 10 | 201 | 35 | 16 | 50 | 114 | 9 | 20 | 52 | 30 | 0 | 19 | 0 | 310 | 142 | 385 | 38 | 0 | 0 | 86 | 0 | 0 | 84 | 30 | 0 | 17 | 174 | 0 | 78 | 115 | 0 | 1 | 13.22 | 12 | 7318.82 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.99 | 0 | 0 | 1365 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 24.45 | 173 | 0 | 175 | 0 | 169 | 0 | 300 | 0 | 1.96 | 0 | 167 | 57 | 0 | 0 | 0 | 0 | 0 | 2.9 | 89 | 0.1 | 0 | 0 | 8 | 120 | 220 | 0 | 0 | 1220 | 0 | 5146.4 | 12465.22 | 80.59
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 2 | 17 | 95 | 64 | 30 | 0 | 20 | 17 | 0 | 4 | 420 | 293 | 450 | 0 | 0 | 0 | 271 | 0 | 0 | 22 | 31 | 17.7 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 100 | 0 | 2 | 40 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1224 | 14 | 51 | 10 | 8 | 0 | 358 | 330 | 10 | 183 | 35 | 26 | 50 | 106 | 9 | 20 | 72 | 34 | 0 | 38 | 0 | 305 | 165 | 348 | 39 | 0 | 0 | 97 | 0 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 77 | 115 | 0 | 1 | 38.4 | 12 | 7637.1 | 874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 1314 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 40.63 | 173 | 0 | 175 | 0 | 140 | 0 | 380 | 0 | 3.33 | 0 | 171 | 57 | 35 | 0 | 0 | 0 | 0 | 4.2 | 116 | 0.29 | 0 | 88 | 0 | 120 | 220 | 0 | 0 | 1191 | 0 | 5326.45 | 12963.55 | 80.58
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 17 | 95 | 90 | 47 | 0 | 35 | 17 | 0 | 32 | 450 | 295 | 400 | 0 | 35 | 0 | 284 | 0 | 0 | 21 | 35 | 17 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 34 | 0 | 0 | 89 | 0 | 2 | 40 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1224 | 17 | 51 | 45 | 26 | 0 | 351 | 330 | 10 | 196 | 31 | 50 | 50 | 114 | 9 | 20 | 46 | 32 | 0 | 11 | 0 | 310 | 200 | 372 | 39 | 0 | 0 | 101 | 0 | 0 | 81 | 30 | 0 | 17 | 175 | 0 | 77 | 115 | 0 | 2 | 38.03 | 12 | 7881.03 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 1270 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 48.86 | 173 | 0 | 173 | 0 | 140 | 0 | 350 | 0 | 3.97 | 0 | 168 | 57 | 35 | 28 | 0 | 0 | 0 | 5.9 | 173 | 0.61 | 0 | 146 | 0 | 120 | 220 | 0 | 0 | 1150 | 0 | 5436.34 | 13317.37 | 80.57
11:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 108 | 128 | 260 | 28 | 35 | 54 | 0 | 54 | 450 | 292 | 400 | 0 | 35 | 0 | 275 | 0 | 0 | 31 | 35 | 17 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 100 | 20 | 2 | 40 | 0 | 2 | 575 | 53 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1224 | 18 | 51 | 89 | 81 | 0 | 351 | 330 | 10 | 185 | 31 | 59 | 50 | 105 | 9 | 20 | 43 | 34 | 2 | 1 | 0 | 310 | 210 | 360 | 39 | 0 | 0 | 101 | 0 | 0 | 78 | 30 | 0 | 17 | 175 | 0 | 76 | 115 | 0 | 2 | 38.29 | 12 | 8423.29 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 1270 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 58.71 | 173 | 0 | 168 | 0 | 140 | 0 | 380 | 0 | 3.75 | 0 | 169 | 56 | 0 | 0 | 0 | 0 | 0 | 7 | 188 | 0.56 | 0 | 157 | 7 | 120 | 220 | 0 | 0 | 1118 | 0 | 5440.02 | 13863.31 | 80.56
12:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 113 | 128 | 295 | 55 | 35 | 54 | 0 | 67 | 380 | 300 | 400 | 0 | 35 | 0 | 310 | 0 | 0 | 27 | 44 | 17 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 51 | 0 | 0 | 100 | 20 | 4 | 40 | 0 | 4 | 576 | 53 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1224 | 18 | 51 | 92 | 76 | 0 | 340 | 330 | 10 | 201 | 33 | 89 | 50 | 132 | 9 | 20 | 50 | 36 | 8 | 35 | 14 | 305 | 320 | 396 | 39 | 0 | 0 | 100 | 0 | 0 | 81 | 30 | 0 | 17 | 175 | 17 | 75 | 112 | 0 | 2 | 36.36 | 12 | 8785.36 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 1282 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 44.24 | 171 | 0 | 166 | 0 | 155 | 0 | 414 | 0 | 3.53 | 0 | 167 | 56 | 0 | 23 | 0 | 0 | 0 | 6.9 | 204 | 0.43 | 0 | 203 | 7 | 120 | 220 | 0 | 0 | 1100 | 0 | 5576.1 | 14361.46 | 80.56
13:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 113 | 128 | 295 | 55 | 35 | 54 | 0 | 67 | 380 | 275 | 430 | 0 | 55 | 0 | 313 | 0 | 0 | 25 | 52 | 17.5 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 8 | 51 | 0 | 0 | 100 | 60 | 4 | 40 | 0 | 6 | 575 | 108 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1170 | 18 | 51 | 97 | 26 | 0 | 345 | 330 | 10 | 182 | 33 | 110 | 45 | 161 | 9 | 20 | 50 | 38 | 14 | 25 | 14 | 295 | 320 | 350 | 38 | 0 | 0 | 100 | 0 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 75 | 112 | 0 | 2 | 32.79 | 12 | 8784.29 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 1365 | 0 | 0 | 0 | 113 | 0 | 0 | 25 | 0 | 0 | 100 | 0 | 33.3 | 170 | 0 | 162 | 0 | 155 | 0 | 414 | 0 | 3.06 | 0 | 169 | 55 | 68 | 26 | 0 | 0 | 0 | 7.1 | 171 | 0.26 | 0 | 307 | 6 | 120 | 220 | 0 | 0 | 1180 | 0 | 5877.72 | 14662.01 | 80.55
14:00 | 8 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 113 | 128 | 295 | 55 | 35 | 54 | 0 | 67 | 420 | 297 | 450 | 0 | 55 | 0 | 313 | 0 | 0 | 22 | 52 | 17.5 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 6 | 51 | 0 | 0 | 100 | 60 | 4 | 37 | 0 | 3 | 576 | 108 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1150 | 16 | 51 | 97 | 8 | 0 | 338 | 330 | 10 | 207 | 31 | 115 | 45 | 178 | 9 | 20 | 85 | 38 | 43 | 26 | 14 | 300 | 320 | 384 | 38 | 0 | 0 | 100 | 0 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 74 | 102 | 0 | 2 | 34.26 | 12 | 8913.76 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 10 | 1362.2 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 0 | 0 | 36 | 0 | 42.97 | 165 | 0 | 158 | 0 | 153 | 0 | 414 | 0 | 3.26 | 0 | 161 | 53 | 70 | 16 | 0 | 0 | 0 | 4.8 | 169 | 0.47 | 0 | 270 | 0 | 120 | 220 | 0 | 96 | 1120 | 0 | 5758.7 | 14672.46 | 80.55
15:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 113 | 126 | 295 | 55 | 35 | 54 | 0 | 67 | 420 | 280 | 400 | 0 | 55 | 0 | 314 | 0 | 0 | 12 | 52 | 17.5 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 48 | 0 | 0 | 100 | 60 | 3 | 36 | 0 | 2 | 470 | 108 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1150 | 12 | 51 | 90 | 8 | 0 | 354 | 330 | 10 | 212 | 31 | 114 | 45 | 183 | 9 | 20 | 80 | 38 | 43 | 39 | 29 | 295 | 320 | 350 | 38 | 0 | 0 | 102 | 6 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 74 | 109 | 0 | 0 | 15.38 | 12 | 8654.88 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 355 | 35 | 1370.46 | 0 | 0 | 0 | 113 | 0 | 0 | 90 | 0 | 0 | 23 | 0 | 19.49 | 163 | 0 | 155 | 0 | 150 | 0 | 414 | 0 | 1.91 | 0 | 169 | 53 | 100 | 14 | 30 | 0 | 0 | 4.3 | 102 | 0.22 | 0 | 243 | 0 | 120 | 220 | 0 | 160 | 1040 | 0 | 6109.38 | 14764.26 | 80.54
16:00 | 32 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 113 | 126 | 295 | 55 | 35 | 60 | 0 | 67 | 420 | 286 | 400 | 0 | 55 | 0 | 316 | 0 | 0 | 8 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 48 | 0 | 0 | 100 | 60 | 2 | 40 | 0 | 2 | 470 | 72 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1111 | 8 | 51 | 92 | 8 | 0 | 347 | 330 | 10 | 212 | 31 | 114 | 45 | 167 | 24 | 20 | 80 | 36 | 43 | 15 | 29 | 290 | 320 | 350 | 38 | 0 | 0 | 97 | 6 | 0 | 83 | 30 | 0 | 17 | 175 | 10 | 65 | 120 | 0 | 1 | 12.25 | 12 | 8564.25 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 378 | 35 | 1359.56 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 0 | 0 | 17 | 0 | 12.69 | 160 | 0 | 154 | 0 | 152 | 0 | 350 | 0 | 1.18 | 0 | 175 | 53 | 115 | 12 | 35 | 0 | 0 | 3.5 | 51 | 0.25 | 0 | 200 | 0 | 120 | 220 | 0 | 233 | 962 | 0 | 5909.18 | 14473.43 | 80.54
17:00 | 50 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 113 | 132 | 295 | 55 | 35 | 90 | 0 | 67 | 420 | 287 | 400 | 0 | 55 | 0 | 317 | 0 | 0 | 2 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 49 | 0 | 0 | 100 | 60 | 1 | 40 | 0 | 5 | 500 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1100 | 3 | 51 | 98 | 8 | 0 | 348 | 330 | 10 | 212 | 32 | 114 | 50 | 155 | 37 | 20 | 43 | 38 | 25 | 8 | 29 | 300 | 320 | 351 | 38 | 20 | 0 | 98 | 6 | 0 | 83 | 30 | 0 | 18 | 175 | 16 | 75 | 135 | 0 | 0 | 5.61 | 12 | 8609.61 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 378 | 35 | 1361.04 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 7 | 0 | 5.68 | 163 | 0 | 154 | 0 | 155 | 0 | 414 | 0 | 0.49 | 0 | 171 | 52 | 54 | 4 | 40 | 0 | 0 | 0.4 | 19 | 0.01 | 0 | 200 | 4 | 120 | 220 | 0 | 254 | 902 | 0 | 5722.62 | 14332.23 | 80.53
18:00 | 90 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 113 | 142 | 295 | 55 | 35 | 108 | 0 | 67 | 420 | 288 | 350 | 0 | 55 | 0 | 316 | 0 | 0 | 0 | 52 | 18 | 18 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 60 | 0 | 40 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1109 | 0 | 51 | 105 | 8 | 0 | 344 | 330 | 10 | 212 | 32 | 68 | 50 | 120 | 36 | 20 | 28 | 40 | 16 | 0 | 30 | 300 | 320 | 351 | 38 | 20 | 0 | 101 | 6 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 93 | 155 | 0 | 0 | 0.62 | 12 | 8496.62 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 405 | 35 | 1366.25 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 3 | 0 | 0.46 | 164 | 0 | 154 | 0 | 156 | 0 | 414 | 0 | 0.06 | 0 | 170 | 52 | 35 | 1 | 41 | 0 | 0 | 0.2 | 2 | 0 | 0 | 230 | 11 | 120 | 220 | 0 | 244 | 900 | 0 | 5690.47 | 14187.09 | 80.53
19:00 | 81 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 113 | 144 | 295 | 55 | 35 | 162 | 0 | 67 | 420 | 301 | 400 | 0 | 55 | 0 | 320 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 2 | 102 | 24 | 0 | 100 | 100 | 0 | 40 | 5 | 3 | 575 | 5 | 0 | 0 | 0 | 10 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 113 | 8 | 0 | 344 | 330 | 10 | 208 | 32 | 79 | 50 | 123 | 38 | 20 | 98 | 44 | 43 | 0 | 38 | 295 | 320 | 387 | 38 | 20 | 0 | 102 | 6 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 94 | 155 | 0 | 0 | 0 | 12 | 9291 | 891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 38 | 1365.18 | 0 | 20 | 0 | 18 | 5 | 94 | 70 | 12 | 26 | 0 | 30 | 0 | 166 | 0 | 155 | 0 | 155 | 0 | 414 | 0 | 0 | 0 | 168 | 52 | 115 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 283 | 11 | 120 | 220 | 0 | 267 | 950 | 0 | 6234.18 | 15525.18 | 80.52
19:30 | 81 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 35 | 17 | 113 | 144 | 295 | 55 | 35 | 162 | 0 | 67 | 420 | 288 | 350 | 0 | 55 | 0 | 323 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 102 | 30 | 0 | 100 | 100 | 0 | 40 | 20 | 8 | 575 | 17 | 0 | 0 | 0 | 68 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 8 | 0 | 356 | 330 | 10 | 207 | 32 | 115 | 50 | 163 | 38 | 20 | 98 | 42 | 52.2 | 0 | 38 | 300 | 320 | 350 | 38 | 30 | 0 | 97 | 6 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 104 | 157 | 0 | 0 | 0 | 12 | 9416.2 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 52 | 1368.38 | 0 | 41 | 0 | 113 | 12 | 94 | 113 | 30 | 43 | 0 | 30 | 0 | 166 | 0 | 154 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 167 | 52 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 250 | 950 | 0 | 6476.38 | 15892.58
20:00 | 81 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 35 | 17 | 113 | 144 | 295 | 55 | 35 | 162 | 0 | 67 | 420 | 270 | 350 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 160 | 18.5 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 2 | 102 | 50 | 0 | 100 | 100 | 0 | 40 | 42 | 15 | 565 | 17 | 0 | 0 | 0 | 62 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 8 | 0 | 359 | 330 | 10 | 199 | 32 | 115 | 50 | 168 | 37 | 20 | 98 | 44 | 52.2 | 0 | 38 | 290 | 320 | 325 | 37 | 29 | 0 | 95 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 20 | 104 | 158 | 0 | 0 | 0 | 12 | 9400.7 | 876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 51 | 1365.75 | 0 | 41 | 0 | 108 | 25 | 94 | 70 | 37 | 43 | 0 | 30 | 0 | 166 | 0 | 155 | 0 | 155 | 0 | 414 | 0 | 0 | 0 | 167 | 53 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 279 | 950 | 0 | 6477.75 | 15878.45 | 80.52
21:00 | 98 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 | 35 | 17 | 113 | 144 | 295 | 55 | 35 | 162 | 0 | 67 | 420 | 285 | 350 | 0 | 55 | 0 | 326 | 0 | 0 | 0 | 160 | 18.5 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 102 | 65 | 0 | 100 | 50 | 0 | 40 | 51 | 3 | 536 | 0 | 0 | 0 | 0 | 68 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 8 | 0 | 359 | 330 | 10 | 197 | 32 | 115 | 70 | 165 | 37 | 20 | 98 | 42 | 52.2 | 0 | 38 | 295 | 320 | 350 | 37 | 28 | 0 | 86 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 35 | 104 | 149 | 0 | 0 | 0 | 12 | 9395.7 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 35 | 1363.27 | 0 | 33 | 0 | 113 | 25 | 94 | 35 | 36 | 34 | 0 | 30 | 0 | 166 | 0 | 155 | 0 | 156 | 0 | 414 | 0 | 0 | 0 | 168 | 53 | 73 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 318 | 950 | 0 | 6456.27 | 15851.97 | 80.51
22:00 | 50 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 17 | 113 | 110 | 295 | 55 | 35 | 108 | 0 | 68 | 420 | 305 | 350 | 0 | 55 | 0 | 326 | 0 | 0 | 0 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 101 | 70 | 0 | 100 | 30 | 0 | 40 | 34 | 13 | 575 | 0 | 0 | 0 | 0 | 51 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 8 | 0 | 350 | 330 | 10 | 196 | 32 | 115 | 50 | 172 | 38 | 20 | 98 | 42 | 8 | 0 | 37 | 300 | 320 | 375 | 39 | 28 | 0 | 101 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 35 | 104 | 149 | 0 | 0 | 0 | 12 | 9154 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 35 | 1373.97 | 0 | 33 | 0 | 70 | 25 | 94 | 0 | 36 | 0 | 0 | 30 | 0 | 166 | 0 | 154 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 174 | 53 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 320 | 1052 | 0 | 6423.97 | 15577.97 | 80.51
23:00 | 32 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 17 | 113 | 110 | 295 | 55 | 35 | 72 | 0 | 68 | 420 | 298 | 370 | 0 | 55 | 0 | 324 | 0 | 0 | 0 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 101 | 69 | 0 | 100 | 60 | 0 | 40 | 34 | 17 | 575 | 0 | 0 | 0 | 0 | 51 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 8 | 0 | 353 | 330 | 10 | 196 | 33 | 115 | 50 | 178 | 37 | 20 | 98 | 44 | 38 | 0 | 38 | 305 | 320 | 381 | 39 | 30 | 0 | 101 | 8 | 0 | 83 | 25 | 0 | 17 | 174 | 20 | 105 | 148 | 0 | 0 | 0 | 10 | 9158 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 512 | 35 | 1353.89 | 0 | 35 | 0 | 70 | 25 | 96 | 0 | 36 | 0 | 0 | 30 | 0 | 167 | 0 | 154 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 171 | 57 | 35 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 317 | 1031 | 0 | 6384.89 | 15542.89 | 80.5
Total KWH | 600912 | 801600 | 409440 | 0 | 0 | 0 | 0 | 0 | 9662400 | 0 | 0 | 388440 | 426600 | 2631024 | 2438880 | 4780067 | 885494 | 787714 | 1385280 | 0 | 1122240 | 9721000 | 7085004 | 9633523 | 0 | 979897 | 0 | 7233712 | 0 | 0 | 177106 | 1460400 | 424800 | 428040 | 0 | 10170000 | 195709 | 554509 | 21120 | 0 | 126720 | 1436182 | 555596 | 31309 | 2232000 | 1050240 | 29020 | 936000 | 712579 | 258720 | 12487272.73 | 886545 | 0 | 33120 | 19303.2 | 712581 | 3567651 | 0 | 0 | 0 | 28739998 | 136350 | 1089476 | 2236436 | 384727 | 0 | 8772200 | 8012000 | 249120 | 4814000 | 779544 | 2134080 | 1206410 | 3694080 | 453600 | 469340 | 1891260 | 793920 | 693653 | 241082 | 680704 | 7340000 | 5179200 | 9187000 | 896000 | 478680 | 0 | 2277000 | 79824 | 0 | 1980480 | 701184 | 0 | 398000 | 4596560 | 353880 | 1766400 | 2853600 | 0 | 13300 | 298410 | 276240 | 205627487.93 | 23770909 | 0 | 0 | 55200 | 82176 | 0 | 0 | 0 | 0 | 0 | 0 | 586080 | 4334545 | 706080 | 32387581 | 0 | 278150 | 0 | 2219904 | 104456 | 706016 | 756960 | 263806 | 239544 | 556170 | 281360 | 345752 | 4077273 | 0 | 4093209 | 0 | 4027655 | 0 | 9373963 | 0 | 28560 | 0 | 4101000 | 1284654 | 1302089 | 139383 | 962678 | 0 | 0 | 45075.48 | 1321200 | 3051 | 295968 | 3644000 | 188046 | 2582000 | 5017490 | 0 | 2488727 | 27221818.18 | 444000 | 140316528.66 | 345944016.59

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14361.46 | MW | 12:00 Hr. | Energy Generated |  |  | 345.944 |  | MKWHr.
| Day Peak Demand |  |  | 14482.46 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.679 |  | MKWHr.
| Evening Peak Generation |  |  | 15892.58 | MW | 19:30 Hr. | Energy Demand |  |  | 348.623 |  | MKWHr.
| Evening Peak Demand |  |  | 16050.58 | MW | 19:30 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 12465.22 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1060.69 |  | MMCFD
| Maximum Generation of the Day |  |  | 15892.58 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 7.1614 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 54.3585 | 0 | 19.098 | 0 | 0 | 0.17711 | 0 | 0 | 73.6336 | Gas | 146.4352 | Gas | 515880797.86
| Chattogram Zone |  |  | 3.8264 | 41.2273 | 8.4408 | 0 | 0.936 | 0.16537 | 0 | 0.12672 | 54.7225 | Coal | 84.302 | Coal | 584343673.529
| Cumilla Zone |  |  | 25.7768 | 0 | 11.7838 | 0 | 0 | 0.24108 | 0.79392 | 0 | 38.5956 | HFO | 53.2711 | HFO | 999902581.244
| Mymensingh Zone |  |  | 0 | 0 | 5.2501 | 0 | 0 | 0.31171 | 0 | 0 | 5.5618 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.1139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.1139 | Hydro | 0.936 | Hydro | 93600
| Khulna Zone |  |  | 0 | 4.3345 | 0.84346 | 0 | 0 | 0.58608 | 23.7709 | 0 | 29.535 | Solar | 3.9205 | Solar | 65219135.0228
| Barishal Zone |  |  | 7.7875 | 33.3545 | 0.73997 | 0 | 0 | 0.003051 | 0 | 0 | 41.8851 | Import | 56.9524 | Import | 310145787.71
| Rajshahi Zone |  |  | 21.5721 | 0 | 4.8502 | 0 | 0 | 0.93048 | 32.3876 | 0 | 59.7404 | Wind | 0.12672 | Wind | 1855180.8
| Rangpur Zone |  |  | 0 | 5.3857 | 2.2648 | 0 | 0 | 1.5057 | 0 | 0 | 9.1561
| Total |  |  | 146.4352 | 84.302 | 53.2711 | 0 | 0.936 | 3.9205 | 56.9524 | 0.12672 | 345.944
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 515880797.86 |  | Hydro | 93600
|  |  |  | Coal | 584343673.529 |  | Solar | 65219135.0228
|  |  |  | HFO | 999902581.244 |  | Import | 310145787.71
|  |  |  | HSD | 0 |  | Wind | 1855180.8
[5 empty] | Total: | 247,74,40,756 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 23.7709 | Peak Hr Flow | 875.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 11470545.53 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.3876 | Peak Hr Flow | 1368.38 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 732 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.79392 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 962 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.9524 | Peak Hr Flow | 2285.38 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 55 |  | 5809
|  |  |  | Chattogram |  | 0 |  | 1598
|  |  |  | Cumilla |  | 0 |  | 1400
|  |  |  | Mymensingh |  | 96 |  | 1185
|  |  |  | Sylhet |  | 0 |  | 541
|  |  |  | Khulna |  | 0 |  | 1877
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 0 |  | 1778
|  |  |  | Rangpur |  | 0 |  | 722
|  |  |  | Total |  | 151 |  | 15388
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Tangail Palli Power Gen 22 MW |  |  | 22
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115 | 5 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
[5 empty] | Total | 660 |  |  |  | Total | 511.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1171.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:00 |  | Rangpur-Saidpur 132kV Ckt-2 Forced S/D from Rangpur 132/33kV end.
| 08:02 |  | Rangpur-Saidpur 132kV Ckt-1 Forced S/D from Rangpur 132/33kV end.
| 08:10 |  | Barishal Electric 307 MW PS was synchronized.
| 08:10 |  | Barisal 307 MW Synchronized
| 11:40 | 12:58 | New Tongi S/S T1(403T) HT Scheduled S/D Due to Multification meter connection
| 12:23 | 17:20 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Forced S/D Due to Emergency
Maintenance
| 12:23 | 17:26 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Forced S/D Due to Emergency
Maintenance
|  | 12:39 | Rampura 230/132kV S/S Auto Transformer - 02 HT is restored.
|  | 12:43 | Rampura 230/132kV S/S Auto Transformer - 02 LT is restored.
| 12:58 | 16:22 | BIPTC S/S 10CF14 Tripped showing 87.1 (Differential relay) relays Due to C1 unbalance
60/61 instant L2 tripped
|  | 13:01 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
|  | 13:04 | Bhulta-Rampura 230 kV Ckt-1 is restored.
| 13:25 |  | Patuakhali 1320 MW (RNPL) Unit-2 was synchronized.
| 14:01 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 15:51 | 16:22 | BIPTC S/S 10CF14 Forced S/D Due to Due to tripped by showing unbalance 60/61 instant
trip.
| 16:31 | 17:57 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) LT Scheduled S/D Due to 33 kv Fakirhat-2 | [7 empty] | 20.0MW load
|  |  | feeder red hot maintenance work. | [7 empty] | interrup.
| 16:32 | 17:56 | Bagerhat 132/33kV S/S Transformer-3 ( 423 T) HT Scheduled S/D Due to 33 kv Fakirhat-2 | [7 empty] | 20.0MW load
|  |  | feeder red hot maintenance work. | [7 empty] | interrup.
|  | 16:36 | Rajbari 132/33kV S/S 132 kV Bus-I is restored.
|  | 16:50 | Rajbari 132/33kV S/S Transformer-3 HT is restored.
|  | 17:02 | Rajbari 132/33kV S/S Transformer-3 LT is restored.
|  | 17:11 | Shahjadpur-Ullahpara 132kV Ckt-1 is restored.
| 18:09 | 19:23 | Khagrachari-Rangamati 132kV Ckt-1 Forced S/D from Rangamati 132/33kV end Due to
Rangamati-Khagrachari Ckt-01 taken emergency shutdown due to remove straw from Y-phase.
| 19:30 |  | Peak generation 15892MW
|  | 21:46 | Aminbazar 400/230/132kV S/S Bus-1 (400kV) is restored.
| 03:23 | 04:06 | Barapukuria-Saidpur 132 kV Ckt-2 Tripped from Saidpur 132/33kV end showing Distance
realy- B-Phase Z1 relays Due to None
| 03:50 | 04:15 | Purbasadipur-Saidpur 132kV Ckt-1 Tripped from Purbasadipur 132/33kV end showing Distance | [7 empty] | 10.0MW load
|  |  | Relay relays. | [7 empty] | interrup.
Purbasadipur
132/33kV end
| 03:50 | 06:34 | Purbasadipur-Saidpur 132kV Ckt-2 Tripped from Saidpur 132/33kV end showing C-Phase Z1 | [7 empty] | and 10.0MW load
|  |  | relays. and from Purbasadipur 132/33kV end showing Distance Relay (SIMENS SIPROTEC, Model | [7 empty] | interrup.
|  |  | :- SA87 ) relays. | [7 empty] | Purbasadipur
132/33kV end
| 04:10 | 06:32 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-1 Forced S/D from Purbasadipur 132/33kV end Due to
high Voltage problem
| 04:20 | 06:36 | Purbasadipur-Thakurgaon-EPV 132kV Ckt-2 Forced S/D from Thakurgaon 132/33kV end Due to
For high voltage
| 05:31 | 07:08 | Barapukuria-Rangpur 132 kV Ckt-2 Forced S/D from Barapukuria 230/132/33kV end Due to Over
voltage
| 05:32 | 06:40 | Barapukuria-Saidpur 132 kV Ckt-2 Forced S/D from Barapukuria 230/132/33kV end Due to Over
voltage
| 07:00 |  | Minimum Generation 11596 MW
| 07:44 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Tripped showing dist, protection | [7 empty] | 1.0MW load
|  |  | relay relays Due to heavy rain fall | [7 empty] | interrup.
| 07:44 |  | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Tripped showing DISTANCE PROTECTION | [7 empty] | 1.0MW load
|  |  | RELAY relays Due to HEAVY RAIN FALL. | [7 empty] | interrup.
| 07:45 | 07:50 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Tripped from Fenchuganj 230/132/33kV end | [7 empty] | 34.0MW load
|  |  | showing REL 670, REC 650 relays Due to Bad weather | [7 empty] | interrup.
Fenchuganj
230/132/33kV end
| 07:51 |  | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Forced S/D from Fenchuganj 230/132/33kV | [7 empty] | 34.0MW load
|  |  | end Due to After trip | [7 empty] | interrup.
Fenchuganj
230/132/33kV end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 405 | 9662400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9721000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 288 | 7085004 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 885494 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 323 | 7233712 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 81 | 600912 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 388440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 2438880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 787714 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 979897 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 424800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 428040 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 409440 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 295 | 4780067 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 2631024 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 801600 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 1122240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1385280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 177106 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 426600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10170000 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 350 | 9633523 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1460400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3518 | 73633573
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 19303.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 136350 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 33120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 936000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 147 | 3567651 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 712581 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 30 | 555596 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 1436182 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2232000 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 258720 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 21120 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 29020 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 554509 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 31309 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 20 | 712579 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1050240 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 195709 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 886545 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28739998 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 3 | 126720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12487272.73 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2434 | 54722524.93
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 207 | 4814000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8772200 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 8012000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 32 | 779544 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 249120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 384727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1089476 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 118 | 2236436 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 38 | 680704 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1206410 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 163 | 3694080 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 42 | 793920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 693653 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 469340 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 1891260 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 453600 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2134080 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 241082 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1728.2 | 38595632
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 157 | 2853600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1766400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 298410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 276240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 353880 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 290 | 5561830
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 896000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 478680 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 97 | 2277000 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 701184 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1980480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 175 | 4596560 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 398000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 79824 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7340000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 9187000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 5179200 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1446 | 33113928
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 875 | 23770909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 55200 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 82176 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 52 | 706080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 586080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 512 | 4334545 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1439 | 29534990
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 250 | 2488727 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 295968 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 188046 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 120 | 2582000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 950 | 27221818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5017490 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 444000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 3644000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3051 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1858 | 41885100.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 41 | 278150 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 12 | 104456 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 30 | 263806 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 166 | 4077273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 154 | 4093209 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 154 | 4027655 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9373963 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 281360 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 239544 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 706016 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2219904 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 756960 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28560 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1368.38 | 32387581 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 345752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 556170 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2732.38 | 59740359
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 1284654 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 167 | 4101000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 962678 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45075.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1302089 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 139383 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1321200 | -
Rangpur Area Total |  |  |  |  | 950 | 447 | 9156079.48
Eastern Grid Total |  |  |  |  | 16921.242 | 9416.2 | 205627487.93
Western Grid Total |  |  |  |  | 11614.5 | 6476.38 | 140316528.66
National Grid Total |  |  |  |  | 28535.742 | 15892.58 | 345944016.59
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10381.02 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4855.3 | MW
i) Dhaka area |  |  | 5753.52 |  | MW | i) Khulna area |  |  |  | 1877 | MW
ii) Chattogram area |  |  | 1597.5 |  | MW | ii) Barishal area |  |  |  | 478.3 | MW
iii) Cumilla area |  |  | 1400 |  | MW | iii) Rajshahi area |  |  |  | 1778 | MW
iv) Mymensingh area |  |  | 1089 |  | MW | iv) Rangpur area |  |  |  | 722 | MW
v) Sylhet area |  |  | 541 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15236.32 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 86 | 19:30 | 133 | Patuakhali | 86 | 00:00
2 | AKSML | 20 | 06:00 | 68 | Jaldhaka | 57 | 19:00 | 134 | Payra | 34 | 00:00
3 | Aftabnagar | 42 | 15:00 | 69 | Jamalpur | 134 | 12:00 | 135 | Postogola | 59 | 13:00
4 | Agargaon | 148 | 16:00 | 70 | Jashore | 154 | 19:30 | 136 | Purbachal | 22 | 00:00
5 | Agrabad | 98 | 15:00 | 71 | Jhenaidah | 137 | 21:00 | 137 | Purbasadipur | 134 | 00:00
6 | Amnura | 51 | 06:00 | 72 | Joydebpur | 162 | 17:00 | 138 | Rahanpur | 38 | 00:00
7 | Ashuganj | 107 | 23:00 | 73 | Joypurhat | 84 | 00:00 | 139 | Rahim | 50 | 17:00
8 | BSRM | 200 | 18:30 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 88 | 20:00
9 | Bagerhat | 92 | 00:00 | 75 | KSRM | 13 | 00:00 | 141 | Rajendrapur | 146 | 19:30
10 | Bajitpur | 57 | 21:00 | 76 | Kabirpur | 261 | 09:00 | 142 | Rajshahi | 169 | 00:00
11 | Bakulia | 98 | 21:00 | 77 | Kachua | 96 | 00:00 | 143 | Rajshahi-230 | 91 | 21:00
12 | Banani | 50 | 12:00 | 78 | Kallyanpur | 120 | 00:00 | 144 | Ramganj | 118 | 20:00
13 | Bangabhaban | 20 | 10:00 | 79 | Kalurghat | 60 | 11:00 | 145 | Rampur | 44 | 22:00
14 | Barapukuria | 72 | 19:30 | 80 | Kamrangirchar | 72 | 16:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 24 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 115 | 18:00
16 | Barishal | 117 | 00:00 | 82 | Kasba | 39 | 00:00 | 148 | Ruppur | 7.8 | 11:00
17 | Barishal-230 | 106 | 02:00 | 83 | Kazla | 99 | 22:00 | 149 | SSM | 9 | 00:00
18 | Baroaulia | 61 | 07:00 | 84 | Keranigonj | 85 | 18:30 | 150 | Saidpur | 102 | 14:00
19 | Baroirhat | 63 | 00:00 | 85 | Khagrachori | 32 | 19:00 | 151 | Satkhira | 142 | 21:00
20 | Bashundhara | 223 | 15:00 | 86 | Khulna | 63 | 13:00 | 152 | Satmasjid | 114 | 16:00
21 | BashundharaCement | 9 | 16:00 | 87 | Khulshi | 189 | 17:00 | 153 | Savar | 234 | 18:30
22 | Beanibazar | 78 | 00:00 | 88 | Kishoreganj | 136 | 19:00 | 154 | SevenRings | 16.57 | 05:00
23 | Benapole | 72 | 20:00 | 89 | Kodda | 302 | 19:30 | 155 | ShahCement | 38 | 02:00
24 | Bhaluka | 162 | 01:00 | 90 | Kulaura | 51 | 00:00 | 156 | Shahjadpur | 103 | 20:00
25 | Bhandaria | 90 | 01:00 | 91 | Kurigram | 28 | 22:00 | 157 | Shahjibazar | 115 | 21:00
26 | Bhangura | 50 | 19:30 | 92 | Kushtia | 162 | 19:00 | 158 | Shahmirpur | 64 | 01:00
27 | Bheramara(GK) | 70 | 00:00 | 93 | Lalbag | 72 | 13:00 | 159 | Shariatpur | 97 | 00:00
28 | Bhulta | 227 | 01:00 | 94 | Lalmonirhat | 45 | 19:00 | 160 | Sherpur | 140 | 19:00
29 | Bog-Sherpur | 82 | 00:00 | 95 | MI_Cement | 18.4 | 18:00 | 161 | Shikalbaha | 30 | 19:00
30 | Bogura | 186 | 20:00 | 96 | Madanganj | 48 | 19:00 | 162 | Shitalakhya | 93 | 15:00
31 | Borhanuddin | 94 | 22:00 | 97 | Madaripur | 118 | 01:00 | 163 | Sholosohor | 47 | 15:00
32 | Brahmanbaria | 133 | 20:00 | 98 | Madartek | 99.25 | 23:00 | 164 | Shyampur | 182 | 11:00
33 | Cantonment | 144 | 13:00 | 99 | Madunaghat | 54 | 20:00 | 165 | Siddhirganj | 128 | 15:00
34 | Chandina | 0 | 00:00 | 100 | Magura | 69 | 19:00 | 166 | Sirajganj | 130 | 19:30
35 | Chandpur | 80 | 00:00 | 101 | Mahasthangarh | 90 | 01:00 | 167 | Sonargaon | 132 | 00:00
36 | Chandraghona | 38 | 19:00 | 102 | Manikganj | 131 | 03:00 | 168 | Sreemongol | 85 | 21:00
37 | Chapai | 85 | 00:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 115 | 16:00
38 | Charsaidpur | 42 | 07:00 | 104 | Matarbari | 50 | 00:00 | 170 | Srinagar | 52.8 | 20:00
39 | Chauddagram | 79 | 00:00 | 105 | Matuail | 70 | 15:00 | 171 | Sunamganj | 57 | 22:00
40 | Chhatak | 37 | 00:00 | 106 | Millgate | 127 | 15:00 | 172 | Sylhet | 46 | 01:00
41 | Chowmuhani | 226 | 21:00 | 107 | Mirpur | 152 | 16:00 | 173 | Sylhet-132 | 119 | 21:00
42 | Chuadanga | 114 | 21:00 | 108 | Mirsorai | 10 | 17:00 | 174 | TK | 37 | 00:00
43 | Coxsbazar | 140 | 19:30 | 109 | Mirzapur | 52 | 11:00 | 175 | Tangail | 202 | 01:00
44 | Cumilla(N) | 174 | 00:00 | 110 | Mithapukur | 54 | 16:00 | 176 | Thakurgaon | 103 | 00:00
45 | Cumilla(S) | 180 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 139 | 11:00
46 | Daudkandi | 144 | 02:00 | 112 | Mogbazar | 175.7 | 15:00 | 178 | Ullahpara | 49 | 01:00
47 | Dhaka | 70 | 12:00 | 113 | Mongla | 49 | 15:00 | 179 | Ullon | 44 | 00:00
48 | Dhamrai | 140 | 18:30 | 114 | Motijheel | 46 | 13:00 | 180 | Uttara | 103 | 15:00
49 | Dhanmondi | 176 | 13:00 | 115 | Muktagacha | 40 | 00:00 | 181 | UttaraNew | 57 | 00:00
50 | Dohazari | 102 | 19:00 | 116 | Munshiganj | 131 | 22:00 | 182 | Zigatola | 82 | 15:00
51 | Faridpur | 185 | 22:00 | 117 | Muradnagar | 30 | 22:00
52 | Fatullah | 115 | 15:00 | 118 | Mymensingh | 216 | 21:00
53 | Fenchuganj | 42 | 00:00 | 119 | Naogaon | 167 | 01:00
54 | Feni | 125 | 00:00 | 120 | Narail | 61 | 19:00
55 | GPH | 74 | 13:00 | 121 | Narinda | 85 | 13:00
56 | Ghatail | 98 | 01:00 | 122 | Narshingdi | 195 | 21:00
57 | Ghorashal | 16 | 10:00 | 123 | Natore | 178 | 21:00
58 | Ghorashal-230 | 102 | 19:30 | 124 | Nawabganj | 67.2 | 21:00
59 | Goalpara | 38 | 23:00 | 125 | Netrakona | 122 | 20:00
60 | Gollamari | 100 | 23:00 | 126 | New | 78.3 | 00:00
61 | Gopalganj | 111 | 00:00 | 127 | Niamatpur | 118 | 00:00
62 | Gulshan | 142 | 13:00 | 128 | Noapara | 49 | 19:30
63 | Halishahar | 85 | 15:00 | 129 | PHP | 6 | 13:00
64 | HaripurSBU | 175 | 21:00 | 130 | Pabna | 132 | 19:30
65 | Hasnabad | 95 | 20:00 | 131 | Palashbari | 120 | 19:00
66 | Hathazari | 89 | 20:00 | 132 | Panchagarh | 55 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15060.24 | 350 |  | 15425.99
1:00 | 14950.78 | 96 |  | 15050.78
2:00 | 14440.81 | 57 |  | 14500.81
3:00 | 13582.8 | 0 |  | 13582.8
4:00 | 13004.71 | 0 |  | 13004.71
5:00 | 12782.36 | 0 |  | 12782.36
6:00 | 12534.42 | 0 |  | 12534.42
7:00 | 12570.28 | 0 |  | 12570.28
8:00 | 12465.22 | 18 |  | 12484.22
9:00 | 12963.55 | 37 |  | 13002.55
10:00 | 13317.37 | 53 |  | 13372.37
11:00 | 13863.31 | 66 |  | 13932.31
12:00 | 14361.46 | 116 |  | 14482.46
13:00 | 14662.01 | 143 |  | 14811.01
14:00 | 14672.46 | 144 |  | 14822.46
15:00 | 14764.26 | 276 |  | 15052.26
16:00 | 14473.43 | 266 |  | 14751.43
17:00 | 14332.23 | 191 |  | 14532.23
18:00 | 14187.09 | 110 |  | 14302.09
19:00 | 15525.18 | 138 |  | 15669.18
19:30 | 15892.58 | 151 |  | 16050.58
20:00 | 15878.45 | 130 |  | 16014.45
21:00 | 15851.97 | 95 |  | 15950.97
22:00 | 15577.97 | 194 |  | 15780.97
23:00 | 15542.89 | 199 |  | 15750.85
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 9495.2 | 5565.04 | 15060.24 | DAILY GENERATION CURVE
00:30 | 9340.2 | 5665.31 | 15005.51
01:00 | 9185.2 | 5765.58 | 14950.78 | 27-04-2025
01:30 | 8992.2 | 5703.595 | 14695.795
02:00 | 8799.2 | 5641.61 | 14440.81
02:30 | 8440.95 | 5570.855 | 14011.805
03:00 | 8082.7 | 5500.1 | 13582.8
03:30 | 7966.2 | 5327.555 | 13293.755
04:00 | 7849.7 | 5155.01 | 13004.71
04:30 | 7777.7 | 5115.835 | 12893.535
05:00 | 7705.7 | 5076.66 | 12782.36
05:30 | 7576.315 | 5082.075 | 12658.39
06:00 | 7446.93 | 5087.49 | 12534.42
06:30 | 7471.67 | 5080.68 | 12552.35
07:00 | 7496.41 | 5073.87 | 12570.28
07:30 | 7407.615 | 5110.135 | 12517.75
08:00 | 7318.82 | 5146.4 | 12465.22
08:30 | 7477.96 | 5236.425 | 12714.385
09:00 | 7637.1 | 5326.45 | 12963.55
09:30 | 7759.065 | 5381.395 | 13140.46
10:00 | 7881.03 | 5436.34 | 13317.37
10:30 | 8152.16 | 5438.18 | 13590.34
11:00 | 8423.29 | 5440.02 | 13863.31
11:30 | 8604.325 | 5508.06 | 14112.385
12:00 | 8785.36 | 5576.1 | 14361.46
12:30 | 8784.825 | 5726.91 | 14511.735
13:00 | 8784.29 | 5877.72 | 14662.01
13:30 | 8849.025 | 5818.21 | 14667.235
14:00 | 8913.76 | 5758.7 | 14672.46
14:30 | 8784.32 | 5934.04 | 14718.36
15:00 | 8654.88 | 6109.38 | 14764.26
15:30 | 8609.565 | 6009.28 | 14618.845
16:00 | 8564.25 | 5909.18 | 14473.43
16:30 | 8586.93 | 5815.9 | 14402.83
17:00 | 8609.61 | 5722.62 | 14332.23
17:30 | 8553.115 | 5706.545 | 14259.66
18:00 | 8496.62 | 5690.47 | 14187.09
18:30 | 8893.81 | 5962.325 | 14856.135
19:00 | 9291 | 6234.18 | 15525.18
19:30 | 9416.2 | 6476.38 | 15892.58
20:00 | 9400.7 | 6477.75 | 15878.45
20:30 | 9398.2 | 6467.01 | 15865.21 |  | Executive Engineer
21:00 | 9395.7 | 6456.27 | 15851.97 |  | Network Operation Division
21:30 | 9274.85 | 6440.12 | 15714.97
22:00 | 9154 | 6423.97 | 15577.97
22:30 | 9156 | 6404.43 | 15560.43
23:00 | 9158 | 6384.89 | 15542.89

## En-Curve
QF-LDC-12
Date | 27-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3416 | 2246 | 913 | 0 | 46 | 1359.84 | 40 | 3105 | 0 | 717 | 3203.4 | 0 | 0 | 14 | 350 | DAILY ENERGY CURVE
00:30 | 3422 | 2290 | 913 | 0 | 45 | 1359.61 | 40 | 3076.5 | 0 | 711 | 3133.4 | 0 | 0 | 15 | 223 | 27-04-2025
01:00 | 3428 | 2334 | 913 | 0 | 44 | 1359.38 | 40 | 3048 | 0 | 705 | 3063.4 | 0 | 0 | 16 | 96
01:30 | 3407 | 2371.5 | 912.5 | 0 | 44 | 1357.395 | 40 | 2993.5 | 0 | 607 | 2950.4 | 0 | 0 | 12.5 | 76.5 | Energy Generated | 345.944 |  | MKWHr
02:00 | 3386 | 2409 | 912 | 0 | 44 | 1355.41 | 40 | 2939 | 0 | 509 | 2837.4 | 0 | 0 | 9 | 57 | Energy not Served | 2.679 |  | MKWHr
02:30 | 3409 | 2433.25 | 912.5 | 0 | 43 | 1357.255 | 40 | 3027 | 0 | 435.5 | 2349.3 | 0 | 0 | 5 | 28.5 | Total Energy Requirement | 348.623 |  | MKWHr
03:00 | 3432 | 2457.5 | 913 | 0 | 42 | 1359.1 | 40 | 3115 | 0 | 362 | 1861.2 | 0 | 0 | 1 | 0
03:30 | 3484.5 | 2426.5 | 912.5 | 0 | 41 | 1362.555 | 40 | 3186.5 | 0 | 292 | 1547.7 | 0 | 0 | 0.5 | 0
04:00 | 3537 | 2395.5 | 912 | 0 | 40 | 1366.01 | 40 | 3258 | 0 | 222 | 1234.2 | 0 | 0 | 0 | 0
04:30 | 3571.5 | 2400.5 | 912.5 | 0 | 40 | 1363.835 | 40 | 3263.5 | 0 | 207 | 1091.7 | 0 | 0 | 3 | 0
05:00 | 3606 | 2405.5 | 913 | 0 | 40 | 1361.66 | 40 | 3269 | 0 | 192 | 949.2 | 0 | 0 | 6 | 0
05:30 | 3580 | 2406.5 | 915.5 | 0 | 39 | 1361.78 | 40 | 3270.5 | 10.01 | 180 | 845.6 | 0 | 0 | 9.5 | 0
06:00 | 3554 | 2407.5 | 918 | 0 | 38 | 1361.9 | 40 | 3272 | 20.02 | 168 | 742 | 0 | 0 | 13 | 0
06:30 | 3517.5 | 2390.25 | 918.5 | 0 | 37 | 1360.395 | 40 | 3272 | 62.205 | 168 | 772.5 | 0 | 0 | 14 | 0
07:00 | 3481 | 2373 | 919 | 0 | 36 | 1358.89 | 40 | 3272 | 104.39 | 168 | 803 | 0 | 0 | 15 | 0
07:30 | 3497 | 2359.3 | 897 | 0 | 33 | 1361.945 | 40 | 3257.5 | 169.005 | 145.5 | 749.5 | 0 | 0 | 8 | 9
08:00 | 3513 | 2345.6 | 875 | 0 | 30 | 1365 | 40 | 3243 | 233.62 | 123 | 696 | 0 | 0 | 1 | 18
08:30 | 3501.5 | 2394.15 | 874.5 | 0 | 32 | 1339.5 | 40 | 3274.5 | 312.235 | 164.5 | 778 | 0 | 0 | 3.5 | 27.5
09:00 | 3490 | 2442.7 | 874 | 0 | 34 | 1314 | 40 | 3306 | 390.85 | 206 | 860 | 0 | 0 | 6 | 37
09:30 | 3522.5 | 2446.85 | 898.5 | 0 | 33 | 1292 | 40 | 3313 | 440.11 | 221 | 930 | 0 | 0 | 3.5 | 45
10:00 | 3555 | 2451 | 923 | 0 | 32 | 1270 | 40 | 3320 | 489.37 | 236 | 1000 | 0 | 0 | 1 | 53
10:30 | 3567.5 | 2479 | 923.5 | 0 | 33 | 1270 | 40 | 3309.5 | 503.34 | 258 | 1206 | 0 | 0 | 0.5 | 59.5
11:00 | 3580 | 2507 | 924 | 0 | 34 | 1270 | 40 | 3299 | 517.31 | 280 | 1412 | 0 | 0 | 0 | 66
11:30 | 3695.5 | 2473 | 923.5 | 0 | 35 | 1276 | 40 | 3312.5 | 559.385 | 297 | 1495 | 0 | 0 | 5.5 | 91
12:00 | 3811 | 2439 | 923 | 0 | 36 | 1282 | 40 | 3326 | 601.46 | 314 | 1578 | 0 | 0 | 11 | 116
12:30 | 3777 | 2413.25 | 923 | 0 | 37 | 1323.5 | 40 | 3391 | 566.985 | 318 | 1712.5 | 0 | 0 | 9.5 | 129.5
13:00 | 3743 | 2387.5 | 923 | 0 | 38 | 1365 | 40 | 3456 | 532.51 | 322 | 1847 | 0 | 0 | 8 | 143
13:30 | 3762.5 | 2417.5 | 923 | 0 | 38 | 1363.6 | 38.5 | 3441 | 476.135 | 304.5 | 1895.5 | 0 | 0 | 7 | 143.5
14:00 | 3782 | 2447.5 | 923 | 0 | 38 | 1362.2 | 37 | 3426 | 419.76 | 287 | 1944 | 0 | 0 | 6 | 144
14:30 | 3772 | 2390 | 923.5 | 0 | 38 | 1366.33 | 36.5 | 3533 | 353.03 | 287.5 | 2013.5 | 0 | 0 | 5 | 210
15:00 | 3762 | 2332.5 | 924 | 0 | 38 | 1370.46 | 36 | 3640 | 286.3 | 288 | 2083 | 0 | 0 | 4 | 276
15:30 | 3727 | 2330.75 | 923.5 | 0 | 37 | 1365.01 | 38 | 3611 | 234.585 | 288 | 2060.5 | 0 | 0 | 3.5 | 271
16:00 | 3692 | 2329 | 923 | 0 | 36 | 1359.56 | 40 | 3582 | 182.87 | 288 | 2038 | 0 | 0 | 3 | 266
16:30 | 3742.5 | 2338.5 | 923 | 0 | 37 | 1360.3 | 40 | 3569.5 | 127.53 | 300.5 | 1959.5 | 0 | 0 | 4.5 | 228.5
17:00 | 3793 | 2348 | 923 | 0 | 38 | 1361.04 | 40 | 3557 | 72.19 | 313 | 1881 | 0 | 0 | 6 | 191
17:30 | 3791 | 2302 | 922.5 | 0 | 39 | 1363.645 | 40 | 3558.5 | 40.015 | 354.5 | 1845.5 | 0 | 0 | 3 | 150.5
18:00 | 3789 | 2256 | 922 | 0 | 40 | 1366.25 | 40 | 3560 | 7.84 | 396 | 1810 | 0 | 0 | 0 | 110
18:30 | 3809 | 2311 | 906.5 | 0 | 42 | 1365.715 | 40 | 3779.5 | 3.92 | 551 | 2046.5 | 0 | 0 | 1 | 124
19:00 | 3829 | 2366 | 891 | 0 | 44 | 1365.18 | 40 | 3999 | 0 | 706 | 2283 | 0 | 0 | 2 | 138
19:30 | 3818 | 2308 | 875 | 0 | 42 | 1368.38 | 40 | 4037 | 0 | 758 | 2643.2 | 0 | 0 | 3 | 151
20:00 | 3790 | 2287.5 | 876 | 0 | 44 | 1365.75 | 40 | 4057 | 0 | 798 | 2618.2 | 0 | 0 | 2 | 130
20:30 | 3812.5 | 2287 | 899 | 0 | 43 | 1364.51 | 40 | 4062.5 | 0 | 801 | 2554.7 | 0 | 0 | 1 | 112.5
21:00 | 3835 | 2286.5 | 922 | 0 | 42 | 1363.27 | 40 | 4068 | 0 | 804 | 2491.2 | 0 | 0 | 0 | 95
21:30 | 3831 | 2311.25 | 922 | 0 | 42 | 1368.62 | 40 | 4142.5 | 0 | 734.5 | 2323.1 | 0 | 0 | 0 | 144.5
22:00 | 3827 | 2336 | 922 | 0 | 42 | 1373.97 | 40 | 4217 | 0 | 665 | 2155 | 0 | 0 | 0 | 194
22:30 | 3829 | 2347 | 922 | 0 | 43 | 1363.93 | 40 | 4205.5 | 0 | 658 | 2152 | 0 | 0 | 0 | 196.5
23:00 | 3831 | 2358 | 922 | 0 | 44 | 1353.89 | 40 | 4194 | 0 | 651 | 2149 | 0 | 0 | 0 | 199
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 18:00 | 373 | 10:00 | Payra | 413 | 18:00 | 400 | 12:00
Ashuganj | 399 | 2:00 | 377 | 10:00 | Rahanpur | 413 | 01:00 | 400 | 14:00
Bhulta | 392 | 02:00 | 373 | 10:00 | Rampal | 399 | 18:00 | 376 | 12:00
Bibiana | 387 | 17:00 | 379 | 10:00
BIPTC | 400 | 09:00 | 390 | 23:00
Bogura | 409 | 01:00 | 390 | 22:00
Gopalganj | 395 | 18:00 | 378 | 13:00
Kaliakoir | 363 | 20:00 | 347 | 10:00
Madunaghat | 400 | 02:00 | 389 | 11:00
Meghnaghat | 390 | 02:00 | 379 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 02:00 | 213 | 10:00 | Keranigonj | 221 | 02:00 | 212 | 10:00
AKSML | 231 | 02:00 | 221 | 10:00 | Khulna(S) | 228 | 18:00 | 212 | 13:00
Aminbazar | 222 | 00:00 | 213 | 12:00 | Madunaghat | 238 | 17:00 | 223 | 10:00
Ashuganj | 229 | 05:00 | 221 | 10:00 | Madunaghat-400 | 234 | 00:00 | 224 | 11:00
Ashuganj-400 | 229 | 05:00 | 221 | 10:00 | Maniknagar | 221 | 07:00 | 210 | 10:00
Baghabari | 229 | 00:00 | 222 | 13:00 | Meghnaghat | 230 | 06:00 | 220 | 10:00
Barapukuria | 226 | 01:00 | 216 | 12:00 | Meghnaghat-400 | 225 | 02:00 | 216 | 10:00
Barapukuria-230 | 226 | 01:00 | 216 | 12:00 | Mirsorai | 232 | 01:00 | 216 | 10:00
Barishal | 238 | 18:00 | 220 | 00:00 | Rajshahi | 233 | 18:00 | 219 | 14:00
Bheramara | 233 | 18:00 | 221 | 14:00 | Rampal | 228 | 18:00 | 212 | 12:00
Bhulta | 222 | 02:00 | 211 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 223 | 06:00 | 217 | 10:00 | Rampura | 221 | 03:00 | 209 | 10:00
BIPTC | 234 | 18:00 | 219 | 14:00 | Shikalbaha | 232 | 00:00 | 221 | 10:00
Bogura | 228 | 01:00 | 218 | 22:00 | Shyampur | 222 | 02:00 | 212 | 10:00
Bogura-400 | 228 | 01:00 | 218 | 22:00 | Siddhirganj | 223 | 00:00 | 220 | 05:00
Borhanuddin | 242 | 18:00 | 220 | 00:00 | Sirajgonj | 238 | 03:00 | 232 | 22:00
BSRM | 230 | 02:00 | 216 | 10:00 | Sreepur | 229 | 03:00 | 220 | 11:00
Cumilla(N) | 220 | 05:00 | 214 | 10:00 | Tongi | 220 | 17:00 | 212 | 09:00
Faridpur | 236 | 17:00 | 217 | 00:00
Fenchuganj | 224 | 02:00 | 218 | 14:00
Ghorashal | 228 | 01:00 | 224 | 00:00
Ghorashal-230 | 222 | 02:00 | 212 | 10:00
Gopalganj | 239 | 17:00 | 220 | 00:00
GPH | 232 | 01:00 | 220 | 10:00
Haripur | 222 | 07:00 | 212 | 10:00
Hasnabad | 222 | 02:00 | 212 | 10:00
Hathazari | 232 | 00:00 | 221 | 10:00
Ishurdi | 234 | 18:00 | 222 | 14:00
Jhenaidah | 226 | 19:30 | 210 | 14:00
Kaliakoir | 224 | 00:00 | 213 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 06:00 | 122 | 11:00 | Madartek | 132 | 02:00 | 121 | 11:00
Agargaon | 131 | 02:00 | 123 | 13:00 | Madunaghat | 134 | 01:00 | 127 | 10:00
Agrabad | 133 | 00:00 | 125 | 10:00 | Magura | 132 | 01:00 | 118 | 23:00
AKS | 131 | 01:00 | 125 | 10:00 | Mahasthangarh | 134 | 00:00 | 126 | 13:00
Aminbazar | 129 | 02:00 | 121 | 12:00 | Manikganj | 128 | 07:00 | 110 | 10:00
Amnura | 136 | 00:00 | 124 | 15:00 | Maniknagar | 130 | 07:00 | 122 | 10:00
Ashuganj | 135 | 01:00 | 131 | 14:00 | Matarbari | 118 | 17:00 | 110 | 22:00
Bagerhat | 136 | 18:00 | 117 | 14:00 | Matuail | 128 | 01:00 | 122 | 10:00
Bajitpur | 134 | 03:00 | 125 | 14:00 | Millgate | 126 | 00:00 | 118 | 10:00
Bakulia | 134 | 00:00 | 127 | 08:00 | Mirpur | 128 | 04:00 | 120 | 10:00
Banani | 133 | 02:00 | 121 | 12:00 | Mirzapur | 127 | 20:00 | 116 | 10:00
Bangabhaban | 130 | 02:00 | 120 | 12:00 | Mithapukur | 137 | 01:00 | 123 | 14:00
Barapukuria | 137 | 01:00 | 128 | 12:00 | MI_Cement | 130 | 01:00 | 122 | 10:00
Barguna | 134 | 01:00 | 129 | 05:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 17:00 | 125 | 00:00 | Mogbazar | 135 | 03:00 | 122 | 11:00
Barishal-230 | 131 | 17:00 | 123 | 00:00 | Mongla | 136 | 18:00 | 118 | 14:00
Baroaulia | 135 | 00:00 | 121 | 01:00 | Motijheel | 130 | 02:00 | 120 | 12:00
Baroirhat | 123 | 07:00 | 118 | 20:00 | Muktagacha | 131 | 20:00 | 118 | 13:00
Bashundhara | 133 | 02:00 | 117 | 10:00 | Munshiganj | 128 | 02:00 | 121 | 10:00
BashundharaCement | 130 | 07:00 | 121 | 10:00 | Muradnagar | 125 | 07:00 | 116 | 23:00
Beanibazar | 134 | 03:00 | 124 | 00:00 | Mymensingh | 131 | 19:00 | 114 | 00:00
Benapole | 134 | 00:00 | 115 | 14:00 | Naogaon | 127 | 06:00 | 120 | 22:00
Bhaluka | 131 | 19:30 | 122 | 10:00 | Narail | 132 | 07:00 | 118 | 14:00
Bhandaria | 130 | 17:00 | 116 | 22:00 | Narinda | 128 | 07:00 | 110 | 10:00
Bhangura | 129 | 01:00 | 125 | 14:00 | Narshingdi | 128 | 01:00 | 115 | 10:00
Bheramara | 134 | 18:00 | 125 | 14:00 | Natore | 132 | 00:00 | 124 | 14:00
Bheramara(GK) | 134 | 18:00 | 124 | 23:00 | Nawabganj | 132 | 04:00 | 124 | 12:00
Bhulta | 125 | 05:00 | 117 | 10:00 | Netrakona | 123 | 19:30 | 112 | 11:00
Bog-Sherpur | 131 | 01:00 | 125 | 22:00 | New | 127 | 00:00 | 119 | 09:00
Bogura | 135 | 01:00 | 128 | 22:00 | Niamatpur | 134 | 09:00 | 129 | 22:00
Bogura-230 | 135 | 01:00 | 128 | 22:00 | Noapara | 135 | 00:00 | 121 | 13:00
Brahmanbaria | 131 | 21:00 | 121 | 23:00 | Pabna | 132 | 09:00 | 125 | 22:00
Cantonment | 131 | 02:00 | 123 | 10:00 | Palashbari | 134 | 01:00 | 121 | 14:00
Chandina | 126 | 00:00 | 122 | 20:00 | Panchagarh | 138 | 15:00 | 119 | 12:00
Chandpur | 129 | 16:00 | 118 | 08:00 | Patuakhali | 137 | 02:00 | 130 | 05:00
Chandraghona | 134 | 01:00 | 128 | 11:00 | Payra | 135 | 15:00 | 131 | 12:00
Chapai | 131 | 13:00 | 127 | 15:00 | PHP | 122 | 16:00 | 116 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 02:00 | 122 | 10:00 | Postogola | 130 | 00:00 | 124 | 12:00
Chauddagram | 122 | 09:00 | 118 | 02:00 | Purbachal | 133 | 02:00 | 121 | 12:00
Chhatak | 133 | 06:00 | 122 | 00:00 | Purbasadipur | 132 | 01:00 | 117 | 12:00
Chowmuhani | 120 | 11:00 | 111 | 22:00 | Rahanpur | 136 | 01:00 | 131 | 22:00
Chuadanga | 131 | 18:00 | 115 | 23:00 | Rahanpur-400 | 137 | 02:00 | 132 | 22:00
Coxsbazar | 117 | 17:00 | 110 | 18:30 | Rahim | 132 | 02:00 | 123 | 10:00
Cumilla(N) | 126 | 00:00 | 122 | 10:00 | Rajbari | 137 | 17:00 | 126 | 00:00
Cumilla(S) | 132 | 04:00 | 119 | 23:00 | Rajendrapur | 133 | 03:00 | 119 | 12:00
Daudkandi | 128 | 18:00 | 113 | 23:00 | Rajshahi | 132 | 18:00 | 125 | 14:00
Dhaka | 133 | 01:00 | 123 | 10:00 | Rajshahi-230 | 133 | 01:00 | 118 | 22:00
Dhamrai | 131 | 20:00 | 123 | 10:00 | Ramganj | 123 | 02:00 | 112 | 08:00
Dhanmondi | 133.5 | 06:00 | 122 | 12:00 | Rampur | 132 | 00:00 | 125 | 12:00
Dohazari | 129 | 00:00 | 124 | 10:00 | Rampura | 133 | 02:00 | 122 | 11:00
Faridpur | 138 | 17:00 | 129 | 00:00 | Rangamati | 133 | 04:00 | 126 | 10:00
Fatullah | 129 | 02:00 | 123 | 10:00 | Rangpur | 140 | 01:00 | 124 | 17:00
Fenchuganj | 135 | 04:00 | 130 | 22:00 | Ruppur | 136 | 18:00 | 130 | 14:00
Feni | 123 | 14:00 | 115 | 22:00 | Saidpur | 134 | 02:00 | 119 | 12:00
Ghatail | 126 | 03:00 | 114 | 10:00 | Satkhira | 135 | 00:00 | 117 | 14:00
Ghorashal | 133 | 01:00 | 129 | 11:00 | Satmasjid | 131 | 07:00 | 122 | 13:00
Goalpara | 135 | 18:00 | 122 | 13:00 | Savar | 128 | 03:00 | 119 | 10:00
Gollamari | 136 | 00:00 | 125 | 12:00 | SevenRings | 133 | 02:00 | 128 | 10:00
Gopalganj | 135 | 17:00 | 126 | 12:00 | ShahCement | 129 | 02:00 | 122 | 10:00
Gopalganj-400 | 137 | 18:00 | 130 | 10:00 | Shahjadpur | 138 | 04:00 | 130 | 13:00
Gulshan | 132 | 04:00 | 121 | 12:00 | Shahjibazar | 134 | 04:00 | 123 | 21:00
Halishahar | 134 | 01:00 | 125 | 10:00 | Shahmirpur | 136 | 01:00 | 128 | 10:00
Haripur | 128 | 01:00 | 123 | 10:00 | Shariatpur | 134 | 17:00 | 126 | 00:00
HaripurSBU | 128 | 03:00 | 123 | 10:00 | Sherpur | 137 | 04:00 | 121 | 13:00
Hasnabad | 130 | 01:00 | 124 | 09:00 | Shikalbaha | 125 | 01:00 | 117 | 10:00
Hathazari | 133 | 00:00 | 127 | 10:00 | Shikalbaha-230 | 136 | 00:00 | 128 | 10:00
Ishurdi | 136 | 08:00 | 130 | 14:00 | Shitalakhya | 130 | 01:00 | 122 | 10:00
Jaldhaka | 132 | 02:00 | 119 | 12:00 | Sholosohor | 134 | 00:00 | 127 | 10:00
Jamalpur | 139 | 20:00 | 125 | 13:00 | Shyampur | 129 | 18:00 | 122 | 10:00
Jashore | 130 | 01:00 | 117 | 14:00 | Shyampur-230 | 129 | 02:00 | 122 | 10:00
Jhenaidah | 132 | 18:00 | 120 | 14:00 | Siddhirganj | 130 | 01:00 | 122 | 10:00
Jhenaidah-230 | 132 | 18:00 | 121 | 14:00 | Sirajganj | 128 | 06:00 | 123 | 16:00
Joydebpur | 128 | 00:00 | 122 | 10:00 | Sonargaon | 128 | 02:00 | 120 | 10:00
Joypurhat | 123 | 06:00 | 114 | 22:00 | Sreemongol | 134 | 04:00 | 123 | 21:00
Juldah | 134 | 00:00 | 127 | 10:00 | Sreepur | 134 | 03:00 | 127 | 11:00
Kabirpur | 130 | 15:00 | 115 | 10:00 | Srinagar | 132 | 04:00 | 125 | 11:00
Kachua | 126 | 16:00 | 118 | 08:00 | SSM | 134 | 02:00 | 130 | 14:00
Kaliakoir | 134 | 19:00 | 123 | 10:00 | Sunamganj | 134 | 03:00 | 122 | 00:00
Kallyanpur | 129 | 05:00 | 121 | 12:00 | Sylhet | 134 | 03:00 | 126 | 00:00
Kalurghat | 134 | 00:00 | 128 | 11:00 | Sylhet-132 | 134 | 03:00 | 128 | 00:00
Kamrangirchar | 132 | 05:00 | 123 | 12:00 | Tangail | 126 | 15:00 | 114 | 10:00
Kaptai | 134 | 6:00 | 120 | 12:00 | Thakurgaon | 139 | 15:00 | 119 | 12:00
Kasba | 124 | 07:00 | 117 | 23:00 | TK | 136 | 00:00 | 128 | 13:00
Kazla | 129 | 02:00 | 120 | 13:00 | Tongi | 129 | 04:00 | 123 | 09:00
Keranigonj | 132 | 02:00 | 126 | 10:00 | Ullahpara | 129 | 19:00 | 125 | 12:00
Khagrachori | 131 | 00:00 | 125 | 10:00 | Ullon | 133 | 05:00 | 122 | 12:00
Khulna | 134 | 18:00 | 123 | 13:00 | Uttara | 128 | 03:00 | 120 | 12:00
Khulna(S) | 136 | 00:00 | 125 | 13:00 | UttaraNew | 128 | 02:00 | 120 | 10:00
Khulshi | 132 | 00:00 | 124 | 10:00 | Zigatola | 132 | 03:00 | 124 | 13:00
Kishoreganj | 131 | 07:00 | 122 | 01:00
Kodda | 129 | 20:00 | 119 | 10:00
KSRM | 133 | 00:00 | 126 | 07:00
Kulaura | 136 | 03:00 | 129 | 00:00
Kurigram | 138 | 04:00 | 123 | 13:00
Kushtia | 132 | 18:00 | 121 | 14:00
Lalbag | 132 | 06:00 | 124 | 12:00
Lalmonirhat | 138 | 01:00 | 122 | 12:00
Madanganj | 130 | 07:00 | 121 | 10:00
Madaripur | 135 | 18:00 | 129 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division