## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-04-2025 | [28 empty] | Date: | 28-04-2025 | [28 empty] | Date: | 28-04-2025 | [28 empty] | Date: | 28-04-2025 | [28 empty] | Date: | 28-04-2025 | [16 empty] | Date: | 28-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 113 | 110 | 295 | 55 | 35 | 72 | 0 | 68 | 420 | 293 | 370 | 0 | 55 | 0 | 328 | 0 | 0 | 0 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 101 | 69 | 0 | 100 | 100 | 0 | 40 | 34 | 20 | 354 | 0 | 0 | 0 | 0 | 51 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 8 | 0 | 353 | 330 | 10 | 204 | 34 | 115 | 50 | 175 | 26 | 20 | 98 | 44 | 52.2 | 0 | 38 | 300 | 320 | 369 | 39 | 30 | 0 | 101 | 8 | 0 | 83 | 25 | 0 | 17 | 174 | 17 | 86 | 141 | 0 | 0 | 0 | 10 | 8884.2 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 35 | 1362.76 | 0 | 35 | 0 | 105 | 12 | 89 | 100 | 0 | 25 | 0 | 30 | 0 | 166 | 0 | 157 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 170 | 57 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 317 | 1020 | 0 | 6565.76 | 15449.96 | 80.8
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 113 | 80 | 295 | 55 | 35 | 17 | 0 | 50 | 420 | 293 | 370 | 0 | 55 | 0 | 326 | 0 | 0 | 0 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 15 | 0 | 0 | 84 | 63 | 0 | 100 | 100 | 0 | 40 | 34 | 17 | 212 | 0 | 0 | 0 | 0 | 51 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 112 | 8 | 0 | 355 | 330 | 10 | 205 | 34 | 115 | 50 | 178 | 9 | 20 | 98 | 42 | 52.2 | 0 | 38 | 300 | 320 | 373 | 39 | 30 | 0 | 102 | 0 | 0 | 83 | 25 | 0 | 17 | 174 | 17 | 48 | 95 | 0 | 0 | 0 | 12 | 8482.2 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 35 | 1358.79 | 0 | 35 | 0 | 113 | 0 | 0 | 113 | 36 | 52.2 | 0 | 30 | 0 | 166 | 0 | 157 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 168 | 54 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 317 | 1011 | 0 | 6530.99 | 15013.19 | 80.49
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 113 | 64 | 195 | 55 | 35 | 17 | 0 | 51 | 420 | 277 | 370 | 0 | 55 | 0 | 324 | 0 | 0 | 0 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 22 | 0 | 0 | 51 | 63 | 0 | 100 | 100 | 0 | 40 | 17 | 29 | 155 | 0 | 0 | 0 | 0 | 17 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 8 | 0 | 359 | 330 | 10 | 200 | 34 | 115 | 50 | 163 | 9 | 20 | 98 | 42 | 52.2 | 0 | 38 | 295 | 320 | 386 | 39 | 30 | 0 | 90 | 0 | 0 | 83 | 28 | 0 | 17 | 174 | 17 | 48 | 95 | 0 | 0 | 0 | 12 | 8219.2 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 35 | 1366.77 | 0 | 35 | 0 | 113 | 0 | 0 | 113 | 36 | 52.2 | 0 | 30 | 0 | 166 | 0 | 157 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 168 | 47 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 319 | 950 | 0 | 6473.97 | 14693.17 | 80.49
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 113 | 64 | 145 | 0 | 35 | 17 | 0 | 51 | 420 | 283 | 370 | 0 | 55 | 0 | 322 | 0 | 0 | 0 | 52 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 63 | 0 | 100 | 50 | 0 | 40 | 17 | 29 | 156 | 0 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 1224 | 0 | 51 | 117 | 8 | 0 | 359 | 330 | 10 | 205 | 34 | 115 | 45 | 161 | 9 | 20 | 98 | 40 | 52.2 | 0 | 38 | 295 | 320 | 300 | 39 | 30 | 0 | 81 | 0 | 0 | 83 | 28 | 0 | 17 | 174 | 17 | 47 | 94 | 0 | 0 | 0 | 12 | 7900.2 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 511 | 17 | 1362.84 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 166 | 0 | 157 | 0 | 154 | 0 | 414 | 0 | 0 | 0 | 173 | 53 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 320 | 938 | 0 | 6057.84 | 13958.04 | 80.48
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 113 | 48 | 45 | 0 | 35 | 17 | 0 | 51 | 420 | 284 | 450 | 0 | 17 | 0 | 324 | 0 | 0 | 0 | 52 | 19 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 100 | 30 | 0 | 40 | 0 | 32 | 157 | 0 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 1150 | 0 | 51 | 80 | 8 | 0 | 356 | 330 | 10 | 211 | 34 | 115 | 45 | 166 | 9 | 20 | 98 | 38 | 52.2 | 0 | 38 | 300 | 320 | 301 | 39 | 30 | 0 | 83 | 0 | 0 | 83 | 28 | 0 | 17 | 174 | 17 | 49 | 95 | 0 | 0 | 0 | 12 | 7690.2 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 1256.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 157 | 0 | 155 | 0 | 414 | 0 | 0 | 0 | 171 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 220 | 0 | 320 | 899 | 0 | 5578.95 | 13269.15 | 80.48
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 17 | 101 | 48 | 15 | 0 | 35 | 17 | 0 | 16 | 420 | 305 | 450 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 52 | 18.5 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 100 | 10 | 0 | 40 | 0 | 33 | 157 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1100 | 0 | 51 | 12 | 8 | 0 | 349 | 330 | 10 | 210 | 34 | 115 | 45 | 168 | 9 | 20 | 98 | 38 | 52.2 | 0 | 38 | 300 | 320 | 333 | 39 | 30 | 0 | 85 | 0 | 0 | 83 | 28 | 0 | 17 | 174 | 17 | 49 | 95 | 0 | 0 | 0 | 12 | 7449.7 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461 | 0 | 1190.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 155 | 0 | 153 | 0 | 300 | 0 | 0 | 0 | 171 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 120 | 220 | 0 | 320 | 891 | 0 | 5388.93 | 12838.63 | 80.47
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 91 | 48 | 15 | 0 | 35 | 17 | 0 | 16 | 380 | 265 | 400 | 0 | 0 | 0 | 264 | 0 | 0 | 1 | 52 | 18 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 88 | 10 | 0 | 40 | 0 | 33 | 157 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1105 | 1 | 51 | 12 | 8 | 0 | 359 | 330 | 10 | 203 | 34 | 102 | 45 | 167 | 9 | 20 | 41 | 36 | 52.2 | 5 | 38 | 285 | 320 | 303 | 39 | 30 | 0 | 82 | 0 | 0 | 84 | 30 | 0 | 17 | 174 | 17 | 49 | 95 | 0 | 0 | 0.83 | 12 | 7113.03 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.95 | 415 | 0 | 980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0.05 | 0 | 170 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 200 | 10 | 120 | 180 | 0 | 320 | 864 | 0 | 4885.01 | 11998.04 | 80.47
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 114 | 48 | 0 | 0 | 35 | 17 | 0 | 16 | 380 | 300 | 400 | 0 | 0 | 0 | 275 | 0 | 0 | 6 | 17 | 18 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 68 | 0 | 1 | 40 | 0 | 30 | 157 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1102 | 5 | 51 | 10 | 8 | 0 | 357 | 330 | 10 | 198 | 34 | 70 | 45 | 115 | 9 | 19 | 17 | 34 | 8 | 11 | 38 | 280 | 320 | 307 | 39 | 30 | 0 | 80 | 0 | 0 | 84 | 30 | 0 | 17 | 174 | 17 | 25 | 45 | 0 | 0 | 2.02 | 12 | 6863.02 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.71 | 376 | 0 | 871.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 164 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0.1 | 0 | 200 | 9 | 120 | 180 | 0 | 320 | 830 | 0 | 4734.3 | 11597.32 | 80.46
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 11 | 17 | 113 | 0 | 0 | 0 | 17 | 17 | 0 | 16 | 380 | 305 | 400 | 0 | 0 | 0 | 285 | 0 | 0 | 11 | 0 | 18 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 68 | 0 | 2 | 40 | 0 | 6 | 156 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1002 | 10 | 51 | 0 | 8 | 0 | 351 | 330 | 10 | 201 | 34 | 50 | 40 | 101 | 9 | 8 | 17 | 32 | 8 | 33 | 38 | 295 | 320 | 326 | 39 | 30 | 0 | 80 | 0 | 0 | 84 | 30 | 0 | 17 | 174 | 17 | 8 | 8 | 0 | 1 | 0.81 | 0 | 6564.81 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.89 | 377 | 0 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 6.46 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0 | 0 | 178 | 58 | 0 | 0 | 0 | 0 | 0 | 1.1 | 37 | 0.28 | 0 | 150 | 8 | 120 | 180 | 0 | 320 | 750 | 0 | 4617.73 | 11182.54 | 80.46
09:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 17 | 17 | 100 | 32 | 0 | 0 | 28 | 17 | 0 | 10 | 380 | 304 | 370 | 0 | 0 | 0 | 294 | 0 | 0 | 13 | 0 | 18 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 68 | 0 | 3 | 40 | 0 | 2 | 156 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 955 | 15 | 43 | 1 | 8 | 0 | 349 | 330 | 10 | 203 | 34 | 56 | 40 | 108 | 9 | 6 | 32 | 22 | 8 | 45 | 38 | 300 | 320 | 316 | 39 | 30 | 0 | 83 | 0 | 0 | 81 | 30 | 0 | 17 | 174 | 17 | 8 | 8 | 0 | 1 | 9.86 | 6 | 6609.86 | 879 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.45 | 376 | 0 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 16.39 | 130 | 0 | 130 | 0 | 130 | 0 | 280 | 0 | 1.2 | 0 | 171 | 58 | 0 | 0 | 0 | 0 | 0 | 3.2 | 140 | 0.13 | 0 | 150 | 7 | 120 | 180 | 0 | 319 | 749 | 0 | 4795.37 | 11405.23 | 80.45
10:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 17 | 104 | 32 | 15 | 0 | 35 | 17 | 0 | 16 | 340 | 291 | 370 | 0 | 0 | 0 | 272 | 0 | 0 | 26 | 0 | 18 | 18 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 68 | 15 | 4 | 40 | 0 | 2 | 156 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 855 | 9 | 51 | 12 | 8 | 0 | 330 | 330 | 10 | 223 | 33 | 75 | 35 | 107 | 9 | 17 | 29 | 32 | 8 | 42 | 16 | 300 | 320 | 314 | 39 | 30 | 0 | 82 | 0 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 8 | 8 | 0 | 1 | 48.15 | 12 | 6485.15 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.95 | 374 | 0 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 45.8 | 130 | 0 | 130 | 0 | 130 | 0 | 280 | 0 | 2.68 | 0 | 172 | 58 | 0 | 0 | 0 | 0 | 0 | 3.9 | 186 | 0.6 | 0 | 150 | 7 | 120 | 180 | 0 | 320 | 700 | 0 | 4903.93 | 11389.08 | 80.45
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 20 | 95 | 32 | 15 | 0 | 35 | 54 | 0 | 16 | 340 | 313 | 370 | 0 | 0 | 0 | 296 | 0 | 0 | 31 | 0 | 18 | 18 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 68 | 20 | 4 | 40 | 0 | 3 | 158 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 855 | 14 | 51 | 12 | 8 | 0 | 330 | 330 | 10 | 206 | 31 | 96 | 40 | 127 | 9 | 0 | 34 | 32 | 8 | 39 | 16 | 295 | 320 | 334 | 39 | 30 | 0 | 88 | 0 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 8 | 27 | 0 | 2 | 52.34 | 12 | 6637.34 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.02 | 375 | 0 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 53.5 | 130 | 0 | 130 | 0 | 130 | 0 | 320 | 0 | 4.62 | 0 | 173 | 58 | 0 | 0 | 0 | 0 | 0 | 5.4 | 209 | 0.1 | 0 | 150 | 7 | 118 | 180 | 0 | 318 | 700 | 0 | 5047.64 | 11684.98 | 80.44
12:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 35 | 95 | 64 | 15 | 0 | 35 | 72 | 0 | 16 | 400 | 299 | 400 | 0 | 0 | 0 | 290 | 0 | 0 | 30 | 0 | 17.5 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 85 | 20 | 2 | 40 | 0 | 5 | 156 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 903 | 15 | 51 | 12 | 8 | 0 | 359 | 330 | 10 | 196 | 31 | 96 | 40 | 132 | 9 | 0 | 32 | 32 | 8 | 73 | 16 | 300 | 320 | 312 | 39 | 30 | 0 | 92 | 0 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 38 | 65 | 0 | 2 | 37.61 | 12 | 6996.11 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.23 | 376 | 0 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 58.78 | 138 | 0 | 187 | 0 | 190 | 0 | 350 | 0 | 5.04 | 0 | 171 | 58 | 0 | 18 | 0 | 0 | 0 | 2.8 | 129 | 0.76 | 0 | 150 | 6 | 118 | 220 | 0 | 318 | 730 | 0 | 5238.61 | 12234.72 | 80.43
13:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 0 | 96 | 64 | 0 | 0 | 35 | 54 | 0 | 16 | 400 | 296 | 400 | 0 | 0 | 0 | 282 | 0 | 0 | 32 | 17 | 19 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 100 | 50 | 5 | 40 | 0 | 4 | 156 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 904 | 17 | 51 | 0 | 8 | 0 | 359 | 330 | 10 | 197 | 33 | 52 | 40 | 114 | 9 | 0 | 14 | 28 | 0 | 67 | 0 | 300 | 320 | 317 | 39 | 30 | 0 | 86 | 0 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 55 | 83 | 0 | 1 | 48.79 | 12 | 6923.79 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.24 | 375 | 0 | 1131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 35.01 | 180 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 3 | 0 | 173 | 57 | 0 | 15 | 0 | 0 | 0 | 2.7 | 64 | 0.56 | 0 | 150 | 0 | 118 | 220 | 0 | 318 | 760 | 0 | 5193.51 | 12117.3 | 80.42
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 14 | 0 | 95 | 88 | 0 | 0 | 35 | 35 | 0 | 16 | 360 | 301 | 450 | 0 | 0 | 0 | 282 | 0 | 0 | 8 | 17 | 20.5 | 18 | 0 | 450 | 0 | 0 | 0 | 0 | 11 | 32 | 0 | 0 | 100 | 50 | 2 | 40 | 0 | 4 | 158 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 909 | 16 | 51 | 0 | 8 | 0 | 359 | 330 | 10 | 194 | 34 | 52 | 35 | 68 | 9 | 0 | 14 | 24 | 0 | 12 | 0 | 305 | 320 | 323 | 39 | 30 | 0 | 83 | 0 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 78 | 112 | 0 | 1 | 19.86 | 12 | 6863.36 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.15 | 376 | 0 | 1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 29.21 | 150 | 0 | 140 | 0 | 140 | 0 | 250 | 0 | 2.39 | 0 | 173 | 55 | 0 | 9 | 0 | 0 | 0 | 1.8 | 24 | 0.34 | 0 | 150 | 8 | 118 | 220 | 0 | 318 | 790 | 0 | 5328.89 | 12192.25 | 80.41
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 0 | 95 | 99 | 0 | 0 | 35 | 35 | 0 | 16 | 360 | 294 | 450 | 0 | 0 | 0 | 290 | 0 | 0 | 5 | 0 | 21 | 18 | 0 | 460 | 0 | 0 | 0 | 0 | 9 | 32 | 0 | 0 | 100 | 60 | 2 | 36 | 0 | 3 | 157 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 905 | 13 | 51 | 0 | 8 | 0 | 360 | 330 | 10 | 204 | 34 | 34 | 35 | 51 | 9 | 10 | 17 | 30 | 0 | 51 | 0 | 305 | 320 | 385 | 39 | 30 | 0 | 97 | 0 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 78 | 112 | 0 | 0 | 19.67 | 12 | 6995.67 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.85 | 380 | 0 | 1367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 18.62 | 150 | 0 | 140 | 0 | 140 | 0 | 230 | 0 | 1.53 | 0 | 173 | 56 | 0 | 2 | 0 | 0 | 0 | 1.8 | 18 | 0.01 | 0 | 187 | 8 | 118 | 220 | 0 | 319 | 800 | 0 | 5343.81 | 12339.48 | 80.4
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 0 | 95 | 99 | 0 | 0 | 35 | 35 | 0 | 16 | 360 | 297 | 400 | 0 | 0 | 0 | 275 | 0 | 0 | 1 | 17 | 21 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 9 | 32 | 0 | 0 | 100 | 60 | 2 | 37 | 0 | 2 | 157 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 853 | 8 | 51 | 0 | 8 | 0 | 350 | 330 | 10 | 189 | 35 | 34 | 35 | 34 | 26 | 10 | 14 | 26 | 0 | 31 | 0 | 290 | 320 | 358 | 39 | 30 | 0 | 89 | 0 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 78 | 113 | 0 | 1 | 11.35 | 12 | 6702.35 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.24 | 380 | 0 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 16.2 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 1.14 | 0 | 172 | 55 | 0 | 1 | 0 | 0 | 0 | 0.6 | 6 | 0.04 | 0 | 150 | 0 | 120 | 180 | 0 | 318 | 720 | 0 | 5090.22 | 11792.57 | 80.39
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 8 | 95 | 99 | 0 | 0 | 35 | 35 | 0 | 16 | 300 | 287 | 350 | 0 | 0 | 0 | 272 | 0 | 0 | 1 | 17 | 21 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 100 | 60 | 1 | 38 | 0 | 7 | 157 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 859 | 3 | 51 | 0 | 8 | 0 | 300 | 330 | 10 | 182 | 35 | 31 | 35 | 30 | 37 | 18 | 14 | 28 | 0 | 1 | 0 | 300 | 320 | 348 | 39 | 30 | 0 | 84 | 0 | 0 | 84 | 30 | 0 | 18 | 176 | 0 | 78 | 113 | 0 | 0 | 4.89 | 12 | 6521.89 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 379 | 0 | 1382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 6.2 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0.5 | 0 | 172 | 55 | 0 | 2 | 0 | 0 | 0 | 0.7 | 6 | 0 | 0 | 150 | 5 | 120 | 180 | 0 | 306 | 700 | 0 | 5050.4 | 11572.29 | 80.38
18:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 35 | 0 | 94 | 99 | 0 | 0 | 35 | 35 | 0 | 16 | 300 | 282 | 200 | 0 | 0 | 0 | 230 | 0 | 0 | 1 | 17 | 20.5 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 60 | 0 | 40 | 0 | 8 | 157 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 828 | 0 | 51 | 0 | 8 | 0 | 300 | 330 | 10 | 145 | 35 | 34 | 40 | 29 | 38 | 18 | 14 | 28 | 0 | 0 | 0 | 295 | 320 | 287 | 39 | 30 | 0 | 80 | 0 | 0 | 60 | 20 | 0 | 17 | 176 | 0 | 104 | 125 | 0 | 0 | 2.49 | 12 | 6096.99 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 380 | 0 | 1538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.76 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0.14 | 0 | 171 | 55 | 0 | 0 | 0 | 0 | 0 | 0.3 | 1 | 0 | 0 | 150 | 8 | 120 | 180 | 0 | 316 | 672 | 0 | 5166.1 | 11263.09 | 80.37
19:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 0 | 17 | 0 | 75 | 150 | 0 | 0 | 35 | 35 | 0 | 0 | 450 | 314 | 350 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 70 | 20.5 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 90 | 0 | 40 | 0 | 6 | 156 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 965 | 0 | 51 | 0 | 16 | 0 | 359 | 330 | 10 | 208 | 35 | 39 | 40 | 33 | 38 | 0 | 26 | 32 | 0 | 0 | 0 | 295 | 320 | 355 | 39 | 30 | 0 | 96 | 7 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 105 | 170 | 0 | 0 | 0 | 8 | 7152.5 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 166 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 5 | 120 | 220 | 0 | 318 | 660 | 0 | 5484 | 12636.5 | 80.36
19:30 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 17 | 0 | 80 | 150 | 0 | 0 | 35 | 35 | 0 | 0 | 450 | 298 | 350 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 20.5 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 100 | 0 | 40 | 0 | 9 | 156 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 8 | 0 | 360 | 330 | 10 | 192 | 35 | 50 | 40 | 61 | 38 | 7 | 45 | 34 | 0 | 0 | 0 | 300 | 320 | 315 | 39 | 30 | 0 | 96 | 7 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 106 | 171 | 0 | 0 | 0 | 12 | 7150.5 | 865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 501 | 0 | 1571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 164 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 120 | 220 | 0 | 319 | 780 | 0 | 5670 | 12820.5 | 0
20:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 0 | 89 | 114 | 0 | 0 | 35 | 17 | 0 | 0 | 450 | 293 | 350 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 70 | 20.5 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 100 | 0 | 40 | 0 | 8 | 155 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 960 | 0 | 51 | 0 | 8 | 0 | 359 | 330 | 10 | 187 | 36 | 45 | 50 | 60 | 38 | 7 | 47 | 32 | 0 | 0 | 0 | 300 | 320 | 315 | 39 | 30 | 0 | 97 | 7 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 85 | 171 | 0 | 0 | 0 | 12 | 7028.5 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 451 | 0 | 1569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 168 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 318 | 806 | 0 | 5648 | 12676.5 | 80.35
21:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 95 | 98 | 0 | 0 | 17 | 0 | 0 | 0 | 450 | 312 | 400 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 35 | 20.5 | 2 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 100 | 0 | 40 | 0 | 13 | 156 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 8 | 0 | 360 | 330 | 10 | 208 | 32 | 34 | 50 | 64 | 39 | 7 | 49 | 32 | 0 | 0 | 0 | 305 | 320 | 348 | 39 | 30 | 0 | 103 | 7 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 65 | 163 | 0 | 0 | 0 | 12 | 7094.5 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1567.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 167 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 5 | 120 | 220 | 0 | 319 | 850 | 0 | 5572.51 | 12667.01 | 80.34
22:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 95 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 300 | 400 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 17 | 20 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 87 | 100 | 0 | 40 | 0 | 15 | 156 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 8 | 0 | 359 | 330 | 10 | 195 | 35 | 34 | 50 | 51 | 38 | 19 | 47 | 32 | 0 | 0 | 0 | 295 | 320 | 380 | 39 | 30 | 0 | 106 | 7 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 45 | 164 | 0 | 0 | 0 | 12 | 7021 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1575.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 167 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 4 | 106 | 220 | 0 | 315 | 852 | 0 | 5561.11 | 12582.11 | 80.33
23:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 88 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 293 | 400 | 0 | 0 | 0 | 273 | 0 | 0 | 0 | 17 | 21 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 87 | 80 | 0 | 40 | 0 | 14 | 157 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 8 | 0 | 360 | 330 | 10 | 189 | 35 | 34 | 50 | 45 | 38 | 19 | 44 | 34 | 0 | 0 | 0 | 290 | 320 | 362 | 39 | 30 | 0 | 96 | 7 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 45 | 154 | 0 | 0 | 0 | 12 | 6775 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1578.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 165 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 10 | 106 | 220 | 0 | 316 | 800 | 0 | 5474.63 | 12249.63 | 80.32
Total KWH | 34416 | 714240 | 407040 | 0 | 0 | 0 | 0 | 0 | 8787600 | 0 | 0 | 222480 | 290520 | 2373696 | 1757280 | 959225 | 131652 | 756294 | 624960 | 0 | 430080 | 9058000 | 7105076 | 9412841 | 0 | 220895 | 0 | 6998485 | 0 | 0 | 151478 | 685200 | 451800 | 371880 | 0 | 9717727 | 0 | 0 | 38400 | 0 | 43200 | 810985 | 214604 | 0 | 2212800 | 1320000 | 29441 | 948000 | 126290 | 338880 | 3869090.91 | 0 | 0 | 0 | 0 | 132145 | 3470604 | 0 | 0 | 0 | 23814543 | 128655 | 1165276 | 630618 | 217455 | 0 | 8749800 | 8034000 | 246240 | 4846000 | 816768 | 1669440 | 1014050 | 2355840 | 451080 | 305470 | 1084140 | 930240 | 395928 | 392045 | 413392 | 7229000 | 7684000 | 8377000 | 914000 | 685080 | 0 | 2149036 | 41088 | 0 | 1985280 | 691776 | 0 | 409000 | 3607490 | 170280 | 1284000 | 2344800 | 0 | 11100 | 232440 | 274800 | 170968454.91 | 21714909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 388080 | 10029090 | 129600 | 30163636 | 0 | 105263 | 0 | 408384 | 0 | 56112 | 261024 | 89668 | 101626 | 544770 | 88581 | 291744 | 3652818 | 0 | 3613791 | 0 | 3582991 | 0 | 7825018 | 0 | 22800 | 0 | 4151000 | 1324800 | 290358 | 44248 | 378576 | 0 | 0 | 25623.96 | 915120 | 2989 | 0 | 5324000 | 181336 | 2820000 | 5207660 | 0 | 7606512 | 20135272.73 | 0 | 131477400.69 | 302445855.6

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-04-2025 | during | 29-04-2025 | during | 29-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 376 | 338 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 299 | 298 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 150 | 149.36 | 149.36 | 150 | 150 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 20.5 | 30 | 30 | 19 | 19 | -
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 0 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 95 | 80 | 149 | 149 | 130 | 130 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 0 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 72 | 35 | 162 | 162 | 54 | 162 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 0 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 400 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 400 | 350 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2621.5 | 2600.5 | 5234.9 | 5300.9 | 3882.79 | 4092.79
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 147 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 64 | 82 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 34 | 85 | 85 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 85 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 9 | 7 | 12 | 7 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 4.1 | 0 | 4.1 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 250 | 250 | Liquid fuel shortage
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 108 | 108 | Engine Problem
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 903 | 1000 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 12 | 5 | 12 | 5 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 156 | 156 | 420 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1386 | 1586 | 3247.82 | 2981.72 | 2937.82 | 2936.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 196 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 359 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 330 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 31 | 35 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 190 | 190 | 81 | 81 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 12 | 0 | 150 | 150 | 130 | 130 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 16 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 40 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 132 | 61 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 7 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 32 | 45 | 105.3 | 105.3 | 105.3 | 105.3 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 96 | 50 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 73 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1435 | 1261 | 2437.29 | 2377.29 | 2151.85 | 2120.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-04-2025 | during | 29-04-2025 | during | 29-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 171 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 38 | 106 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 37.61 | 0 | 49.68 | 0 | 49.68 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 154.61 | 289 | 600.78 | 549 | 273.78 | 312
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 39 | 38 | 38 | 36 | 36 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | machine problem
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 92 | 96 | 113 | 113 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 175 | 176 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 7 | 8 | 8 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 312 | 315 | 385 | 385 | 337 | 337 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1399 | 1414 | 1536 | 1536 | 1492 | 1492
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 926 | 865 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78.23 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 376 | 501 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1380.23 | 1366 | 3574.2 | 3514.2 | 2442.01 | 2382.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 318 | 319 | 660 | 660 | 660 | 660 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 118 | 120 | 120 | 120 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 730 | 780 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.76 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1542.76 | 1753 | 2822.12 | 2821.12 | 2822.12 | 2821.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 138 | 150 | 214 | 214 | 173 | 173 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 187 | 130 | 220 | 220 | 175 | 175 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 130 | 220 | 220 | 166 | 166 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 350 | 350 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 93 | 93 | 93 | 93 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.04 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 912 | 1571 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.78 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1936.82 | 2331 | 3112.53 | 2946.53 | 2920.15 | 2754.15
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 58 | 56 | 56 | 56 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 171 | 164 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 18 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 129 | 0 | 170 | 0 | 170 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 378.8 | 220 | 662.4 | 468 | 661.4 | 467
System Total |  |  |  |  | 27566.2 | 28535.742 | 12234.72 | 12820.5 | 23228.04 | 22494.76 | 19583.92 | 19378.64
Forecast Scenario (29-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12920 |  | 0 |  | 12920
|  |  |  | 1:00 | 12550 |  | 0 |  | 12550
|  |  |  | 2:00 | 12000 |  | 0 |  | 12000
|  |  |  | 3:00 | 11080 |  | 0 |  | 11080
|  |  |  | 4:00 | 10500 |  | 0 |  | 10500
|  |  |  | 5:00 | 10280 |  | 0 |  | 10280
|  |  |  | 6:00 | 10030 |  | 0 |  | 10030
|  |  |  | 7:00 | 10070 |  | 0 |  | 10070
|  |  |  | 8:00 | 9980 |  | 0 |  | 9980
|  |  |  | 9:00 | 10500 |  | 0 |  | 10500
|  |  |  | 10:00 | 10870 |  | 0 |  | 10870
|  |  |  | 11:00 | 11430 |  | 0 |  | 11430
|  |  |  | 12:00 | 11980 |  | 0 |  | 11980
|  |  |  | 13:00 | 12310 |  | 0 |  | 12310
|  |  |  | 14:00 | 12320 |  | 0 |  | 12320
|  |  |  | 15:00 | 12550 |  | 0 |  | 12550
|  |  |  | 16:00 | 12250 |  | 0 |  | 12250
|  |  |  | 17:00 | 12030 |  | 0 |  | 12030
|  |  |  | 18:00 | 11800 |  | 0 |  | 11800
|  |  |  | 18:30 | 12500 |  | 0 |  | 12500
|  |  |  | 19:00 | 13160 |  | 0 |  | 13160
|  |  |  | 19:30 | 13550 |  | 0 |  | 13550
|  |  |  | 20:00 | 13510 |  | 0 |  | 13510
|  |  |  | 21:00 | 13450 |  | 0 |  | 13450
|  |  |  | 22:00 | 13280 |  | 0 |  | 13280
|  |  |  | 23:00 | 13250 |  | 0 |  | 13250
Probable Maximum Temperature: |  |  | 28.60°C
Probable Maximum Demand at Day Peak: |  |  | 11980.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 13550.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13550.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 284.10 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:46 hrs on 29-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12234.72 | MW | 12:00 Hr. | Energy Generated |  |  | 302.4459 |  | MKWHr.
| Day Peak Demand |  |  | 12234.72 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.274 |  | MKWHr.
| Evening Peak Generation |  |  | 12820.5 | MW | 19:30 Hr. | Energy Demand |  |  | 303.7199 |  | MKWHr.
| Evening Peak Demand |  |  | 12820.5 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 11182.54 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 999.64 |  | MMCFD
| Maximum Generation of the Day |  |  | 15449.96 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.1221 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 51.9034 | 0 | 9.608 | 0 | 0 | 0.15148 | 0 | 0 | 61.6629 | Gas | 141.7643 | Gas | 500254561.25
| Chattogram Zone |  |  | 3.8095 | 27.6836 | 4.8552 | 0 | 0.948 | 0.1581 | 0 | 0.0432 | 37.4976 | Coal | 76.2543 | Coal | 495678773.8665
| Cumilla Zone |  |  | 25.3951 | 0 | 7.0004 | 0 | 0 | 0.39204 | 0.93024 | 0 | 33.7178 | HFO | 27.4467 | HFO | 514466976.58
| Mymensingh Zone |  |  | 0 | 0 | 4.0739 | 0 | 0 | 0.24354 | 0 | 0 | 4.3174 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.7728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.7728 | Hydro | 0.948 | Hydro | 94800
| Khulna Zone |  |  | 0 | 10.0291 | 0.1296 | 0 | 0 | 0.38808 | 21.7149 | 0 | 32.2617 | Solar | 3.1805 | Solar | 50969347.7056
| Barishal Zone |  |  | 8.209 | 33.0658 | 0 | 0 | 0 | 0.002989 | 0 | 0 | 41.2778 | Import | 52.8088 | Import | 289501465.01
| Rajshahi Zone |  |  | 18.6746 | 0 | 1.1107 | 0 | 0 | 0.85931 | 30.1636 | 0 | 50.8082 | Wind | 0.0432 | Wind | 632448
| Rangpur Zone |  |  | 0 | 5.4758 | 0.66893 | 0 | 0 | 0.98499 | 0 | 0 | 7.1297
| Total |  |  | 141.7643 | 76.2543 | 27.4467 | 0 | 0.948 | 3.1805 | 52.8088 | 0.0432 | 302.4459
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 500254561.25 |  | Hydro | 94800
|  |  |  | Coal | 495678773.8665 |  | Solar | 50969347.7056
|  |  |  | HFO | 514466976.58 |  | Import | 289501465.01
|  |  |  | HSD | 0 |  | Wind | 632448
[5 empty] | Total: | 185,15,98,372 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7149 | Peak Hr Flow | 865.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35641872.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.1636 | Peak Hr Flow | 1571.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 692 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.93024 | Peak Hr Flow | 34.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1026 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 52.8088 | Peak Hr Flow | 2470.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4787
|  |  |  | Chattogram |  | 0 |  | 1542
|  |  |  | Cumilla |  | 0 |  | 969
|  |  |  | Mymensingh |  | 0 |  | 1021
|  |  |  | Sylhet |  | 0 |  | 396
|  |  |  | Khulna |  | 0 |  | 1320
|  |  |  | Barishal |  | 0 |  | 262
|  |  |  | Rajshahi |  | 0 |  | 1411
|  |  |  | Rangpur |  | 0 |  | 689
|  |  |  | Total |  | 0 |  | 12397
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:28 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
|  | 08:28 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 is restored.
|  | 08:28 | Fenchuganj -Sylhet 132kV Ckt-1 is restored.
|  | 08:30 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 is restored.
|  | 08:30 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 is restored.
|  | 09:45 | Narshingdi 132/33kV S/S T-4 LT is restored.
| 09:53 | 11:01 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Tripped showing distance protection
relay relays Due to thundering
| 09:53 | 11:01 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Tripped showing DISTANCE PROTECTION
RELAY relays Due to THUNDERING
| 09:53 | 11:00 | Fenchuganj -Sylhet 132kV Ckt-1 Tripped from Beanibazar 132/33kV end showing REL670
relays Due to HEAVY RAIN
| 09:53 | 11:00 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Tripped from Beanibazar 132/33kV end | [7 empty] | and 18.0MW load
|  |  | showing 1.REC670 2.REL670 relays Due to HEAVY RAIN and from Fenchuganj 230/132/33kV end | [7 empty] | interrup.
|  |  | showing REL670 & REC650 relays Due to Bad weather | [7 empty] | Fenchuganj
230/132/33kV end
| 10:00 | 10:59 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Forced S/D from Fenchuganj 230/132/33kV | [7 empty] | 18.0MW load
|  |  | end Due to After Trip | [7 empty] | interrup.
Fenchuganj
230/132/33kV end
| 10:14 | 10:48 | Ashuganj-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing 1.
Primary Distance Protection - Mode: RE, Value: D1P, 2. Secondary Distance Protection-A
Phase 3.Auto reclosed 1 & 3 Pole relays.
| 10:14 |  | Aminbazar 400/230/132kV S/S Bus-2 (400kV) Scheduled S/D Due to Project Development Work
| 10:26 | 20:45 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to IDRNPP project work.
| 10:26 | 13:18 | Hasnabad 132/33kV S/S 33kv Reserve Bus Scheduled S/D Due to Dohar feeder Bus isolator
problem
| 10:28 |  | Narshingdi 132/33kV S/S T-4 LT Tripped showing dF/dt relays Due to 33 kV Hasnabad and | [7 empty] | 11.0MW load
|  |  | Shibpur feeeder earth fault triped. | [7 empty] | interrup.
| 10:40 | 21:35 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T HT Forced S/D Due to Emergency
Maintenance work by NESCO.
| 10:41 | 21:42 | Barapukuria 230/132/33kV S/S 132/33 KV T-5, 424T LT Forced S/D Due to Emergency
Maintenance work by NESCO.
| 12:00 |  | Day Peak Gen.12234 MW
| 13:50 |  | AGC test of RNPL U-2 can't be conducted successfully in A- shift.
|  | 17:17 | Goalpara- Khulna (C) 132kV Ckt-2 is restored.
| 19:53 | 20:05 | Goalpara 132/33kV S/S T-5 LT Tripped showing Dir OC, EG relays Due to Trip due to PBS | [7 empty] | 10.0MW load
|  |  | 33KV feeder fault | [7 empty] | interrup.
| 19:53 | 20:05 | Goalpara 132/33kV S/S T-6 LT Tripped showing Dir OC,EF relays Due to Trip due to PBS 33KV | [7 empty] | 10.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 23:10 | 00:31 | Barishal 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to To remove red hot problem | [7 empty] | 30.0MW load
interrup.
| 23:11 | 00:30 | Barishal 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to To remove red hot problem | [7 empty] | 30.0MW load
interrup.
| 00:05 | 00:11 | Goalpara 132/33kV S/S T-6 LT Tripped showing E/F relays Due to Trip due to WZPDCL 33KV | [7 empty] | 10.0MW load
|  |  | Chandnimohal feeder fault | [7 empty] | interrup.
| 00:05 | 00:11 | Goalpara 132/33kV S/S T-5 LT Tripped showing E/F relays Due to Trip due to WZPDCL 33KV | [7 empty] | 10.0MW load
|  |  | Chandnimohal feeder fault | [7 empty] | interrup.
|  | 00:30 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
|  | 00:30 | Barishal 132/33kV S/S T-1 (405T) HT is restored.
| 04:16 |  | Hathazari 230/132/33kV S/S T-01 LT Tripped showing Simens Siprotec relays Due to 33 Kv
cable puncture R Phase
| 04:37 |  | Shikalbaha 230/132kV S/S Interconnection-2 Tripped showing red670 relays. | [7 empty] | 23.0MW load
interrup.
| 04:37 | 06:04 | Halishahar 132/33kV S/S 405T(TR-1) HT Tripped showing O/C relay relays Due to Due to 33kV
feeder fault.
| 04:37 | 06:48 | Shikalbaha 230/132kV S/S Interconnection-1 Tripped showing red670 relays. | [7 empty] | 21.0MW load
interrup.
| 06:09 | 07:39 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to To remove red hot problem
| 06:10 | 07:38 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to To remove red hot problem.
| 07:45 |  | Bagerhat-Bhandaria 132 kV Ckt-1 Project Work S/D from Bhandaria 132/33kV end Due to
EEGBPSB project work.
| 07:55 |  | Hathazari 230/132/33kV S/S T-01 HT Forced S/D Due to 33 Kv XLPE Cable R phase faulty
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 338 | 8787600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9058000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 298 | 7105076 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 131652 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6998485 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 34416 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 222480 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 150 | 1757280 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 756294 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 220895 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20.5 | 451800 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 371880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 407040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 959225 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 80 | 2373696 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 714240 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 430080 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 624960 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 151478 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 290520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9717727 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 350 | 9412841 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 685200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2600.5 | 61662865
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 128655 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 948000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 147 | 3470604 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 132145 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 214604 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 810985 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2212800 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 338880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 38400 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 29441 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 126290 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1320000 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 23814543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 43200 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 156 | 3869090.91 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1586 | 37497637.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 192 | 4846000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8749800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 8034000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 816768 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 246240 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1165276 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 630618 | Machine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 413392 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 40 | 1014050 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 61 | 2355840 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 34 | 930240 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 395928 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 7 | 305470 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 45 | 1084140 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 451080 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 1669440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 392045 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1261 | 33717782
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 171 | 2344800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 106 | 1284000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 232440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 274800 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 170280 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 289 | 4317420
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 914000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 685080 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 96 | 2149036 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 691776 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1985280 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 176 | 3607490 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 409000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 41088 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7229000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 315 | 8377000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7684000 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1414 | 33772750
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 865 | 21714909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 129600 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 388080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 501 | 10029090 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1366 | 32261679
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 319 | 7606512 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 181336 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 120 | 2820000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 780 | 20135272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5207660 | -
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5324000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2989 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1753 | 41277769.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 105263 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 89668 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 150 | 3652818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 130 | 3613791 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 130 | 3582991 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 7825018 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 88581 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 101626 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 56112 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 408384 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 261024 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1571 | 30163636 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 291744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 544770 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2331 | 50808226
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1324800 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 4151000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 378576 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25623.96 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 290358 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 44248 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 915120 | -
Rangpur Area Total |  |  |  |  | 950 | 220 | 7129725.96
Eastern Grid Total |  |  |  |  | 16921.242 | 7150.5 | 170968454.91
Western Grid Total |  |  |  |  | 11614.5 | 5670 | 131477400.69
National Grid Total |  |  |  |  | 28535.742 | 12820.5 | 302445855.6
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8715 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3682.3 | MW
i) Dhaka area |  |  | 4786.8 |  | MW | i) Khulna area |  |  |  | 1320.5 | MW
ii) Chattogram area |  |  | 1542.2 |  | MW | ii) Barishal area |  |  |  | 262 | MW
iii) Cumilla area |  |  | 969 |  | MW | iii) Rajshahi area |  |  |  | 1410.8 | MW
iv) Mymensingh area |  |  | 1021 |  | MW | iv) Rangpur area |  |  |  | 689 | MW
v) Sylhet area |  |  | 396 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12397.3 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 79 | 00:00 | 133 | Patuakhali | 84 | 00:00
2 | AKSML | 23.8 | 15:00 | 68 | Jaldhaka | 49 | 00:00 | 134 | Payra | 34 | 00:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jamalpur | 120 | 19:00 | 135 | Postogola | 58 | 00:00
4 | Agargaon | 135 | 00:00 | 70 | Jashore | 146 | 00:00 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 100 | 15:00 | 71 | Jhenaidah | 129 | 00:00 | 137 | Purbasadipur | 119 | 00:00
6 | Amnura | 51 | 00:00 | 72 | Joydebpur | 143 | 11:00 | 138 | Rahanpur | 32 | 00:00
7 | Ashuganj | 104 | 00:00 | 73 | Joypurhat | 76 | 00:00 | 139 | Rahim | 49 | 05:00
8 | BSRM | 201 | 19:30 | 74 | Juldah | 13 | 13:00 | 140 | Rajbari | 85 | 00:00
9 | Bagerhat | 80 | 00:00 | 75 | KSRM | 16 | 00:00 | 141 | Rajendrapur | 142 | 00:00
10 | Bajitpur | 53 | 00:00 | 76 | Kabirpur | 274 | 15:00 | 142 | Rajshahi | 127 | 00:00
11 | Bakulia | 100 | 15:00 | 77 | Kachua | 85 | 02:00 | 143 | Rajshahi-230 | 92 | 00:00
12 | Banani | 42 | 09:00 | 78 | Kallyanpur | 108 | 01:00 | 144 | Ramganj | 112 | 01:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 44 | 15:00 | 145 | Rampur | 45 | 00:00
14 | Barapukuria | 60 | 00:00 | 80 | Kamrangirchar | 67 | 12:00 | 146 | Rangamati | 16 | 18:30
15 | Barguna | 24 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 111 | 19:30
16 | Barishal | 108 | 00:00 | 82 | Kasba | 35 | 00:00 | 148 | Ruppur | 6.8 | 11:00
17 | Barishal-230 | 96 | 00:00 | 83 | Kazla | 101 | 00:00 | 149 | SSM | 9 | 00:00
18 | Baroaulia | 68 | 12:00 | 84 | Keranigonj | 81 | 00:00 | 150 | Saidpur | 89 | 19:00
19 | Baroirhat | 56 | 00:00 | 85 | Khagrachori | 26 | 11:00 | 151 | Satkhira | 140 | 01:00
20 | Bashundhara | 183 | 00:00 | 86 | Khulna | 64 | 00:00 | 152 | Satmasjid | 107 | 00:00
21 | BashundharaCement | 15 | 11:00 | 87 | Khulshi | 191 | 15:00 | 153 | Savar | 222 | 08:00
22 | Beanibazar | 56 | 00:00 | 88 | Kishoreganj | 130 | 00:00 | 154 | SevenRings | 6.02 | 04:00
23 | Benapole | 68 | 00:00 | 89 | Kodda | 309 | 19:30 | 155 | ShahCement | 29 | 00:00
24 | Bhaluka | 137 | 06:00 | 90 | Kulaura | 42 | 00:00 | 156 | Shahjadpur | 89 | 00:00
25 | Bhandaria | 53 | 00:00 | 91 | Kurigram | 32 | 19:00 | 157 | Shahjibazar | 113 | 01:00
26 | Bhangura | 46 | 00:00 | 92 | Kushtia | 162 | 00:00 | 158 | Shahmirpur | 61 | 04:00
27 | Bheramara(GK) | 64 | 01:00 | 93 | Lalbag | 68 | 11:00 | 159 | Shariatpur | 91 | 00:00
28 | Bhulta | 233 | 12:00 | 94 | Lalmonirhat | 43 | 00:00 | 160 | Sherpur | 126 | 19:00
29 | Bog-Sherpur | 78 | 00:00 | 95 | MI_Cement | 18.3 | 03:00 | 161 | Shikalbaha | 32 | 19:00
30 | Bogura | 182 | 02:00 | 96 | Madanganj | 40 | 02:00 | 162 | Shitalakhya | 86.9 | 10:00
31 | Borhanuddin | 87 | 00:00 | 97 | Madaripur | 110 | 00:00 | 163 | Sholosohor | 45 | 10:00
32 | Brahmanbaria | 125 | 00:00 | 98 | Madartek | 97.32 | 00:00 | 164 | Shyampur | 152 | 03:00
33 | Cantonment | 126 | 00:00 | 99 | Madunaghat | 52 | 15:00 | 165 | Siddhirganj | 126 | 09:00
34 | Chandina | 0.98 | 19:00 | 100 | Magura | 66 | 00:00 | 166 | Sirajganj | 118 | 00:00
35 | Chandpur | 73 | 01:00 | 101 | Mahasthangarh | 90 | 00:00 | 167 | Sonargaon | 139 | 00:00
36 | Chandraghona | 35 | 19:00 | 102 | Manikganj | 121 | 04:00 | 168 | Sreemongol | 83 | 01:00
37 | Chapai | 75 | 00:00 | 103 | Maniknagar | 80 | 00:00 | 169 | Sreepur | 102 | 18:00
38 | Charsaidpur | 42 | 10:00 | 104 | Matarbari | 50 | 00:00 | 170 | Srinagar | 49 | 00:00
39 | Chauddagram | 69 | 01:00 | 105 | Matuail | 66 | 12:00 | 171 | Sunamganj | 41 | 01:00
40 | Chhatak | 22 | 23:00 | 106 | Millgate | 120 | 09:00 | 172 | Sylhet | 40 | 01:00
41 | Chowmuhani | 216 | 00:00 | 107 | Mirpur | 132 | 00:00 | 173 | Sylhet-132 | 96 | 18:30
42 | Chuadanga | 113 | 01:00 | 108 | Mirsorai | 10 | 10:00 | 174 | TK | 33.5 | 23:00
43 | Coxsbazar | 138 | 12:00 | 109 | Mirzapur | 50 | 15:00 | 175 | Tangail | 196 | 00:00
44 | Cumilla(N) | 167 | 05:00 | 110 | Mithapukur | 44 | 00:00 | 176 | Thakurgaon | 87 | 00:00
45 | Cumilla(S) | 164 | 01:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 138 | 00:00
46 | Daudkandi | 132 | 21:00 | 112 | Mogbazar | 145.6 | 11:00 | 178 | Ullahpara | 46 | 00:00
47 | Dhaka | 58 | 11:00 | 113 | Mongla | 44 | 13:00 | 179 | Ullon | 42 | 01:00
48 | Dhamrai | 134 | 00:00 | 114 | Motijheel | 37 | 00:00 | 180 | Uttara | 84 | 00:00
49 | Dhanmondi | 141.3 | 13:00 | 115 | Muktagacha | 34 | 06:00 | 181 | UttaraNew | 57 | 00:00
50 | Dohazari | 104 | 00:00 | 116 | Munshiganj | 110 | 00:00 | 182 | Zigatola | 81 | 00:00
51 | Faridpur | 177 | 00:00 | 117 | Muradnagar | 27 | 00:00
52 | Fatullah | 108 | 10:00 | 118 | Mymensingh | 180 | 00:00
53 | Fenchuganj | 39 | 00:00 | 119 | Naogaon | 154 | 00:00
54 | Feni | 107 | 00:00 | 120 | Narail | 55 | 00:00
55 | GPH | 93 | 19:00 | 121 | Narinda | 72 | 13:00
56 | Ghatail | 70 | 00:00 | 122 | Narshingdi | 190 | 00:00
57 | Ghorashal | 16 | 01:00 | 123 | Natore | 172 | 00:00
58 | Ghorashal-230 | 99 | 00:00 | 124 | Nawabganj | 62 | 00:00
59 | Goalpara | 38 | 00:00 | 125 | Netrakona | 103 | 19:00
60 | Gollamari | 104 | 00:00 | 126 | New | 88.8 | 09:00
61 | Gopalganj | 103 | 00:00 | 127 | Niamatpur | 103 | 00:00
62 | Gulshan | 118 | 09:00 | 128 | Noapara | 45 | 00:00
63 | Halishahar | 82 | 16:00 | 129 | PHP | 3 | 02:00
64 | HaripurSBU | 187 | 09:00 | 130 | Pabna | 124 | 00:00
65 | Hasnabad | 94 | 00:00 | 131 | Palashbari | 100 | 00:00
66 | Hathazari | 81 | 00:00 | 132 | Panchagarh | 39 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15449.96 | 205 |  | 15664.19
1:00 | 15013.19 | 218 |  | 15241.19
2:00 | 14693.17 | 180 |  | 14881.17
3:00 | 13958.04 | 156 |  | 14121.04
4:00 | 13269.15 | 145 |  | 13421.15
5:00 | 12838.63 | 108 |  | 12951.63
6:00 | 11998.04 | 90 |  | 12092.04
7:00 | 11597.32 | 0 |  | 11597.32
8:00 | 11182.54 | 0 |  | 11182.54
9:00 | 11405.23 | 0 |  | 11405.23
10:00 | 11389.08 | 0 |  | 11389.08
11:00 | 11684.98 | 0 |  | 11684.98
12:00 | 12234.72 | 0 |  | 12234.72
13:00 | 12117.3 | 0 |  | 12117.3
14:00 | 12192.25 | 20 |  | 12213.25
15:00 | 12339.48 | 28 |  | 12368.48
16:00 | 11792.57 | 28 |  | 11821.57
17:00 | 11572.29 | 29 |  | 11602.29
18:00 | 11263.09 | 0 |  | 11263.09
19:00 | 12636.5 | 0 |  | 12636.5
19:30 | 12820.5 | 0 |  | 12820.5
20:00 | 12676.5 | 15 |  | 12692.5
21:00 | 12667.01 | 15 |  | 12682.69
22:00 | 12582.11 | 17 |  | 12600.11
23:00 | 12249.63 | 20 |  | 12270.63
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8884.2 | 6565.76 | 15449.96 | DAILY GENERATION CURVE
00:30 | 8683.2 | 6548.375 | 15231.575
01:00 | 8482.2 | 6530.99 | 15013.19 | 28-04-2025
01:30 | 8350.7 | 6502.48 | 14853.18
02:00 | 8219.2 | 6473.97 | 14693.17
02:30 | 8059.7 | 6265.905 | 14325.605
03:00 | 7900.2 | 6057.84 | 13958.04
03:30 | 7795.2 | 5818.395 | 13613.595
04:00 | 7690.2 | 5578.95 | 13269.15
04:30 | 7569.95 | 5483.94 | 13053.89
05:00 | 7449.7 | 5388.93 | 12838.63
05:30 | 7281.365 | 5136.97 | 12418.335
06:00 | 7113.03 | 4885.01 | 11998.04
06:30 | 6988.025 | 4809.655 | 11797.68
07:00 | 6863.02 | 4734.3 | 11597.32
07:30 | 6713.915 | 4676.015 | 11389.93
08:00 | 6564.81 | 4617.73 | 11182.54
08:30 | 6587.335 | 4706.55 | 11293.885
09:00 | 6609.86 | 4795.37 | 11405.23
09:30 | 6547.505 | 4849.65 | 11397.155
10:00 | 6485.15 | 4903.93 | 11389.08
10:30 | 6561.245 | 4975.785 | 11537.03
11:00 | 6637.34 | 5047.64 | 11684.98
11:30 | 6816.725 | 5143.125 | 11959.85
12:00 | 6996.11 | 5238.61 | 12234.72
12:30 | 6959.95 | 5216.06 | 12176.01
13:00 | 6923.79 | 5193.51 | 12117.3
13:30 | 6893.575 | 5261.2 | 12154.775
14:00 | 6863.36 | 5328.89 | 12192.25
14:30 | 6929.515 | 5336.35 | 12265.865
15:00 | 6995.67 | 5343.81 | 12339.48
15:30 | 6849.01 | 5217.015 | 12066.025
16:00 | 6702.35 | 5090.22 | 11792.57
16:30 | 6612.12 | 5070.31 | 11682.43
17:00 | 6521.89 | 5050.4 | 11572.29
17:30 | 6309.44 | 5108.25 | 11417.69
18:00 | 6096.99 | 5166.1 | 11263.09
18:30 | 6624.745 | 5325.05 | 11949.795
19:00 | 7152.5 | 5484 | 12636.5
19:30 | 7150.5 | 5670 | 12820.5
20:00 | 7028.5 | 5648 | 12676.5
20:30 | 7061.5 | 5610.255 | 12671.755 |  | Executive Engineer
21:00 | 7094.5 | 5572.51 | 12667.01 |  | Network Operation Division
21:30 | 7057.75 | 5566.81 | 12624.56
22:00 | 7021 | 5561.11 | 12582.11
22:30 | 6898 | 5517.87 | 12415.87
23:00 | 6775 | 5474.63 | 12249.63

## En-Curve
QF-LDC-12
Date | 28-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3835 | 2351 | 922 | 0 | 44 | 1362.76 | 40 | 3959 | 0 | 578 | 2358.2 | 0 | 0 | 0 | 205 | DAILY ENERGY CURVE
00:30 | 3838 | 2346 | 922 | 0 | 43 | 1360.775 | 40 | 3881 | 0 | 510.5 | 2290.3 | 0 | 0 | 0 | 211.5 | 28-04-2025
01:00 | 3841 | 2341 | 922 | 0 | 42 | 1358.79 | 40 | 3803 | 0 | 443 | 2222.4 | 0 | 0 | 0 | 218
01:30 | 3847.5 | 2330.5 | 921.5 | 0 | 42 | 1362.78 | 40 | 3742 | 0 | 418.5 | 2148.4 | 0 | 0 | 0 | 199 | Energy Generated | 302.4459 |  | MKWHr
02:00 | 3854 | 2320 | 921 | 0 | 42 | 1366.77 | 40 | 3681 | 0 | 394 | 2074.4 | 0 | 0 | 0 | 180 | Energy not Served | 1.274 |  | MKWHr
02:30 | 3810.5 | 2318 | 921.5 | 0 | 41 | 1364.805 | 40 | 3681.5 | 0 | 341.5 | 1806.8 | 0 | 0 | 0 | 168 | Total Energy Requirement | 303.7199 |  | MKWHr
03:00 | 3767 | 2316 | 922 | 0 | 40 | 1362.84 | 40 | 3682 | 0 | 289 | 1539.2 | 0 | 0 | 0 | 156
03:30 | 3770.5 | 2387 | 922 | 0 | 39 | 1309.895 | 40 | 3573.5 | 0 | 234.5 | 1337.2 | 0 | 0 | 0 | 150.5
04:00 | 3774 | 2458 | 922 | 0 | 38 | 1256.95 | 40 | 3465 | 0 | 180 | 1135.2 | 0 | 0 | 0 | 145
04:30 | 3707 | 2469.75 | 922 | 0 | 38 | 1223.94 | 40 | 3436.5 | 0 | 180 | 1036.7 | 0 | 0 | 0 | 126.5
05:00 | 3640 | 2481.5 | 922 | 0 | 38 | 1190.93 | 40 | 3408 | 0 | 180 | 938.2 | 0 | 0 | 0 | 108
05:30 | 3519 | 2387.75 | 922 | 0 | 37 | 1085.465 | 40 | 3348.5 | 6.92 | 180 | 891.7 | 0 | 0 | 0 | 99
06:00 | 3398 | 2294 | 922 | 0 | 36 | 980 | 40 | 3289 | 13.84 | 180 | 845.2 | 0 | 0 | 0 | 90
06:30 | 3397.5 | 2305.5 | 922 | 0 | 35 | 925.745 | 40 | 3248 | 41.335 | 162.5 | 720.1 | 0 | 0 | 0 | 45
07:00 | 3397 | 2317 | 922 | 0 | 34 | 871.49 | 40 | 3207 | 68.83 | 145 | 595 | 0 | 0 | 0 | 0
07:30 | 3407 | 2284 | 900.5 | 0 | 33 | 867.745 | 40 | 3099 | 110.185 | 112.5 | 536 | 0 | 0 | 0 | 0
08:00 | 3417 | 2251 | 879 | 0 | 32 | 864 | 40 | 2991 | 151.54 | 80 | 477 | 0 | 0 | 0 | 0
08:30 | 3441 | 2232.5 | 879 | 0 | 27 | 866 | 40 | 2962.5 | 243.385 | 109 | 493.5 | 0 | 0 | 0 | 0
09:00 | 3465 | 2214 | 879 | 0 | 22 | 868 | 40 | 2934 | 335.23 | 138 | 510 | 0 | 0 | 0 | 0
09:30 | 3446.5 | 2169.5 | 902.5 | 0 | 27 | 868 | 40 | 2859.5 | 412.155 | 131 | 541 | 0 | 0 | 0 | 0
10:00 | 3428 | 2125 | 926 | 0 | 32 | 868 | 40 | 2785 | 489.08 | 124 | 572 | 0 | 0 | 0 | 0
10:30 | 3469 | 2130 | 926 | 0 | 32 | 867.5 | 40 | 2786 | 548.53 | 124 | 614 | 0 | 0 | 0 | 0
11:00 | 3510 | 2135 | 926 | 0 | 32 | 867 | 40 | 2787 | 607.98 | 124 | 656 | 0 | 0 | 0 | 0
11:30 | 3590.5 | 2222.75 | 926 | 0 | 32 | 889.5 | 40 | 2824.5 | 578.1 | 140 | 716.5 | 0 | 0 | 0 | 0
12:00 | 3671 | 2310.5 | 926 | 0 | 32 | 912 | 40 | 2862 | 548.22 | 156 | 777 | 0 | 0 | 0 | 0
12:30 | 3609 | 2303.25 | 926.5 | 0 | 30 | 1021.5 | 40 | 2877.5 | 461.76 | 165 | 733.5 | 0 | 0 | 8 | 0
13:00 | 3547 | 2296 | 927 | 0 | 28 | 1131 | 40 | 2893 | 375.3 | 174 | 690 | 0 | 0 | 16 | 0
13:30 | 3501.5 | 2334.25 | 927 | 0 | 26 | 1254.5 | 40 | 2911 | 285.025 | 172 | 690 | 0 | 0 | 13.5 | 10
14:00 | 3456 | 2372.5 | 927 | 0 | 24 | 1378 | 40 | 2929 | 194.75 | 170 | 690 | 0 | 0 | 11 | 20
14:30 | 3498 | 2385.75 | 927 | 0 | 27 | 1372.5 | 38 | 2953 | 207.115 | 167 | 680.5 | 0 | 0 | 10 | 24
15:00 | 3540 | 2399 | 927 | 0 | 30 | 1367 | 36 | 2977 | 219.48 | 164 | 671 | 0 | 0 | 9 | 28
15:30 | 3488 | 2309.5 | 927 | 0 | 28 | 1371 | 36.5 | 2891 | 163.525 | 172.5 | 670 | 0 | 0 | 9 | 28
16:00 | 3436 | 2220 | 927 | 0 | 26 | 1375 | 37 | 2805 | 107.57 | 181 | 669 | 0 | 0 | 9 | 28
16:30 | 3403.5 | 2171.5 | 927.5 | 0 | 27 | 1378.5 | 37.5 | 2791.5 | 75.93 | 181 | 684 | 0 | 0 | 4.5 | 28.5
17:00 | 3371 | 2123 | 928 | 0 | 28 | 1382 | 38 | 2778 | 44.29 | 181 | 699 | 0 | 0 | 0 | 29
17:30 | 3290.5 | 1971.75 | 927.5 | 0 | 28 | 1460 | 39 | 2753.5 | 28.44 | 204 | 715 | 0 | 0 | 0 | 14.5
18:00 | 3210 | 1820.5 | 927 | 0 | 28 | 1538 | 40 | 2729 | 12.59 | 227 | 731 | 0 | 0 | 0 | 0
18:30 | 3416 | 2072.5 | 896 | 0 | 30 | 1555.5 | 40 | 2903.5 | 6.295 | 279 | 751 | 0 | 0 | 0 | 0
19:00 | 3622 | 2324.5 | 865 | 0 | 32 | 1573 | 40 | 3078 | 0 | 331 | 771 | 0 | 0 | 0 | 0
19:30 | 3529 | 2317.5 | 865 | 0 | 34 | 1571 | 40 | 3283 | 0 | 331 | 850 | 0 | 0 | 0 | 0
20:00 | 3525 | 2314.5 | 864 | 0 | 32 | 1569 | 40 | 3221 | 0 | 295 | 816 | 0 | 0 | 0 | 15
20:30 | 3575 | 2356 | 827 | 0 | 32 | 1568.255 | 40 | 3218.5 | 0 | 278 | 777 | 0 | 0 | 0 | 15
21:00 | 3625 | 2397.5 | 790 | 0 | 32 | 1567.51 | 40 | 3216 | 0 | 261 | 738 | 0 | 0 | 0 | 15
21:30 | 3626.5 | 2402.25 | 790 | 0 | 32 | 1571.31 | 40 | 3214 | 0 | 243 | 705.5 | 0 | 0 | 0 | 16
22:00 | 3628 | 2407 | 790 | 0 | 32 | 1575.11 | 40 | 3212 | 0 | 225 | 673 | 0 | 0 | 0 | 17
22:30 | 3596.5 | 2399 | 790 | 0 | 33 | 1576.87 | 40 | 3114.5 | 0 | 216 | 650 | 0 | 0 | 0 | 18.5
23:00 | 3565 | 2391 | 790 | 0 | 34 | 1578.63 | 40 | 3017 | 0 | 207 | 627 | 0 | 0 | 0 | 20
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 393 | 18:00 | 379 | 00:00 | Payra | 415 | 18:00 | 408 | 00:00
Ashuganj | 399 | 18:00 | 385 | 16:00 | Rahanpur | 411 | 06:00 | 394 | 19:30
Bhulta | 393 | 06:00 | 383 | 00:00 | Rampal | 405 | 18:00 | 385 | 00:00
Bibiana | 389 | 18:00 | 383 | 15:00
BIPTC | 400 | 06:00 | 391 | 00:00
Bogura | 405 | 06:00 | 379 | 19:30
Gopalganj | 402 | 18:00 | 385 | 00:00
Kaliakoir | 363 | 18:00 | 352 | 08:00
Madunaghat | 399 | 18:00 | 392 | 00:00
Meghnaghat | 394 | 23:00 | 385 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 18:00 | 219 | 00:00 | Keranigonj | 226 | 18:00 | 217 | 00:00
AKSML | 230 | 18:00 | 222 | 15:00 | Khulna(S) | 231 | 18:00 | 215 | 00:00
Aminbazar | 226 | 18:30 | 220 | 00:00 | Madunaghat | 230 | 18:00 | 226 | 09:00
Ashuganj | 229 | 09:00 | 222 | 00:00 | Madunaghat-400 | 230 | 02:00 | 226 | 00:00
Ashuganj-400 | 229 | 09:00 | 222 | 00:00 | Maniknagar | 221 | 18:00 | 216 | 00:00
Baghabari | 233 | 07:00 | 224 | 19:00 | Meghnaghat | 230 | 04:00 | 226 | 00:00
Barapukuria | 231 | 06:00 | 216 | 19:00 | Meghnaghat-400 | 226 | 18:00 | 221 | 00:00
Barapukuria-230 | 231 | 06:00 | 216 | 19:00 | Mirsorai | 226 | 11:00 | 219 | 00:00
Barishal | 241 | 06:00 | 232 | 00:00 | Rajshahi | 233 | 06:00 | 221 | 19:00
Bheramara | 235 | 06:00 | 222 | 13:00 | Rampal | 230 | 18:00 | 216 | 00:00
Bhulta | 223 | 06:00 | 217 | 00:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 222 | 02:00 | 218 | 00:00 | Rampura | 222 | 06:00 | 216 | 00:00
BIPTC | 233 | 06:00 | 222 | 03:00 | Shikalbaha | 228 | 18:00 | 223 | 12:00
Bogura | 234 | 06:00 | 219 | 19:00 | Shyampur | 226 | 18:00 | 218 | 00:00
Bogura-400 | 234 | 06:00 | 219 | 19:30 | Siddhirganj | 224 | 18:00 | 220 | 05:00
Borhanuddin | 244 | 06:00 | 237 | 00:00 | Sirajgonj | 238 | 08:00 | 233 | 00:00
BSRM | 225 | 18:00 | 219 | 00:00 | Sreepur | 230 | 09:00 | 220 | 00:00
Cumilla(N) | 222 | 18:00 | 216 | 00:00 | Tongi | 221 | 23:00 | 213 | 15:00
Faridpur | 238 | 06:00 | 228 | 00:00
Fenchuganj | 228 | 09:00 | 220 | 01:00
Ghorashal | 232 | 01:00 | 225 | 15:00
Ghorashal-230 | 223 | 18:00 | 216 | 00:00
Gopalganj | 241 | 06:00 | 233 | 00:00
GPH | 227 | 06:00 | 221 | 09:00
Haripur | 224 | 18:00 | 218 | 00:00
Hasnabad | 225 | 18:00 | 220 | 00:00
Hathazari | 229 | 04:00 | 225 | 09:00
Ishurdi | 233 | 06:00 | 224 | 19:30
Jhenaidah | 226 | 16:00 | 210 | 00:00
Kaliakoir | 226 | 18:00 | 219 | 08:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 03:00 | 129 | 12:00 | Madartek | 133 | 06:00 | 128 | 09:00
Agargaon | 133 | 18:00 | 127 | 00:00 | Madunaghat | 132 | 18:00 | 129 | 09:00
Agrabad | 131 | 06:00 | 127 | 09:00 | Magura | 132 | 18:00 | 119 | 00:00
AKS | 128 | 04:00 | 125 | 11:00 | Mahasthangarh | 139 | 06:00 | 125 | 19:00
Aminbazar | 131 | 15:00 | 126 | 00:00 | Manikganj | 129 | 06:00 | 114 | 09:00
Amnura | 135 | 06:00 | 124 | 19:00 | Maniknagar | 130 | 18:00 | 125 | 00:00
Ashuganj | 136 | 06:00 | 132 | 00:00 | Matarbari | 116 | 14:00 | 108 | 18:30
Bagerhat | 135 | 17:00 | 120 | 00:00 | Matuail | 131.4 | 18:00 | 126 | 00:00
Bajitpur | 134 | 07:00 | 126 | 00:00 | Millgate | 129 | 18:00 | 123 | 05:00
Bakulia | 132 | 18:00 | 128 | 07:00 | Mirpur | 131 | 18:00 | 123 | 00:00
Banani | 133 | 05:00 | 128 | 09:00 | Mirzapur | 128 | 19:00 | 122 | 00:00
Bangabhaban | 130 | 06:00 | 125 | 12:00 | Mithapukur | 140 | 06:00 | 121 | 20:00
Barapukuria | 139 | 04:00 | 124 | 19:30 | MI_Cement | 132 | 18:00 | 125.8 | 09:00
Barguna | 135 | 11:00 | 130 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 15:00 | 126 | 00:00 | Mogbazar | 134 | 04:00 | 130 | 00:00
Barishal-230 | 135 | 15:00 | 127 | 00:00 | Mongla | 136 | 18:00 | 121 | 00:00
Baroaulia | 130 | 00:00 | 127 | 12:00 | Motijheel | 130 | 06:00 | 125 | 12:00
Baroirhat | 127 | 14:00 | 118 | 00:00 | Muktagacha | 132 | 06:00 | 122 | 09:00
Bashundhara | 133 | 02:00 | 122 | 09:00 | Munshiganj | 131 | 18:00 | 125 | 00:00
BashundharaCement | 130 | 18:00 | 125 | 10:00 | Muradnagar | 128 | 11:00 | 117 | 00:00
Beanibazar | 133 | 09:00 | 127 | 00:00 | Mymensingh | 137 | 07:00 | 116 | 06:00
Benapole | 132 | 16:00 | 116 | 00:00 | Naogaon | 137 | 06:00 | 123 | 00:00
Bhaluka | 134 | 09:00 | 123 | 15:00 | Narail | 132 | 17:00 | 117 | 00:00
Bhandaria | 130 | 15:00 | 117 | 00:00 | Narinda | 130 | 18:00 | 126 | 11:00
Bhangura | 133 | 08:00 | 127 | 00:00 | Narshingdi | 134 | 10:00 | 116 | 00:00
Bheramara | 135 | 06:00 | 126 | 00:00 | Natore | 135 | 07:00 | 126 | 19:00
Bheramara(GK) | 134 | 05:00 | 126 | 00:00 | Nawabganj | 136 | 18:00 | 127 | 00:00
Bhulta | 128 | 18:00 | 120 | 09:00 | Netrakona | 133 | 08:00 | 118 | 14:00
Bog-Sherpur | 137 | 07:00 | 126 | 19:00 | New | 130 | 22:00 | 123 | 09:00
Bogura | 141 | 06:00 | 35 | 04:00 | Niamatpur | 135 | 06:00 | 129 | 14:00
Bogura-230 | 140 | 06:00 | 129 | 19:00 | Noapara | 135 | 18:00 | 122 | 00:00
Brahmanbaria | 134 | 10:00 | 121 | 00:00 | Pabna | 134 | 08:00 | 126 | 00:00
Cantonment | 134 | 18:00 | 127 | 00:00 | Palashbari | 138 | 06:00 | 121 | 19:00
Chandina | 129 | 13:00 | 121 | 08:00 | Panchagarh | 140 | 02:00 | 118 | 18:30
Chandpur | 130 | 11:00 | 119 | 15:00 | Patuakhali | 135 | 11:00 | 131 | 00:00
Chandraghona | 132 | 14:00 | 129 | 09:00 | Payra | 136 | 06:00 | 133 | 00:00
Chapai | 130 | 04:00 | 127 | 14:00 | PHP | 126 | 14:00 | 117 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 18:00 | 126 | 00:00 | Postogola | 134 | 18:00 | 129 | 00:00
Chauddagram | 125 | 13:00 | 117 | 00:00 | Purbachal | 134 | 06:00 | 128 | 09:00
Chhatak | 133 | 09:00 | 127 | 00:00 | Purbasadipur | 136 | 03:00 | 116 | 19:30
Chowmuhani | 122 | 18:00 | 110 | 00:00 | Rahanpur | 136 | 06:00 | 131 | 14:00
Chuadanga | 131 | 06:00 | 119 | 01:00 | Rahanpur-400 | 137 | 06:00 | 131 | 19:00
Coxsbazar | 116 | 08:00 | 108 | 12:00 | Rahim | 132 | 18:30 | 126 | 00:00
Cumilla(N) | 129 | 11:00 | 122 | 00:00 | Rajbari | 138 | 09:00 | 131 | 00:00
Cumilla(S) | 133 | 02:00 | 120 | 00:00 | Rajendrapur | 133 | 09:00 | 123 | 00:00
Daudkandi | 127 | 12:00 | 114 | 00:00 | Rajshahi | 134 | 06:00 | 126 | 00:00
Dhaka | 134 | 05:00 | 129 | 09:00 | Rajshahi-230 | 135 | 06:00 | 119 | 00:00
Dhamrai | 133 | 18:00 | 127 | 08:00 | Ramganj | 123 | 12:00 | 113 | 00:00
Dhanmondi | 134 | 05:00 | 126 | 15:00 | Rampur | 131 | 02:00 | 125 | 12:00
Dohazari | 127 | 05:00 | 123 | 12:00 | Rampura | 134 | 06:00 | 129 | 00:00
Faridpur | 139 | 08:00 | 134 | 00:00 | Rangamati | 131 | 06:00 | 128 | 09:00
Fatullah | 133 | 18:00 | 127 | 00:00 | Rangpur | 142 | 06:00 | 121 | 19:00
Fenchuganj | 136 | 10:00 | 131 | 00:00 | Ruppur | 137 | 08:00 | 130 | 19:30
Feni | 124 | 13:00 | 114 | 00:00 | Saidpur | 140 | 04:00 | 114 | 19:00
Ghatail | 131 | 07:00 | 120 | 00:00 | Satkhira | 136 | 23:00 | 118 | 00:00
Ghorashal | 134 | 08:00 | 131 | 01:00 | Satmasjid | 133 | 18:00 | 126 | 00:00
Goalpara | 138 | 17:00 | 125 | 00:00 | Savar | 130 | 18:00 | 124 | 09:00
Gollamari | 138 | 17:00 | 126 | 00:00 | SevenRings | 135 | 18:00 | 131 | 00:00
Gopalganj | 138 | 16:00 | 127 | 00:00 | ShahCement | 131 | 18:00 | 126 | 00:00
Gopalganj-400 | 138 | 16:00 | 132 | 00:00 | Shahjadpur | 137 | 08:00 | 131 | 19:30
Gulshan | 133 | 06:00 | 129 | 00:00 | Shahjibazar | 138 | 10:00 | 123 | 00:00
Halishahar | 131 | 02:00 | 126 | 09:00 | Shahmirpur | 132 | 01:00 | 129 | 09:00
Haripur | 131 | 18:00 | 126 | 00:00 | Shariatpur | 137 | 15:00 | 127 | 00:00
HaripurSBU | 131 | 18:00 | 126 | 00:00 | Sherpur | 141 | 07:00 | 117 | 10:00
Hasnabad | 132 | 23:00 | 128 | 00:00 | Shikalbaha | 122 | 02:00 | 118 | 15:00
Hathazari | 133 | 18:30 | 130 | 00:00 | Shikalbaha-230 | 133 | 01:00 | 129 | 11:00
Ishurdi | 138 | 08:00 | 131 | 00:00 | Shitalakhya | 132 | 18:00 | 125.8 | 09:00
Jaldhaka | 141 | 04:00 | 116 | 19:30 | Sholosohor | 131 | 01:00 | 128 | 15:00
Jamalpur | 139 | 07:00 | 120 | 09:00 | Shyampur | 131 | 18:00 | 126 | 00:00
Jashore | 133 | 16:00 | 118 | 00:00 | Shyampur-230 | 132 | 18:00 | 126 | 00:00
Jhenaidah | 133 | 05:00 | 121 | 00:00 | Siddhirganj | 131 | 18:00 | 126 | 09:00
Jhenaidah-230 | 133 | 16:00 | 121 | 00:00 | Sirajganj | 135 | 07:00 | 125 | 00:00
Joydebpur | 131 | 09:00 | 124 | 15:00 | Sonargaon | 128 | 13:00 | 124 | 09:00
Joypurhat | 135 | 06:00 | 117 | 00:00 | Sreemongol | 133 | 12:00 | 125 | 00:00
Juldah | 133 | 01:00 | 130 | 08:00 | Sreepur | 134 | 08:00 | 127 | 00:00
Kabirpur | 129 | 19:00 | 120 | 08:00 | Srinagar | 136 | 18:00 | 128 | 00:00
Kachua | 128 | 12:00 | 119 | 01:00 | SSM | 132 | 00:00 | 131 | 07:00
Kaliakoir | 135 | 18:00 | 122 | 05:00 | Sunamganj | 132 | 08:00 | 125 | 01:00
Kallyanpur | 133 | 18:00 | 125 | 01:00 | Sylhet | 134 | 09:00 | 128 | 00:00
Kalurghat | 132 | 02:00 | 129 | 09:00 | Sylhet-132 | 133 | 09:00 | 129 | 01:00
Kamrangirchar | 136 | 18:00 | 128 | 00:00 | Tangail | 126 | 06:00 | 120 | 00:00
Kaptai | 135 | 1:00 | 132 | 8:00 | Thakurgaon | 142 | 02:00 | 119 | 19:30
Kasba | 128 | 11:00 | 118 | 00:00 | TK | 132 | 06:00 | 129 | 08:00
Kazla | 130 | 19:00 | 125 | 00:00 | Tongi | 131 | 21:00 | 126 | 00:00
Keranigonj | 136 | 18:00 | 128 | 00:00 | Ullahpara | 135 | 08:00 | 127 | 00:00
Khagrachori | 131 | 14:00 | 127 | 09:00 | Ullon | 133 | 06:00 | 129 | 01:00
Khulna | 137 | 17:00 | 123 | 00:00 | Uttara | 131 | 18:00 | 124 | 00:00
Khulna(S) | 138 | 17:00 | 126 | 00:00 | UttaraNew | 131 | 18:00 | 124 | 00:00
Khulshi | 130 | 18:00 | 125 | 09:00 | Zigatola | 135 | 18:30 | 128 | 00:00
Kishoreganj | 135 | 08:00 | 123 | 00:00
Kodda | 130 | 22:00 | 118 | 08:00
KSRM | 132 | 02:00 | 10 | 19:00
Kulaura | 136 | 10:00 | 130 | 00:00
Kurigram | 142 | 06:00 | 122 | 18:30
Kushtia | 132 | 18:00 | 122 | 00:00
Lalbag | 135 | 18:00 | 128 | 00:00
Lalmonirhat | 137 | 05:00 | 122 | 18:00
Madanganj | 130 | 18:00 | 125 | 09:00
Madaripur | 137 | 17:00 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division