## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-04-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-04-2025 | during | 30-04-2025 | during | 30-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 366 | 330 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 380 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 278 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 266 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 24 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 5 | 54 | 53.97 | 53.97 | 53 | 53 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 98 | 147 | 149.36 | 149.36 | 100 | 149 | Loop Oil Shortage
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 23 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 45 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 21 | 21 | 30 | 30 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 19 | 17 | 22 | 22 | 19 | 19 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 125 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 85 | 97 | 149 | 149 | 130 | 130 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 22 | 67 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 144 | 162 | 162 | 54 | 162 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 35 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 470 | 480 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 470 | 480 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 125 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2949 | 3292 | 5269.9 | 5333.9 | 3836.29 | 4075.29
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 32 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 150 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 24 | 48 | 72 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 62 | 75 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 6 | 5 | 7 | 12 | 7 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 1.94 | 0 | 1.94 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 108 | 108 | Engine Problem
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 641 | 1000 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 440 | 155 | 155 | 155 | 155 | 155 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1351 | 1721 | 2968.66 | 2979.72 | 2960.66 | 2971.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 203 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 348 | 340 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 345 | 340 | 340 | 345 | 345 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 33 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 20 | 40 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 113 | 45 | 190 | 190 | 81 | 81 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 113 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 45 | 50 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 30 | 163 | 200 | 200 | 180 | 180 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 98 | 105.3 | 105.3 | 105.3 | 105.3 | FGMO
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1391 | 1717 | 2457.29 | 2387.29 | 2197.85 | 2156.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-04-2025 | during | 30-04-2025 | during | 30-04-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 170 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 105 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.75 | 0 | 49.68 | 0 | 49.68 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 48 | 54.5 | 54.5 | 17 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 257.75 | 335 | 600.78 | 549 | 273.78 | 312
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 39 | 38 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 103 | 91 | 113 | 113 | 103 | 103 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 176 | 175 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 311 | 385 | 385 | 337 | 337 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1474 | 1403 | 1563 | 1563 | 1454 | 1454
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 925 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 99.51 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 375 | 505 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1399.51 | 1399 | 3604.2 | 3514.2 | 2472.01 | 2382.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 288 | 220 | 315 | 315 | 315 | 315 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 0 | 9 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 113 | 100 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 600 | 1012 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.75 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1421.75 | 1868 | 2487.12 | 2486.12 | 2487.12 | 2486.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 184 | 174 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 160 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 179 | 164 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 320 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 93 | 93 | 93 | 93 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.72 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 928 | 1320.22 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.82 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 100 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2042.54 | 2138.22 | 3107.53 | 2941.53 | 3055.15 | 2889.15
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 56 | 56 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 166 | 164 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.9 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 24 | 0 | 20 | 0 | 20 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 210 | 0 | 173.57 | 0 | 173.57 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 459.9 | 290 | 666.97 | 467 | 666.97 | 467
System Total |  |  |  |  | 27566.2 | 28535.742 | 12746.45 | 14163.22 | 22725.45 | 22221.76 | 19403.83 | 19194.14
Forecast Scenario (30-04-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13720 |  | 0 |  | 13720
|  |  |  | 1:00 | 13350 |  | 0 |  | 13350
|  |  |  | 2:00 | 12800 |  | 0 |  | 12800
|  |  |  | 3:00 | 11880 |  | 0 |  | 11880
|  |  |  | 4:00 | 11300 |  | 0 |  | 11300
|  |  |  | 5:00 | 11080 |  | 0 |  | 11080
|  |  |  | 6:00 | 10830 |  | 0 |  | 10830
|  |  |  | 7:00 | 10870 |  | 0 |  | 10870
|  |  |  | 8:00 | 10780 |  | 0 |  | 10780
|  |  |  | 9:00 | 11300 |  | 0 |  | 11300
|  |  |  | 10:00 | 11670 |  | 0 |  | 11670
|  |  |  | 11:00 | 12230 |  | 0 |  | 12230
|  |  |  | 12:00 | 12780 |  | 0 |  | 12780
|  |  |  | 13:00 | 13110 |  | 0 |  | 13110
|  |  |  | 14:00 | 13120 |  | 0 |  | 13120
|  |  |  | 15:00 | 13350 |  | 0 |  | 13350
|  |  |  | 16:00 | 13050 |  | 0 |  | 13050
|  |  |  | 17:00 | 12830 |  | 0 |  | 12830
|  |  |  | 18:00 | 12600 |  | 0 |  | 12600
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 13960 |  | 0 |  | 13960
|  |  |  | 19:30 | 14350 |  | 0 |  | 14350
|  |  |  | 20:00 | 14310 |  | 0 |  | 14310
|  |  |  | 21:00 | 14250 |  | 0 |  | 14250
|  |  |  | 22:00 | 14080 |  | 0 |  | 14080
|  |  |  | 23:00 | 14050 |  | 0 |  | 14050
Probable Maximum Temperature: |  |  | 31.10°C
Probable Maximum Demand at Day Peak: |  |  | 12780.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14350.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14350.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 303.30 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:20 hrs on 30-04-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-04-2025 | [28 empty] | Date: | 29-04-2025 | [28 empty] | Date: | 29-04-2025 | [28 empty] | Date: | 29-04-2025 | [28 empty] | Date: | 29-04-2025 | [16 empty] | Date: | 29-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 75 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 292 | 400 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 17 | 21 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 87 | 70 | 0 | 40 | 0 | 20 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 830 | 0 | 51 | 0 | 8 | 0 | 360 | 330 | 10 | 182 | 35 | 34 | 45 | 44 | 15 | 19 | 44 | 32 | 0 | 0 | 0 | 295 | 320 | 300 | 39 | 30 | 0 | 93 | 7 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 45 | 155 | 0 | 0 | 0 | 7 | 6608 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1576.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 164 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 100 | 220 | 0 | 316 | 750 | 0 | 5263.55 | 11871.55 | 80.32
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 29 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 273 | 350 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 21 | 18 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 87 | 50 | 0 | 40 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 750 | 0 | 51 | 0 | 8 | 0 | 359 | 330 | 10 | 182 | 35 | 34 | 45 | 45 | 9 | 19 | 44 | 32 | 0 | 0 | 0 | 295 | 320 | 300 | 39 | 30 | 0 | 81 | 7 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 6210 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1432.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 162 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 100 | 220 | 0 | 316 | 600 | 0 | 5104.11 | 11314.11 | 80.3
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 35 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 291 | 300 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 20 | 18 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 87 | 50 | 0 | 40 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 700 | 0 | 5 | 0 | 8 | 0 | 300 | 330 | 10 | 182 | 35 | 34 | 45 | 43 | 9 | 19 | 14 | 30 | 0 | 0 | 0 | 300 | 320 | 300 | 39 | 30 | 0 | 80 | 7 | 0 | 10 | 20 | 0 | 17 | 175 | 0 | 48 | 97 | 0 | 0 | 0 | 12 | 5781 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 1117.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 162 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 100 | 180 | 0 | 316 | 597 | 0 | 4736.89 | 10517.89 | 80.29
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 35 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 298 | 250 | 0 | 0 | 0 | 284 | 0 | 0 | 0 | 0 | 19.5 | 18 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 87 | 50 | 0 | 38 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 700 | 0 | 5 | 0 | 8 | 0 | 300 | 330 | 10 | 195 | 5 | 0 | 45 | 0 | 9 | 19 | 0 | 22 | 0 | 0 | 0 | 300 | 320 | 320 | 39 | 30 | 0 | 81 | 7 | 0 | 0 | 20 | 0 | 17 | 175 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 5625.5 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 831.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 166 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 106 | 180 | 0 | 254 | 500 | 0 | 4281.2 | 9906.7 | 80.28
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 35 | 34 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 276 | 200 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 280 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 87 | 50 | 0 | 38 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 690 | 0 | 5 | 0 | 8 | 0 | 300 | 330 | 0 | 185 | 5 | 0 | 45 | 0 | 9 | 0 | 0 | 22 | 0 | 0 | 0 | 305 | 320 | 300 | 39 | 30 | 0 | 80 | 7 | 0 | 0 | 20 | 0 | 17 | 175 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 5415 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 824.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0 | 0 | 168 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 102 | 180 | 0 | 217 | 500 | 0 | 4223.38 | 9638.38 | 80.27
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 17 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 250 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 630 | 0 | 0 | 0 | 0 | 0 | 290 | 300 | 0 | 130 | 0 | 0 | 45 | 0 | 0 | 6 | 0 | 22 | 0 | 0 | 0 | 225 | 320 | 331 | 39 | 30 | 0 | 83 | 0 | 0 | 0 | 20 | 0 | 17 | 176 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 4927 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 824.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0 | 0 | 121 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 102 | 180 | 0 | 221 | 500 | 0 | 4131.19 | 9058.19 | 80.26
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 17 | 24 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 250 | 0 | 0 | 0 | 290 | 0 | 0 | 2 | 0 | 21 | 19 | 0 | 280 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 290 | 300 | 0 | 136 | 0 | 0 | 50 | 0 | 0 | 6 | 0 | 20 | 0 | 1 | 0 | 180 | 320 | 337 | 39 | 30 | 0 | 84 | 0 | 0 | 0 | 20 | 0 | 17 | 175 | 0 | 48 | 106 | 0 | 0 | 1.46 | 12 | 4958.46 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58 | 373 | 0 | 824.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.87 | 130 | 0 | 130 | 0 | 130 | 0 | 300 | 0 | 0.17 | 0 | 119 | 54 | 0 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0.02 | 0 | 140 | 0 | 116 | 180 | 0 | 221 | 500 | 0 | 4150.71 | 9109.17 | 80.25
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 17 | 39 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 250 | 0 | 0 | 0 | 318 | 0 | 0 | 6 | 0 | 21 | 19 | 0 | 280 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 4 | 156 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 290 | 345 | 0 | 218 | 0 | 0 | 50 | 0 | 0 | 13 | 0 | 18 | 0 | 8 | 0 | 180 | 320 | 365 | 39 | 30 | 0 | 97 | 0 | 0 | 0 | 20 | 0 | 17 | 175 | 0 | 68 | 126 | 0 | 0 | 6.14 | 12 | 5276.14 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.39 | 373 | 0 | 825.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 9.91 | 142 | 0 | 130 | 0 | 130 | 0 | 350 | 0 | 0.78 | 0 | 142 | 54 | 0 | 1 | 0 | 0 | 0 | 1.2 | 7 | 0.16 | 0 | 140 | 0 | 121 | 180 | 0 | 220 | 500 | 0 | 4285.78 | 9561.92 | 80.24
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 17 | 66 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 305 | 300 | 0 | 0 | 0 | 300 | 0 | 0 | 14 | 0 | 21 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 156 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 0 | 0 | 290 | 345 | 0 | 204 | 0 | 0 | 50 | 0 | 0 | 20 | 0 | 18 | 0 | 26 | 0 | 190 | 320 | 349 | 39 | 30 | 0 | 95 | 0 | 0 | 0 | 20 | 0 | 17 | 176 | 0 | 69 | 125 | 0 | 1 | 7.66 | 12 | 5450.66 | 882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.27 | 373 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 23.49 | 190 | 0 | 160 | 0 | 160 | 0 | 414 | 0 | 1.89 | 0 | 110 | 56 | 0 | 12 | 0 | 0 | 0 | 1.2 | 32 | 0.22 | 0 | 140 | 0 | 116 | 180 | 0 | 220 | 500 | 0 | 4482.07 | 9932.73 | 80.23
09:00 | 0 | 20 | 25 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 17 | 74 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 308 | 400 | 0 | 0 | 0 | 302 | 0 | 0 | 22 | 0 | 21 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 4 | 158 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 601 | 6 | 0 | 0 | 8 | 0 | 355 | 345 | 0 | 203 | 0 | 0 | 46 | 0 | 0 | 20 | 0 | 20 | 0 | 47 | 0 | 290 | 320 | 348 | 39 | 30 | 0 | 95 | 0 | 0 | 0 | 20 | 0 | 17 | 175 | 0 | 69 | 126 | 0 | 1 | 29.05 | 12 | 6004.05 | 882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.42 | 372 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 38.1 | 188 | 0 | 160 | 0 | 160 | 0 | 414 | 0 | 3.05 | 0 | 122 | 56 | 0 | 19 | 0 | 0 | 0 | 3.8 | 100 | 0.41 | 0 | 140 | 0 | 126 | 220 | 0 | 221 | 500 | 0 | 4653.78 | 10657.83 | 80.22
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 17 | 85 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 292 | 470 | 0 | 0 | 0 | 280 | 0 | 0 | 28 | 35 | 21 | 21 | 0 | 470 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 3 | 40 | 0 | 2 | 211 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 601 | 18 | 15 | 0 | 26 | 0 | 355 | 345 | 1 | 195 | 29 | 0 | 40 | 0 | 0 | 20 | 0 | 26 | 0 | 59 | 0 | 295 | 320 | 362 | 39 | 30 | 0 | 109 | 0 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 78 | 106 | 0 | 2 | 45.89 | 12 | 6483.89 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.31 | 371 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 52.77 | 190 | 0 | 195 | 0 | 160 | 0 | 414 | 0 | 4.21 | 0 | 163 | 56 | 0 | 16 | 0 | 0 | 0 | 8 | 189 | 0.63 | 0 | 140 | 0 | 100 | 220 | 0 | 218 | 530 | 0 | 4953.92 | 11437.81 | 80.21
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 85 | 80 | 0 | 0 | 15 | 40 | 0 | 0 | 450 | 307 | 470 | 0 | 0 | 0 | 287 | 0 | 0 | 30 | 70 | 21 | 19 | 0 | 470 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 60 | 0 | 5 | 40 | 0 | 3 | 420 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 608 | 18 | 51 | 0 | 81 | 0 | 354 | 345 | 10 | 198 | 30 | 15 | 40 | 13 | 5 | 17 | 0 | 28 | 0 | 48 | 0 | 295 | 320 | 375 | 39 | 30 | 0 | 102 | 6 | 0 | 84 | 30 | 0 | 17 | 176 | 0 | 78 | 115 | 0 | 1 | 45.83 | 12 | 7035.83 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.04 | 375 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 53.99 | 188 | 0 | 184 | 0 | 178 | 0 | 414 | 0 | 4.44 | 0 | 167 | 56 | 0 | 16 | 0 | 0 | 0 | 7.4 | 211 | 0.7 | 0 | 200 | 0 | 116 | 220 | 0 | 220 | 600 | 0 | 5158.57 | 12194.4 | 80.2
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 5 | 0 | 85 | 98 | 0 | 0 | 23 | 90 | 0 | 22 | 450 | 306 | 470 | 0 | 45 | 0 | 300 | 0 | 0 | 32 | 70 | 21 | 19 | 0 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 5 | 40 | 0 | 6 | 440 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 641 | 14 | 43 | 0 | 113 | 0 | 348 | 345 | 20 | 203 | 30 | 52 | 45 | 30 | 9 | 17 | 34 | 32 | 0 | 70 | 0 | 285 | 320 | 387 | 39 | 30 | 0 | 103 | 6 | 0 | 81 | 30 | 0 | 17 | 176 | 0 | 78 | 114 | 0 | 2 | 51.75 | 12 | 7422.75 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.51 | 375 | 0 | 928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 51.82 | 184 | 0 | 181 | 0 | 179 | 0 | 414 | 0 | 4.72 | 0 | 166 | 56 | 0 | 24 | 0 | 0 | 0 | 3.9 | 210 | 0.75 | 0 | 200 | 0 | 113 | 220 | 0 | 288 | 600 | 0 | 5323.7 | 12746.45 | 80.2
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 32 | 0 | 85 | 98 | 0 | 0 | 35 | 126 | 0 | 31 | 450 | 302 | 470 | 0 | 35 | 0 | 267 | 0 | 0 | 30 | 70 | 21 | 18 | 0 | 500 | 0 | 0 | 0 | 0 | 4 | 15 | 0 | 0 | 86 | 50 | 4 | 40 | 0 | 6 | 430 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 700 | 18 | 43 | 0 | 90 | 0 | 354 | 345 | 37 | 216 | 30 | 76 | 45 | 51 | 9 | 14 | 34 | 34 | 0 | 70 | 32 | 280 | 320 | 349 | 38 | 30 | 0 | 104 | 6 | 0 | 81 | 30 | 0 | 17 | 176 | 0 | 77 | 112 | 0 | 2 | 47.98 | 12 | 7675.98 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.84 | 375 | 0 | 1009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 53.03 | 182 | 0 | 177 | 0 | 173 | 0 | 414 | 0 | 4.43 | 0 | 166 | 56 | 0 | 26 | 0 | 0 | 0 | 7.6 | 110 | 0.76 | 0 | 200 | 0 | 100 | 220 | 0 | 320 | 625 | 0 | 5333.66 | 13009.64 | 80.19
14:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 0 | 85 | 98 | 0 | 0 | 35 | 144 | 0 | 55 | 450 | 302 | 420 | 0 | 55 | 0 | 300 | 0 | 0 | 26 | 70 | 21 | 18 | 0 | 500 | 0 | 0 | 0 | 0 | 10 | 34 | 0 | 0 | 86 | 76 | 2 | 40 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 700 | 12 | 43 | 0 | 26 | 0 | 342 | 350 | 20 | 208 | 30 | 112 | 45 | 51 | 9 | 5 | 34 | 34 | 0 | 62 | 34 | 290 | 320 | 394 | 38 | 29 | 0 | 92 | 8 | 0 | 81 | 30 | 0 | 17 | 175 | 0 | 77 | 113 | 0 | 1 | 44.34 | 12 | 7636.34 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.02 | 375 | 0 | 1029.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 25.18 | 179 | 0 | 174 | 0 | 169 | 0 | 414 | 0 | 2.35 | 0 | 164 | 55 | 0 | 22 | 0 | 0 | 0 | 7.2 | 44 | 0.69 | 0 | 200 | 0 | 118 | 220 | 0 | 320 | 650 | 0 | 5230.33 | 12866.67 | 80.19
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 54 | 0 | 79 | 98 | 10 | 0 | 35 | 144 | 0 | 66 | 450 | 290 | 540 | 0 | 55 | 0 | 285 | 0 | 0 | 20 | 52 | 21 | 18 | 0 | 550 | 0 | 0 | 0 | 0 | 14 | 32 | 0 | 0 | 86 | 100 | 3 | 37 | 0 | 2 | 214 | 0 | 0 | 4 | 0 | 0 | 143 | 0 | 0 | 0 | 750 | 13 | 43 | 1 | 8 | 0 | 349 | 350 | 23 | 195 | 30 | 115 | 50 | 51 | 9 | 19 | 46 | 34 | 0 | 14 | 38 | 285 | 320 | 365 | 37 | 29 | 0 | 99 | 8 | 0 | 80 | 30 | 0 | 15 | 175 | 0 | 77 | 112 | 0 | 1 | 32.14 | 12 | 7609.14 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67.24 | 378 | 0 | 1134.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 22.53 | 176 | 0 | 166 | 0 | 165 | 0 | 370 | 0 | 2.76 | 0 | 163 | 55 | 0 | 17 | 0 | 0 | 0 | 5.9 | 66 | 0.54 | 0 | 200 | 0 | 110 | 220 | 0 | 327 | 720 | 0 | 5335.94 | 12945.08 | 80.18
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 1 | 79 | 98 | 45 | 0 | 35 | 144 | 0 | 67 | 450 | 286 | 500 | 0 | 55 | 0 | 280 | 0 | 0 | 13 | 52 | 21 | 17 | 0 | 500 | 0 | 0 | 0 | 0 | 17 | 34 | 0 | 0 | 86 | 70 | 1 | 36 | 0 | 2 | 156 | 0 | 0 | 25 | 0 | 0 | 144 | 0 | 0 | 0 | 750 | 8 | 43 | 31 | 26 | 0 | 348 | 350 | 30 | 190 | 30 | 103 | 50 | 67 | 20 | 20 | 59 | 32 | 0 | 38 | 38 | 285 | 320 | 359 | 38 | 20 | 0 | 98 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 0 | 77 | 113 | 0 | 1 | 19.49 | 12 | 7539.49 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.89 | 378 | 0 | 1119.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 7.71 | 175 | 0 | 165 | 0 | 165 | 0 | 340 | 0 | 0.79 | 0 | 164 | 55 | 0 | 16 | 0 | 0 | 0 | 1.4 | 100 | 0.35 | 0 | 200 | 9 | 100 | 220 | 0 | 342 | 750 | 0 | 5293.93 | 12833.42 | 80.18
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 54 | 32 | 79 | 113 | 45 | 0 | 35 | 90 | 0 | 67 | 350 | 302 | 420 | 0 | 55 | 0 | 296 | 0 | 0 | 5 | 52 | 21 | 17 | 0 | 450 | 0 | 0 | 0 | 0 | 12 | 34 | 0 | 0 | 86 | 70 | 1 | 36 | 0 | 5 | 156 | 0 | 0 | 19 | 0 | 0 | 144 | 0 | 0 | 0 | 751 | 3 | 43 | 50 | 45 | 0 | 342 | 345 | 30 | 208 | 30 | 115 | 50 | 85 | 36 | 20 | 52 | 34 | 0 | 16 | 37 | 290 | 320 | 377 | 38 | 20 | 0 | 98 | 8 | 0 | 50 | 30 | 0 | 18 | 175 | 0 | 77 | 122 | 0 | 0 | 6.12 | 12 | 7357.12 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.63 | 381 | 0 | 1063.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 1.12 | 174 | 0 | 165 | 0 | 140 | 0 | 340 | 0 | 0.11 | 0 | 166 | 56 | 0 | 7 | 0 | 0 | 0 | 0.9 | 40 | 0.19 | 0 | 200 | 0 | 110 | 180 | 0 | 251 | 720 | 0 | 4950.17 | 12307.29 | 80.17
18:00 | 8 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 54 | 35 | 94 | 113 | 45 | 2 | 35 | 90 | 0 | 67 | 350 | 294 | 450 | 0 | 55 | 0 | 283 | 0 | 0 | 0 | 60 | 20 | 17 | 0 | 450 | 0 | 0 | 0 | 0 | 3 | 42 | 0 | 0 | 75 | 70 | 0 | 40 | 0 | 6 | 156 | 0 | 0 | 19 | 0 | 0 | 144 | 0 | 0 | 0 | 801 | 0 | 43 | 50 | 45 | 0 | 352 | 345 | 30 | 195 | 30 | 113 | 50 | 80 | 37 | 20 | 46 | 32 | 0 | 1 | 37 | 295 | 320 | 364 | 38 | 39 | 0 | 100 | 8 | 0 | 52 | 30 | 0 | 17 | 175 | 0 | 104 | 167 | 0 | 0 | 0.94 | 12 | 7510.94 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.88 | 380 | 0 | 1064.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 175 | 0 | 165 | 0 | 140 | 0 | 340 | 0 | 0 | 0 | 165 | 55 | 0 | 1 | 0 | 0 | 0 | 0.1 | 7 | 0.01 | 0 | 200 | 0 | 100 | 180 | 0 | 220 | 720 | 0 | 4851.62 | 12362.56 | 80.17
19:00 | 22 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 35 | 97 | 147 | 107 | 22 | 35 | 144 | 0 | 67 | 420 | 287 | 583 | 0 | 55 | 0 | 266 | 0 | 0 | 0 | 125 | 21 | 17 | 0 | 550 | 0 | 0 | 6 | 0 | 0 | 98 | 24 | 0 | 75 | 100 | 0 | 40 | 0 | 2 | 154 | 0 | 0 | 19 | 1 | 0 | 148 | 0 | 0 | 0 | 1000 | 0 | 43 | 80 | 45 | 0 | 355 | 345 | 32 | 184 | 33 | 115 | 50 | 85 | 38 | 20 | 80 | 38 | 8 | 0 | 32 | 290 | 320 | 348 | 38 | 40 | 0 | 100 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 5 | 104 | 169 | 0 | 0 | 0 | 12 | 8451 | 878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 1316.21 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 160 | 0 | 167 | 0 | 414 | 0 | 0 | 0 | 166 | 55 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 100 | 220 | 0 | 219 | 850 | 0 | 5618.21 | 14069.21 | 80.16
19:30 | 24 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 35 | 97 | 147 | 125 | 55 | 35 | 144 | 0 | 67 | 380 | 278 | 480 | 0 | 55 | 0 | 266 | 0 | 0 | 0 | 125 | 21 | 17 | 0 | 480 | 0 | 0 | 30 | 0 | 0 | 102 | 24 | 0 | 75 | 100 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 32 | 8 | 0 | 150 | 0 | 0 | 0 | 1000 | 0 | 43 | 113 | 45 | 0 | 340 | 345 | 40 | 181 | 33 | 115 | 50 | 163 | 38 | 20 | 98 | 38 | 16 | 0 | 39 | 290 | 320 | 311 | 38 | 40 | 0 | 91 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 48 | 105 | 170 | 0 | 0 | 0 | 12 | 8468 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 17 | 1320.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 160 | 0 | 164 | 0 | 320 | 0 | 0 | 0 | 164 | 56 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 100 | 220 | 0 | 220 | 1012 | 0 | 5695.22 | 14163.22
20:00 | 24 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 35 | 97 | 112 | 95 | 50 | 35 | 144 | 0 | 67 | 380 | 283 | 480 | 0 | 55 | 0 | 272 | 0 | 0 | 0 | 125 | 20 | 17 | 0 | 480 | 0 | 0 | 29 | 0 | 0 | 102 | 24 | 0 | 85 | 70 | 0 | 40 | 0 | 15 | 156 | 0 | 0 | 31 | 8 | 0 | 149 | 0 | 0 | 0 | 1050 | 0 | 43 | 112 | 45 | 0 | 320 | 345 | 42 | 189 | 33 | 115 | 50 | 155 | 38 | 20 | 98 | 38 | 16 | 0 | 39 | 290 | 320 | 301 | 38 | 40 | 0 | 81 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 51 | 105 | 171 | 0 | 0 | 0 | 12 | 8415 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 34 | 1361.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 160 | 0 | 164 | 0 | 320 | 0 | 0 | 0 | 162 | 56 | 17 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 100 | 190 | 0 | 220 | 1018 | 0 | 5517.57 | 13932.57 | 80.16
21:00 | 24 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 54 | 35 | 97 | 112 | 15 | 15 | 35 | 126 | 0 | 55 | 380 | 300 | 520 | 0 | 55 | 0 | 273 | 0 | 0 | 0 | 90 | 21 | 17 | 0 | 520 | 0 | 0 | 17 | 0 | 0 | 102 | 40 | 0 | 88 | 12 | 0 | 40 | 0 | 19 | 156 | 0 | 0 | 19 | 8 | 0 | 149 | 0 | 0 | 0 | 1050 | 0 | 43 | 40 | 45 | 0 | 359 | 345 | 50 | 183 | 34 | 90 | 50 | 120 | 38 | 20 | 68 | 38 | 16 | 0 | 39 | 300 | 320 | 311 | 38 | 40 | 0 | 87 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 54.5 | 85 | 161 | 0 | 0 | 0 | 12 | 8167.5 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 17 | 1360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 156 | 0 | 161 | 0 | 414 | 0 | 0 | 0 | 161 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 220 | 0 | 221 | 1070 | 0 | 5618 | 13785.5 | 80.15
22:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 54 | 35 | 97 | 130 | 15 | 0 | 35 | 108 | 0 | 66 | 380 | 293 | 520 | 0 | 55 | 0 | 268 | 0 | 0 | 0 | 90 | 21 | 17 | 0 | 520 | 0 | 0 | 12 | 0 | 0 | 102 | 40 | 0 | 90 | 12 | 0 | 40 | 0 | 25 | 155 | 0 | 0 | 19 | 0 | 0 | 150 | 0 | 0 | 0 | 1050 | 0 | 43 | 30 | 45 | 0 | 360 | 345 | 50 | 185 | 34 | 90 | 50 | 100 | 38 | 20 | 62 | 40 | 16 | 0 | 39 | 290 | 320 | 332 | 39 | 40 | 0 | 97 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 35 | 95 | 161 | 0 | 0 | 0 | 12 | 8098 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 1359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 149 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 166 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 220 | 0 | 220 | 1100 | 0 | 5594 | 13692 | 80.16
23:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 54 | 35 | 90 | 130 | 0 | 0 | 35 | 54 | 0 | 66 | 380 | 295 | 520 | 0 | 17 | 0 | 294 | 0 | 0 | 0 | 90 | 21 | 17 | 0 | 520 | 0 | 0 | 12 | 0 | 2 | 68 | 8 | 0 | 100 | 12 | 0 | 40 | 0 | 28 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 43 | 6 | 45 | 0 | 355 | 345 | 50 | 201 | 34 | 90 | 50 | 100 | 38 | 20 | 45 | 40 | 16 | 0 | 40 | 290 | 320 | 362 | 39 | 40 | 0 | 97 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 35 | 95 | 160 | 0 | 0 | 0 | 10 | 7875 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 148 | 0 | 147 | 0 | 370 | 0 | 0 | 0 | 171 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 221 | 1089 | 0 | 5533 | 13408 | 80.14
Total KWH | 71856 | 765120 | 414240 | 0 | 0 | 0 | 0 | 0 | 8496000 | 0 | 0 | 637920 | 541800 | 1757664 | 1973760 | 387655 | 125802 | 482811 | 1448640 | 0 | 723840 | 8919500 | 7022778 | 9904091 | 0 | 537035 | 0 | 6929067 | 0 | 0 | 225031 | 1104000 | 502200 | 437040 | 0 | 10350000 | 0 | 0 | 91200 | 0 | 185760 | 852734 | 148800 | 0 | 1498560 | 902400 | 31500 | 924000 | 0 | 272640 | 4843636.36 | 0 | 0 | 178080 | 19490.4 | 0 | 3267782 | 0 | 0 | 0 | 18163634 | 117720 | 700160 | 510181 | 719273 | 0 | 8424400 | 8254000 | 513600 | 4652000 | 556272 | 1406400 | 1124380 | 1234080 | 382200 | 380760 | 780900 | 721920 | 84696 | 466900 | 417360 | 6688000 | 7670700 | 8698000 | 909000 | 711120 | 0 | 2254418 | 134424 | 0 | 1229760 | 649728 | 0 | 410000 | 4606980 | 221400 | 1718400 | 2971200 | 0 | 13550 | 331910 | 290880 | 166094738.76 | 16987636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 730800 | 9432727 | 73920 | 25560000 | 0 | 0 | 0 | 21888 | 0 | 0 | 0 | 0 | 0 | 655710 | 0 | 351752 | 4089818 | 0 | 3959200 | 0 | 3881273 | 0 | 9042763 | 0 | 29400 | 0 | 3861000 | 1294690 | 53981 | 192725 | 43584 | 0 | 0 | 50883.72 | 1080720 | 5079 | 16320 | 4843000 | 93352 | 2577000 | 5148330 | 0 | 6152112 | 17381818.18 | 0 | 117611481.9 | 283706220.66

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12746.45 | MW | 12:00 Hr. | Energy Generated |  |  | 283.7062 |  | MKWHr.
| Day Peak Demand |  |  | 12788.45 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.704 |  | MKWHr.
| Evening Peak Generation |  |  | 14163.22 | MW | 19:30 Hr. | Energy Demand |  |  | 284.4102 |  | MKWHr.
| Evening Peak Demand |  |  | 14163.22 | MW | 19:30 Hr. | Maximum Temperature |  |  | 30.5 |  | °C
| Minimum Generation of the Day |  |  | 9058.19 | MW | 05:00 Hr. | Total Gas Supplied |  |  | 1072.16 |  | MMCFD
| Maximum Generation of the Day |  |  | 14163.22 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.0604 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 52.5607 | 0 | 10.9721 | 0 | 0 | 0.22503 | 0 | 0 | 63.7578 | Gas | 144.1798 | Gas | 504912286.98
| Chattogram Zone |  |  | 3.5404 | 23.0073 | 3.6913 | 0 | 0.924 | 0.14922 | 0 | 0.18576 | 31.4979 | Coal | 65.9726 | Coal | 434215596.039
| Cumilla Zone |  |  | 25.3248 | 0 | 4.8158 | 0 | 0 | 0.4669 | 0.72192 | 0 | 31.3295 | HFO | 24.8908 | HFO | 467044974.868
| Mymensingh Zone |  |  | 0 | 0 | 5.2019 | 0 | 0 | 0.34546 | 0 | 0 | 5.5473 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.9621 | Hydro | 0.924 | Hydro | 92400
| Khulna Zone |  |  | 0 | 9.4327 | 0.07392 | 0 | 0 | 0.7308 | 16.9876 | 0 | 27.2251 | Solar | 4.2837 | Solar | 69570755.1092
| Barishal Zone |  |  | 7.8187 | 28.3769 | 0.01632 | 0 | 0 | 0.005079 | 0 | 0 | 36.217 | Import | 43.2696 | Import | 240830447.88
| Rajshahi Zone |  |  | 20.9731 | 0 | 0.021888 | 0 | 0 | 1.0369 | 25.56 | 0 | 47.5918 | Wind | 0.18576 | Wind | 2719526.4
| Rangpur Zone |  |  | 0 | 5.1557 | 0.097565 | 0 | 0 | 1.3243 | 0 | 0 | 6.5776
| Total |  |  | 144.1798 | 65.9726 | 24.8908 | 0 | 0.924 | 4.2837 | 43.2696 | 0.18576 | 283.7062
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 504912286.98 |  | Hydro | 92400
|  |  |  | Coal | 434215596.039 |  | Solar | 69570755.1092
|  |  |  | HFO | 467044974.868 |  | Import | 240830447.88
|  |  |  | HSD | 0 |  | Wind | 2719526.4
[5 empty] | Total: | 171,93,85,987 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 16.9876 | Peak Hr Flow | 877.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33778672.8 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.56 | Peak Hr Flow | 1320.22 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 692 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.72192 | Peak Hr Flow | 38.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 974 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.2696 | Peak Hr Flow | 2235.22 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5129
|  |  |  | Chattogram |  | 0 |  | 1462
|  |  |  | Cumilla |  | 0 |  | 1325
|  |  |  | Mymensingh |  | 0 |  | 1154
|  |  |  | Sylhet |  | 0 |  | 507
|  |  |  | Khulna |  | 0 |  | 1592
|  |  |  | Barishal |  | 0 |  | 366
|  |  |  | Rajshahi |  | 0 |  | 1330
|  |  |  | Rangpur |  | 0 |  | 749
|  |  |  | Total |  | 0 |  | 13614
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:33 | Hathazari 230/132/33kV S/S T-01 HT is restored.
|  | 08:34 | Hathazari 230/132/33kV S/S T-01 LT is restored.
| 08:42 | 16:51 | KSRM 132/33kV S/S Transformer-01 HT Scheduled S/D Due to 33 KV side Isolator Maintenance
| 10:12 | 12:37 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Project Work S/D Due to IDRNPP Project work.
| 10:35 | 11:41 | Sreepur 230/132/33kV S/S Auxiliary Transformer - 2 LT Forced S/D
| 10:35 | 11:41 | Sreepur 230/132/33kV S/S Auxiliary Transformer - 2 HT Forced S/D
| 10:35 | 10:48 | Gopalganj 132/33kV S/S T2 LT Tripped showing Insist O/C relays Due to Reb-8 Fault | [7 empty] | 28.0MW load
interrup.
| 11:22 | 11:34 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance
Protection 21/1(Z1-CN) Distance trip21.Z1 relays Due to N/A
| 11:30 | 15:16 | Chandina 132/33kV S/S TR-2 HT Project Work S/D Due to For TR-02 33kv side interlock
system check
| 11:39 | 12:47 | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Metering purpose | [7 empty] | 20.0MW load
interrup.
| 11:40 | 12:45 | Bhaluka 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Metering purpose | [7 empty] | 20.0MW load
interrup.
| 12:00 |  | Day Peak Gen. 12742 MW
| 12:00 |  | Day Peak 12742 MW.
| 12:49 | 13:38 | Bhaluka 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Metering purpose | [7 empty] | 20.0MW load
interrup.
| 12:50 | 13:37 | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Metering purpose | [7 empty] | 20.0MW load
interrup.
| 13:19 |  | Full load interruption is occurring under TK Chemical substation from 13:19 hrs. due to
tearing of 132 kV Y-phase loop conductor.
| 13:39 | 15:46 | Sikalbaha-TKCL 132kV Ckt-1 Forced S/D from Shikalbaha 230/132kV end.
| 14:08 | 14:52 | Bhaluka 132/33kV S/S Transformer-03 LT Scheduled S/D Due to Metering purpose | [7 empty] | 18.0MW load interrup.
| 14:09 | 14:51 | Bhaluka 132/33kV S/S Transformer-03 HT Scheduled S/D Due to Metering purpose | [7 empty] | 18.0MW load interrup.
| 14:15 | 17:28 | Sonargaon 132/33kV S/S Tr-2 LT Scheduled S/D Due to 33 kv side bus loop change & 33 kv | [7 empty] | 25.0MW load
|  |  | incoming side CT -Y phase loop change | [7 empty] | interrup.
| 14:16 | 17:25 | Sonargaon 132/33kV S/S Tr-2 HT Scheduled S/D Due to 33 kv side , 33 KV Bus to DS loop change | [7 empty] | 25.0MW load interrup.
| 15:10 | 17:37 | Madaripur-Shariatpur 132kV Ckt-2 Scheduled S/D from Shariatpur 132/33kV end Due to SF6 Refilled work
|  | 15:31 | Bagerhat-Bhandaria 132 kV Ckt-1 is restored.
| 17:55 | 18:24 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Distance Relay
relays Due to no u/f
| 19:00 | 23:06 | Kabirpur 132/33kV S/S XFR, T-3 LT Tripped showing Protection relay relays Due to 33 kv | [7 empty] | 80.0MW load
|  |  | EPZ feeder fault. | [7 empty] | interrup.
| 19:30 |  | Evening Peak Generation: 14163 MW.
|  | 19:52 | APR-Hasnabad 230kV Ckt-2 is restored.
| 20:59 | 23:05 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to S/ D is taken by Dhaka Pbs-1 for | [7 empty] | 80.0MW load
|  |  | 33 kv EPZ feeder underground cable maintenance. | [7 empty] | interrup.
| 20:59 | 23:06 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to S/D is taken by Dhaka PBS-1 for 33 | [7 empty] | 80.0MW load
|  |  | kv EPZ feeder underground cable maintenance. | [7 empty] | interrup.
| 06:31 | 07:46 | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Red hot maintenance of 33 kv | [7 empty] | 35.0MW load
|  |  | PBS feeder | [7 empty] | interrup.
| 06:31 | 07:46 | Ramganj 132/33kV S/S Transformer -02 HT Scheduled S/D Due to Red hot maintenance of 33 kv | [7 empty] | 35.0MW load
|  |  | PBS feeder | [7 empty] | interrup.
| 07:35 |  | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Scheduled S/D Due to 33 kv Bus Section-03 | [7 empty] | 3.0MW load
|  |  | Maintenance work (Nesco CB junction point Redhot) | [7 empty] | interrup.
| 07:35 |  | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Scheduled S/D Due to 33 kv Bus Section-03 | [7 empty] | 3.0MW load
|  |  | Maintenance work (Nesco CB junction point Redhot) | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 330 | 8496000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8919500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 278 | 7022778 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 125802 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 266 | 6929067 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 71856 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 637920 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 1973760 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 482811 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 537035 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 21 | 502200 | -
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 437040 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 414240 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 125 | 387655 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 97 | 1757664 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 765120 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 67 | 723840 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1448640 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 225031 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 35 | 541800 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 480 | 10350000 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 480 | 9904091 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 125 | 1104000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3292 | 63757850
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 19490.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 117720 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 178080 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 924000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3267782 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 24 | 148800 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 852734 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 75 | 1498560 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 272640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 91200 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 31500 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | Liquid fuel shortage
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 902400 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Engine Problem
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1000 | 18163634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 185760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 155 | 4843636.36 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1721 | 31497936.76
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4652000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 340 | 8424400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8254000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 556272 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 40 | 513600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 719273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 700160 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 113 | 510181 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 417360 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1124380 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 163 | 1234080 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 721920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 84696 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 380760 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 780900 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 382200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1406400 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 466900 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1717 | 31329482
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13550 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 2971200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1718400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 331910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 290880 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 48 | 221400 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 335 | 5547340
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 909000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 711120 | machine problem
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 91 | 2254418 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 649728 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1229760 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 175 | 4606980 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 410000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 134424 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6688000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 311 | 8698000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7670700 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1403 | 33962130
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 16987636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 73920 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 730800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 505 | 9432727 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1399 | 27225083
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 220 | 6152112 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 16320 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 9 | 93352 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 100 | 2577000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1012 | 17381818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5148330 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4843000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5079 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1868 | 36217011.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4089818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 160 | 3959200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 164 | 3881273 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 320 | 9042763 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 21888 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1320.22 | 25560000 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 351752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 655710 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2138.22 | 47591804
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 56 | 1294690 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 3861000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 43584 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50883.72 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 53981 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 192725 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1080720 | -
Rangpur Area Total |  |  |  |  | 950 | 290 | 6577583.72
Eastern Grid Total |  |  |  |  | 16921.242 | 8468 | 166094738.76
Western Grid Total |  |  |  |  | 11614.5 | 5695.22 | 117611481.9
National Grid Total |  |  |  |  | 28535.742 | 14163.22 | 283706220.66
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9576.77 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4037 | MW
i) Dhaka area |  |  | 5129.23 |  | MW | i) Khulna area |  |  |  | 1592.5 | MW
ii) Chattogram area |  |  | 1462 |  | MW | ii) Barishal area |  |  |  | 365.5 | MW
iii) Cumilla area |  |  | 1324.54 |  | MW | iii) Rajshahi area |  |  |  | 1330 | MW
iv) Mymensingh area |  |  | 1154 |  | MW | iv) Rangpur area |  |  |  | 749 | MW
v) Sylhet area |  |  | 507 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13613.77 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 72 | 13:00 | 133 | Patuakhali | 65.9 | 00:00
2 | AKSML | 18.2 | 02:00 | 68 | Jaldhaka | 56 | 19:00 | 134 | Payra | 28 | 00:00
3 | Aftabnagar | 34 | 13:00 | 69 | Jamalpur | 130 | 19:30 | 135 | Postogola | 53 | 13:00
4 | Agargaon | 119 | 13:00 | 70 | Jashore | 134 | 19:30 | 136 | Purbachal | 18 | 19:00
5 | Agrabad | 82 | 00:00 | 71 | Jhenaidah | 108 | 21:00 | 137 | Purbasadipur | 100 | 19:30
6 | Amnura | 40 | 19:00 | 72 | Joydebpur | 143 | 18:30 | 138 | Rahanpur | 21 | 01:00
7 | Ashuganj | 102.5 | 21:00 | 73 | Joypurhat | 64 | 19:00 | 139 | Rahim | 45 | 01:00
8 | BSRM | 208 | 21:00 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 61.5 | 13:00
9 | Bagerhat | 83 | 19:30 | 75 | KSRM | 14 | 00:00 | 141 | Rajendrapur | 137 | 19:30
10 | Bajitpur | 46 | 19:00 | 76 | Kabirpur | 276 | 16:00 | 142 | Rajshahi | 100 | 19:30
11 | Bakulia | 97 | 19:30 | 77 | Kachua | 79 | 19:30 | 143 | Rajshahi-230 | 87 | 13:00
12 | Banani | 42 | 13:00 | 78 | Kallyanpur | 99 | 18:30 | 144 | Ramganj | 114 | 19:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kalurghat | 40 | 15:00 | 145 | Rampur | 41 | 00:00
14 | Barapukuria | 56 | 19:00 | 80 | Kamrangirchar | 69.7 | 13:00 | 146 | Rangamati | 15 | 18:30
15 | Barguna | 18 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 119 | 20:00
16 | Barishal | 105 | 13:00 | 82 | Kasba | 33 | 20:00 | 148 | Ruppur | 7 | 10:00
17 | Barishal-230 | 66 | 19:00 | 83 | Kazla | 103 | 19:30 | 149 | SSM | 12 | 07:00
18 | Baroaulia | 69 | 15:00 | 84 | Keranigonj | 76 | 19:30 | 150 | Saidpur | 88 | 19:00
19 | Baroirhat | 58 | 19:30 | 85 | Khagrachori | 30 | 19:00 | 151 | Satkhira | 127 | 19:30
20 | Bashundhara | 178 | 14:00 | 86 | Khulna | 60 | 18:30 | 152 | Satmasjid | 94 | 13:00
21 | BashundharaCement | 9 | 19:30 | 87 | Khulshi | 199 | 16:00 | 153 | Savar | 226 | 16:00
22 | Beanibazar | 60 | 20:00 | 88 | Kishoreganj | 126 | 20:00 | 154 | SevenRings | 16.52 | 16:00
23 | Benapole | 62 | 20:00 | 89 | Kodda | 309 | 21:00 | 155 | ShahCement | 30 | 09:00
24 | Bhaluka | 144 | 19:00 | 90 | Kulaura | 37 | 19:00 | 156 | Shahjadpur | 85 | 12:00
25 | Bhandaria | 50 | 21:00 | 91 | Kurigram | 43 | 19:00 | 157 | Shahjibazar | 115 | 21:00
26 | Bhangura | 42 | 14:00 | 92 | Kushtia | 145 | 19:00 | 158 | Shahmirpur | 51 | 00:00
27 | Bheramara(GK) | 58 | 14:00 | 93 | Lalbag | 67 | 19:30 | 159 | Shariatpur | 76 | 22:00
28 | Bhulta | 244 | 20:00 | 94 | Lalmonirhat | 41 | 19:30 | 160 | Sherpur | 148 | 19:00
29 | Bog-Sherpur | 62 | 07:00 | 95 | MI_Cement | 18.3 | 12:00 | 161 | Shikalbaha | 32 | 00:00
30 | Bogura | 152 | 00:00 | 96 | Madanganj | 40 | 18:00 | 162 | Shitalakhya | 80.1 | 16:00
31 | Borhanuddin | 77 | 00:00 | 97 | Madaripur | 100 | 20:00 | 163 | Sholosohor | 47 | 15:00
32 | Brahmanbaria | 118 | 23:00 | 98 | Madartek | 82.6 | 22:00 | 164 | Shyampur | 150 | 00:00
33 | Cantonment | 122 | 13:00 | 99 | Madunaghat | 50 | 14:00 | 165 | Siddhirganj | 122 | 19:00
34 | Chandina | 19.17 | 22:00 | 100 | Magura | 61 | 19:00 | 166 | Sirajganj | 102 | 20:00
35 | Chandpur | 66 | 19:00 | 101 | Mahasthangarh | 70 | 19:00 | 167 | Sonargaon | 113 | 18:30
36 | Chandraghona | 35 | 18:30 | 102 | Manikganj | 129 | 20:00 | 168 | Sreemongol | 73 | 18:30
37 | Chapai | 62 | 21:00 | 103 | Maniknagar | 72 | 13:00 | 169 | Sreepur | 115 | 19:00
38 | Charsaidpur | 45 | 21:00 | 104 | Matarbari | 50 | 19:00 | 170 | Srinagar | 42.53 | 22:00
39 | Chauddagram | 69 | 19:30 | 105 | Matuail | 64 | 15:00 | 171 | Sunamganj | 52 | 19:30
40 | Chhatak | 29 | 18:30 | 106 | Millgate | 110 | 16:00 | 172 | Sylhet | 32 | 20:00
41 | Chowmuhani | 212 | 21:00 | 107 | Mirpur | 123 | 19:00 | 173 | Sylhet-132 | 113 | 19:00
42 | Chuadanga | 95 | 19:00 | 108 | Mirsorai | 10 | 12:00 | 174 | TK | 34.5 | 21:00
43 | Coxsbazar | 135 | 19:00 | 109 | Mirzapur | 49 | 21:00 | 175 | Tangail | 176 | 12:00
44 | Cumilla(N) | 142 | 23:00 | 110 | Mithapukur | 50 | 18:30 | 176 | Thakurgaon | 87 | 19:30
45 | Cumilla(S) | 158 | 15:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 124 | 19:30
46 | Daudkandi | 147 | 19:00 | 112 | Mogbazar | 129.9 | 15:00 | 178 | Ullahpara | 42 | 15:00
47 | Dhaka | 56 | 12:00 | 113 | Mongla | 45 | 19:00 | 179 | Ullon | 44 | 20:00
48 | Dhamrai | 134 | 18:00 | 114 | Motijheel | 36 | 12:00 | 180 | Uttara | 81 | 13:00
49 | Dhanmondi | 125 | 13:00 | 115 | Muktagacha | 35 | 19:00 | 181 | UttaraNew | 45 | 19:00
50 | Dohazari | 98 | 22:00 | 116 | Munshiganj | 98 | 20:00 | 182 | Zigatola | 68 | 13:00
51 | Faridpur | 140 | 20:00 | 117 | Muradnagar | 25 | 20:00
52 | Fatullah | 100 | 16:00 | 118 | Mymensingh | 197 | 19:00
53 | Fenchuganj | 32 | 19:30 | 119 | Naogaon | 115 | 19:30
54 | Feni | 108 | 19:00 | 120 | Narail | 57.5 | 19:30
55 | GPH | 86 | 03:00 | 121 | Narinda | 72 | 13:00
56 | Ghatail | 68 | 14:00 | 122 | Narshingdi | 172 | 23:00
57 | Ghorashal | 15 | 16:00 | 123 | Natore | 132 | 13:00
58 | Ghorashal-230 | 88 | 23:00 | 124 | Nawabganj | 51.7 | 20:00
59 | Goalpara | 34 | 19:30 | 125 | Netrakona | 125 | 19:00
60 | Gollamari | 90 | 19:30 | 126 | New | 83.9 | 15:00
61 | Gopalganj | 102 | 19:30 | 127 | Niamatpur | 76 | 19:00
62 | Gulshan | 112 | 13:00 | 128 | Noapara | 44 | 19:00
63 | Halishahar | 78 | 16:00 | 129 | PHP | 4 | 12:00
64 | HaripurSBU | 180 | 16:00 | 130 | Pabna | 103 | 13:00
65 | Hasnabad | 85 | 22:00 | 131 | Palashbari | 98 | 19:00
66 | Hathazari | 79 | 19:00 | 132 | Panchagarh | 43 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11871.55 | 13 |  | 11885.14
1:00 | 11314.11 | 25 |  | 11340.11
2:00 | 10517.89 | 0 |  | 10517.89
3:00 | 9906.7 | 0 |  | 9906.7
4:00 | 9638.38 | 0 |  | 9638.38
5:00 | 9058.19 | 0 |  | 9058.19
6:00 | 9109.17 | 0 |  | 9109.17
7:00 | 9561.92 | 0 |  | 9561.92
8:00 | 9932.73 | 0 |  | 9932.73
9:00 | 10657.83 | 0 |  | 10657.83
10:00 | 11437.81 | 0 |  | 11437.81
11:00 | 12194.4 | 0 |  | 12194.4
12:00 | 12746.45 | 40 |  | 12788.45
13:00 | 13009.64 | 99 |  | 13112.64
14:00 | 12866.67 | 92 |  | 12962.67
15:00 | 12945.08 | 133 |  | 13084.08
16:00 | 12833.42 | 116 |  | 12954.42
17:00 | 12307.29 | 100 |  | 12411.29
18:00 | 12362.56 | 86 |  | 12452.56
19:00 | 14069.21 | 0 |  | 14069.21
19:30 | 14163.22 | 0 |  | 14163.22
20:00 | 13932.57 | 0 |  | 13932.57
21:00 | 13785.5 | 0 |  | 13785.5
22:00 | 13692 | 0 |  | 13692
23:00 | 13408 | 0 |  | 13408
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6608 | 5263.55 | 11871.55 | DAILY GENERATION CURVE
00:30 | 6409 | 5183.83 | 11592.83
01:00 | 6210 | 5104.11 | 11314.11 | 29-04-2025
01:30 | 5995.5 | 4920.5 | 10916
02:00 | 5781 | 4736.89 | 10517.89
02:30 | 5703.25 | 4509.045 | 10212.295
03:00 | 5625.5 | 4281.2 | 9906.7
03:30 | 5520.25 | 4252.29 | 9772.54
04:00 | 5415 | 4223.38 | 9638.38
04:30 | 5171 | 4177.285 | 9348.285
05:00 | 4927 | 4131.19 | 9058.19
05:30 | 4942.73 | 4140.95 | 9083.68
06:00 | 4958.46 | 4150.71 | 9109.17
06:30 | 5117.3 | 4218.245 | 9335.545
07:00 | 5276.14 | 4285.78 | 9561.92
07:30 | 5363.4 | 4383.925 | 9747.325
08:00 | 5450.66 | 4482.07 | 9932.73
08:30 | 5727.355 | 4567.925 | 10295.28
09:00 | 6004.05 | 4653.78 | 10657.83
09:30 | 6243.97 | 4803.85 | 11047.82
10:00 | 6483.89 | 4953.92 | 11437.81
10:30 | 6759.86 | 5056.245 | 11816.105
11:00 | 7035.83 | 5158.57 | 12194.4
11:30 | 7229.29 | 5241.135 | 12470.425
12:00 | 7422.75 | 5323.7 | 12746.45
12:30 | 7549.365 | 5328.68 | 12878.045
13:00 | 7675.98 | 5333.66 | 13009.64
13:30 | 7656.16 | 5281.995 | 12938.155
14:00 | 7636.34 | 5230.33 | 12866.67
14:30 | 7622.74 | 5283.135 | 12905.875
15:00 | 7609.14 | 5335.94 | 12945.08
15:30 | 7574.315 | 5314.935 | 12889.25
16:00 | 7539.49 | 5293.93 | 12833.42
16:30 | 7448.305 | 5122.05 | 12570.355
17:00 | 7357.12 | 4950.17 | 12307.29
17:30 | 7434.03 | 4900.895 | 12334.925
18:00 | 7510.94 | 4851.62 | 12362.56
18:30 | 7980.97 | 5234.915 | 13215.885
19:00 | 8451 | 5618.21 | 14069.21
19:30 | 8468 | 5695.22 | 14163.22
20:00 | 8415 | 5517.57 | 13932.57
20:30 | 8291.25 | 5567.785 | 13859.035 |  | Executive Engineer
21:00 | 8167.5 | 5618 | 13785.5 |  | Network Operation Division
21:30 | 8132.75 | 5606 | 13738.75
22:00 | 8098 | 5594 | 13692
22:30 | 7986.5 | 5563.5 | 13550
23:00 | 7875 | 5533 | 13408

## En-Curve
QF-LDC-12
Date | 29-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3426 | 2398 | 790 | 0 | 32 | 1576.55 | 40 | 2843 | 0 | 190 | 576 | 0 | 0 | 0 | 13 | DAILY ENERGY CURVE
00:30 | 3449.5 | 2299 | 857.5 | 0 | 32 | 1504.33 | 40 | 2703.5 | 0 | 158 | 549 | 0 | 0 | 0 | 19 | 29-04-2025
01:00 | 3473 | 2200 | 925 | 0 | 32 | 1432.11 | 40 | 2564 | 0 | 126 | 522 | 0 | 0 | 0 | 25
01:30 | 3435.5 | 2046 | 925.5 | 0 | 31 | 1275 | 40 | 2536.5 | 0 | 126 | 500.5 | 0 | 0 | 0 | 12.5 | Energy Generated | 283.7062 |  | MKWHr
02:00 | 3398 | 1892 | 926 | 0 | 30 | 1117.89 | 40 | 2509 | 0 | 126 | 479 | 0 | 0 | 0 | 0 | Energy not Served | 0.704 |  | MKWHr
02:30 | 3407 | 1865.75 | 926 | 0 | 26 | 974.545 | 39 | 2431.5 | 0 | 117.5 | 425 | 0 | 0 | 0 | 0 | Total Energy Requirement | 284.4102 |  | MKWHr
03:00 | 3416 | 1839.5 | 926 | 0 | 22 | 831.2 | 38 | 2354 | 0 | 109 | 371 | 0 | 0 | 0 | 0
03:30 | 3381 | 1771.25 | 926 | 0 | 22 | 827.79 | 38 | 2325.5 | 0 | 109 | 371 | 0 | 0 | 1 | 0
04:00 | 3346 | 1703 | 926 | 0 | 22 | 824.38 | 38 | 2297 | 0 | 109 | 371 | 0 | 0 | 2 | 0
04:30 | 3259 | 1672.5 | 926 | 0 | 22 | 824.285 | 31.5 | 2246 | 0 | 83 | 283 | 0 | 0 | 1 | 0
05:00 | 3172 | 1642 | 926 | 0 | 22 | 824.19 | 25 | 2195 | 0 | 57 | 195 | 0 | 0 | 0 | 0
05:30 | 3184 | 1621 | 926 | 0 | 21 | 824.58 | 25 | 2179 | 5.6 | 66 | 201 | 0 | 0 | 30.5 | 0
06:00 | 3196 | 1600 | 926 | 0 | 20 | 824.97 | 25 | 2163 | 11.2 | 75 | 207 | 0 | 0 | 61 | 0
06:30 | 3350 | 1612 | 926 | 0 | 19 | 825.155 | 32.5 | 2174 | 41.89 | 75 | 234.5 | 0 | 0 | 45.5 | 0
07:00 | 3504 | 1624 | 926 | 0 | 18 | 825.34 | 40 | 2185 | 72.58 | 75 | 262 | 0 | 0 | 30 | 0
07:30 | 3582.5 | 1714 | 904 | 0 | 18 | 823.67 | 40 | 2171 | 141.655 | 58 | 275.5 | 0 | 0 | 19 | 0
08:00 | 3661 | 1804 | 882 | 0 | 18 | 822 | 40 | 2157 | 210.73 | 41 | 289 | 0 | 0 | 8 | 0
08:30 | 3720.5 | 1986 | 882 | 0 | 19 | 819.5 | 40 | 2163.5 | 297.78 | 63 | 293.5 | 0 | 0 | 10.5 | 0
09:00 | 3780 | 2168 | 882 | 0 | 20 | 817 | 40 | 2170 | 384.83 | 85 | 298 | 0 | 0 | 13 | 0
09:30 | 3790 | 2317 | 903.5 | 0 | 23 | 822 | 40 | 2230 | 492.82 | 123.5 | 299 | 0 | 0 | 7 | 0
10:00 | 3800 | 2466 | 925 | 0 | 26 | 827 | 40 | 2290 | 600.81 | 162 | 300 | 0 | 0 | 1 | 0
10:30 | 3809.5 | 2536 | 925 | 0 | 27 | 827.5 | 40 | 2468 | 618.105 | 194.5 | 369 | 0 | 0 | 1.5 | 0
11:00 | 3819 | 2606 | 925 | 0 | 28 | 828 | 40 | 2646 | 635.4 | 227 | 438 | 0 | 0 | 2 | 0
11:30 | 3834.5 | 2618 | 925 | 0 | 30 | 878 | 40 | 2706 | 652.425 | 236 | 549.5 | 0 | 0 | 1 | 20
12:00 | 3850 | 2630 | 925 | 0 | 32 | 928 | 40 | 2766 | 669.45 | 245 | 661 | 0 | 0 | 0 | 40
12:30 | 3813.5 | 2636 | 925 | 0 | 33 | 968.5 | 40 | 2819 | 616.545 | 268.5 | 756 | 0 | 0 | 2 | 69.5
13:00 | 3777 | 2642 | 925 | 0 | 34 | 1009 | 40 | 2872 | 563.64 | 292 | 851 | 0 | 0 | 4 | 99
13:30 | 3807 | 2570 | 925 | 0 | 34 | 1019.445 | 40 | 2848 | 474.21 | 289 | 924.5 | 0 | 0 | 7 | 95.5
14:00 | 3837 | 2498 | 925 | 0 | 34 | 1029.89 | 40 | 2824 | 384.78 | 286 | 998 | 0 | 0 | 10 | 92
14:30 | 3778 | 2577 | 927.5 | 0 | 34 | 1082.43 | 38.5 | 2815.5 | 344.445 | 269.5 | 1027 | 0 | 0 | 12 | 112.5
15:00 | 3719 | 2656 | 930 | 0 | 34 | 1134.97 | 37 | 2807 | 304.11 | 253 | 1056 | 0 | 0 | 14 | 133
15:30 | 3682.5 | 2627 | 930 | 0 | 33 | 1127.38 | 36.5 | 2801 | 282.87 | 254 | 1099.5 | 0 | 0 | 15.5 | 124.5
16:00 | 3646 | 2598 | 930 | 0 | 32 | 1119.79 | 36 | 2795 | 261.63 | 255 | 1143 | 0 | 0 | 17 | 116
16:30 | 3656.5 | 2463.5 | 930 | 0 | 33 | 1091.505 | 36 | 2738 | 183.35 | 262 | 1162 | 0 | 0 | 14.5 | 108
17:00 | 3667 | 2329 | 930 | 0 | 34 | 1063.22 | 36 | 2681 | 105.07 | 269 | 1181 | 0 | 0 | 12 | 100
17:30 | 3657 | 2344.5 | 929.5 | 0 | 33 | 1063.925 | 38 | 2689 | 62.5 | 290.5 | 1219.5 | 0 | 0 | 7.5 | 93
18:00 | 3647 | 2360 | 929 | 0 | 32 | 1064.63 | 40 | 2697 | 19.93 | 312 | 1258 | 0 | 0 | 3 | 86
18:30 | 3671.5 | 2545 | 903.5 | 0 | 35 | 1190.42 | 40 | 2979 | 9.965 | 407.5 | 1432.5 | 0 | 0 | 1.5 | 43
19:00 | 3696 | 2730 | 878 | 0 | 38 | 1316.21 | 40 | 3261 | 0 | 503 | 1607 | 0 | 0 | 0 | 0
19:30 | 3544 | 2510 | 877 | 0 | 38 | 1320.22 | 40 | 3419 | 0 | 514 | 1901 | 0 | 0 | 0 | 0
20:00 | 3532 | 2486 | 735 | 0 | 38 | 1361.57 | 40 | 3424 | 0 | 479 | 1837 | 0 | 0 | 0 | 0
20:30 | 3604 | 2565 | 735 | 0 | 38 | 1360.785 | 40 | 3450 | 0 | 469.5 | 1596.75 | 0 | 0 | 0 | 0
21:00 | 3676 | 2644 | 735 | 0 | 38 | 1360 | 40 | 3476 | 0 | 460 | 1356.5 | 0 | 0 | 0 | 0
21:30 | 3676 | 2643.5 | 735 | 0 | 39 | 1359.5 | 40 | 3471.5 | 0 | 469 | 1305.25 | 0 | 0 | 0 | 0
22:00 | 3676 | 2643 | 735 | 0 | 40 | 1359 | 40 | 3467 | 0 | 478 | 1254 | 0 | 0 | 0 | 0
22:30 | 3690 | 2645 | 735 | 0 | 40 | 1361 | 40 | 3439.5 | 0 | 436.5 | 1162 | 0 | 0 | 1 | 0
23:00 | 3704 | 2647 | 735 | 0 | 40 | 1363 | 40 | 3412 | 0 | 395 | 1070 | 0 | 0 | 2 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 398 | 04:00 | 336 | 21:00 | Payra | 417 | 04:00 | 410 | 19:00
Ashuganj | 408 | 4:00 | 384 | 11:00 | Rahanpur | 412 | 04:00 | 388 | 19:00
Bhulta | 401 | 04:00 | 380 | 11:00 | Rampal | 406 | 05:00 | 390 | 11:00
Bibiana | 391 | 19:30 | 382 | 12:00
BIPTC | 399 | 20:00 | 393 | 19:30
Bogura | 401 | 04:00 | 371 | 19:00
Gopalganj | 405 | 05:00 | 391 | 12:00
Kaliakoir | 370 | 19:30 | 352 | 15:00
Madunaghat | 406 | 05:00 | 388 | 12:00
Meghnaghat | 398 | 05:00 | 385 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 04:00 | 220 | 10:00 | Keranigonj | 230 | 04:00 | 217 | 12:00
AKSML | 235 | 04:00 | 220 | 12:00 | Khulna(S) | 235 | 04:00 | 219 | 19:00
Aminbazar | 251 | 10:00 | 220 | 12:00 | Madunaghat | 237 | 06:00 | 224 | 10:00
Ashuganj | 232 | 03:00 | 223 | 15:00 | Madunaghat-400 | 237 | 05:00 | 223 | 12:00
Ashuganj-400 | 234 | 4:00 | 222 | 11:00 | Maniknagar | 225 | 06:00 | 215 | 12:00
Baghabari | 234 | 18:00 | 227 | 15:00 | Meghnaghat | 235 | 05:00 | 222 | 11:00
Barapukuria | 226 | 05:00 | 220 | 00:00 | Meghnaghat-400 | 231 | 04:00 | 220 | 12:00
Barapukuria-230 | 226 | 5:00 | 221 | 21:00 | Mirsorai | 232 | 05:00 | 219 | 13:00
Barishal | 241 | 04:00 | 232 | 19:00 | Rajshahi | 236 | 05:00 | 222 | 11:00
Bheramara | 235 | 20:00 | 222 | 11:00 | Rampal | 233 | 04:00 | 220 | 18:30
Bhulta | 228 | 04:00 | 216 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 04:00 | 218 | 15:00 | Rampura | 227 | 04:00 | 215 | 11:00
BIPTC | 235 | 20:00 | 227 | 19:00 | Shikalbaha | 236 | 04:00 | 220 | 11:00
Bogura | 235 | 06:00 | 224 | 00:00 | Shyampur | 230 | 04:00 | 218 | 11:00
Bogura-400 | 235 | 06:00 | 225 | 00:00 | Siddhirganj | 226 | 07:00 | 218 | 11:00
Borhanuddin | 245 | 05:00 | 238 | 21:00 | Sirajgonj | 241 | 04:00 | 235 | 15:00
BSRM | 231 | 06:00 | 219 | 11:00 | Sreepur | 230 | 04:00 | 225 | 15:00
Cumilla(N) | 227 | 03:00 | 215 | 11:00 | Tongi | 225 | 04:00 | 210 | 15:00
Faridpur | 239 | 06:00 | 228 | 12:00
Fenchuganj | 228 | 06:00 | 222 | 12:00
Ghorashal | 230 | 00:00 | 220 | 15:00
Ghorashal-230 | 228 | 04:00 | 215 | 15:00
Gopalganj | 239 | 04:00 | 230 | 12:00
GPH | 233 | 05:00 | 220 | 12:00
Haripur | 229 | 04:00 | 218 | 11:00
Hasnabad | 228 | 04:00 | 217 | 12:00
Hathazari | 236 | 04:00 | 23 | 07:00
Ishurdi | 236 | 04:00 | 226 | 11:00
Jhenaidah | 236 | 22:00 | 217 | 15:00
Kaliakoir | 231 | 04:00 | 218 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 129 | 11:00 | Madartek | 136 | 04:00 | 129 | 11:00
Agargaon | 137 | 04:00 | 128 | 12:00 | Madunaghat | 137 | 06:00 | 128 | 10:00
Agrabad | 138 | 05:00 | 125 | 11:00 | Magura | 134 | 02:00 | 123 | 13:00
AKS | 135 | 04:00 | 124 | 12:00 | Mahasthangarh | 136 | 06:00 | 131 | 00:00
Aminbazar | 135 | 04:00 | 127 | 10:00 | Manikganj | 128 | 19:30 | 118 | 15:00
Amnura | 136 | 05:00 | 122 | 21:00 | Maniknagar | 135 | 04:00 | 125 | 12:00
Ashuganj | 136 | 04:00 | 131 | 15:00 | Matarbari | 137 | 05:00 | 112 | 12:00
Bagerhat | 140 | 05:00 | 121 | 19:30 | Matuail | 133 | 04:00 | 125 | 12:00
Bajitpur | 132 | 05:00 | 126 | 14:00 | Millgate | 133 | 03:00 | 121 | 11:00
Bakulia | 139 | 05:00 | 127 | 11:00 | Mirpur | 133 | 06:00 | 125 | 10:00
Banani | 135 | 03:00 | 128 | 10:00 | Mirzapur | 130 | 19:30 | 121 | 11:00
Bangabhaban | 135 | 05:00 | 125 | 12:00 | Mithapukur | 131 | 03:00 | 128 | 12:00
Barapukuria | 133 | 17:00 | 128 | 21:00 | MI_Cement | 133 | 05:00 | 125 | 11:00
Barguna | 137 | 06:00 | 132 | 12:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 137 | 04:00 | 127 | 19:00 | Mogbazar | 137 | 04:00 | 129 | 12:00
Barishal-230 | 137 | 04:00 | 128 | 19:00 | Mongla | 138 | 01:00 | 122 | 19:00
Baroaulia | 134 | 05:00 | 130 | 00:00 | Motijheel | 135 | 05:00 | 125 | 12:00
Baroirhat | 127 | 06:00 | 118 | 10:00 | Muktagacha | 132 | 00:00 | 123 | 15:00
Bashundhara | 136 | 03:00 | 121 | 11:00 | Munshiganj | 132 | 04:00 | 124 | 11:00
BashundharaCement | 132 | 04:00 | 124 | 11:00 | Muradnagar | 131 | 04:00 | 121 | 11:00
Beanibazar | 132 | 03:00 | 127 | 18:30 | Mymensingh | 133 | 00:00 | 117 | 15:00
Benapole | 136 | 04:00 | 120 | 15:00 | Naogaon | 134 | 04:00 | 128 | 00:00
Bhaluka | 130 | 04:00 | 125 | 16:00 | Narail | 136 | 04:00 | 122 | 15:00
Bhandaria | 134 | 03:00 | 119 | 21:00 | Narinda | 135 | 4:00 | 125 | 12:00
Bhangura | 134 | 03:00 | 128 | 11:00 | Narshingdi | 129 | 02:00 | 120 | 12:00
Bheramara | 135 | 02:00 | 127 | 15:00 | Natore | 134 | 18:00 | 129 | 11:00
Bheramara(GK) | 135 | 02:00 | 128 | 11:00 | Nawabganj | 138 | 04:00 | 129 | 11:00
Bhulta | 128 | 05:00 | 120 | 11:00 | Netrakona | 127 | 03:00 | 115 | 18:30
Bog-Sherpur | 136 | 04:00 | 130 | 00:00 | New | 132 | 05:00 | 122 | 15:00
Bogura | 138 | 04:00 | 133 | 00:00 | Niamatpur | 135 | 05:00 | 127 | 19:30
Bogura-230 | 138 | 04:00 | 133 | 00:00 | Noapara | 139 | 02:00 | 125 | 13:00
Brahmanbaria | 130 | 00:00 | 125 | 14:00 | Pabna | 137 | 18:00 | 129 | 15:00
Cantonment | 137 | 04:00 | 128 | 11:00 | Palashbari | 131 | 02:00 | 126 | 19:00
Chandina | 133 | 03:00 | 122 | 11:00 | Panchagarh | 134 | 04:00 | 122 | 10:00
Chandpur | 131 | 04:00 | 116 | 11:00 | Patuakhali | 136 | 02:00 | 132 | 11:00
Chandraghona | 137 | 05:00 | 127 | 12:00 | Payra | 138 | 03:00 | 134 | 12:00
Chapai | 132 | 03:00 | 123 | 20:00 | PHP | 134 | 04:00 | 116 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 03:00 | 125 | 12:00 | Postogola | 136 | 05:00 | 127 | 11:00
Chauddagram | 134 | 04:00 | 117 | 11:00 | Purbachal | 136 | 03:00 | 128 | 12:00
Chhatak | 131 | 04:00 | 125 | 18:30 | Purbasadipur | 129 | 18:30 | 121 | 07:00
Chowmuhani | 131 | 04:00 | 111 | 15:00 | Rahanpur | 134 | 04:00 | 129 | 00:00
Chuadanga | 135 | 04:00 | 122 | 16:00 | Rahanpur-400 | 137 | 04:00 | 129 | 19:00
Coxsbazar | 132 | 06:00 | 110 | 18:30 | Rahim | 132 | 04:00 | 125 | 12:00
Cumilla(N) | 133 | 03:00 | 122 | 11:00 | Rajbari | 140 | 04:00 | 133 | 12:00
Cumilla(S) | 134 | 04:00 | 120 | 11:00 | Rajendrapur | 133 | 04:00 | 120 | 00:00
Daudkandi | 130 | 04:00 | 119 | 11:00 | Rajshahi | 135 | 05:00 | 129 | 11:00
Dhaka | 136 | 03:00 | 129 | 11:00 | Rajshahi-230 | 136 | 05:00 | 117 | 19:00
Dhamrai | 136 | 03:00 | 125 | 15:00 | Ramganj | 126 | 06:00 | 112 | 11:00
Dhanmondi | 135 | 22:00 | 129 | 09:00 | Rampur | 137 | 05:00 | 124 | 12:00
Dohazari | 138 | 06:00 | 122 | 12:00 | Rampura | 136 | 04:00 | 128 | 12:00
Faridpur | 140 | 04:00 | 134 | 15:00 | Rangamati | 136 | 05:00 | 126 | 12:00
Fatullah | 134 | 05:00 | 126 | 11:00 | Rangpur | 131 | 04:00 | 125 | 00:00
Fenchuganj | 136 | 06:00 | 132 | 14:00 | Ruppur | 139 | 04:00 | 132 | 15:00
Feni | 131 | 03:00 | 110 | 00:00 | Saidpur | 131 | 04:00 | 122 | 19:00
Ghatail | 129 | 00:00 | 121 | 11:00 | Satkhira | 140 | 02:00 | 123 | 13:00
Ghorashal | 135 | 19:30 | 129 | 15:00 | Satmasjid | 137 | 04:00 | 128 | 12:00
Goalpara | 141 | 01:00 | 127 | 15:00 | Savar | 133 | 02:00 | 125 | 10:00
Gollamari | 140 | 01:00 | 129 | 13:00 | SevenRings | 137 | 04:00 | 129 | 11:00
Gopalganj | 139 | 01:00 | 129 | 19:00 | ShahCement | 132 | 03:00 | 125 | 12:00
Gopalganj-400 | 139 | 02:00 | 133 | 15:00 | Shahjadpur | 139 | 18:00 | 132 | 16:00
Gulshan | 136 | 06:00 | 128 | 11:00 | Shahjibazar | 132 | 01:00 | 127 | 15:00
Halishahar | 138 | 05:00 | 125 | 12:00 | Shahmirpur | 139 | 05:00 | 127 | 12:00
Haripur | 133 | 04:00 | 126 | 11:00 | Shariatpur | 138 | 03:00 | 129 | 19:00
HaripurSBU | 133 | 04:00 | 126 | 11:00 | Sherpur | 136 | 20:00 | 124 | 12:00
Hasnabad | 135 | 04:00 | 128 | 09:00 | Shikalbaha | 123 | 04:00 | 112 | 00:00
Hathazari | 138 | 04:00 | 129 | 13:00 | Shikalbaha-230 | 140 | 05:00 | 128 | 10:00
Ishurdi | 139 | 04:00 | 133 | 11:00 | Shitalakhya | 133 | 05:00 | 125 | 11:00
Jaldhaka | 127 | 04:00 | 120 | 07:00 | Sholosohor | 136 | 05:00 | 127 | 13:00
Jamalpur | 138 | 18:30 | 128 | 11:00 | Shyampur | 135 | 19:30 | 127 | 11:00
Jashore | 136 | 02:00 | 121 | 13:00 | Shyampur-230 | 134 | 04:00 | 125 | 11:00
Jhenaidah | 137 | 05:00 | 124 | 15:00 | Siddhirganj | 133 | 05:00 | 126 | 11:00
Jhenaidah-230 | 137 | 04:00 | 125 | 15:00 | Sirajganj | 133 | 06:00 | 128 | 12:00
Joydebpur | 135 | 09:00 | 123 | 14:00 | Sonargaon | 134 | 19:30 | 123 | 12:00
Joypurhat | 134 | 06:00 | 124 | 00:00 | Sreemongol | 132 | 00:00 | 127 | 15:00
Juldah | 139 | 05:00 | 128 | 11:00 | Sreepur | 133 | 04:00 | 130 | 01:00
Kabirpur | 131 | 05:00 | 120 | 15:00 | Srinagar | 138 | 05:00 | 129 | 12:00
Kachua | 130 | 03:00 | 117 | 11:00 | SSM | 138 | 05:00 | 132 | 00:00
Kaliakoir | 138 | 03:00 | 125 | 11:00 | Sunamganj | 130 | 04:00 | 124 | 19:30
Kallyanpur | 135 | 03:00 | 127 | 10:00 | Sylhet | 132 | 03:00 | 129 | 14:00
Kalurghat | 136 | 05:00 | 127 | 12:00 | Sylhet-132 | 132 | 05:00 | 129 | 15:00
Kamrangirchar | 137 | 02:00 | 128 | 12:00 | Tangail | 127 | 00:00 | 120 | 11:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 135 | 04:00 | 125 | 00:00
Kasba | 131 | 04:00 | 121 | 11:00 | TK | 137 | 06:00 | 128 | 11:00
Kazla | 134 | 04:00 | 125 | 12:00 | Tongi | 133 | 04:00 | 124 | 15:00
Keranigonj | 139 | 04:00 | 129 | 12:00 | Ullahpara | 135 | 04:00 | 129 | 15:00
Khagrachori | 137 | 05:00 | 125 | 12:00 | Ullon | 136 | 04:00 | 128 | 10:00
Khulna | 141 | 04:00 | 124 | 20:00 | Uttara | 134 | 04:00 | 125 | 10:00
Khulna(S) | 141 | 02:00 | 129 | 13:00 | UttaraNew | 134 | 03:00 | 125 | 10:00
Khulshi | 137 | 05:00 | 124 | 12:00 | Zigatola | 138 | 03:00 | 128 | 00:00
Kishoreganj | 130 | 04:00 | 122 | 15:00
Kodda | 134 | 19:00 | 119 | 14:00
KSRM | 137 | 05:00 | 127 | 11:00
Kulaura | 135 | 05:00 | 131 | 15:00
Kurigram | 130 | 19:30 | 124 | 07:00
Kushtia | 135 | 04:00 | 125 | 15:00
Lalbag | 138 | 04:00 | 128 | 12:00
Lalmonirhat | 129 | 05:00 | 122 | 19:00
Madanganj | 132 | 04:00 | 124 | 11:00
Madaripur | 136 | 04:00 | 130 | 20:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division