## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-04-2025 | during | 01-05-2025 | during | 01-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 367 | 346 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 294 | 281 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 30 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 286 | 284 | 335 | 335 | 300 | 300 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 16 | 8 | 102 | 8 | 102
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 130 | 148 | 149.36 | 149.36 | 149 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 30 | 55 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 17 | 17 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 139 | 95 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 109 | 149 | 149 | 130 | 130 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 53 | 105 | 105 | 17 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 26 | 85 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 144 | 162 | 162 | 162 | 54 | 162 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 11 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 520 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 400 | 520 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 3072 | 3318 | 5236.9 | 5300.9 | 3790.01 | 4024.01
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 8 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 148 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 16 | 64 | 82 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 8 | 7 | 22 | 7 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 12 | 108 | 108 | 60 | 60 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 4.66 | 0 | 4.66 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 60 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 108 | 108 | Engine Problem
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 901 | 1045 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 156 | 155 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1453 | 1651 | 3405.38 | 3419.72 | 3333.38 | 3353.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 193 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 345 | 320 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 305 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 33 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 43 | 47 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 45 | 63 | 190 | 190 | 113 | 113 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 55 | 100 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 8 | 39 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 86 | 120 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 24 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 52 | 105.3 | 105.3 | 105.3 | 105.3 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 94 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 14 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1479 | 1592 | 2457.29 | 2387.29 | 2216.85 | 2175.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-04-2025 | during | 01-05-2025 | during | 01-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 122 | 163 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 105 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 27.45 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 54.5 | 54.5 | 54.5 | 55 | 55 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 230.45 | 334.5 | 601.1 | 549 | 312.1 | 332
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 37 | 38 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 101 | 91 | 113 | 113 | 103 | 103 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 83 | 83 | 83 | 83 | 83
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 175 | 175 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 10 | 10 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 315 | 385 | 385 | 337 | 337 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 353 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1505 | 1429 | 1563 | 1563 | 1454 | 1454
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 930 | 872 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89.13 | 0 | 88 | 0 | 88 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 428 | 478 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1447.13 | 1350 | 3602.2 | 3514.2 | 2470.01 | 2382.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 220 | 300 | 315 | 315 | 315 | 315 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 9 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 110 | 90 | 120 | 120 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 900 | 920 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.25 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1706.25 | 1846 | 2477.12 | 2476.12 | 2435.12 | 2434.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 164 | 156 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 152 | 149 | 220 | 220 | 195 | 195 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 162 | 152 | 220 | 220 | 173 | 173 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 350 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 12 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.9 | 0 | 4.9 | 0 | 4.9 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1054 | 1364.92 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.44 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 18 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2026.34 | 2288.92 | 3109.43 | 2943.53 | 2960.64 | 2794.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 55 | 54 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 156 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 37 | 0 | 27 | 0 | 27 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 209 | 0 | 197.03 | 0 | 197.03 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 467 | 350 | 697.43 | 467 | 697.43 | 467
System Total |  |  |  |  | 27566.2 | 28535.742 | 13386.17 | 14159.42 | 23149.85 | 22620.76 | 19669.54 | 19417.45
Forecast Scenario (01-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13700 |  | 0 |  | 13700
|  |  |  | 1:00 | 13390 |  | 0 |  | 13390
|  |  |  | 2:00 | 13010 |  | 0 |  | 13010
|  |  |  | 3:00 | 12570 |  | 0 |  | 12570
|  |  |  | 4:00 | 12170 |  | 0 |  | 12170
|  |  |  | 5:00 | 11800 |  | 0 |  | 11800
|  |  |  | 6:00 | 11180 |  | 0 |  | 11180
|  |  |  | 7:00 | 10740 |  | 0 |  | 10740
|  |  |  | 8:00 | 10540 |  | 0 |  | 10540
|  |  |  | 9:00 | 10390 |  | 0 |  | 10390
|  |  |  | 10:00 | 10270 |  | 0 |  | 10270
|  |  |  | 11:00 | 10670 |  | 0 |  | 10670
|  |  |  | 12:00 | 11220 |  | 0 |  | 11220
|  |  |  | 13:00 | 11680 |  | 0 |  | 11680
|  |  |  | 14:00 | 11220 |  | 0 |  | 11220
|  |  |  | 15:00 | 11640 |  | 0 |  | 11640
|  |  |  | 16:00 | 11490 |  | 0 |  | 11490
|  |  |  | 17:00 | 10890 |  | 0 |  | 10890
|  |  |  | 18:00 | 10430 |  | 0 |  | 10430
|  |  |  | 18:30 | 11400 |  | 0 |  | 11400
|  |  |  | 19:00 | 12370 |  | 0 |  | 12370
|  |  |  | 19:30 | 13280 |  | 0 |  | 13280
|  |  |  | 20:00 | 13130 |  | 0 |  | 13130
|  |  |  | 21:00 | 13390 |  | 0 |  | 13390
|  |  |  | 22:00 | 13340 |  | 0 |  | 13340
|  |  |  | 23:00 | 13300 |  | 0 |  | 13300
Probable Maximum Temperature: |  |  | 31.20°C
Probable Maximum Demand at Day Peak: |  |  | 11220.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 13390.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13390.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 284.53 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:51 hrs on 01-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-04-2025 | [28 empty] | Date: | 30-04-2025 | [28 empty] | Date: | 30-04-2025 | [28 empty] | Date: | 30-04-2025 | [28 empty] | Date: | 30-04-2025 | [16 empty] | Date: | 30-04-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 54 | 35 | 79 | 150 | 0 | 0 | 35 | 54 | 0 | 67 | 380 | 293 | 450 | 0 | 17 | 0 | 266 | 0 | 0 | 0 | 70 | 21 | 17 | 0 | 520 | 0 | 0 | 12 | 0 | 0 | 68 | 0 | 0 | 100 | 12 | 0 | 40 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 45 | 0 | 355 | 345 | 51 | 181 | 34 | 90 | 50 | 108 | 13 | 20 | 80 | 40 | 16 | 0 | 41 | 290 | 320 | 358 | 39 | 40 | 0 | 101 | 8 | 0 | 81 | 30 | 0 | 17 | 174 | 35 | 48 | 142 | 0 | 0 | 0 | 10 | 7671 | 735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 1364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 156 | 0 | 147 | 0 | 414 | 0 | 0 | 0 | 170 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 100 | 220 | 0 | 220 | 1083 | 0 | 5558 | 13229 | 80.14
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 20 | 78 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 304 | 450 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 70 | 21.5 | 17 | 0 | 450 | 0 | 0 | 12 | 0 | 0 | 63 | 0 | 0 | 100 | 12 | 0 | 40 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 910 | 0 | 43 | 0 | 45 | 0 | 334 | 345 | 51 | 185 | 31 | 91 | 70 | 120 | 9 | 20 | 80 | 36 | 0 | 0 | 41 | 285 | 320 | 353 | 39 | 40 | 0 | 97 | 8 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 48 | 95 | 0 | 0 | 0 | 12 | 7091.5 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 1367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 155 | 0 | 142 | 0 | 350 | 0 | 0 | 0 | 169 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 100 | 220 | 0 | 220 | 950 | 0 | 5461 | 12552.5 | 80.13
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 294 | 400 | 0 | 0 | 0 | 268 | 0 | 0 | 0 | 52 | 17.5 | 17 | 0 | 450 | 0 | 0 | 12 | 0 | 1 | 68 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 43 | 0 | 45 | 0 | 305 | 345 | 51 | 186 | 31 | 70 | 70 | 120 | 9 | 20 | 80 | 36 | 0 | 0 | 41 | 295 | 320 | 346 | 39 | 40 | 0 | 96 | 8 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 6828.5 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 1265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 162 | 0 | 151 | 0 | 350 | 0 | 0 | 0 | 168 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 110 | 220 | 0 | 221 | 891 | 0 | 5276 | 12104.5 | 80.13
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 17 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 298 | 400 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 52 | 17.5 | 17 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 0 | 0 | 38 | 0 | 24 | 157 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 850 | 0 | 43 | 0 | 45 | 0 | 305 | 345 | 51 | 182 | 31 | 50 | 50 | 120 | 9 | 20 | 80 | 34 | 0 | 0 | 0 | 295 | 320 | 347 | 39 | 40 | 0 | 97 | 5 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 6723.5 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 1104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 114 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 110 | 220 | 0 | 221 | 889 | 0 | 5025 | 11748.5 | 80.12
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 301 | 400 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 52 | 17 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 0 | 0 | 36 | 0 | 24 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 820 | 0 | 43 | 0 | 45 | 0 | 305 | 345 | 50 | 194 | 31 | 50 | 50 | 100 | 9 | 20 | 52 | 32 | 0 | 0 | 0 | 290 | 320 | 358 | 39 | 40 | 0 | 97 | 5 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 6625 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 116 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 100 | 220 | 0 | 220 | 823 | 0 | 4764 | 11389 | 80.12
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 301 | 400 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 100 | 0 | 0 | 38 | 0 | 25 | 157 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 705 | 0 | 43 | 0 | 45 | 0 | 305 | 345 | 50 | 193 | 31 | 50 | 50 | 100 | 9 | 20 | 28 | 32 | 0 | 0 | 0 | 295 | 320 | 350 | 39 | 40 | 0 | 99 | 5 | 0 | 81 | 30 | 0 | 17 | 173 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 6475 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0 | 0 | 164 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 100 | 220 | 0 | 222 | 750 | 0 | 4717 | 11192 | 80.11
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 68 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 292 | 450 | 0 | 0 | 0 | 265 | 0 | 0 | 1 | 35 | 17 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 0 | 0 | 38 | 0 | 28 | 157 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 750 | 1 | 43 | 0 | 45 | 0 | 305 | 345 | 50 | 184 | 31 | 50 | 50 | 85 | 9 | 20 | 0 | 30 | 0 | 4 | 0 | 290 | 320 | 350 | 39 | 40 | 0 | 99 | 5 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 48 | 101 | 0 | 0 | 3.84 | 12 | 6431.84 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.04 | 373 | 0 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1.7 | 179 | 0 | 140 | 0 | 140 | 0 | 414 | 0 | 0.16 | 0 | 111 | 56 | 0 | 1 | 0 | 0 | 0 | 0.1 | 8 | 0.03 | 0 | 150 | 7 | 100 | 220 | 0 | 220 | 705 | 0 | 4685.03 | 11116.87 | 80.11
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 79 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 380 | 282 | 350 | 0 | 0 | 0 | 265 | 0 | 0 | 6 | 35 | 17 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 0 | 1 | 40 | 0 | 27 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 805 | 5 | 43 | 0 | 45 | 0 | 300 | 345 | 50 | 183 | 31 | 50 | 51 | 85 | 9 | 11 | 0 | 22 | 0 | 16 | 0 | 285 | 320 | 350 | 39 | 40 | 0 | 80 | 5 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 68 | 125 | 0 | 0 | 7.96 | 12 | 6414.96 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.71 | 373 | 0 | 962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 7.38 | 160 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 0.74 | 0 | 110 | 56 | 0 | 7 | 0 | 0 | 0 | 2.1 | 27 | 0.17 | 0 | 200 | 7 | 100 | 220 | 0 | 221 | 760 | 0 | 4808.1 | 11223.06 | 80.1
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 85 | 50 | 0 | 0 | 0 | 17 | 0 | 0 | 380 | 287 | 350 | 0 | 0 | 0 | 284 | 0 | 0 | 14 | 35 | 17 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 100 | 0 | 2 | 40 | 0 | 3 | 157 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 806 | 10 | 43 | 0 | 45 | 0 | 300 | 345 | 50 | 193 | 34 | 50 | 50 | 51 | 9 | 18 | 0 | 28 | 0 | 35 | 0 | 295 | 320 | 382 | 39 | 40 | 0 | 80 | 5 | 0 | 81 | 30 | 0 | 17 | 174 | 0 | 68 | 124 | 0 | 1 | 21.93 | 12 | 6485.93 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.08 | 372 | 0 | 964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 19.43 | 160 | 0 | 140 | 0 | 140 | 0 | 350 | 0 | 1.83 | 0 | 149 | 56 | 0 | 16 | 0 | 0 | 0 | 4 | 98 | 0.32 | 0 | 200 | 6 | 110 | 220 | 0 | 220 | 800 | 0 | 4961.66 | 11447.59 | 80.1
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 17 | 88 | 50 | 0 | 0 | 1 | 17 | 0 | 0 | 420 | 292 | 350 | 0 | 0 | 0 | 275 | 0 | 0 | 20 | 35 | 29 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 3 | 40 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 805 | 17 | 43 | 0 | 45 | 0 | 359 | 345 | 50 | 188 | 34 | 50 | 50 | 51 | 9 | 3 | 0 | 30 | 0 | 51 | 0 | 290 | 320 | 304 | 39 | 40 | 0 | 99 | 5 | 0 | 81 | 30 | 0 | 17 | 175 | 0 | 68 | 124 | 0 | 2 | 34.14 | 12 | 6600.14 | 878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51 | 372 | 0 | 1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 38.51 | 166 | 0 | 165 | 0 | 161 | 0 | 414 | 0 | 3.34 | 0 | 136 | 56 | 0 | 25 | 0 | 0 | 0 | 5.9 | 152 | 0.34 | 0 | 250 | 5 | 106 | 220 | 0 | 220 | 823 | 0 | 5280.6 | 11880.74 | 80.09
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 113 | 133 | 0 | 0 | 30 | 85 | 0 | 0 | 420 | 299 | 400 | 0 | 0 | 0 | 282 | 0 | 0 | 21 | 52 | 20 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 89 | 0 | 4 | 40 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 805 | 18 | 43 | 0 | 45 | 0 | 350 | 345 | 50 | 196 | 31 | 56 | 50 | 51 | 9 | 13 | 34 | 28 | 0 | 58 | 0 | 300 | 320 | 352 | 39 | 40 | 0 | 101 | 5 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 68 | 124 | 0 | 2 | 45.78 | 12 | 7060.78 | 878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.21 | 372 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 42.58 | 173 | 0 | 163 | 0 | 156 | 0 | 414 | 0 | 3.95 | 0 | 119 | 56 | 0 | 34 | 0 | 0 | 0 | 7.5 | 186 | 0.18 | 0 | 250 | 6 | 106 | 220 | 0 | 220 | 901 | 0 | 5415.42 | 12476.2 | 80.09
11:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 10 | 28 | 113 | 132 | 57 | 15 | 35 | 144 | 0 | 10 | 420 | 293 | 400 | 0 | 0 | 0 | 283 | 0 | 0 | 29 | 70 | 20 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 89 | 15 | 3 | 40 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 900 | 13 | 43 | 10 | 45 | 0 | 348 | 345 | 48 | 195 | 29 | 90 | 50 | 60 | 9 | 19 | 34 | 30 | 16 | 27 | 0 | 300 | 320 | 373 | 36 | 40 | 0 | 102 | 10 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 68 | 124 | 0 | 2 | 38.93 | 12 | 7418.93 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.15 | 420 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 48.16 | 167 | 0 | 159 | 0 | 160 | 0 | 414 | 0 | 3.15 | 0 | 161 | 56 | 0 | 36 | 0 | 0 | 0 | 5.8 | 208 | 0.12 | 0 | 250 | 6 | 110 | 220 | 0 | 220 | 900 | 0 | 5551.38 | 12970.31 | 80.08
12:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 35 | 0 | 113 | 130 | 139 | 30 | 35 | 144 | 0 | 26 | 420 | 294 | 400 | 0 | 30 | 0 | 286 | 0 | 0 | 11 | 90 | 20 | 17 | 0 | 400 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 100 | 88 | 2 | 40 | 0 | 2 | 156 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 901 | 9 | 43 | 55 | 45 | 0 | 345 | 345 | 43 | 199 | 32 | 94 | 50 | 86 | 9 | 19 | 34 | 34 | 24 | 14 | 8 | 290 | 353 | 368 | 37 | 40 | 0 | 101 | 10 | 0 | 84 | 30 | 0 | 17 | 175 | 0 | 67 | 122 | 0 | 2 | 27.45 | 12 | 7739.45 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.13 | 428 | 0 | 1054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 57.44 | 164 | 0 | 152 | 0 | 162 | 0 | 414 | 0 | 4.9 | 0 | 158 | 55 | 0 | 37 | 0 | 0 | 0 | 8 | 209 | 0.25 | 0 | 250 | 6 | 110 | 220 | 0 | 220 | 900 | 0 | 5646.72 | 13386.17 | 80.08
13:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 35 | 3 | 113 | 130 | 195 | 55 | 35 | 144 | 0 | 50 | 380 | 267 | 400 | 0 | 55 | 0 | 265 | 0 | 0 | 1 | 160 | 20 | 16 | 0 | 400 | 0 | 0 | 13 | 0 | 12 | 0 | 0 | 0 | 100 | 88 | 1 | 40 | 0 | 9 | 155 | 0 | 0 | 0 | 4 | 0 | 148 | 0 | 0 | 0 | 851 | 18 | 43 | 92 | 45 | 0 | 359 | 345 | 43 | 181 | 32 | 111 | 40 | 136 | 9 | 20 | 86 | 36 | 52.2 | 35 | 39 | 285 | 320 | 348 | 36 | 40 | 0 | 96 | 10 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 67 | 122 | 0 | 2 | 49.67 | 12 | 8001.87 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.34 | 426 | 0 | 1163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 56.19 | 158 | 0 | 147 | 0 | 161 | 0 | 414 | 0 | 5.12 | 0 | 164 | 55 | 35 | 35 | 0 | 0 | 0 | 8 | 202 | 0.68 | 0 | 250 | 6 | 110 | 220 | 0 | 220 | 879 | 0 | 5686.33 | 13688.2 | 80.07
14:00 | 8 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 35 | 35 | 113 | 129 | 45 | 55 | 35 | 144 | 0 | 64 | 380 | 279 | 350 | 0 | 55 | 0 | 265 | 0 | 0 | 3 | 125 | 20 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 70 | 30 | 0 | 40 | 0 | 5 | 155 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 800 | 17 | 43 | 60 | 45 | 0 | 356 | 345 | 44 | 181 | 32 | 90 | 40 | 120 | 9 | 20 | 17 | 34 | 16 | 41 | 38 | 295 | 320 | 303 | 37 | 40 | 0 | 81 | 10 | 0 | 83 | 30 | 0 | 17 | 175 | 17 | 76 | 111 | 0 | 2 | 45.36 | 12 | 7354.36 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.37 | 407 | 0 | 1267.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 25.96 | 157 | 0 | 147 | 0 | 154 | 0 | 350 | 0 | 3.27 | 0 | 162 | 55 | 0 | 31 | 0 | 0 | 0 | 6.8 | 172 | 0.25 | 0 | 307 | 6 | 99 | 220 | 0 | 220 | 921 | 0 | 5751.63 | 13105.99 | 80.07
15:00 | 8 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 35 | 113 | 128 | 45 | 15 | 35 | 144 | 0 | 66 | 420 | 292 | 350 | 0 | 55 | 0 | 297 | 0 | 0 | 2 | 108 | 20 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 40 | 10 | 0 | 40 | 0 | 4 | 155 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 803 | 15 | 43 | 20 | 45 | 0 | 335 | 345 | 43 | 197 | 32 | 90 | 40 | 85 | 9 | 20 | 17 | 32 | 16 | 14 | 38 | 305 | 320 | 330 | 37 | 39 | 0 | 91 | 10 | 0 | 83 | 30 | 0 | 16 | 174 | 17 | 66 | 111 | 0 | 2 | 31.57 | 12 | 7288.57 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.86 | 405 | 0 | 1268.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 9.74 | 156 | 0 | 147 | 0 | 149 | 0 | 414 | 0 | 1.07 | 0 | 161 | 55 | 0 | 25 | 0 | 0 | 0 | 5.9 | 145 | 0.37 | 0 | 307 | 6 | 110 | 220 | 0 | 236 | 900 | 0 | 5691.14 | 12979.71 | 80.06
16:00 | 32 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 38 | 19 | 103 | 143 | 45 | 15 | 35 | 144 | 0 | 66 | 420 | 284 | 350 | 0 | 55 | 0 | 267 | 0 | 0 | 2 | 52 | 20 | 17 | 0 | 350 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 30 | 10 | 0 | 40 | 0 | 3 | 156 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 801 | 9 | 43 | 20 | 45 | 0 | 346 | 345 | 43 | 187 | 32 | 90 | 40 | 85 | 19 | 20 | 17 | 30 | 16 | 7 | 38 | 310 | 320 | 302 | 38 | 40 | 0 | 98 | 10 | 0 | 83 | 30 | 0 | 16 | 174 | 17 | 65 | 120 | 0 | 0 | 8.4 | 12 | 7110.4 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.34 | 406 | 0 | 1264.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 7.41 | 155 | 0 | 147 | 0 | 148 | 0 | 414 | 0 | 0.65 | 0 | 155 | 56 | 0 | 16 | 0 | 0 | 0 | 4.2 | 85 | 0.35 | 0 | 250 | 6 | 104 | 220 | 0 | 300 | 900 | 0 | 5619.02 | 12729.42 | 80.06
17:00 | 50 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 96 | 144 | 45 | 15 | 35 | 144 | 0 | 66 | 420 | 275 | 300 | 0 | 55 | 0 | 267 | 0 | 0 | 1 | 52 | 20 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 36 | 0 | 7 | 156 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 802 | 3 | 43 | 20 | 45 | 0 | 354 | 340 | 43 | 183 | 32 | 90 | 40 | 52 | 37 | 20 | 17 | 34 | 16 | 8 | 38 | 305 | 320 | 308 | 38 | 40 | 0 | 81 | 10 | 0 | 83 | 30 | 0 | 16 | 174 | 22 | 65 | 121 | 0 | 0 | 0.04 | 12 | 6995.04 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.39 | 405 | 0 | 1161.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3.31 | 155 | 0 | 147 | 0 | 147 | 0 | 414 | 0 | 0.29 | 0 | 160 | 55 | 0 | 7 | 0 | 0 | 0 | 1.9 | 14 | 0.19 | 0 | 250 | 6 | 98 | 180 | 0 | 300 | 820 | 0 | 5268.92 | 12263.96 | 80.05
18:00 | 98 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 17 | 96 | 144 | 45 | 15 | 35 | 144 | 0 | 66 | 300 | 300 | 300 | 0 | 55 | 0 | 295 | 0 | 0 | 1 | 70 | 20 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 30 | 0 | 37 | 0 | 8 | 158 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 802 | 0 | 43 | 20 | 45 | 0 | 300 | 300 | 44 | 205 | 33 | 90 | 40 | 51 | 38 | 20 | 17 | 36 | 16 | 1 | 38 | 310 | 320 | 358 | 38 | 39 | 0 | 83 | 10 | 0 | 83 | 20 | 0 | 16 | 174 | 54.5 | 93 | 132 | 0 | 0 | 0 | 12 | 7122.5 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.81 | 405 | 0 | 1167.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43 | 153 | 0 | 147 | 0 | 147 | 0 | 300 | 0 | 0.07 | 0 | 156 | 54 | 0 | 1 | 0 | 0 | 0 | 0.5 | 11 | 0.02 | 0 | 200 | 6 | 110 | 220 | 0 | 300 | 722 | 0 | 5027.24 | 12149.74 | 80.05
19:00 | 16 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 17 | 109 | 148 | 70 | 15 | 35 | 162 | 0 | 73 | 450 | 278 | 583 | 0 | 55 | 0 | 267 | 0 | 0 | 0 | 70 | 20 | 17 | 0 | 575 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 60 | 0 | 40 | 0 | 4 | 156 | 17 | 0 | 0 | 1 | 0 | 148 | 0 | 0 | 0 | 1045 | 0 | 43 | 36 | 56 | 0 | 354 | 345 | 44 | 182 | 33 | 95 | 50 | 58 | 38 | 20 | 52 | 38 | 16 | 0 | 38 | 300 | 320 | 391 | 38 | 39 | 0 | 103 | 10 | 0 | 83 | 30 | 0 | 16 | 174 | 54.5 | 102 | 162 | 0 | 0 | 0 | 12 | 8354.5 | 878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480 | 0 | 1329.31 | 0 | 0 | 0 | 10 | 0 | 0 | 25 | 0 | 8 | 0 | 0 | 0 | 154 | 0 | 147 | 0 | 149 | 0 | 414 | 0 | 0 | 0 | 157 | 55 | 35 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 100 | 220 | 0 | 300 | 760 | 0 | 5583.31 | 13937.81 | 80.04
19:30 | 16 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 54 | 17 | 109 | 148 | 95 | 15 | 35 | 162 | 0 | 85 | 400 | 281 | 520 | 0 | 55 | 0 | 284 | 0 | 0 | 0 | 70 | 20 | 17 | 0 | 520 | 0 | 0 | 12 | 0 | 0 | 34 | 16 | 0 | 100 | 60 | 0 | 40 | 0 | 8 | 155 | 17 | 0 | 8 | 8 | 0 | 148 | 0 | 0 | 0 | 1045 | 0 | 43 | 100 | 63 | 0 | 320 | 305 | 47 | 193 | 33 | 115 | 50 | 120 | 38 | 20 | 52 | 38 | 16 | 0 | 39 | 310 | 320 | 315 | 38 | 40 | 0 | 91 | 10 | 0 | 83 | 30 | 0 | 17 | 175 | 54.5 | 105 | 163 | 0 | 0 | 0 | 12 | 8324.5 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478 | 0 | 1364.92 | 0 | 0 | 0 | 70 | 0 | 0 | 35 | 0 | 12 | 0 | 0 | 0 | 156 | 0 | 149 | 0 | 152 | 0 | 350 | 0 | 0 | 0 | 156 | 54 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 90 | 220 | 0 | 300 | 920 | 0 | 5834.92 | 14159.42
20:00 | 16 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 54 | 17 | 113 | 148 | 95 | 15 | 35 | 162 | 0 | 80 | 400 | 263 | 480 | 0 | 55 | 0 | 266 | 0 | 0 | 0 | 70 | 20 | 17 | 0 | 480 | 0 | 0 | 10 | 0 | 0 | 34 | 16 | 0 | 100 | 60 | 0 | 40 | 0 | 15 | 155 | 17 | 0 | 12 | 8 | 0 | 152 | 0 | 0 | 0 | 1040 | 0 | 43 | 88 | 63 | 0 | 320 | 300 | 47 | 182 | 32 | 115 | 50 | 120 | 38 | 20 | 52 | 38 | 16 | 0 | 39 | 300 | 320 | 313 | 38 | 40 | 0 | 87 | 10 | 0 | 83 | 30 | 0 | 17 | 175 | 54.5 | 106 | 164 | 0 | 0 | 0 | 12 | 8161.5 | 730 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 1367.22 | 0 | 0 | 0 | 88 | 0 | 0 | 35 | 0 | 16 | 0 | 0 | 0 | 156 | 0 | 149 | 0 | 152 | 0 | 414 | 0 | 0 | 0 | 158 | 54 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 100 | 220 | 0 | 300 | 942 | 0 | 5813.22 | 13974.72 | 80.04
21:00 | 16 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 54 | 17 | 113 | 148 | 95 | 0 | 35 | 162 | 0 | 83 | 400 | 285 | 420 | 0 | 55 | 0 | 271 | 0 | 0 | 0 | 70 | 20 | 17 | 0 | 420 | 0 | 0 | 12 | 0 | 0 | 34 | 16 | 0 | 100 | 20 | 0 | 40 | 0 | 19 | 155 | 17 | 0 | 10 | 8 | 0 | 151 | 0 | 0 | 0 | 1040 | 0 | 43 | 100 | 63 | 0 | 320 | 345 | 47 | 183 | 33 | 115 | 50 | 120 | 39 | 20 | 52 | 38 | 16 | 0 | 39 | 305 | 320 | 349 | 38 | 40 | 0 | 96 | 10 | 0 | 83 | 30 | 0 | 17 | 175 | 54.5 | 106 | 164 | 0 | 0 | 0 | 12 | 8129.5 | 725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 477 | 0 | 1363.03 | 0 | 0 | 0 | 50 | 0 | 0 | 35 | 0 | 16 | 0 | 0 | 0 | 158 | 0 | 152 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 160 | 55 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 100 | 220 | 0 | 300 | 990 | 0 | 5790.03 | 13919.53 | 80.03
22:00 | 0 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 17 | 113 | 148 | 45 | 0 | 35 | 162 | 0 | 40 | 400 | 300 | 420 | 0 | 55 | 0 | 280 | 0 | 0 | 0 | 52 | 20 | 17 | 0 | 420 | 0 | 0 | 12 | 0 | 0 | 34 | 0 | 0 | 100 | 20 | 0 | 40 | 0 | 13 | 155 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1040 | 0 | 43 | 50 | 63 | 0 | 320 | 345 | 47 | 198 | 34 | 90 | 50 | 85 | 39 | 20 | 52 | 40 | 16 | 0 | 39 | 300 | 320 | 358 | 39 | 40 | 0 | 99 | 10 | 0 | 83 | 30 | 0 | 17 | 175 | 54.5 | 65 | 130 | 0 | 0 | 0 | 12 | 7789.5 | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 478 | 0 | 1368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 152 | 0 | 153 | 0 | 414 | 0 | 0 | 0 | 159 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 100 | 220 | 0 | 300 | 992 | 0 | 5658 | 13447.5 | 80.03
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17 | 17 | 105 | 149 | 15 | 0 | 17 | 90 | 0 | 16 | 400 | 297 | 420 | 0 | 17 | 0 | 287 | 0 | 0 | 0 | 35 | 20 | 14 | 0 | 420 | 0 | 0 | 12 | 0 | 0 | 34 | 0 | 0 | 60 | 20 | 0 | 40 | 0 | 31 | 155 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1040 | 0 | 43 | 20 | 63 | 0 | 320 | 345 | 47 | 198 | 34 | 90 | 50 | 85 | 38 | 20 | 52 | 40 | 16 | 0 | 40 | 300 | 320 | 380 | 39 | 40 | 0 | 88 | 10 | 0 | 83 | 30 | 0 | 17 | 174 | 53 | 65 | 130 | 0 | 0 | 0 | 12 | 7513 | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 479 | 0 | 1364.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 150 | 0 | 156 | 0 | 414 | 0 | 0 | 0 | 165 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 100 | 180 | 0 | 300 | 984 | 0 | 5578.25 | 13091.25 | 80.02
Total KWH | 225360 | 785280 | 360960 | 0 | 0 | 0 | 0 | 0 | 8506800 | 0 | 0 | 590040 | 457560 | 2329056 | 2560320 | 964745 | 272375 | 540732 | 2141280 | 0 | 793920 | 9195000 | 7044189 | 9526364 | 0 | 596880 | 0 | 6832258 | 0 | 0 | 107932 | 1534800 | 464400 | 398880 | 0 | 9965454 | 0 | 0 | 136320 | 0 | 90720 | 545957 | 33888 | 0 | 2066880 | 544320 | 18480 | 944000 | 0 | 340800 | 3716363.64 | 26764 | 0 | 32160 | 32983.2 | 0 | 3547221 | 0 | 0 | 0 | 21032725 | 126495 | 961940 | 791200 | 1204364 | 0 | 8193000 | 8256000 | 1129920 | 4718000 | 777816 | 1978560 | 1153820 | 2252640 | 440160 | 435600 | 915820 | 808320 | 294614 | 319491 | 553984 | 7181500 | 7720900 | 8825000 | 906000 | 909360 | 0 | 2246891 | 195960 | 0 | 1980480 | 710112 | 0 | 408000 | 4591340 | 466560 | 1622400 | 2875200 | 0 | 14400 | 332590 | 294960 | 175897563.84 | 21221090 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377280 | 9847273 | 0 | 27982416 | 0 | 0 | 0 | 256416 | 0 | 0 | 83712 | 0 | 31848 | 277330 | 0 | 327752 | 3964364 | 0 | 3769118 | 0 | 3842709 | 0 | 9370618 | 0 | 29580 | 0 | 3680000 | 1294691 | 337232 | 270564 | 220185 | 0 | 0 | 60670.92 | 1528560 | 2994 | 3648 | 6066000 | 190695 | 2526000 | 5349100 | 0 | 6021216 | 21672727.27 | 0 | 130605789.19 | 306503353.03

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-04-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13386.17 | MW | 12:00 Hr. | Energy Generated |  |  | 306.5034 |  | MKWHr.
| Day Peak Demand |  |  | 13421.7 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.866 |  | MKWHr.
| Evening Peak Generation |  |  | 14159.42 | MW | 19:30 Hr. | Energy Demand |  |  | 307.3694 |  | MKWHr.
| Evening Peak Demand |  |  | 14159.42 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31 |  | °C
| Minimum Generation of the Day |  |  | 11116.87 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1057.15 |  | MMCFD
| Maximum Generation of the Day |  |  | 14159.42 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.277 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 51.9333 | 0 | 14.1533 | 0 | 0 | 0.10793 | 0 | 0 | 66.1946 | Gas | 147.34 | Gas | 520529813.68
| Chattogram Zone |  |  | 3.888 | 24.7491 | 3.4193 | 0 | 0.944 | 0.14497 | 0 | 0.09072 | 33.2361 | Coal | 73.331 | Coal | 485305855.1335
| Cumilla Zone |  |  | 26.8305 | 0 | 7.227 | 0 | 0 | 0.31949 | 0.80832 | 0 | 35.1852 | HFO | 30.9917 | HFO | 581596406.734
| Mymensingh Zone |  |  | 0 | 0 | 5.2591 | 0 | 0 | 0.34699 | 0 | 0 | 5.6061 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6755 | Hydro | 0.944 | Hydro | 94400
| Khulna Zone |  |  | 0 | 9.8473 | 0 | 0 | 0 | 0.37728 | 21.2211 | 0 | 31.4456 | Solar | 3.7941 | Solar | 64081476.0312
| Barishal Zone |  |  | 8.0658 | 33.7599 | 0.003648 | 0 | 0 | 0.002994 | 0 | 0 | 41.8324 | Import | 50.0118 | Import | 270987382.74
| Rajshahi Zone |  |  | 20.9468 | 0 | 0.37198 | 0 | 0 | 0.63466 | 27.9824 | 0 | 49.9359 | Wind | 0.09072 | Wind | 1328140.8
| Rangpur Zone |  |  | 0 | 4.9747 | 0.55742 | 0 | 0 | 1.8598 | 0 | 0 | 7.3919
| Total |  |  | 147.34 | 73.331 | 30.9917 | 0 | 0.944 | 3.7941 | 50.0118 | 0.09072 | 306.5034
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 520529813.68 |  | Hydro | 94400
|  |  |  | Coal | 485305855.1335 |  | Solar | 64081476.0312
|  |  |  | HFO | 581596406.734 |  | Import | 270987382.74
|  |  |  | HSD | 0 |  | Wind | 1328140.8
[5 empty] | Total: | 192,39,23,475 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.2211 | Peak Hr Flow | 872.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36287745.53 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.9824 | Peak Hr Flow | 1364.92 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 680 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.80832 | Peak Hr Flow | 38.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 992 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.0118 | Peak Hr Flow | 2274.92 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5214
|  |  |  | Chattogram |  | 0 |  | 1412
|  |  |  | Cumilla |  | 0 |  | 1299
|  |  |  | Mymensingh |  | 0 |  | 1042
|  |  |  | Sylhet |  | 0 |  | 571
|  |  |  | Khulna |  | 0 |  | 1463
|  |  |  | Barishal |  | 0 |  | 396
|  |  |  | Rajshahi |  | 0 |  | 1371
|  |  |  | Rangpur |  | 0 |  | 894
|  |  |  | Total |  | 0 |  | 13662
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:55 | 09:05 | Niamatpur 132/33kV S/S Transformer-3(426T) LT Tripped showing OC/EF &33 KV Lockout OPTD | [7 empty] | 12.0MW load
|  |  | relays Due to Rajshahi-2 33 kV feeder fault. | [7 empty] | interrup.
| 09:11 | 16:25 | Chowmuhani-Ramganj 132 kV Ckt-1 Project Work S/D from Chowmuhani 132/33kV end Due to
Maggar and parameter test and from Ramganj 132/33kV end Due to order from NLDC
| 09:41 |  | Faridpur 132/33kV S/S ATR-2 LT Scheduled S/D Due to ATR-2 WTI Checking
| 09:42 |  | Faridpur 132/33kV S/S ATR-2 HT Scheduled S/D Due to ATR-2 WTI Checking
| 10:15 |  | Haripur 230/132kV S/S 132KV Bhulta-2 Project Work S/D Due to GNDP Project Work.
| 10:31 | 12:33 | Kaliakoir 400/230/132kV S/S 400kV Bus 2 Project Work S/D Due to Project Work
| 10:34 | 16:19 | Chandina 132/33kV S/S TR-2 HT Project Work S/D Due to 33 KV bay and Substation auxiliary
transformer commissioning.
|  | 11:06 | BSRM 230/33kV S/S 230/33 kV Transformer-1 (125/140 MVA) HT is restored.
|  | 11:43 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT is restored.
|  | 11:44 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT is restored.
| 11:57 | 16:48 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Blast wall painting
| 11:58 | 16:48 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Blast wall painting
| 12:00 |  | Day peak generation: 13384 MW
| 19:30 |  | Evening Peak Gen. 14159 MW
| 21:13 | 23:01 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to PBS Feeder Red Hot | [7 empty] | 30.0MW load
interrup.
| 21:13 | 23:01 | Sherpur 132/33kV S/S Transformer- 03 HT Forced S/D Due to Red hot remove | [7 empty] | 25.0MW load
interrup.
| 06:10 |  | Ghorasal-Tongi 230kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to 230kV Dia-2
Control Panel Annunciators Replacement Work
| 06:12 |  | Tongi 230/132/33kV S/S T-02 LT Scheduled S/D Due to 230kV Dia-2 Control Panel
Annunciators Replacement Work
| 06:12 |  | Tongi 230/132/33kV S/S T-02 HT Scheduled S/D Due to 230kV Dia-2 Control Panel
Annunciators Replacement Work
| 06:21 |  | Barishal 230/132kV S/S T-5 LT Scheduled S/D Due to Banaripara 33 kv feeder Bus DS repair | [7 empty] | 30.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 06:22 |  | Barishal 230/132kV S/S T-5 HT Scheduled S/D Due to Banaripara 33 kv feeder Bus DS repair | [7 empty] | 30.0MW load
|  |  | maintenance work. | [7 empty] | interrup.
| 06:48 |  | Aminbazar 400/230/132kV S/S Bus-1 (400kV) Project Work S/D Due to 400KV Bay extention
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-04-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 346 | 8506800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9195000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 281 | 7044189 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 272375 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 284 | 6832258 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 225360 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 590040 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 148 | 2560320 | Loop Oil Shortage
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 540732 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 55 | 596880 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 464400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 398880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 360960 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 95 | 964745 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 109 | 2329056 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 53 | 785280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 85 | 793920 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2141280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 107932 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 457560 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 520 | 9965454 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 520 | 9526364 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 1534800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3318 | 66194585
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 32983.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126495 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 8 | 32160 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 944000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 148 | 3547221 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 16 | 33888 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 545957 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2066880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 340800 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 12 | 136320 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 18480 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 544320 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Engine Problem
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 26764 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1045 | 21032725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 90720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 155 | 3716363.64 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1651 | 33236076.84
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 193 | 4718000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 320 | 8193000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 305 | 8256000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 777816 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 1129920 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 1204364 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 961940 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 791200 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 553984 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1153820 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 2252640 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 808320 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 294614 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 435600 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 915820 | FGMO
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 440160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1978560 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 319491 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1592 | 35185249
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 163 | 2875200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1622400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 332590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294960 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 466560 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 334.5 | 5606110
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 906000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 909360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 91 | 2246891 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 710112 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1980480 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 175 | 4591340 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 408000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 195960 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7181500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 315 | 8825000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7720900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1429 | 35675543
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 872 | 21221090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 377280 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 478 | 9847273 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1350 | 31445643
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 300 | 6021216 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 3648 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 9 | 190695 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 90 | 2526000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 920 | 21672727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5349100 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6066000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2994 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1846 | 41832380.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 156 | 3964364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 149 | 3769118 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 152 | 3842709 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 9370618 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 12 | 31848 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 256416 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 83712 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29580 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1364.92 | 27982416 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 327752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 277330 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2288.92 | 49935863
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1294691 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 156 | 3680000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 220185 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 60670.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 337232 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 270564 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1528560 | -
Rangpur Area Total |  |  |  |  | 950 | 350 | 7391902.92
Eastern Grid Total |  |  |  |  | 16921.242 | 8324.5 | 175897563.84
Western Grid Total |  |  |  |  | 11614.5 | 5834.92 | 130605789.19
National Grid Total |  |  |  |  | 28535.742 | 14159.42 | 306503353.03
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-04-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9538.13 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4124.2 | MW
i) Dhaka area |  |  | 5213.73 |  | MW | i) Khulna area |  |  |  | 1463 | MW
ii) Chattogram area |  |  | 1412 |  | MW | ii) Barishal area |  |  |  | 396 | MW
iii) Cumilla area |  |  | 1299.4 |  | MW | iii) Rajshahi area |  |  |  | 1371.2 | MW
iv) Mymensingh area |  |  | 1042 |  | MW | iv) Rangpur area |  |  |  | 894 | MW
v) Sylhet area |  |  | 571 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13662.33 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 69 | 13:00 | 133 | Patuakhali | 66 | 19:30
2 | AKSML | 18 | 03:00 | 68 | Jaldhaka | 64 | 19:30 | 134 | Payra | 26 | 19:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jamalpur | 119 | 13:00 | 135 | Postogola | 53 | 18:00
4 | Agargaon | 126 | 13:00 | 70 | Jashore | 118 | 13:00 | 136 | Purbachal | 18 | 19:00
5 | Agrabad | 72 | 13:00 | 71 | Jhenaidah | 95 | 00:00 | 137 | Purbasadipur | 117 | 19:30
6 | Amnura | 49 | 13:00 | 72 | Joydebpur | 152 | 12:00 | 138 | Rahanpur | 24 | 21:00
7 | Ashuganj | 108 | 23:00 | 73 | Joypurhat | 75 | 19:30 | 139 | Rahim | 56 | 01:00
8 | BSRM | 207 | 05:00 | 74 | Juldah | 14 | 00:00 | 140 | Rajbari | 64 | 22:00
9 | Bagerhat | 74 | 00:00 | 75 | KSRM | 11 | 22:00 | 141 | Rajendrapur | 125 | 15:00
10 | Bajitpur | 47 | 23:00 | 76 | Kabirpur | 274 | 12:00 | 142 | Rajshahi | 93 | 12:00
11 | Bakulia | 92 | 19:00 | 77 | Kachua | 84 | 21:00 | 143 | Rajshahi-230 | 92 | 13:00
12 | Banani | 40 | 13:00 | 78 | Kallyanpur | 93 | 12:00 | 144 | Ramganj | 110 | 19:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kalurghat | 38 | 09:00 | 145 | Rampur | 39 | 00:00
14 | Barapukuria | 64 | 19:00 | 80 | Kamrangirchar | 70 | 13:00 | 146 | Rangamati | 16 | 19:00
15 | Barguna | 16 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 136 | 19:30
16 | Barishal | 103 | 19:00 | 82 | Kasba | 35 | 21:00 | 148 | Ruppur | 7 | 09:00
17 | Barishal-230 | 84 | 18:30 | 83 | Kazla | 103 | 13:00 | 149 | SSM | 10 | 01:00
18 | Baroaulia | 66 | 14:00 | 84 | Keranigonj | 79 | 19:30 | 150 | Saidpur | 103 | 19:00
19 | Baroirhat | 56 | 19:00 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 116 | 00:00
20 | Bashundhara | 183 | 13:00 | 86 | Khulna | 59 | 20:00 | 152 | Satmasjid | 96 | 13:00
21 | BashundharaCement | 14 | 11:00 | 87 | Khulshi | 206 | 12:00 | 153 | Savar | 228 | 12:00
22 | Beanibazar | 72 | 21:00 | 88 | Kishoreganj | 122 | 21:00 | 154 | SevenRings | 23 | 11:00
23 | Benapole | 56 | 00:00 | 89 | Kodda | 307 | 11:00 | 155 | ShahCement | 34 | 23:00
24 | Bhaluka | 146 | 15:00 | 90 | Kulaura | 40 | 22:00 | 156 | Shahjadpur | 95 | 10:00
25 | Bhandaria | 45 | 01:00 | 91 | Kurigram | 52 | 19:30 | 157 | Shahjibazar | 115 | 21:00
26 | Bhangura | 38 | 13:00 | 92 | Kushtia | 122 | 11:00 | 158 | Shahmirpur | 58 | 16:00
27 | Bheramara(GK) | 50 | 11:00 | 93 | Lalbag | 70 | 13:00 | 159 | Shariatpur | 81 | 22:00
28 | Bhulta | 240 | 14:00 | 94 | Lalmonirhat | 56 | 19:00 | 160 | Sherpur | 138 | 21:00
29 | Bog-Sherpur | 64 | 13:00 | 95 | MI_Cement | 14 | 01:00 | 161 | Shikalbaha | 28 | 00:00
30 | Bogura | 147 | 16:00 | 96 | Madanganj | 40 | 00:00 | 162 | Shitalakhya | 85 | 12:00
31 | Borhanuddin | 75 | 21:00 | 97 | Madaripur | 101 | 22:00 | 163 | Sholosohor | 43 | 12:00
32 | Brahmanbaria | 122 | 23:00 | 98 | Madartek | 82 | 20:00 | 164 | Shyampur | 176 | 12:00
33 | Cantonment | 136 | 13:00 | 99 | Madunaghat | 55 | 19:00 | 165 | Siddhirganj | 119 | 12:00
34 | Chandina | 15 | 22:00 | 100 | Magura | 43 | 00:00 | 166 | Sirajganj | 108 | 21:00
35 | Chandpur | 62 | 21:00 | 101 | Mahasthangarh | 76 | 19:30 | 167 | Sonargaon | 123 | 23:00
36 | Chandraghona | 33 | 19:00 | 102 | Manikganj | 125 | 19:30 | 168 | Sreemongol | 81 | 19:00
37 | Chapai | 65 | 21:00 | 103 | Maniknagar | 74 | 13:00 | 169 | Sreepur | 101 | 15:00
38 | Charsaidpur | 49 | 13:00 | 104 | Matarbari | 48 | 19:00 | 170 | Srinagar | 43 | 22:00
39 | Chauddagram | 64 | 00:00 | 105 | Matuail | 66 | 12:00 | 171 | Sunamganj | 58 | 20:00
40 | Chhatak | 35 | 22:00 | 106 | Millgate | 117 | 14:00 | 172 | Sylhet | 36 | 19:00
41 | Chowmuhani | 207 | 19:30 | 107 | Mirpur | 125 | 12:00 | 173 | Sylhet-132 | 121 | 18:30
42 | Chuadanga | 89 | 13:00 | 108 | Mirsorai | 9 | 12:00 | 174 | TK | 32 | 19:00
43 | Coxsbazar | 136 | 13:00 | 109 | Mirzapur | 47 | 14:00 | 175 | Tangail | 176 | 13:00
44 | Cumilla(N) | 150 | 20:00 | 110 | Mithapukur | 52 | 19:00 | 176 | Thakurgaon | 94 | 19:30
45 | Cumilla(S) | 164 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 109 | 18:30
46 | Daudkandi | 152 | 20:00 | 112 | Mogbazar | 146 | 13:00 | 178 | Ullahpara | 39 | 13:00
47 | Dhaka | 58 | 11:00 | 113 | Mongla | 42 | 06:00 | 179 | Ullon | 43 | 19:00
48 | Dhamrai | 134 | 11:00 | 114 | Motijheel | 39 | 13:00 | 180 | Uttara | 84 | 13:00
49 | Dhanmondi | 147 | 13:00 | 115 | Muktagacha | 31 | 19:00 | 181 | UttaraNew | 46 | 21:00
50 | Dohazari | 96 | 00:00 | 116 | Munshiganj | 102 | 00:00 | 182 | Zigatola | 72 | 13:00
51 | Faridpur | 130 | 19:00 | 117 | Muradnagar | 27 | 19:30
52 | Fatullah | 104 | 12:00 | 118 | Mymensingh | 197 | 13:00
53 | Fenchuganj | 40 | 18:30 | 119 | Naogaon | 124 | 21:00
54 | Feni | 105 | 19:30 | 120 | Narail | 51 | 19:00
55 | GPH | 21 | 10:00 | 121 | Narinda | 73 | 13:00
56 | Ghatail | 66 | 13:00 | 122 | Narshingdi | 175 | 21:00
57 | Ghorashal | 16 | 09:00 | 123 | Natore | 134 | 19:30
58 | Ghorashal-230 | 91 | 19:00 | 124 | Nawabganj | 51 | 21:00
59 | Goalpara | 32 | 00:00 | 125 | Netrakona | 111 | 20:00
60 | Gollamari | 84 | 19:30 | 126 | New | 89 | 12:00
61 | Gopalganj | 94 | 19:30 | 127 | Niamatpur | 83 | 13:00
62 | Gulshan | 118 | 13:00 | 128 | Noapara | 42 | 19:30
63 | Halishahar | 81 | 09:00 | 129 | PHP | 7 | 11:00
64 | HaripurSBU | 182 | 12:00 | 130 | Pabna | 95 | 19:30
65 | Hasnabad | 82 | 14:00 | 131 | Palashbari | 112 | 19:30
66 | Hathazari | 76 | 19:30 | 132 | Panchagarh | 48 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-04-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13229 | 0 |  | 13229
1:00 | 12552.5 | 36 |  | 12590.5
2:00 | 12104.5 | 39 |  | 12145.5
3:00 | 11748.5 | 50 |  | 11800.5
4:00 | 11389 | 49 |  | 11440
5:00 | 11192 | 51 |  | 11245
6:00 | 11116.87 | 67 |  | 11186.89
7:00 | 11223.06 | 68 |  | 11294.12
8:00 | 11447.59 | 81 |  | 11532.59
9:00 | 11880.74 | 0 |  | 11880.74
10:00 | 12476.2 | 0 |  | 12476.2
11:00 | 12970.31 | 0 |  | 12970.31
12:00 | 13386.17 | 34 |  | 13421.7
13:00 | 13688.2 | 23 |  | 13712.2
14:00 | 13105.99 | 22 |  | 13128.99
15:00 | 12979.71 | 52 |  | 13033.71
16:00 | 12729.42 | 156 |  | 12892.42
17:00 | 12263.96 | 47 |  | 12312.96
18:00 | 12149.74 | 27 |  | 12177.74
19:00 | 13937.81 | 0 |  | 13937.81
19:30 | 14159.42 | 0 |  | 14159.42
20:00 | 13974.72 | 0 |  | 13974.72
21:00 | 13919.53 | 0 |  | 13919.53
22:00 | 13447.5 | 32 |  | 13480.5
23:00 | 13091.25 | 32 |  | 13124.25
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-04-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7671 | 5558 | 13229 | DAILY GENERATION CURVE
00:30 | 7381.25 | 5509.5 | 12890.75
01:00 | 7091.5 | 5461 | 12552.5 | 30-04-2025
01:30 | 6960 | 5368.5 | 12328.5
02:00 | 6828.5 | 5276 | 12104.5
02:30 | 6776 | 5150.5 | 11926.5
03:00 | 6723.5 | 5025 | 11748.5
03:30 | 6674.25 | 4894.5 | 11568.75
04:00 | 6625 | 4764 | 11389
04:30 | 6550 | 4740.5 | 11290.5
05:00 | 6475 | 4717 | 11192
05:30 | 6453.42 | 4701.015 | 11154.435
06:00 | 6431.84 | 4685.03 | 11116.87
06:30 | 6423.4 | 4746.565 | 11169.965
07:00 | 6414.96 | 4808.1 | 11223.06
07:30 | 6450.445 | 4884.88 | 11335.325
08:00 | 6485.93 | 4961.66 | 11447.59
08:30 | 6543.035 | 5121.13 | 11664.165
09:00 | 6600.14 | 5280.6 | 11880.74
09:30 | 6830.46 | 5348.01 | 12178.47
10:00 | 7060.78 | 5415.42 | 12476.2
10:30 | 7239.855 | 5483.4 | 12723.255
11:00 | 7418.93 | 5551.38 | 12970.31
11:30 | 7579.19 | 5599.05 | 13178.24
12:00 | 7739.45 | 5646.72 | 13386.17
12:30 | 7870.66 | 5666.525 | 13537.185
13:00 | 8001.87 | 5686.33 | 13688.2
13:30 | 7678.115 | 5718.98 | 13397.095
14:00 | 7354.36 | 5751.63 | 13105.99
14:30 | 7321.465 | 5721.385 | 13042.85
15:00 | 7288.57 | 5691.14 | 12979.71
15:30 | 7199.485 | 5655.08 | 12854.565
16:00 | 7110.4 | 5619.02 | 12729.42
16:30 | 7052.72 | 5443.97 | 12496.69
17:00 | 6995.04 | 5268.92 | 12263.96
17:30 | 7058.77 | 5148.08 | 12206.85
18:00 | 7122.5 | 5027.24 | 12149.74
18:30 | 7738.5 | 5305.275 | 13043.775
19:00 | 8354.5 | 5583.31 | 13937.81
19:30 | 8324.5 | 5834.92 | 14159.42
20:00 | 8161.5 | 5813.22 | 13974.72
20:30 | 8145.5 | 5801.625 | 13947.125 |  | Executive Engineer
21:00 | 8129.5 | 5790.03 | 13919.53 |  | Network Operation Division
21:30 | 7959.5 | 5724.015 | 13683.515
22:00 | 7789.5 | 5658 | 13447.5
22:30 | 7651.25 | 5618.125 | 13269.375
23:00 | 7513 | 5578.25 | 13091.25

## En-Curve
QF-LDC-12
Date | 30-04-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3704 | 2574 | 735 | 0 | 40 | 1364 | 40 | 3394 | 0 | 371 | 1007 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3661 | 2540.25 | 830 | 0 | 38 | 1365.5 | 40 | 3239 | 0 | 335 | 842 | 0 | 0 | 0 | 18 | 30-04-2025
01:00 | 3618 | 2506.5 | 925 | 0 | 36 | 1367 | 40 | 3084 | 0 | 299 | 677 | 0 | 0 | 0 | 36
01:30 | 3609.5 | 2478.5 | 926 | 0 | 36 | 1316 | 40 | 2999 | 0 | 267.5 | 655.5 | 0 | 0 | 0.5 | 37.5 | Energy Generated | 306.5034 |  | MKWHr
02:00 | 3601 | 2450.5 | 927 | 0 | 36 | 1265 | 40 | 2914 | 0 | 236 | 634 | 0 | 0 | 1 | 39 | Energy not Served | 0.866 |  | MKWHr
02:30 | 3579 | 2451.5 | 926.5 | 0 | 35 | 1184.5 | 39 | 2886.5 | 0 | 207 | 617 | 0 | 0 | 0.5 | 44.5 | Total Energy Requirement | 307.3694 |  | MKWHr
03:00 | 3557 | 2452.5 | 926 | 0 | 34 | 1104 | 38 | 2859 | 0 | 178 | 600 | 0 | 0 | 0 | 50
03:30 | 3570.5 | 2425.25 | 925.5 | 0 | 33 | 1012 | 37 | 2811.5 | 0 | 178 | 576 | 0 | 0 | 0 | 49.5
04:00 | 3584 | 2398 | 925 | 0 | 32 | 920 | 36 | 2764 | 0 | 178 | 552 | 0 | 0 | 0 | 49
04:30 | 3583 | 2402 | 924.5 | 0 | 32 | 907 | 37 | 2695.5 | 0 | 169.5 | 540 | 0 | 0 | 0 | 50
05:00 | 3582 | 2406 | 924 | 0 | 32 | 894 | 38 | 2627 | 0 | 161 | 528 | 0 | 0 | 0 | 51
05:30 | 3600.5 | 2400 | 925 | 0 | 31 | 910.5 | 38 | 2574.5 | 13.435 | 152.5 | 509 | 0 | 0 | 0 | 59
06:00 | 3619 | 2394 | 926 | 0 | 30 | 927 | 38 | 2522 | 26.87 | 144 | 490 | 0 | 0 | 0 | 67
06:30 | 3568 | 2322 | 925.5 | 0 | 26 | 944.5 | 39 | 2601.5 | 73.465 | 144 | 526 | 0 | 0 | 0 | 67.5
07:00 | 3517 | 2250 | 925 | 0 | 22 | 962 | 40 | 2681 | 120.06 | 144 | 562 | 0 | 0 | 0 | 68
07:30 | 3553.5 | 2248.5 | 901 | 0 | 25 | 963 | 40 | 2720.5 | 200.825 | 135.5 | 547.5 | 0 | 0 | 0 | 74.5
08:00 | 3590 | 2247 | 877 | 0 | 28 | 964 | 40 | 2760 | 281.59 | 127 | 533 | 0 | 0 | 0 | 81
08:30 | 3645.5 | 2263 | 877.5 | 0 | 29 | 996 | 40 | 2789 | 344.665 | 144.5 | 535 | 0 | 0 | 0 | 40.5
09:00 | 3701 | 2279 | 878 | 0 | 30 | 1028 | 40 | 2818 | 407.74 | 162 | 537 | 0 | 0 | 0 | 0
09:30 | 3724 | 2351 | 878 | 0 | 29 | 1027.5 | 40 | 2848.5 | 455.47 | 212 | 612.5 | 0 | 0 | 0.5 | 0
10:00 | 3747 | 2423 | 878 | 0 | 28 | 1027 | 40 | 2879 | 503.2 | 262 | 688 | 0 | 0 | 1 | 0
10:30 | 3753.5 | 2425 | 904 | 0 | 29 | 1027 | 40 | 2970.5 | 483.755 | 270.5 | 817.5 | 0 | 0 | 2.5 | 0
11:00 | 3760 | 2427 | 930 | 0 | 30 | 1027 | 40 | 3062 | 464.31 | 279 | 947 | 0 | 0 | 4 | 0
11:30 | 3775 | 2420.5 | 930 | 0 | 32 | 1040.5 | 40 | 3065 | 476.74 | 292 | 1099 | 0 | 0 | 7.5 | 17
12:00 | 3790 | 2414 | 930 | 0 | 34 | 1054 | 40 | 3068 | 489.17 | 305 | 1251 | 0 | 0 | 11 | 34
12:30 | 3728 | 2378.5 | 930 | 0 | 35 | 1108.5 | 40 | 3034 | 472.085 | 355.5 | 1444.1 | 0 | 0 | 11.5 | 28.5
13:00 | 3666 | 2343 | 930 | 0 | 36 | 1163 | 40 | 3000 | 455 | 406 | 1637.2 | 0 | 0 | 12 | 23
13:30 | 3602 | 2295.5 | 927 | 0 | 35 | 1215.49 | 40 | 3013.5 | 459.005 | 374.5 | 1427.1 | 0 | 0 | 8 | 22.5
14:00 | 3538 | 2248 | 924 | 0 | 34 | 1267.98 | 40 | 3027 | 463.01 | 343 | 1217 | 0 | 0 | 4 | 22
14:30 | 3608.5 | 2283.5 | 924.5 | 0 | 33 | 1268.09 | 40 | 3024.5 | 379.76 | 325 | 1130.5 | 0 | 0 | 25.5 | 37
15:00 | 3679 | 2319 | 925 | 0 | 32 | 1268.2 | 40 | 3022 | 296.51 | 307 | 1044 | 0 | 0 | 47 | 52
15:30 | 3642.5 | 2320.5 | 925 | 0 | 31 | 1266.135 | 40 | 3023 | 245.93 | 286.5 | 1048.5 | 0 | 0 | 25.5 | 104
16:00 | 3606 | 2322 | 925 | 0 | 30 | 1264.07 | 40 | 3024 | 195.35 | 266 | 1053 | 0 | 0 | 4 | 156
16:30 | 3598.5 | 2238.5 | 925 | 0 | 32 | 1212.955 | 38 | 2986 | 126.235 | 266.5 | 1071 | 0 | 0 | 2 | 101.5
17:00 | 3591 | 2155 | 925 | 0 | 34 | 1161.84 | 36 | 2948 | 57.12 | 267 | 1089 | 0 | 0 | 0 | 47
17:30 | 3552 | 2132 | 924.5 | 0 | 35 | 1164.625 | 36.5 | 2872.5 | 37.475 | 294 | 1158.25 | 0 | 0 | 0 | 37
18:00 | 3513 | 2109 | 924 | 0 | 36 | 1167.41 | 37 | 2797 | 17.83 | 321 | 1227.5 | 0 | 0 | 0 | 27
18:30 | 3599 | 2462 | 901 | 0 | 37 | 1248.36 | 38.5 | 3028.5 | 8.915 | 340 | 1380.5 | 0 | 0 | 0 | 13.5
19:00 | 3685 | 2815 | 878 | 0 | 38 | 1329.31 | 40 | 3260 | 0 | 359 | 1533.5 | 0 | 0 | 0 | 0
19:30 | 3511 | 2662 | 872 | 0 | 38 | 1364.92 | 40 | 3415 | 0 | 376 | 1880.5 | 0 | 0 | 0 | 0
20:00 | 3541 | 2557 | 730 | 0 | 38 | 1367.22 | 40 | 3432 | 0 | 376 | 1893.5 | 0 | 0 | 0 | 0
20:30 | 3587.5 | 2517.5 | 727.5 | 0 | 38 | 1365.125 | 40 | 3458 | 0 | 376 | 1837.5 | 0 | 0 | 0 | 0
21:00 | 3634 | 2478 | 725 | 0 | 38 | 1363.03 | 40 | 3484 | 0 | 376 | 1781.5 | 0 | 0 | 0 | 0
21:30 | 3659.5 | 2481.5 | 724 | 0 | 39 | 1365.515 | 40 | 3485 | 0 | 359 | 1530 | 0 | 0 | 0 | 16
22:00 | 3685 | 2485 | 723 | 0 | 40 | 1368 | 40 | 3486 | 0 | 342 | 1278.5 | 0 | 0 | 0 | 32
22:30 | 3694 | 2465.5 | 723 | 0 | 40 | 1366.125 | 40 | 3485.5 | 0 | 325 | 1130.25 | 0 | 0 | 0 | 32
23:00 | 3703 | 2446 | 723 | 0 | 40 | 1364.25 | 40 | 3485 | 0 | 308 | 982 | 0 | 0 | 0 | 32
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-04-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 393 | 06:00 | 383 | 10:00 | Payra | 415 | 05:00 | 410 | 00:00
Ashuganj | 402 | 6:00 | 388 | 11:00 | Rahanpur | 400 | 05:00 | 386 | 15:00
Bhulta | 398 | 06:00 | 384 | 11:00 | Rampal | 404 | 06:00 | 394 | 00:00
Bibiana | 391 | 23:00 | 384 | 11:00
BIPTC | 396 | 14:00 | 393 | 15:00
Bogura | 386 | 05:00 | 370 | 15:00
Gopalganj | 401 | 06:00 | 392 | 11:00
Kaliakoir | 368 | 22:00 | 355 | 11:00
Madunaghat | 398 | 06:00 | 391 | 11:00
Meghnaghat | 395 | 06:00 | 386 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 06:00 | 221 | 10:00 | Keranigonj | 227 | 06:00 | 218 | 10:00
AKSML | 228 | 07:00 | 222 | 11:00 | Khulna(S) | 230 | 05:00 | 223 | 11:00
Aminbazar | 229 | 06:00 | 222 | 10:00 | Madunaghat | 231 | 07:00 | 225 | 11:00
Ashuganj | 232 | 07:00 | 225 | 11:00 | Madunaghat-400 | 231 | 07:00 | 225 | 11:00
Ashuganj-400 | 232 | 6:00 | 218 | 11:00 | Maniknagar | 225 | 05:00 | 22 | 18:00
Baghabari | 235 | 05:00 | 225 | 11:00 | Meghnaghat | 232 | 03:00 | 224 | 11:00
Barapukuria | 229 | 05:00 | 220 | 15:00 | Meghnaghat-400 | 228 | 06:00 | 225 | 00:00
Barapukuria-230 | 228 | 5:00 | 220 | 14:00 | Mirsorai | 228 | 07:00 | 220 | 10:00
Barishal | 239 | 06:00 | 233 | 18:30 | Rajshahi | 235 | 03:00 | 221 | 12:00
Bheramara | 235 | 00:00 | 222 | 11:00 | Rampal | 230 | 05:00 | 222 | 12:00
Bhulta | 226 | 05:00 | 217 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 06:00 | 219 | 12:00 | Rampura | 225 | 05:00 | 216 | 10:00
BIPTC | 232 | 17:00 | 225 | 15:00 | Shikalbaha | 228 | 07:00 | 221 | 11:00
Bogura | 235 | 04:00 | 225 | 15:00 | Shyampur | 226 | 05:00 | 218 | 10:00
Bogura-400 | 235 | 04:00 | 226 | 15:00 | Siddhirganj | 227 | 05:00 | 218 | 10:00
Borhanuddin | 242 | 05:00 | 239 | 00:00 | Sirajgonj | 240 | 04:00 | 230 | 00:00
BSRM | 226 | 08:00 | 219 | 15:00 | Sreepur | 229 | 06:00 | 223 | 15:00
Cumilla(N) | 224 | 07:00 | 217 | 15:00 | Tongi | 225 | 19:30 | 215 | 09:00
Faridpur | 235 | 06:00 | 230 | 00:00
Fenchuganj | 226 | 13:00 | 220 | 15:00
Ghorashal | 235 | 04:00 | 230 | 09:00
Ghorashal-230 | 226 | 06:00 | 217 | 10:00
Gopalganj | 237 | 06:00 | 231 | 11:00
GPH | 228 | 07:00 | 222 | 10:00
Haripur | 224 | 18:00 | 218 | 10:00
Hasnabad | 226 | 00:00 | 220 | 10:00
Hathazari | 231 | 13:00 | 223 | 15:00
Ishurdi | 236 | 00:00 | 225 | 11:00
Jhenaidah | 230 | 05:00 | 219 | 12:00
Kaliakoir | 227 | 05:00 | 219 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 128 | 10:00 | Madartek | 136 | 06:00 | 128 | 11:00
Agargaon | 135 | 05:00 | 128 | 10:00 | Madunaghat | 133 | 07:00 | 129 | 00:00
Agrabad | 131 | 06:00 | 125 | 11:00 | Magura | 135 | 06:00 | 128 | 12:00
AKS | 130 | 06:00 | 125 | 15:00 | Mahasthangarh | 136 | 05:00 | 129 | 12:00
Aminbazar | 133 | 05:00 | 128 | 09:00 | Manikganj | 127 | 05:00 | 118 | 12:00
Amnura | 135 | 00:00 | 120 | 15:00 | Maniknagar | 132 | 04:00 | 125 | 12:00
Ashuganj | 137 | 08:00 | 135 | 00:00 | Matarbari | 125 | 16:00 | 111 | 19:00
Bagerhat | 133 | 05:00 | 125 | 00:00 | Matuail | 131 | 01:00 | 126 | 10:00
Bajitpur | 135 | 18:00 | 128 | 00:00 | Millgate | 131 | 06:00 | 124 | 10:00
Bakulia | 133 | 13:00 | 127 | 11:00 | Mirpur | 131 | 04:00 | 126 | 09:00
Banani | 136 | 05:00 | 128 | 11:00 | Mirzapur | 131 | 23:00 | 122 | 11:00
Bangabhaban | 133 | 07:00 | 125 | 10:00 | Mithapukur | 133 | 03:00 | 125 | 12:00
Barapukuria | 135 | 04:00 | 127 | 12:00 | MI_Cement | 131 | 05:00 | 126 | 10:00
Barguna | 135 | 05:00 | 133 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 05:00 | 128 | 00:00 | Mogbazar | 136 | 04:00 | 129 | 12:00
Barishal-230 | 133 | 05:00 | 128 | 18:30 | Mongla | 132 | 14:00 | 126 | 00:00
Baroaulia | 132 | 00:00 | 132 | 00:00 | Motijheel | 133 | 07:00 | 125 | 10:00
Baroirhat | 126 | 07:00 | 119 | 15:00 | Muktagacha | 134 | 21:00 | 122 | 14:00
Bashundhara | 137 | 06:00 | 122 | 11:00 | Munshiganj | 130 | 06:00 | 125 | 10:00
BashundharaCement | 130 | 07:00 | 124 | 10:00 | Muradnagar | 127 | 07:00 | 122 | 10:00
Beanibazar | 131 | 07:00 | 126 | 18:30 | Mymensingh | 135 | 21:00 | 120 | 15:00
Benapole | 133 | 06:00 | 125 | 11:00 | Naogaon | 136 | 05:00 | 126 | 12:00
Bhaluka | 134 | 18:00 | 123 | 08:00 | Narail | 136 | 06:00 | 127 | 11:00
Bhandaria | 129 | 11:00 | 121 | 19:00 | Narinda | 132 | 4:00 | 125 | 12:00
Bhangura | 134 | 03:00 | 127 | 12:00 | Narshingdi | 128 | 06:00 | 120 | 00:00
Bheramara | 136 | 03:00 | 128 | 11:00 | Natore | 135 | 03:00 | 127 | 12:00
Bheramara(GK) | 135 | 00:00 | 128 | 11:00 | Nawabganj | 136 | 05:00 | 129 | 10:00
Bhulta | 125 | 18:30 | 119 | 12:00 | Netrakona | 131 | 17:00 | 118 | 15:00
Bog-Sherpur | 136 | 04:00 | 130 | 12:00 | New | 131 | 05:00 | 124 | 10:00
Bogura | 137 | 07:00 | 132 | 12:00 | Niamatpur | 132 | 03:00 | 126 | 14:00
Bogura-230 | 139 | 04:00 | 132 | 12:00 | Noapara | 136 | 04:00 | 129 | 11:00
Brahmanbaria | 131 | 06:00 | 125 | 12:00 | Pabna | 137 | 03:00 | 129 | 12:00
Cantonment | 135 | 05:00 | 128 | 11:00 | Palashbari | 132 | 03:00 | 125 | 12:00
Chandina | 129 | 07:00 | 124 | 10:00 | Panchagarh | 136 | 04:00 | 120 | 12:00
Chandpur | 133 | 13:00 | 120 | 06:00 | Patuakhali | 135 | 05:00 | 132 | 23:00
Chandraghona | 133 | 06:00 | 128 | 15:00 | Payra | 136 | 02:00 | 134 | 15:00
Chapai | 129 | 05:00 | 122 | 14:00 | PHP | 126 | 13:00 | 116 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 03:00 | 125 | 10:00 | Postogola | 133 | 05:00 | 128 | 06:00
Chauddagram | 126 | 13:00 | 117 | 15:00 | Purbachal | 137 | 06:00 | 128 | 11:00
Chhatak | 130 | 07:00 | 124 | 19:00 | Purbasadipur | 132 | 05:00 | 114 | 13:00
Chowmuhani | 122 | 07:00 | 113 | 18:00 | Rahanpur | 131 | 07:00 | 126 | 23:00
Chuadanga | 134 | 17:00 | 125 | 12:00 | Rahanpur-400 | 133 | 03:00 | 128 | 15:00
Coxsbazar | 120 | 14:00 | 111 | 18:30 | Rahim | 131 | 07:00 | 126 | 10:00
Cumilla(N) | 129 | 07:00 | 124 | 00:00 | Rajbari | 138 | 06:00 | 133 | 10:00
Cumilla(S) | 133 | 05:00 | 121 | 15:00 | Rajendrapur | 134 | 06:00 | 123 | 00:00
Daudkandi | 126 | 13:00 | 120 | 09:00 | Rajshahi | 135 | 06:00 | 127 | 12:00
Dhaka | 137 | 06:00 | 129 | 10:00 | Rajshahi-230 | 135 | 01:00 | 114 | 13:00
Dhamrai | 134 | 02:00 | 127 | 11:00 | Ramganj | 125 | 07:00 | 115 | 00:00
Dhanmondi | 137 | 05:00 | 129 | 11:00 | Rampur | 131 | 07:00 | 126 | 10:00
Dohazari | 130 | 13:00 | 123 | 00:00 | Rampura | 136 | 05:00 | 129 | 10:00
Faridpur | 139 | 06:00 | 134 | 11:00 | Rangamati | 131 | 04:00 | 120 | 21:00
Fatullah | 132 | 05:00 | 126 | 10:00 | Rangpur | 132 | 04:00 | 124 | 16:00
Fenchuganj | 135 | 04:00 | 132 | 15:00 | Ruppur | 138 | 00:00 | 131 | 12:00
Feni | 125 | 13:00 | 120 | 02:00 | Saidpur | 133 | 05:00 | 118 | 14:00
Ghatail | 130 | 19:00 | 120 | 11:00 | Satkhira | 134 | 05:00 | 127 | 00:00
Ghorashal | 136 | 00:00 | 131 | 11:00 | Satmasjid | 134 | 04:00 | 128 | 12:00
Goalpara | 137 | 06:00 | 130 | 01:00 | Savar | 131 | 13:00 | 125 | 09:00
Gollamari | 137 | 06:00 | 132 | 00:00 | SevenRings | 136 | 07:00 | 131 | 10:00
Gopalganj | 136 | 05:00 | 131 | 19:00 | ShahCement | 133 | 03:00 | 125 | 10:00
Gopalganj-400 | 138 | 06:00 | 131 | 22:00 | Shahjadpur | 137 | 05:00 | 131 | 12:00
Gulshan | 136 | 05:00 | 129 | 10:00 | Shahjibazar | 132 | 07:00 | 127 | 01:00
Halishahar | 132 | 07:00 | 125 | 11:00 | Shahmirpur | 134 | 07:00 | 129 | 12:00
Haripur | 131 | 07:00 | 126 | 10:00 | Shariatpur | 141 | 11:00 | 129 | 23:00
HaripurSBU | 131 | 04:00 | 126 | 10:00 | Sherpur | 137 | 19:00 | 123 | 16:00
Hasnabad | 133 | 03:00 | 128 | 10:00 | Shikalbaha | 0 | 00:00 | N/A | N/A
Hathazari | 135 | 13:00 | 128 | 15:00 | Shikalbaha-230 | 134 | 07:00 | 129 | 10:00
Ishurdi | 139 | 00:00 | 132 | 11:00 | Shitalakhya | 131 | 05:00 | 126 | 10:00
Jaldhaka | 131 | 04:00 | 117 | 15:00 | Sholosohor | 132 | 04:00 | 128 | 10:00
Jamalpur | 139 | 21:00 | 124 | 15:00 | Shyampur | 133 | 20:00 | 126 | 12:00
Jashore | 134 | 06:00 | 126 | 12:00 | Shyampur-230 | 132 | 07:00 | 125 | 10:00
Jhenaidah | 136 | 05:00 | 128 | 11:00 | Siddhirganj | 131 | 07:00 | 126 | 10:00
Jhenaidah-230 | 135 | 03:00 | 128 | 12:00 | Sirajganj | 132 | 00:00 | 126 | 11:00
Joydebpur | 136 | 21:00 | 126 | 00:00 | Sonargaon | 130 | 18:00 | 122 | 10:00
Joypurhat | 135 | 08:00 | 121 | 12:00 | Sreemongol | 132 | 06:00 | 127 | 00:00
Juldah | 133 | 05:00 | 128 | 13:00 | Sreepur | 135 | 17:00 | 129 | 15:00
Kabirpur | 133 | 23:00 | 122 | 10:00 | Srinagar | 137 | 06:00 | 130 | 11:00
Kachua | 129 | 13:00 | 120 | 08:00 | SSM | 134 | 00:00 | 134 | 00:00
Kaliakoir | 137 | 22:00 | 125 | 12:00 | Sunamganj | 129 | 08:00 | 123 | 19:00
Kallyanpur | 133 | 07:00 | 127 | 08:00 | Sylhet | 131 | 05:00 | 127 | 19:00
Kalurghat | 132 | 13:00 | 128 | 11:00 | Sylhet-132 | 131 | 05:00 | 129 | 00:00
Kamrangirchar | 136 | 05:00 | 130 | 11:00 | Tangail | 128 | 18:00 | 119 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 04:00 | 121 | 12:00
Kasba | 127 | 07:00 | 121 | 15:00 | TK | 134 | 13:00 | 129 | 09:00
Kazla | 132 | 06:00 | 125 | 12:00 | Tongi | 132 | 04:00 | 125 | 11:00
Keranigonj | 136 | 05:00 | 130 | 10:00 | Ullahpara | 136 | 04:00 | 128 | 11:00
Khagrachori | 131 | 07:00 | 126 | 16:00 | Ullon | 135 | 04:00 | 128 | 11:00
Khulna | 136 | 05:00 | 130 | 12:00 | Uttara | 131 | 06:00 | 125 | 12:00
Khulna(S) | 137 | 05:00 | 132 | 00:00 | UttaraNew | 132 | 04:00 | 126 | 09:00
Khulshi | 130 | 05:00 | 125 | 11:00 | Zigatola | 136 | 07:00 | 130 | 10:00
Kishoreganj | 135 | 18:00 | 126 | 15:00
Kodda | 133 | 23:00 | 122 | 09:00
KSRM | 133 | 07:00 | 127 | 11:00
Kulaura | 134 | 07:00 | 131 | 12:00
Kurigram | 132 | 00:00 | 124 | 16:00
Kushtia | 137 | 04:00 | 127 | 11:00
Lalbag | 135 | 07:00 | 129 | 10:00
Lalmonirhat | 128 | 08:00 | 122 | 16:00
Madanganj | 130 | 07:00 | 124 | 10:00
Madaripur | 136 | 05:00 | 130 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division