## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-05-2025 | [28 empty] | Date: | 01-05-2025 | [28 empty] | Date: | 01-05-2025 | [28 empty] | Date: | 01-05-2025 | [28 empty] | Date: | 01-05-2025 | [16 empty] | Date: | 01-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 17 | 95 | 112 | 15 | 0 | 17 | 90 | 0 | 16 | 400 | 295 | 420 | 0 | 17 | 0 | 281 | 0 | 0 | 0 | 35 | 20 | 17 | 0 | 420 | 0 | 0 | 13 | 0 | 0 | 34 | 0 | 0 | 60 | 20 | 0 | 40 | 0 | 33 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1040 | 0 | 43 | 20 | 63 | 0 | 320 | 345 | 47 | 193 | 31 | 90 | 51 | 85 | 10 | 20 | 52 | 40 | 16 | 0 | 41 | 300 | 320 | 365 | 39 | 40 | 0 | 85 | 10 | 0 | 83 | 30 | 0 | 17 | 175 | 35 | 65 | 95 | 0 | 0 | 0 | 12 | 7373 | 725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 476 | 0 | 1367.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 150 | 0 | 158 | 0 | 414 | 0 | 0 | 0 | 163 | 55 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 96 | 180 | 0 | 220 | 983 | 0 | 5496.84 | 12869.84 | 80.02
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17 | 17 | 80 | 100 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 291 | 420 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 35 | 20.5 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 3 | 34 | 0 | 0 | 60 | 20 | 0 | 40 | 0 | 32 | 155 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1000 | 0 | 43 | 0 | 63 | 0 | 320 | 345 | 48 | 190 | 31 | 90 | 51 | 96 | 9 | 20 | 52 | 40 | 16 | 0 | 41 | 290 | 320 | 355 | 39 | 40 | 0 | 81 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 28 | 49 | 96 | 0 | 0 | 0 | 12 | 7051.5 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 1376.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 149 | 0 | 156 | 0 | 350 | 0 | 0 | 0 | 164 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71 | 0 | 278 | 10 | 100 | 180 | 0 | 221 | 940 | 0 | 5473.56 | 12525.06 | 80.01
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 17 | 70 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 293 | 420 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 35 | 20.5 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 60 | 20 | 0 | 40 | 0 | 32 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 905 | 0 | 43 | 0 | 63 | 0 | 320 | 345 | 48 | 190 | 28 | 90 | 50 | 85 | 9 | 20 | 52 | 38 | 16 | 0 | 41 | 295 | 320 | 370 | 39 | 40 | 0 | 81 | 8 | 0 | 83 | 30 | 0 | 17 | 175 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 6837.5 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 1249.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 149 | 0 | 153 | 0 | 350 | 0 | 0 | 0 | 154 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61 | 0 | 200 | 9 | 100 | 180 | 0 | 221 | 897 | 0 | 5198.52 | 12036.02 | 80.01
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 290 | 420 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 21 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 20 | 0 | 40 | 0 | 32 | 155 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 43 | 0 | 63 | 0 | 320 | 345 | 48 | 190 | 28 | 90 | 50 | 68 | 10 | 20 | 52 | 36 | 16 | 0 | 40 | 285 | 320 | 335 | 39 | 40 | 0 | 84 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 6747 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 1114.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 151 | 0 | 151 | 0 | 350 | 0 | 0 | 0 | 140 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 100 | 180 | 0 | 220 | 880 | 0 | 5000.1 | 11747.1 | 80
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 297 | 420 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 21 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 10 | 0 | 40 | 0 | 32 | 155 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 800 | 0 | 43 | 0 | 63 | 0 | 320 | 345 | 48 | 191 | 28 | 90 | 50 | 68 | 9 | 20 | 38 | 36 | 16 | 0 | 40 | 295 | 320 | 325 | 39 | 40 | 0 | 83 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 6606 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 943.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 151 | 0 | 145 | 0 | 350 | 0 | 0 | 0 | 155 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 100 | 180 | 0 | 221 | 835 | 0 | 4794.64 | 11400.64 | 80
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 294 | 370 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 18 | 17 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 32 | 155 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 800 | 0 | 43 | 0 | 63 | 0 | 320 | 345 | 48 | 182 | 28 | 90 | 50 | 51 | 9 | 20 | 34 | 34 | 8 | 0 | 40 | 300 | 320 | 311 | 39 | 40 | 0 | 82 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 0 | 12 | 6395 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 377 | 0 | 925.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 147 | 0 | 142 | 0 | 350 | 0 | 0 | 0 | 163 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 90 | 180 | 0 | 221 | 788 | 0 | 4724.48 | 11119.48 | 79.99
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 8 | 51 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 276 | 320 | 0 | 0 | 0 | 282 | 0 | 0 | 1 | 0 | 18 | 17 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 32 | 156 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 756 | 0 | 43 | 0 | 63 | 0 | 320 | 300 | 48 | 181 | 28 | 70 | 45 | 51 | 9 | 20 | 17 | 32 | 8 | 5 | 0 | 310 | 320 | 314 | 39 | 40 | 0 | 80 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 49 | 96 | 0 | 0 | 1.88 | 12 | 6012.88 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.75 | 378 | 0 | 834.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 1.8 | 140 | 0 | 145 | 0 | 142 | 0 | 300 | 0 | 0.16 | 0 | 166 | 56 | 0 | 2 | 0 | 0 | 0 | 0.4 | 9 | 0.03 | 0 | 200 | 8 | 90 | 180 | 0 | 221 | 745 | 0 | 4539.9 | 10552.78 | 79.99
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 40 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 295 | 280 | 0 | 0 | 0 | 275 | 0 | 0 | 7 | 0 | 18 | 18 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 29 | 158 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 655 | 2 | 43 | 0 | 63 | 0 | 320 | 300 | 48 | 184 | 31 | 45 | 45 | 34 | 9 | 20 | 0 | 28 | 0 | 17 | 0 | 300 | 320 | 322 | 39 | 40 | 0 | 80 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 68 | 124 | 0 | 0 | 10.69 | 8 | 5829.69 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.61 | 377 | 0 | 828.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 9.95 | 140 | 0 | 152 | 0 | 144 | 0 | 270 | 0 | 0.8 | 0 | 165 | 56 | 0 | 7 | 0 | 0 | 0 | 1.8 | 37 | 0.14 | 0 | 150 | 7 | 90 | 180 | 0 | 221 | 680 | 0 | 4475.05 | 10304.74 | 79.98
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 290 | 240 | 0 | 0 | 0 | 265 | 0 | 0 | 15 | 0 | 13 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 22 | 215 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 611 | 10 | 43 | 0 | 36 | 0 | 300 | 270 | 43 | 181 | 34 | 34 | 45 | 17 | 9 | 20 | 0 | 28 | 0 | 36 | 0 | 295 | 320 | 319 | 39 | 40 | 0 | 80 | 8 | 0 | 11 | 30 | 0 | 17 | 174 | 0 | 68 | 124 | 0 | 1 | 23.87 | 12 | 5577.87 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.82 | 377 | 0 | 817.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 22.71 | 140 | 0 | 140 | 0 | 157 | 0 | 270 | 0 | 1.79 | 0 | 156 | 55 | 0 | 15 | 0 | 0 | 0 | 3.8 | 57 | 0.33 | 0 | 150 | 6 | 90 | 180 | 0 | 221 | 600 | 0 | 4425.19 | 10003.06 | 79.98
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 230 | 240 | 0 | 0 | 0 | 282 | 0 | 0 | 22 | 0 | 14 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 24 | 265 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 609 | 11 | 5 | 0 | 8 | 0 | 300 | 270 | 8 | 134 | 34 | 0 | 45 | 0 | 0 | 20 | 0 | 28 | 0 | 52 | 0 | 300 | 320 | 325 | 39 | 40 | 0 | 83 | 8 | 0 | 11 | 30 | 0 | 17 | 175 | 0 | 48 | 124 | 35 | 1 | 35.24 | 12 | 5418.24 | 876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.09 | 378 | 0 | 819.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 36.46 | 140 | 0 | 140 | 0 | 140 | 0 | 270 | 0 | 3.12 | 0 | 156 | 55 | 0 | 24 | 0 | 0 | 0 | 5.8 | 134 | 0.51 | 0 | 150 | 6 | 94 | 180 | 0 | 222 | 552 | 0 | 4520.91 | 9939.15 | 79.97
10:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 230 | 240 | 0 | 0 | 0 | 280 | 0 | 0 | 28 | 0 | 14 | 22 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 24 | 263 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 609 | 18 | 5 | 0 | 8 | 0 | 300 | 270 | 5 | 134 | 5 | 2 | 50 | 1 | 1 | 20 | 0 | 30 | 3 | 60 | 0 | 305 | 320 | 322 | 38 | 39 | 0 | 80 | 8 | 0 | 11 | 30 | 0 | 17 | 175 | 0 | 48 | 105 | 33 | 2 | 44.48 | 12 | 5360.48 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 376 | 0 | 827.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 48.67 | 140 | 0 | 140 | 0 | 140 | 0 | 270 | 0 | 4.3 | 0 | 159 | 56 | 0 | 29 | 0 | 0 | 0 | 7 | 177 | 0.65 | 0 | 150 | 6 | 94 | 180 | 0 | 221 | 550 | 0 | 4675.71 | 10036.19 | 79.97
11:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 266 | 300 | 0 | 0 | 0 | 292 | 0 | 0 | 31 | 0 | 14 | 10 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 24 | 265 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 619 | 15 | 5 | 0 | 8 | 0 | 300 | 270 | 5 | 204 | 5 | 16 | 51 | 17 | 9 | 20 | 0 | 32 | 8 | 64 | 0 | 310 | 320 | 388 | 37 | 40 | 0 | 95 | 8 | 0 | 11 | 20 | 0 | 17 | 175 | 0 | 48 | 105 | 33 | 2 | 49.51 | 12 | 5737.51 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 370 | 0 | 824.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 56.51 | 140 | 0 | 140 | 0 | 140 | 0 | 300 | 0 | 4.86 | 0 | 162 | 55 | 0 | 34 | 0 | 0 | 0 | 7.7 | 124 | 0.71 | 0 | 150 | 6 | 100 | 180 | 0 | 220 | 552 | 0 | 4686.86 | 10424.37 | 79.95
12:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 289 | 350 | 0 | 0 | 0 | 296 | 0 | 0 | 32 | 17 | 14 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 0 | 8 | 264 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 608 | 15 | 5 | 0 | 8 | 0 | 320 | 300 | 5 | 204 | 5 | 24 | 50 | 18 | 15 | 20 | 0 | 36 | 8 | 70 | 0 | 300 | 320 | 390 | 36 | 39 | 0 | 103 | 8 | 0 | 11 | 20 | 0 | 17 | 173 | 0 | 48 | 124 | 18 | 2 | 44.37 | 12 | 6049.37 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 377 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 58.39 | 156 | 0 | 160 | 0 | 160 | 0 | 360 | 0 | 1.57 | 0 | 165 | 54 | 0 | 31 | 0 | 0 | 0 | 8 | 200 | 0.73 | 0 | 180 | 6 | 100 | 180 | 0 | 220 | 552 | 0 | 4926.69 | 10976.06 | 79.94
13:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 285 | 450 | 0 | 0 | 0 | 295 | 0 | 0 | 31 | 17 | 14 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 0 | 7 | 263 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 607 | 9 | 5 | 0 | 8 | 0 | 320 | 300 | 5 | 200 | 27 | 35 | 50 | 34 | 18 | 19 | 8 | 38 | 8 | 49 | 0 | 305 | 320 | 390 | 39 | 40 | 0 | 102 | 8 | 0 | 11 | 20 | 0 | 17 | 174 | 0 | 48 | 90 | 49 | 2 | 37.75 | 12 | 6264.75 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 377 | 0 | 828.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 55.47 | 160 | 0 | 160 | 0 | 160 | 0 | 350 | 0 | 1.62 | 0 | 166 | 54 | 0 | 35 | 0 | 0 | 0 | 6.9 | 208 | 0 | 0 | 180 | 7 | 100 | 180 | 0 | 220 | 552 | 0 | 4914.25 | 11179 | 79.93
14:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 272 | 400 | 0 | 0 | 0 | 267 | 0 | 0 | 27 | 0 | 0 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 7 | 263 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 608 | 15 | 5 | 0 | 8 | 0 | 320 | 300 | 5 | 182 | 29 | 50 | 50 | 51 | 18 | 19 | 34 | 32 | 8 | 63 | 0 | 305 | 320 | 314 | 37 | 40 | 0 | 95 | 8 | 0 | 11 | 20 | 0 | 16 | 174 | 0 | 8 | 24 | 52 | 1 | 38.96 | 0 | 5815.96 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 377 | 0 | 828.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 42.62 | 160 | 0 | 160 | 0 | 160 | 0 | 321 | 0 | 3.85 | 0 | 117 | 54 | 0 | 31 | 0 | 0 | 0 | 6.9 | 187 | 0.01 | 0 | 180 | 6 | 100 | 180 | 0 | 220 | 506 | 0 | 4729.62 | 10545.58 | 79.92
15:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 263 | 350 | 0 | 0 | 0 | 267 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 7 | 263 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 608 | 13 | 5 | 0 | 8 | 0 | 290 | 295 | 5 | 182 | 5 | 53 | 45 | 63 | 18 | 19 | 34 | 38 | 12 | 51 | 0 | 295 | 320 | 314 | 36 | 40 | 0 | 79 | 8 | 0 | 11 | 20 | 0 | 16 | 173 | 0 | 8 | 8 | 54 | 2 | 3.84 | 0 | 5582.84 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 376 | 0 | 826.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 10.64 | 130 | 0 | 130 | 0 | 130 | 0 | 320 | 0 | 0.79 | 0 | 110 | 54 | 0 | 25 | 0 | 0 | 0 | 3.8 | 148 | 0.5 | 0 | 150 | 8 | 90 | 180 | 0 | 221 | 490 | 0 | 4461.76 | 10044.6 | 79.91
16:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 274 | 220 | 0 | 0 | 0 | 267 | 0 | 0 | 14 | 0 | 15 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 16 | 262 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 608 | 8 | 5 | 0 | 8 | 0 | 290 | 290 | 5 | 141 | 5 | 68 | 45 | 68 | 27 | 19 | 34 | 38 | 25 | 30 | 0 | 270 | 320 | 314 | 36 | 40 | 0 | 79 | 8 | 0 | 11 | 20 | 0 | 16 | 174 | 0 | 16 | 22 | 52 | 1 | 0.35 | 2 | 5290.35 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 376 | 0 | 824.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 6.8 | 130 | 0 | 130 | 0 | 130 | 0 | 319 | 0 | 0.54 | 0 | 172 | 54 | 0 | 15 | 0 | 0 | 0 | 4.3 | 104 | 0.35 | 0 | 150 | 7 | 90 | 180 | 0 | 221 | 495 | 0 | 4417.56 | 9707.91 | 79.9
17:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 300 | 260 | 0 | 0 | 0 | 286 | 0 | 0 | 5 | 0 | 10 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 23 | 264 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 604 | 3 | 5 | 0 | 8 | 0 | 290 | 290 | 5 | 195 | 5 | 34 | 45 | 17 | 36 | 19 | 34 | 26 | 25 | 12 | 0 | 240 | 320 | 332 | 40 | 40 | 0 | 88 | 8 | 0 | 11 | 20 | 0 | 16 | 173 | 0 | 16 | 16 | 68 | 0 | 2.38 | 6 | 4942.38 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 376 | 0 | 825.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 4.31 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0.54 | 0 | 174 | 54 | 0 | 8 | 0 | 0 | 0 | 1.6 | 31 | 0.14 | 0 | 150 | 7 | 100 | 180 | 0 | 175 | 495 | 0 | 4166.01 | 9108.39 | 79.89
18:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 300 | 260 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 26 | 264 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 606 | 0 | 5 | 0 | 8 | 0 | 290 | 290 | 5 | 180 | 5 | 16 | 70 | 17 | 37 | 5 | 17 | 20 | 25 | 2 | 0 | 290 | 320 | 315 | 39 | 40 | 0 | 80 | 8 | 0 | 11 | 20 | 0 | 16 | 173 | 0 | 16 | 16 | 102 | 0 | 1.29 | 12 | 4916.29 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 376 | 0 | 824.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.05 | 130 | 0 | 130 | 0 | 130 | 0 | 250 | 0 | 0.09 | 0 | 170 | 54 | 0 | 1 | 0 | 0 | 0 | 0.4 | 7 | 0.22 | 0 | 150 | 7 | 90 | 180 | 0 | 171 | 500 | 0 | 4094.29 | 9010.58 | 79.88
19:00 | 0 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 300 | 500 | 0 | 0 | 0 | 274 | 101 | 0 | 0 | 17 | 11 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 10 | 0 | 40 | 0 | 21 | 350 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 700 | 0 | 11 | 0 | 33 | 0 | 354 | 345 | 6 | 186 | 34 | 21 | 70 | 19 | 38 | 5 | 34 | 30 | 25 | 0 | 0 | 305 | 320 | 350 | 39 | 40 | 0 | 95 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 55 | 65 | 103 | 0 | 0 | 12 | 6399 | 867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 830.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 164 | 0 | 173 | 0 | 390 | 0 | 0 | 0 | 165 | 57 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 7 | 90 | 220 | 0 | 192 | 549 | 0 | 4540.4 | 10939.4 | 79.87
19:30 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 288 | 500 | 0 | 0 | 0 | 264 | 102 | 0 | 0 | 17 | 12.5 | 22 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 30 | 0 | 40 | 0 | 35 | 354 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 705 | 0 | 43 | 0 | 36 | 0 | 360 | 345 | 27 | 180 | 34 | 34 | 70 | 34 | 38 | 20 | 34 | 34 | 25 | 0 | 0 | 290 | 320 | 355 | 39 | 40 | 0 | 99 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 65 | 65 | 107 | 0 | 0 | 12 | 6558.5 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425 | 0 | 823.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 168 | 0 | 166 | 0 | 356 | 0 | 0 | 0 | 166 | 57 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 10 | 100 | 220 | 0 | 221 | 750 | 0 | 4825.7 | 11384.2 | 79.87
20:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 286 | 583 | 0 | 0 | 0 | 265 | 102 | 0 | 0 | 17 | 11 | 22 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 10 | 0 | 40 | 0 | 35 | 352 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 657 | 0 | 43 | 0 | 55 | 0 | 360 | 345 | 23 | 180 | 34 | 34 | 70 | 34 | 38 | 20 | 34 | 36 | 25 | 0 | 0 | 290 | 320 | 383 | 39 | 40 | 0 | 95 | 8 | 0 | 83 | 30 | 0 | 17 | 172 | 0 | 65 | 65 | 133 | 0 | 0 | 12 | 6710 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 835.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 174 | 0 | 169 | 0 | 372 | 0 | 0 | 0 | 167 | 57 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 5 | 100 | 220 | 0 | 221 | 640 | 0 | 4659.93 | 11369.93 | 79.86
21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 304 | 583 | 0 | 0 | 0 | 276 | 101 | 0 | 0 | 0 | 11 | 22 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 10 | 0 | 40 | 0 | 38 | 361 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 655 | 0 | 43 | 0 | 85 | 0 | 360 | 345 | 46 | 188 | 34 | 50 | 70 | 17 | 38 | 20 | 34 | 32 | 25 | 0 | 0 | 310 | 320 | 361 | 39 | 40 | 0 | 97 | 0 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 45 | 45 | 156 | 0 | 0 | 12 | 6787 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 190 | 0 | 178 | 0 | 387 | 0 | 0 | 0 | 163 | 58 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 105 | 220 | 0 | 220 | 593 | 0 | 4641 | 11428 | 79.85
22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 298 | 583 | 0 | 0 | 0 | 275 | 102 | 0 | 0 | 0 | 11 | 22 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 39 | 361 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 655 | 0 | 43 | 0 | 120 | 0 | 360 | 345 | 51 | 182 | 34 | 16 | 70 | 17 | 39 | 20 | 0 | 30 | 0 | 0 | 0 | 305 | 320 | 348 | 40 | 40 | 0 | 95 | 8 | 0 | 83 | 30 | 0 | 17 | 173 | 0 | 8 | 32 | 156 | 0 | 0 | 12 | 6682 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 176 | 0 | 174 | 0 | 387 | 0 | 0 | 0 | 164 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 8 | 103 | 220 | 0 | 221 | 600 | 0 | 4559 | 11241 | 79.84
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 288 | 583 | 0 | 0 | 0 | 288 | 102 | 0 | 0 | 0 | 11 | 22 | 0 | 584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 42 | 227 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 605 | 0 | 43 | 0 | 120 | 0 | 360 | 345 | 51 | 191 | 35 | 16 | 70 | 0 | 26 | 20 | 0 | 34 | 0 | 0 | 0 | 300 | 320 | 361 | 40 | 40 | 0 | 85 | 8 | 0 | 83 | 30 | 0 | 17 | 174 | 0 | 8 | 32 | 156 | 0 | 0 | 12 | 6616 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 164 | 0 | 158 | 0 | 338 | 0 | 0 | 0 | 162 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 9 | 98 | 220 | 0 | 221 | 598 | 0 | 4461 | 11077 | 79.83
Total KWH | 0 | 305011 | 142560 | 0 | 0 | 0 | 0 | 0 | 6422400 | 0 | 0 | 19548 | 144000 | 459792 | 547680 | 8029 | 0 | 9471 | 48960 | 0 | 27940 | 8600000 | 6908364 | 9296818 | 0 | 9960 | 0 | 6820130 | 483000 | 0 | 231619 | 202800 | 334200 | 446760 | 0 | 9873181 | 0 | 0 | 6720 | 0 | 38400 | 149009 | 0 | 0 | 612480 | 122880 | 30164 | 912000 | 0 | 630240 | 5752727.27 | 0 | 0 | 0 | 0 | 0 | 3502050 | 0 | 0 | 0 | 16625453 | 112320 | 647276 | 16727 | 1070545 | 0 | 8092800 | 7686000 | 664800 | 4509000 | 560448 | 1143360 | 1292080 | 966240 | 469560 | 434750 | 557460 | 796800 | 300744 | 517500 | 222192 | 7229500 | 7637500 | 8655000 | 911000 | 909360 | 0 | 2098227.27 | 177168 | 0 | 1204800 | 630144 | 0 | 407000 | 3583400 | 34200 | 957600 | 1804800 | 1184640 | 13500 | 270250 | 257520 | 147750557.54 | 21813818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 772560 | 9294545 | 0 | 21133029.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748170 | 0 | 350248 | 3795000 | 0 | 3892473 | 0 | 3863600 | 0 | 8010690 | 0 | 25980 | 0 | 3882000 | 1254545 | 146774 | 265213 | 79008 | 0 | 0 | 56487.12 | 1433520 | 5419.5 | 0 | 4298000 | 175134 | 2344000 | 4989830 | 0 | 5178182 | 16312727.27 | 0 | 114120953.65 | 261871511.19

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-05-2025 | during | 02-05-2025 | during | 02-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 379 | 39 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 289 | 304 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 101 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 296 | 276 | 335 | 335 | 300 | 300 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 16 | 0 | 149.36 | 149.36 | 149 | 149 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14 | 11 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 0 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 0 | 149 | 149 | 130 | 130 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 0 | 105 | 105 | 17 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162 | 54 | 162 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 584 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 0 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2212 | 2370 | 5095.1 | 5159.1 | 3790.01 | 4024.01
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both unit under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 144 | 150 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | Generator Problem
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 0 | 64 | 82 | 48 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 48 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 8 | 38 | 3 | 14 | 3 | 14 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 108 | 60 | 60 | Engine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 2.13 | 0 | 2.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 10 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 108 | 108 | Engine Problem
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 608 | 655 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 0 | 1 | 0 | 1 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 264 | 361 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1084 | 1302 | 3281.85 | 3412.72 | 3317.85 | 3346.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 204 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 320 | 360 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 300 | 345 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 5 | 34 | 46.94 | 46.94 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 46 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 85 | 190 | 190 | 190 | 190 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 5 | 43 | 51 | 51 | 43 | 43 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 18 | 17 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 32 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 105.3 | 105.3 | 105.3 | 105.3 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 15 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 24 | 50 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1088 | 1387 | 2457.29 | 2387.29 | 2200.85 | 2159.85
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-05-2025 | during | 02-05-2025 | during | 02-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 18 | 156 | 157.5 | 157.5 | 100 | 100 | -
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 124 | 45 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 45 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 44.37 | 0 | 49.68 | 0 | 49.68 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 55 | 55 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 248.37 | 258 | 600.78 | 549 | 411.78 | 432
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 39 | 36 | 36 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 39 | 40 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 103 | 97 | 113 | 113 | 103 | 103 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 20 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 11 | 83 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 0 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 390 | 361 | 380 | 380 | 380 | 380 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1417 | 1470 | 1516 | 1516 | 1459 | 1459
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 926 | 915 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 377 | 382 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1403 | 1297 | 3604.2 | 3514.2 | 2472.01 | 2382.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 220 | 220 | 315 | 315 | 315 | 315 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 6 | 0 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 105 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 552 | 593 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 180 | 150 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.73 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1238.73 | 1288 | 2487.12 | 2486.12 | 2475.12 | 2474.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 40 | 40 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 156 | 185 | 214 | 214 | 190 | 190 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 190 | 220 | 220 | 180 | 180 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 160 | 178 | 220 | 220 | 180 | 180 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 360 | 387 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.57 | 0 | 5.05 | 0 | 5.05 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 829 | 825 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.39 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 102 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1826.96 | 1765 | 3107.58 | 2941.53 | 2952.79 | 2786.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 58 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 165 | 163 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 200 | 0 | 146.88 | 0 | 146.88 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 458 | 291 | 636.28 | 453 | 636.28 | 453
System Total |  |  |  |  | 27566.2 | 28535.742 | 10976.06 | 11428 | 22786.2 | 22418.96 | 19715.69 | 19517.45
Forecast Scenario (02-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 11300 |  | 0 |  | 11300
|  |  |  | 1:00 | 11190 |  | 0 |  | 11190
|  |  |  | 2:00 | 11000 |  | 0 |  | 11000
|  |  |  | 3:00 | 10760 |  | 0 |  | 10760
|  |  |  | 4:00 | 10550 |  | 0 |  | 10550
|  |  |  | 5:00 | 10370 |  | 0 |  | 10370
|  |  |  | 6:00 | 9950 |  | 0 |  | 9950
|  |  |  | 7:00 | 9700 |  | 0 |  | 9700
|  |  |  | 8:00 | 9700 |  | 0 |  | 9700
|  |  |  | 9:00 | 9740 |  | 0 |  | 9740
|  |  |  | 10:00 | 9810 |  | 0 |  | 9810
|  |  |  | 11:00 | 10410 |  | 0 |  | 10410
|  |  |  | 12:00 | 11150 |  | 0 |  | 11150
|  |  |  | 13:00 | 11800 |  | 0 |  | 11800
|  |  |  | 14:00 | 11180 |  | 0 |  | 11180
|  |  |  | 15:00 | 11430 |  | 0 |  | 11430
|  |  |  | 16:00 | 11120 |  | 0 |  | 11120
|  |  |  | 17:00 | 10350 |  | 0 |  | 10350
|  |  |  | 18:00 | 9720 |  | 0 |  | 9720
|  |  |  | 18:30 | 10500 |  | 0 |  | 10500
|  |  |  | 19:00 | 11490 |  | 0 |  | 11490
|  |  |  | 19:30 | 12230 |  | 0 |  | 12230
|  |  |  | 20:00 | 11910 |  | 0 |  | 11910
|  |  |  | 21:00 | 12000 |  | 0 |  | 12000
|  |  |  | 22:00 | 11950 |  | 0 |  | 11950
|  |  |  | 23:00 | 11910 |  | 0 |  | 11910
Probable Maximum Temperature: |  |  | 30.50°C
Probable Maximum Demand at Day Peak: |  |  | 11150.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 12230.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 12230.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 260.49 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:48 hrs on 02-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 10976.06 | MW | 12:00 Hr. | Energy Generated |  |  | 261.8715 |  | MKWHr.
| Day Peak Demand |  |  | 10976.06 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.368 |  | MKWHr.
| Evening Peak Generation |  |  | 11428 | MW | 21:00 Hr. | Energy Demand |  |  | 262.2395 |  | MKWHr.
| Evening Peak Demand |  |  | 11428 | MW | 21:00 Hr. | Maximum Temperature |  |  | 33.6 |  | °C
| Minimum Generation of the Day |  |  | 9108.39 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 1017.03 |  | MMCFD
| Maximum Generation of the Day |  |  | 12869.84 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.3343 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 49.1849 | 0 | 1.9258 | 0 | 0 | 0.23162 | 0 | 0 | 51.3422 | Gas | 139.9733 | Gas | 494370581.2757
| Chattogram Zone |  |  | 4.1323 | 22.3782 | 0.89109 | 0 | 0.912 | 0.14248 | 0 | 0.0384 | 28.4944 | Coal | 62.5982 | Coal | 417774893.1435
| Cumilla Zone |  |  | 24.9577 | 0 | 3.6763 | 0 | 0 | 0.5175 | 0.7968 | 0 | 29.9483 | HFO | 9.773 | HFO | 183112405.9
| Mymensingh Zone |  |  | 1.1846 | 0 | 3.0541 | 0 | 0 | 0.28375 | 0 | 0 | 4.5225 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 33.4431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.4431 | Hydro | 0.912 | Hydro | 91200
| Khulna Zone |  |  | 0 | 9.2945 | 0 | 0 | 0 | 0.77256 | 21.8138 | 0 | 31.8809 | Solar | 4.833 | Solar | 78763819.4982
| Barishal Zone |  |  | 7.509 | 25.7889 | 0 | 0 | 0 | 0.0054195 | 0 | 0 | 33.3033 | Import | 43.7436 | Import | 222221825.5784
| Rajshahi Zone |  |  | 19.5618 | 0 | 0 | 0 | 0 | 1.1244 | 21.133 | 0 | 41.8192 | Wind | 0.0384 | Wind | 562176
| Rangpur Zone |  |  | 0 | 5.1365 | 0.22578 | 0 | 0 | 1.7552 | 0 | 0 | 7.1175
| Total |  |  | 139.9733 | 62.5982 | 9.773 | 0 | 0.912 | 4.833 | 43.7436 | 0.0384 | 261.8715
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 494370581.2757 |  | Hydro | 91200
|  |  |  | Coal | 417774893.1435 |  | Solar | 78763819.4982
|  |  |  | HFO | 183112405.9 |  | Import | 222221825.5784
|  |  |  | HSD | 0 |  | Wind | 562176
[5 empty] | Total: | 139,68,96,901 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.8138 | Peak Hr Flow | 915.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 9183472.79 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.133 | Peak Hr Flow | 825.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 362 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.7968 | Peak Hr Flow | 32.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 854 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 43.7436 | Peak Hr Flow | 1772.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 3955
|  |  |  | Chattogram |  | 0 |  | 1118
|  |  |  | Cumilla |  | 0 |  | 1137
|  |  |  | Mymensingh |  | 0 |  | 890
|  |  |  | Sylhet |  | 0 |  | 449
|  |  |  | Khulna |  | 0 |  | 1234
|  |  |  | Barishal |  | 0 |  | 291
|  |  |  | Rajshahi |  | 0 |  | 1206
|  |  |  | Rangpur |  | 0 |  | 736
|  |  |  | Total |  | 0 |  | 11016
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:08 | Barishal 230/132kV S/S T-5 HT is restored.
|  | 08:12 | Barishal 230/132kV S/S T-5 LT is restored.
| 08:58 | 12:00 | Panchagarh 132/33kV S/S T-3(A+B)(427T) LT Forced S/D Due to T-3(A+B) Transformer (A)
underground cable and 33KV R phase bussing juntion abnormal sound
| 08:58 | 12:00 | Panchagarh 132/33kV S/S T-3(A+B)(427T) HT Forced S/D Due to T-3(A+B) Transformer (A)
underground cable and 33KV R phase bussing juntion abnormal sound
| 09:16 | 10:13 | Cumilla(N)-Kachua 132 kV Ckt-2 Tripped from Kachua 132/33kV end showing REC 650 REL 670
relays Due to Due to kite flying on the kachua -cumilla north ckt line.
| 10:03 | 10:20 | Kurigram-Rangpur 132kV Ckt-1 Tripped from Kurigram 132/33kV end showing N/A relays Due | [7 empty] | 32.0MW load
|  |  | to N/A | [7 empty] | interrup. Kurigram
132/33kV end
| 11:31 | 20:02 | Aminbazar-Meghnaghat 400kV Ckt-2 Scheduled S/D from Meghnaghat 400/230kV end Due to
Maintenance work done.
| 12:00 |  | Day peak generation 10974MW
|  | 12:37 | Tongi 230/132/33kV S/S T-02 HT is restored.
|  | 12:37 | Tongi 230/132/33kV S/S T-02 LT is restored.
|  | 12:40 | Ghorasal-Tongi 230kV Ckt-2 is restored.
| 12:52 | 12:58 | Sirajganj 132/33kV S/S T1-(415) LT Forced S/D Due to 33kV T1 Section BUS has taken
Shutdown for Emergency Red Hot Maintenance at 33kV KamarKhand Feeder CT. This Shutdown
has been taken By AGM Com Sirajgonj PBS-2
| 14:04 | 14:08 | Sirajganj 132/33kV S/S T1-(415) LT Forced S/D Due to Due to the T-1 33kV Section BUS
charge after maintenance work, T-1 33kV has been taken Shutdown.This Shutdown has been
taken By AGM Com Sirajgonj PBS-2
| 16:20 |  | Haripur 412 MW CCPP Tripped with remarks:- GT & STG
| 17:20 |  | Haripur 412 MW CCPP Tripped with remarks:- ST
| 17:39 |  | Haripur 412 MW CCPP Tripped with remarks:- ST
| 18:22 |  | Siddhirganj GT-1 was sync.
| 19:09 | 19:15 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing 132kv protection operated relays Due | [7 empty] | 30.0MW load
|  |  | to Unknown | [7 empty] | interrup.
| 19:09 | 19:15 | Barishal 132/33kV S/S T-2 (415T) HT Tripped showing OLTC Bucholtz relays Due to Unknown | [7 empty] | 30.0MW load
interrup.
| 19:16 | 22:06 | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to OLTC Bucholz check
| 19:16 | 22:06 | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to OLTC bucholz check
| 19:30 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
| 20:36 | 21:44 | Sylhet 132/33kV S/S T2 HT Tripped showing Over Current relays Due to Flashing | [7 empty] | 26.0MW load
interrup.
| 20:36 | 21:45 | Sylhet 132/33kV S/S T2 LT Tripped showing Over Current relays Due to Flashing | [7 empty] | 26.0MW load
interrup.
| 21:00 |  | Evening peak generation: 11428 MW
| 21:57 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 03:05 |  | Raozan U-2 was synch.
| 06:00 |  | Min. Gen. 9273 MW
| 06:31 |  | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Scheduled S/D from Jhenaidah 230/132kV end. and
from BIPTC end Due to Shutdown has been taken for the installation of the cradle guard
under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project.
| 06:31 |  | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Scheduled S/D from Jhenaidah 230/132kV end. and
from BIPTC end Due to Shutdown has been taken for the installation of the cradle guard
under Rooppur-Gopalganj 400KV Single Circuit Transmission Line Project.
| 06:51 |  | Bheramara-HVDC Bheramara 230 kV Ckt-2 Project Work S/D from BIPTC end Due to Shutdown has
been taken for the installation of the cradle guard under Rooppur-Gopalganj 400KV Single
Circuit Transmission Line Project.
| 06:51 |  | Bheramara-HVDC Bheramara 230 kV Ckt-1 Project Work S/D from BIPTC end Due to Shutdown has
been taken for the installation of the cradle guard under Rooppur-Gopalganj 400KV Single
Circuit Transmission Line Project.
| 07:07 |  | Sylhet 132/33kV S/S T2 HT Forced S/D Due to 33 KV T-2 Bus S/D for BPDB feeder Maintenance
work Purpose.
| 07:07 |  | Sylhet 132/33kV S/S T2 LT Forced S/D Due to 33 KV T-2 Bus S/D for BPDB feeder Maintenance
work Purpose.
| 07:10 |  | Khulna (C) S/S Tr-3 405T LT Scheduled S/D Due to Maintenance of GP-1 ckt. Bus DS
| 07:10 |  | Khulna (C) S/S Tr-2 415 T LT Scheduled S/D Due to Maintenance of GP-1 ckt. Bus DS
| 07:11 |  | Khulna (C) S/S Tr-2 415 T HT Scheduled S/D Due to Maintenance of GP-1 ckt. Bus DS
| 07:11 |  | Khulna (C) S/S Tr-3 405T HT Scheduled S/D Due to Maintenance of GP-1 ckt. Bus DS
| 07:18 |  | Goalpara- Khulna (C) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to Maintenance of
GP-1 ckt. Bus DS and from Goalpara 132/33kVend.
| 07:20 |  | Sikalbaha S/S - ECPV P.P. line was shut down due to annual maint. at ECPV end
| 07:20 |  | Bheramara-HVDC Bheramara 230 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end.
| 07:20 |  | Bheramara-HVDC Bheramara 230 kV Ckt-2 Scheduled S/D from Bheramara 230/132kV end.
| 07:21 |  | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Aircell bag & Magnetic Oil
Indicator replacement
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | -
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 39 | 6422400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8600000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 6908364 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 101 | 483000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 276 | 6820130 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 19548 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 0 | 547680 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 9471 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 9960 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 11 | 334200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 446760 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 142560 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 8029 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 0 | 459792 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 0 | 305011 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 27940 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 48960 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 231619 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 144000 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 584 | 9873181 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 9296818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 0 | 202800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2370 | 51342223
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 112320 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 912000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 150 | 3502050 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 149009 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 48 | 612480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 38 | 630240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 6720 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 30164 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 122880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Engine Problem
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 655 | 16625453 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 38400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 361 | 5752727.27 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1302 | 28494443.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 4509000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 360 | 8092800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 7686000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 560448 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 664800 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 85 | 1070545 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 647276 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 16727 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 222192 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1292080 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 966240 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 32 | 796800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 300744 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 434750 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 557460 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 469560 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 1143360 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 517500 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1387 | 29948282
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 156 | 1184640 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 45 | 1804800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 957600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 270250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 257520 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 34200 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 258 | 4522510
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 39 | 911000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 909360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 97 | 2098227.27 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 630144 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1204800 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 3583400 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 407000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 177168 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7229500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8655000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7637500 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1470 | 33443099.27
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 915 | 21813818 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 772560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 382 | 9294545 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1297 | 31880923
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 220 | 5178182 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 0 | 175134 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 105 | 2344000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 593 | 16312727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4989830 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 150 | 4298000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5419.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1288 | 33303292.77
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 185 | 3795000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 190 | 3892473 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 178 | 3863600 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 387 | 8010690 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25980 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 825 | 21133029.76 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 350248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 748170 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 1765 | 41819190.76
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 58 | 1254545 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 163 | 3882000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 79008 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 56487.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 146774 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 265213 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1433520 | -
Rangpur Area Total |  |  |  |  | 950 | 291 | 7117547.12
Eastern Grid Total |  |  |  |  | 16921.242 | 6787 | 147750557.54
Western Grid Total |  |  |  |  | 11614.5 | 4641 | 114120953.65
National Grid Total |  |  |  |  | 28535.742 | 11428 | 261871511.19
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 7549.65 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3466.6 | MW
i) Dhaka area |  |  | 3954.9 |  | MW | i) Khulna area |  |  |  | 1234 | MW
ii) Chattogram area |  |  | 1118.5 |  | MW | ii) Barishal area |  |  |  | 291 | MW
iii) Cumilla area |  |  | 1137.25 |  | MW | iii) Rajshahi area |  |  |  | 1205.6 | MW
iv) Mymensingh area |  |  | 890 |  | MW | iv) Rangpur area |  |  |  | 736 | MW
v) Sylhet area |  |  | 449 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 11016.25 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 63 | 14:00 | 133 | Patuakhali | 70 | 19:30
2 | AKSML | 20 | 16:00 | 68 | Jaldhaka | 64 | 19:00 | 134 | Payra | 30 | 22:00
3 | Aftabnagar | 30 | 00:00 | 69 | Jamalpur | 129 | 13:00 | 135 | Postogola | 49 | 00:00
4 | Agargaon | 101 | 13:00 | 70 | Jashore | 121 | 13:00 | 136 | Purbachal | 16 | 00:00
5 | Agrabad | 62 | 18:30 | 71 | Jhenaidah | 98 | 13:00 | 137 | Purbasadipur | 120 | 13:00
6 | Amnura | 52 | 12:00 | 72 | Joydebpur | 117 | 00:00 | 138 | Rahanpur | 22 | 01:00
7 | Ashuganj | 106 | 01:00 | 73 | Joypurhat | 71 | 00:00 | 139 | Rahim | 45 | 01:00
8 | BSRM | 180 | 01:00 | 74 | Juldah | 13 | 15:00 | 140 | Rajbari | 64 | 19:00
9 | Bagerhat | 83 | 19:30 | 75 | KSRM | 12 | 13:00 | 141 | Rajendrapur | 113 | 00:00
10 | Bajitpur | 45 | 00:00 | 76 | Kabirpur | 246 | 01:00 | 142 | Rajshahi | 94 | 13:00
11 | Bakulia | 83 | 20:00 | 77 | Kachua | 81 | 00:00 | 143 | Rajshahi-230 | 85 | 11:00
12 | Banani | 24 | 00:00 | 78 | Kallyanpur | 87 | 00:00 | 144 | Ramganj | 108 | 00:00
13 | Bangabhaban | 4 | 10:00 | 79 | Kalurghat | 32 | 00:00 | 145 | Rampur | 37 | 00:00
14 | Barapukuria | 57 | 21:00 | 80 | Kamrangirchar | 61 | 00:00 | 146 | Rangamati | 17 | 19:00
15 | Barguna | 20 | 19:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 121 | 19:30
16 | Barishal | 95 | 00:00 | 82 | Kasba | 34 | 00:00 | 148 | Ruppur | 5.6 | 15:00
17 | Barishal-230 | 72 | 00:00 | 83 | Kazla | 92 | 00:00 | 149 | SSM | 3 | 00:00
18 | Baroaulia | 52 | 22:00 | 84 | Keranigonj | 68 | 00:00 | 150 | Saidpur | 79 | 00:00
19 | Baroirhat | 52 | 19:00 | 85 | Khagrachori | 26 | 00:00 | 151 | Satkhira | 129 | 19:30
20 | Bashundhara | 147 | 00:00 | 86 | Khulna | 60 | 21:00 | 152 | Satmasjid | 84 | 13:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulshi | 178 | 00:00 | 153 | Savar | 170 | 00:00
22 | Beanibazar | 64 | 00:00 | 88 | Kishoreganj | 114 | 00:00 | 154 | SevenRings | 16.73 | 00:00
23 | Benapole | 44 | 00:00 | 89 | Kodda | 266 | 04:00 | 155 | ShahCement | 36 | 09:00
24 | Bhaluka | 120 | 00:00 | 90 | Kulaura | 37 | 00:00 | 156 | Shahjadpur | 83 | 11:00
25 | Bhandaria | 51 | 21:00 | 91 | Kurigram | 51 | 19:00 | 157 | Shahjibazar | 114 | 00:00
26 | Bhangura | 44 | 13:00 | 92 | Kushtia | 116 | 19:30 | 158 | Shahmirpur | 51 | 00:00
27 | Bheramara(GK) | 53 | 14:00 | 93 | Lalbag | 60 | 00:00 | 159 | Shariatpur | 76 | 00:00
28 | Bhulta | 218 | 00:00 | 94 | Lalmonirhat | 50 | 19:00 | 160 | Sherpur | 128 | 20:00
29 | Bog-Sherpur | 56 | 19:30 | 95 | MI_Cement | 14 | 01:00 | 161 | Shikalbaha | 21 | 00:00
30 | Bogura | 145 | 00:00 | 96 | Madanganj | 36 | 00:00 | 162 | Shitalakhya | 68.1 | 13:00
31 | Borhanuddin | 82 | 20:00 | 97 | Madaripur | 99 | 21:00 | 163 | Sholosohor | 37 | 00:00
32 | Brahmanbaria | 112 | 01:00 | 98 | Madartek | 75.86 | 00:00 | 164 | Shyampur | 140 | 01:00
33 | Cantonment | 100 | 12:00 | 99 | Madunaghat | 47 | 19:30 | 165 | Siddhirganj | 107 | 00:00
34 | Chandina | 18.94 | 18:30 | 100 | Magura | 53 | 21:00 | 166 | Sirajganj | 108 | 12:00
35 | Chandpur | 62 | 20:00 | 101 | Mahasthangarh | 68 | 00:00 | 167 | Sonargaon | 121 | 03:00
36 | Chandraghona | 34 | 19:00 | 102 | Manikganj | 111 | 00:00 | 168 | Sreemongol | 73 | 00:00
37 | Chapai | 65 | 11:00 | 103 | Maniknagar | 56 | 00:00 | 169 | Sreepur | 81 | 00:00
38 | Charsaidpur | 48 | 02:00 | 104 | Matarbari | 46 | 19:00 | 170 | Srinagar | 43.5 | 15:00
39 | Chauddagram | 57 | 00:00 | 105 | Matuail | 56 | 00:00 | 171 | Sunamganj | 54 | 00:00
40 | Chhatak | 33 | 00:00 | 106 | Millgate | 86 | 00:00 | 172 | Sylhet | 38 | 22:00
41 | Chowmuhani | 200 | 19:30 | 107 | Mirpur | 104 | 00:00 | 173 | Sylhet-132 | 116 | 18:30
42 | Chuadanga | 84 | 13:00 | 108 | Mirsorai | 8 | 02:00 | 174 | TK | 32 | 01:00
43 | Coxsbazar | 131 | 22:00 | 109 | Mirzapur | 43 | 00:00 | 175 | Tangail | 164 | 12:00
44 | Cumilla(N) | 143 | 00:00 | 110 | Mithapukur | 52 | 19:00 | 176 | Thakurgaon | 91 | 19:30
45 | Cumilla(S) | 154 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 94 | 00:00
46 | Daudkandi | 142 | 00:00 | 112 | Mogbazar | 92.6 | 15:00 | 178 | Ullahpara | 38 | 07:00
47 | Dhaka | 24 | 12:00 | 113 | Mongla | 28 | 00:00 | 179 | Ullon | 41 | 00:00
48 | Dhamrai | 118 | 00:00 | 114 | Motijheel | 27 | 00:00 | 180 | Uttara | 70 | 13:00
49 | Dhanmondi | 86 | 13:00 | 115 | Muktagacha | 30 | 19:00 | 181 | UttaraNew | 41 | 01:00
50 | Dohazari | 102 | 19:00 | 116 | Munshiganj | 101 | 00:00 | 182 | Zigatola | 64 | 00:00
51 | Faridpur | 130 | 20:00 | 117 | Muradnagar | 25 | 00:00
52 | Fatullah | 88 | 00:00 | 118 | Mymensingh | 162 | 13:00
53 | Fenchuganj | 37 | 00:00 | 119 | Naogaon | 119 | 13:00
54 | Feni | 101 | 13:00 | 120 | Narail | 44 | 14:00
55 | GPH | 18 | 02:00 | 121 | Narinda | 49 | 13:00
56 | Ghatail | 70 | 13:00 | 122 | Narshingdi | 172 | 00:00
57 | Ghorashal | 14 | 00:00 | 123 | Natore | 129 | 13:00
58 | Ghorashal-230 | 86 | 00:00 | 124 | Nawabganj | 49.8 | 15:00
59 | Goalpara | 30 | 00:00 | 125 | Netrakona | 111 | 19:00
60 | Gollamari | 78 | 00:00 | 126 | New | 67 | 01:00
61 | Gopalganj | 84 | 22:00 | 127 | Niamatpur | 80 | 13:00
62 | Gulshan | 70 | 12:00 | 128 | Noapara | 37 | 19:00
63 | Halishahar | 47 | 18:00 | 129 | PHP | 6 | 09:00
64 | HaripurSBU | 153 | 01:00 | 130 | Pabna | 99 | 19:00
65 | Hasnabad | 72 | 00:00 | 131 | Palashbari | 110 | 19:30
66 | Hathazari | 81 | 19:30 | 132 | Panchagarh | 52 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12869.84 | 34 |  | 12905.37
1:00 | 12525.06 | 74 |  | 12602.39
2:00 | 12036.02 | 63 |  | 12101.86
3:00 | 11747.1 | 60 |  | 11810.1
4:00 | 11400.64 | 57 |  | 11460.64
5:00 | 11119.48 | 41 |  | 11162.48
6:00 | 10552.78 | 39 |  | 10593.78
7:00 | 10304.74 | 0 |  | 10304.74
8:00 | 10003.06 | 0 |  | 10003.06
9:00 | 9939.15 | 0 |  | 9939.15
10:00 | 10036.19 | 0 |  | 10036.19
11:00 | 10424.37 | 0 |  | 10424.37
12:00 | 10976.06 | 0 |  | 10976.06
13:00 | 11179 | 0 |  | 11179
14:00 | 10545.58 | 0 |  | 10545.58
15:00 | 10044.6 | 0 |  | 10044.6
16:00 | 9707.91 | 0 |  | 9707.91
17:00 | 9108.39 | 0 |  | 9108.39
18:00 | 9010.58 | 0 |  | 9010.58
19:00 | 10939.4 | 0 |  | 10939.4
19:30 | 11384.2 | 0 |  | 11384.2
20:00 | 11369.93 | 0 |  | 11369.93
21:00 | 11428 | 0 |  | 11428
22:00 | 11241 | 0 |  | 11241
23:00 | 11077 | 0 |  | 11077
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## En-Curve
QF-LDC-12
Date | 01-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3695 | 2446 | 725 | 0 | 40 | 1367.84 | 40 | 3400 | 0 | 264 | 892 | 0 | 0 | 0 | 34 | DAILY ENERGY CURVE
00:30 | 3646 | 2436.25 | 820 | 0 | 40 | 1372.345 | 40 | 3316.5 | 0.355 | 249.5 | 775 | 0 | 0 | 1.5 | 54 | 01-05-2025
01:00 | 3597 | 2426.5 | 915 | 0 | 40 | 1376.85 | 40 | 3233 | 0.71 | 235 | 658 | 0 | 0 | 3 | 74
01:30 | 3600.5 | 2429.5 | 914.5 | 0 | 39 | 1313.38 | 40 | 3114.5 | 0.66 | 210 | 617 | 0 | 0 | 1.5 | 68.5 | Energy Generated | 261.8715 |  | MKWHr
02:00 | 3604 | 2432.5 | 914 | 0 | 38 | 1249.91 | 40 | 2996 | 0.61 | 185 | 576 | 0 | 0 | 0 | 63 | Energy not Served | 0.368 |  | MKWHr
02:30 | 3594 | 2427.75 | 915 | 0 | 37 | 1182.005 | 40 | 2961 | 0.305 | 176 | 558.5 | 0 | 0 | 0 | 61.5 | Total Energy Requirement | 262.2395 |  | MKWHr
03:00 | 3584 | 2423 | 916 | 0 | 36 | 1114.1 | 40 | 2926 | 0 | 167 | 541 | 0 | 0 | 0 | 60
03:30 | 3574 | 2430.5 | 915.5 | 0 | 36 | 1028.87 | 40 | 2862.5 | 0 | 158 | 528.5 | 0 | 0 | 0 | 58.5
04:00 | 3564 | 2438 | 915 | 0 | 36 | 943.64 | 40 | 2799 | 0 | 149 | 516 | 0 | 0 | 0 | 57
04:30 | 3538.5 | 2382 | 914.5 | 0 | 35 | 934.56 | 40 | 2778.5 | 0 | 140.5 | 496.5 | 0 | 0 | 0 | 49
05:00 | 3513 | 2326 | 914 | 0 | 34 | 925.48 | 40 | 2758 | 0 | 132 | 477 | 0 | 0 | 0 | 41
05:30 | 3450 | 2251 | 914 | 0 | 33 | 880.12 | 40 | 2718 | 14.01 | 106 | 430 | 0 | 0 | 0 | 40
06:00 | 3387 | 2176 | 914 | 0 | 32 | 834.76 | 40 | 2678 | 28.02 | 80 | 383 | 0 | 0 | 0 | 39
06:30 | 3385 | 2134 | 914 | 0 | 30 | 831.755 | 40 | 2570 | 83.005 | 77 | 364 | 0 | 0 | 0 | 19.5
07:00 | 3383 | 2092 | 914 | 0 | 28 | 828.75 | 40 | 2462 | 137.99 | 74 | 345 | 0 | 0 | 0 | 0
07:30 | 3349 | 2000 | 894.5 | 0 | 28 | 823.245 | 40 | 2423.5 | 208.655 | 65.5 | 321.5 | 0 | 0 | 0 | 0
08:00 | 3315 | 1908 | 875 | 0 | 28 | 817.74 | 40 | 2385 | 279.32 | 57 | 298 | 0 | 0 | 0 | 0
08:30 | 3322 | 1833.5 | 875.5 | 0 | 28 | 818.835 | 40 | 2386 | 373.27 | 53 | 241 | 0 | 0 | 0 | 0
09:00 | 3329 | 1759 | 876 | 0 | 28 | 819.93 | 40 | 2387 | 467.22 | 49 | 184 | 0 | 0 | 0 | 0
09:30 | 3307 | 1758.5 | 900.5 | 0 | 29 | 823.51 | 40 | 2385.5 | 532.66 | 33 | 178 | 0 | 0 | 0 | 0
10:00 | 3285 | 1758 | 925 | 0 | 30 | 827.09 | 40 | 2384 | 598.1 | 17 | 172 | 0 | 0 | 0 | 0
10:30 | 3382.5 | 1835 | 926 | 0 | 31 | 825.585 | 40 | 2388.5 | 591.195 | 17 | 193.5 | 0 | 0 | 0 | 0
11:00 | 3480 | 1912 | 927 | 0 | 32 | 824.08 | 40 | 2393 | 584.29 | 17 | 215 | 0 | 0 | 0 | 0
11:30 | 3563.5 | 2010.5 | 926.5 | 0 | 34 | 826.54 | 40 | 2406.5 | 627.175 | 33.5 | 232 | 0 | 0 | 0 | 0
12:00 | 3647 | 2109 | 926 | 0 | 36 | 829 | 40 | 2420 | 670.06 | 50 | 249 | 0 | 0 | 0 | 0
12:30 | 3667.5 | 2208.5 | 920.5 | 0 | 37 | 828.63 | 40 | 2419.5 | 654.4 | 50 | 251 | 0 | 0 | 0.5 | 0
13:00 | 3688 | 2308 | 915 | 0 | 38 | 828.26 | 40 | 2419 | 638.74 | 50 | 253 | 0 | 0 | 1 | 0
13:30 | 3602.5 | 2190.5 | 914.5 | 0 | 35 | 828.25 | 40 | 2372 | 617.04 | 29 | 224.5 | 0 | 0 | 9 | 0
14:00 | 3517 | 2073 | 914 | 0 | 32 | 828.24 | 40 | 2325 | 595.34 | 8 | 196 | 0 | 0 | 17 | 0
14:30 | 3424.5 | 2020.5 | 914.5 | 0 | 35 | 827.135 | 40 | 2298.5 | 508.955 | 8 | 200.5 | 0 | 0 | 17.5 | 0
15:00 | 3332 | 1968 | 915 | 0 | 38 | 826.03 | 40 | 2272 | 422.57 | 8 | 205 | 0 | 0 | 18 | 0
15:30 | 3308.5 | 1843.5 | 915.5 | 0 | 38 | 825.3 | 40 | 2305 | 349.955 | 8 | 233.5 | 0 | 0 | 9 | 0
16:00 | 3285 | 1719 | 916 | 0 | 38 | 824.57 | 40 | 2338 | 277.34 | 8 | 262 | 0 | 0 | 0 | 0
16:30 | 3145 | 1727.5 | 915 | 0 | 32 | 824.995 | 30 | 2315 | 187.655 | 8 | 223 | 0 | 0 | 0 | 0
17:00 | 3005 | 1736 | 914 | 0 | 26 | 825.42 | 20 | 2292 | 97.97 | 8 | 184 | 0 | 0 | 0 | 0
17:30 | 3002 | 1746.5 | 914.5 | 0 | 23 | 824.975 | 20 | 2291.5 | 59.01 | 8 | 170 | 0 | 0 | 0 | 0
18:00 | 2999 | 1757 | 915 | 0 | 20 | 824.53 | 20 | 2291 | 20.05 | 8 | 156 | 0 | 0 | 0 | 0
18:30 | 3277 | 2152 | 891 | 0 | 25 | 827.465 | 30 | 2483 | 10.025 | 33 | 246.5 | 0 | 0 | 0 | 0
19:00 | 3555 | 2547 | 867 | 0 | 30 | 830.4 | 40 | 2675 | 0 | 58 | 337 | 0 | 0 | 0 | 0
19:30 | 3562 | 2613.5 | 868 | 0 | 34 | 823.7 | 40 | 2913 | 0 | 76 | 454 | 0 | 0 | 0 | 0
20:00 | 3677 | 2769 | 868 | 0 | 36 | 835.93 | 40 | 2633 | 0 | 42 | 469 | 0 | 0 | 0 | 0
20:30 | 3710.5 | 2832.5 | 891.5 | 0 | 34 | 830.465 | 40 | 2607.5 | 0 | 21 | 431.5 | 0 | 0 | 0 | 0
21:00 | 3744 | 2896 | 915 | 0 | 32 | 825 | 40 | 2582 | 0 | 0 | 394 | 0 | 0 | 0 | 0
21:30 | 3739.5 | 2918 | 914.5 | 0 | 31 | 825 | 40 | 2583.5 | 0 | 0 | 283 | 0 | 0 | 0 | 0
22:00 | 3735 | 2940 | 914 | 0 | 30 | 825 | 40 | 2585 | 0 | 0 | 172 | 0 | 0 | 0 | 0
22:30 | 3767 | 2929.5 | 914 | 0 | 32 | 828.5 | 40 | 2491 | 0 | 0 | 157 | 0 | 0 | 0 | 0
23:00 | 3799 | 2919 | 914 | 0 | 34 | 832 | 40 | 2397 | 0 | 0 | 142 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7373 | 5496.84 | 12869.84 | DAILY GENERATION CURVE
00:30 | 7212.25 | 5485.2 | 12697.45
01:00 | 7051.5 | 5473.56 | 12525.06 | 01-05-2025
01:30 | 6944.5 | 5336.04 | 12280.54
02:00 | 6837.5 | 5198.52 | 12036.02
02:30 | 6792.25 | 5099.31 | 11891.56
03:00 | 6747 | 5000.1 | 11747.1
03:30 | 6676.5 | 4897.37 | 11573.87
04:00 | 6606 | 4794.64 | 11400.64
04:30 | 6500.5 | 4759.56 | 11260.06
05:00 | 6395 | 4724.48 | 11119.48
05:30 | 6203.94 | 4632.19 | 10836.13
06:00 | 6012.88 | 4539.9 | 10552.78
06:30 | 5921.285 | 4507.475 | 10428.76
07:00 | 5829.69 | 4475.05 | 10304.74
07:30 | 5703.78 | 4450.12 | 10153.9
08:00 | 5577.87 | 4425.19 | 10003.06
08:30 | 5498.055 | 4473.05 | 9971.105
09:00 | 5418.24 | 4520.91 | 9939.15
09:30 | 5389.36 | 4598.31 | 9987.67
10:00 | 5360.48 | 4675.71 | 10036.19
10:30 | 5548.995 | 4681.285 | 10230.28
11:00 | 5737.51 | 4686.86 | 10424.37
11:30 | 5893.44 | 4806.775 | 10700.215
12:00 | 6049.37 | 4926.69 | 10976.06
12:30 | 6157.06 | 4920.47 | 11077.53
13:00 | 6264.75 | 4914.25 | 11179
13:30 | 6040.355 | 4821.935 | 10862.29
14:00 | 5815.96 | 4729.62 | 10545.58
14:30 | 5699.4 | 4595.69 | 10295.09
15:00 | 5582.84 | 4461.76 | 10044.6
15:30 | 5436.595 | 4439.66 | 9876.255
16:00 | 5290.35 | 4417.56 | 9707.91
16:30 | 5116.365 | 4291.785 | 9408.15
17:00 | 4942.38 | 4166.01 | 9108.39
17:30 | 4929.335 | 4130.15 | 9059.485
18:00 | 4916.29 | 4094.29 | 9010.58
18:30 | 5657.645 | 4317.345 | 9974.99
19:00 | 6399 | 4540.4 | 10939.4
19:30 | 6558.5 | 4825.7 | 11384.2
20:00 | 6710 | 4659.93 | 11369.93
20:30 | 6748.5 | 4650.465 | 11398.965 |  | Executive Engineer
21:00 | 6787 | 4641 | 11428 |  | Network Operation Division
21:30 | 6734.5 | 4600 | 11334.5
22:00 | 6682 | 4559 | 11241
22:30 | 6649 | 4510 | 11159
23:00 | 6616 | 4461 | 11077

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 390 | 23:00 | 390 | 23:00 | Payra | 416 | 18:00 | 412 | 00:00
Ashuganj | 407 | 18:00 | 392 | 11:00 | Rahanpur | 399 | 05:00 | 387 | 00:00
Bhulta | 403 | 08:00 | 392 | 00:00 | Rampal | 406 | 18:00 | 395 | 00:00
Bibiana | 395 | 10:00 | 389 | 00:00
BIPTC | 398 | 18:00 | 393 | 15:00
Bogura | 386 | 06:00 | 372 | 00:00
Gopalganj | 405 | 18:00 | 391 | 00:00
Kaliakoir | 387 | 22:00 | 367 | 17:00
Madunaghat | 399 | 07:00 | 393 | 00:00
Meghnaghat | 400 | 18:00 | 391 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 232 | 18:00 | 223 | 01:00 | Keranigonj | 231 | 18:00 | 221 | 01:00
AKSML | 230 | 12:00 | 223 | 00:00 | Khulna(S) | 233 | 06:00 | 223 | 13:00
Aminbazar | 230 | 23:00 | 230 | 23:00 | Madunaghat | 232 | 08:00 | 227 | 00:00
Ashuganj | 235 | 07:00 | 228 | 01:00 | Madunaghat-400 | 231 | 07:00 | 226 | 01:00
Ashuganj-400 | 235 | 07:00 | 228 | 01:00 | Maniknagar | 228 | 08:00 | 222 | 00:00
Baghabari | 235 | 05:00 | 228 | 12:00 | Meghnaghat | 238 | 19:30 | 225 | 18:30
Barapukuria | 227 | 05:00 | 219 | 19:00 | Meghnaghat-400 | 231 | 08:00 | 225 | 00:00
Barapukuria-230 | 227 | 05:00 | 219 | 19:00 | Mirsorai | 231 | 08:00 | 221 | 01:00
Barishal | 240 | 18:00 | 232 | 00:00 | Rajshahi | 236 | 18:00 | 223 | 11:00
Bheramara | 234 | 04:00 | 223 | 12:00 | Rampal | 233 | 18:00 | 222 | 13:00
Bhulta | 229 | 08:00 | 222 | 01:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 228 | 07:00 | 221 | 01:00 | Rampura | 228 | 06:00 | 220 | 01:00
BIPTC | 236 | 18:00 | 224 | 13:00 | Shikalbaha | 229 | 08:00 | 224 | 00:00
Bogura | 235 | 06:00 | 227 | 01:00 | Shyampur | 230 | 18:00 | 222 | 01:00
Bogura-400 | 235 | 05:00 | 228 | 01:00 | Siddhirganj | 231 | 17:00 | 224 | 00:00
Borhanuddin | 243 | 07:00 | 238 | 01:00 | Sirajgonj | 241 | 06:00 | 236 | 12:00
BSRM | 231 | 18:00 | 219 | 01:00 | Sreepur | 231 | 06:00 | 226 | 00:00
Cumilla(N) | 227 | 18:00 | 220 | 00:00 | Tongi | 231 | 07:00 | 223 | 00:00
Faridpur | 236 | 18:00 | 230 | 00:00
Fenchuganj | 229 | 17:00 | 221 | 02:00
Ghorashal | 235 | 01:00 | 230 | 00:00
Ghorashal-230 | 230 | 06:00 | 223 | 01:00
Gopalganj | 239 | 18:00 | 231 | 00:00
GPH | 231 | 18:00 | 224 | 01:00
Haripur | 229 | 07:00 | 222 | 01:00
Hasnabad | 229 | 04:00 | 222 | 01:00
Hathazari | 231 | 09:00 | 224 | 01:00
Ishurdi | 236 | 04:00 | 226 | 12:00
Jhenaidah | 233 | 18:00 | 219 | 13:00
Kaliakoir | 235 | 06:00 | 227 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 134 | 00:00 | Madartek | 138 | 07:00 | 132 | 12:00
Agargaon | 137 | 18:00 | 132 | 00:00 | Madunaghat | 132 | 06:00 | 129 | 01:00
Agrabad | 132 | 07:00 | 127 | 13:00 | Magura | 137 | 03:00 | 127 | 12:00
AKS | 130 | 07:00 | 126 | 00:00 | Mahasthangarh | 135 | 04:00 | 130 | 19:00
Aminbazar | 132 | 23:00 | 132 | 23:00 | Manikganj | 133 | 06:00 | 125 | 00:00
Amnura | 137 | 18:00 | 122 | 12:00 | Maniknagar | 135 | 08:00 | 130 | 00:00
Ashuganj | 139 | 20:00 | 135 | 11:00 | Matarbari | 120 | 09:00 | 110 | 19:00
Bagerhat | 139 | 23:00 | 127 | 13:00 | Matuail | 134 | 18:00 | 28.7 | 03:00
Bajitpur | 134 | 06:00 | 130 | 10:00 | Millgate | 137 | 14:00 | 130 | 00:00
Bakulia | 133 | 06:00 | 129 | 14:00 | Mirpur | 133 | 08:00 | 128 | 13:00
Banani | 138 | 07:00 | 134 | 00:00 | Mirzapur | 133 | 16:00 | 126 | 17:00
Bangabhaban | 135 | 18:00 | 130 | 00:00 | Mithapukur | 133 | 06:00 | 124 | 19:00
Barapukuria | 133 | 04:00 | 125 | 19:00 | MI_Cement | 134 | 18:00 | 129 | 00:00
Barguna | 136 | 06:00 | 132 | 18:30 | Modern | N/A | N/A | N/A | N/A
Barishal | 133 | 07:00 | 128 | 00:00 | Mogbazar | 139 | 07:00 | 135 | 00:00
Barishal-230 | 133 | 07:00 | 128 | 00:00 | Mongla | 138 | 23:00 | 129 | 12:00
Baroaulia | 133 | 21:00 | 129 | 14:00 | Motijheel | 135 | 18:00 | 130 | 00:00
Baroirhat | 126 | 18:00 | 119 | 12:00 | Muktagacha | 133 | 13:00 | 123 | 08:00
Bashundhara | 137 | 05:00 | 127 | 00:00 | Munshiganj | 133 | 07:00 | 128 | 00:00
BashundharaCement | 133 | 18:00 | 128 | 00:00 | Muradnagar | 131 | 18:00 | 122 | 00:00
Beanibazar | 132 | 18:00 | 127 | 00:00 | Mymensingh | 136 | 14:00 | 123 | 11:00
Benapole | 136 | 05:00 | 125 | 14:00 | Naogaon | 133 | 16:00 | 127 | 00:00
Bhaluka | 134 | 15:00 | 128 | 11:00 | Narail | 138 | 04:00 | 128 | 14:00
Bhandaria | 127 | 07:00 | 121 | 00:00 | Narinda | 135 | 8:00 | 131 | 12:00
Bhangura | 135 | 18:00 | 129 | 12:00 | Narshingdi | 130 | 18:00 | 121 | 00:00
Bheramara | 137 | 04:00 | 129 | 12:00 | Natore | 136 | 16:00 | 128 | 13:00
Bheramara(GK) | 136 | 02:00 | 128 | 13:00 | Nawabganj | 138 | 08:00 | 132 | 00:00
Bhulta | 128 | 18:00 | 122 | 01:00 | Netrakona | 128 | 14:00 | 120 | 18:30
Bog-Sherpur | 136 | 05:00 | 131 | 12:00 | New | 138 | 18:00 | 131 | 00:00
Bogura | 139 | 05:00 | 133 | 19:30 | Niamatpur | 133 | 15:00 | 127 | 00:00
Bogura-230 | 138 | 04:00 | 134 | 00:00 | Noapara | 138 | 05:00 | 128 | 13:00
Brahmanbaria | 132 | 04:00 | 125 | 01:00 | Pabna | 137 | 04:00 | 130 | 12:00
Cantonment | 137 | 18:00 | 132 | 00:00 | Palashbari | 130 | 06:00 | 122 | 19:00
Chandina | 132 | 18:00 | 125 | 00:00 | Panchagarh | 135 | 20:00 | 119 | 19:00
Chandpur | 125 | 18:00 | 114 | 23:00 | Patuakhali | 135 | 06:00 | 132 | 19:00
Chandraghona | 133 | 07:00 | 129 | 01:00 | Payra | 136 | 02:00 | 134 | 00:00
Chapai | 130 | 15:00 | 124 | 00:00 | PHP | 128 | 23:00 | 116 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 18:00 | 128 | 01:00 | Postogola | 136 | 08:00 | 130 | 01:00
Chauddagram | 129 | 18:00 | 118 | 00:00 | Purbachal | 138 | 07:00 | 134 | 00:00
Chhatak | 130 | 06:00 | 125 | 00:00 | Purbasadipur | 129 | 04:00 | 119 | 11:00
Chowmuhani | 123 | 18:30 | 111 | 00:00 | Rahanpur | 132 | 05:00 | 128 | 00:00
Chuadanga | 137 | 04:00 | 124 | 14:00 | Rahanpur-400 | 133 | 04:00 | 129 | 00:00
Coxsbazar | 120 | 09:00 | 110 | 19:00 | Rahim | 133 | 07:00 | 129 | 00:00
Cumilla(N) | 131 | 18:00 | 125 | 00:00 | Rajbari | 138 | 06:00 | 133 | 00:00
Cumilla(S) | 133 | 03:00 | 122 | 00:00 | Rajendrapur | 136 | 15:00 | 126 | 12:00
Daudkandi | 129 | 18:00 | 121 | 00:00 | Rajshahi | 136 | 05:00 | 128 | 13:00
Dhaka | 138 | 06:00 | 134 | 00:00 | Rajshahi-230 | 136 | 04:00 | 117 | 00:00
Dhamrai | 142 | 15:00 | 134 | 00:00 | Ramganj | 120 | 22:00 | 112 | 23:00
Dhanmondi | 138.5 | 08:00 | 135 | 00:00 | Rampur | 132 | 07:00 | 127 | 15:00
Dohazari | 128 | 08:00 | 121 | 23:00 | Rampura | 145 | 08:00 | 132 | 23:00
Faridpur | 138 | 06:00 | 134 | 12:00 | Rangamati | 132 | 08:00 | 128 | 00:00
Fatullah | 135 | 18:00 | 129 | 01:00 | Rangpur | 131 | 16:00 | 122 | 19:00
Fenchuganj | 136 | 16:00 | 132 | 02:00 | Ruppur | 139 | 04:00 | 134 | 12:00
Feni | 124 | 06:00 | 116 | 14:00 | Saidpur | 130 | 20:00 | 120 | 11:00
Ghatail | 133 | 16:00 | 124 | 17:00 | Satkhira | 139 | 23:00 | 127 | 13:00
Ghorashal | 139 | 01:00 | 135 | 00:00 | Satmasjid | 136 | 18:00 | 131 | 01:00
Goalpara | 140 | 06:00 | 132 | 13:00 | Savar | 132 | 18:00 | 128 | 13:00
Gollamari | 139 | 18:00 | 132 | 13:00 | SevenRings | 139 | 07:00 | 134 | 01:00
Gopalganj | 138 | 18:00 | 131 | 13:00 | ShahCement | 134 | 18:00 | 128 | 01:00
Gopalganj-400 | 139 | 18:00 | 134 | 00:00 | Shahjadpur | 138 | 18:00 | 133 | 13:00
Gulshan | 137 | 04:00 | 133 | 01:00 | Shahjibazar | 134 | 07:00 | 127 | 00:00
Halishahar | 132 | 07:00 | 128 | 00:00 | Shahmirpur | 133 | 07:00 | 129 | 22:00
Haripur | 134 | 08:00 | 129 | 00:00 | Shariatpur | 136 | 18:00 | 129 | 00:00
HaripurSBU | 134 | 08:00 | 129 | 00:00 | Sherpur | 135 | 13:00 | 116 | 18:00
Hasnabad | 135 | 07:00 | 131 | 00:00 | Shikalbaha | 121 | 17:00 | 118 | 13:00
Hathazari | 134 | 09:00 | 129 | 01:00 | Shikalbaha-230 | 134 | 07:00 | 130 | 13:00
Ishurdi | 140 | 18:00 | 134 | 12:00 | Shitalakhya | 134 | 18:00 | 129 | 00:00
Jaldhaka | 128 | 06:00 | 117 | 19:00 | Sholosohor | 133 | 08:00 | 129 | 00:00
Jamalpur | 138 | 13:00 | 121 | 17:00 | Shyampur | 134 | 09:00 | 130 | 00:00
Jashore | 138 | 18:00 | 126 | 13:00 | Shyampur-230 | 135 | 18:00 | 128 | 01:00
Jhenaidah | 138 | 04:00 | 127 | 13:00 | Siddhirganj | 134 | 08:00 | 129 | 00:00
Jhenaidah-230 | 138 | 04:00 | 128 | 13:00 | Sirajganj | 134 | 18:00 | 129 | 12:00
Joydebpur | 143 | 14:00 | 132 | 12:00 | Sonargaon | 131 | 07:00 | 125 | 00:00
Joypurhat | 131 | 18:00 | 123 | 00:00 | Sreemongol | 133 | 17:00 | 127 | 00:00
Juldah | 132 | 03:00 | 129 | 13:00 | Sreepur | 136 | 15:00 | 131 | 01:00
Kabirpur | 136 | 16:00 | 128 | 17:00 | Srinagar | 138 | 08:00 | 133 | 00:00
Kachua | 126 | 18:00 | 117 | 11:00 | SSM | 134 | 00:00 | 132 | 11:00
Kaliakoir | 142 | 10:00 | 131 | 01:00 | Sunamganj | 129 | 14:00 | 123 | 00:00
Kallyanpur | 135 | 18:00 | 129 | 01:00 | Sylhet | 132 | 18:00 | 128 | 00:00
Kalurghat | 133 | 06:00 | 130 | 00:00 | Sylhet-132 | 132 | 18:00 | 129 | 00:00
Kamrangirchar | 138 | 07:00 | 132 | 00:00 | Tangail | 132 | 16:00 | 124 | 07:00
Kaptai | 135 | 8:00 | 128 | 17:00 | Thakurgaon | 136 | 20:00 | 120 | 19:00
Kasba | 130 | 18:00 | 121 | 00:00 | TK | 133 | 07:00 | 130 | 00:00
Kazla | 134 | 07:00 | 129 | 00:00 | Tongi | 139 | 19:30 | 132 | 00:00
Keranigonj | 139 | 18:00 | 133 | 00:00 | Ullahpara | 135 | 05:00 | 130 | 12:00
Khagrachori | 131 | 06:00 | 127 | 01:00 | Ullon | 138 | 08:00 | 134 | 00:00
Khulna | 139 | 23:00 | 130 | 13:00 | Uttara | 132 | 06:00 | 128 | 01:00
Khulna(S) | 140 | 23:00 | 132 | 13:00 | UttaraNew | 134 | 14:00 | 129 | 01:00
Khulshi | 131 | 07:00 | 127 | 00:00 | Zigatola | 138 | 06:00 | 133 | 00:00
Kishoreganj | 135 | 14:00 | 128 | 11:00
Kodda | 138 | 14:00 | 126 | 12:00
KSRM | 133 | 05:00 | 129 | 00:00
Kulaura | 135 | 07:00 | 131 | 00:00
Kurigram | 133 | 04:00 | 118 | 18:30
Kushtia | 137 | 18:00 | 127 | 13:00
Lalbag | 138 | 18:30 | 132 | 00:00
Lalmonirhat | 129 | 06:00 | 121 | 19:00
Madanganj | 133 | 18:00 | 128 | 00:00
Madaripur | 136 | 18:00 | 131 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division