## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 05-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-05-2025 | during | 05-05-2025 | during | 05-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 343 | 333 | 400.75 | 400.75 | 375 | 375 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 291 | 304 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 225 | 225 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 9 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 95 | 115 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 23 | 22 | 30 | 30 | 27 | 27 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 7 | 20 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 25 | 52.19 | 52.19 | 16 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 60 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 112 | 115 | 149 | 149 | 130 | 130 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 34 | 50 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 84 | 104 | 104 | 65 | 65 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 86 | 54 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 35 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 450 | 584 | 584 | 583 | 583 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 460 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 110 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2604 | 3028 | 5274.9 | 5333.9 | 3951.87 | 4073.87
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 4 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 146 | 147 | 145 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 40 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 84 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 68 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 8 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 4.99 | 0 | 4.99 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1120 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 4 | 0 | 4 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 503 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1889 | 2214 | 3428.71 | 3411.72 | 3433.71 | 3411.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 187 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 343 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 345 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 34 | 46.94 | 46.94 | 34 | 34 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 48 | 55 | 55 | 49 | 49 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 80 | 45 | 195 | 195 | 178 | 178 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 35 | 43 | 51 | 51 | 35 | 35 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 60 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 90 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 46 | 120 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 97 | 97 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 77 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1457 | 1663 | 2468.99 | 2400.99 | 2189.55 | 2150.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 04-05-2025 | during | 05-05-2025 | during | 05-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 10 | 11 | 157.5 | 157.5 | 135 | 135 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.4 | 0 | 2.4 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 124 | 168 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 85 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 31.12 | 0 | 49.5 | 0 | 49.5 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 246.12 | 293 | 600.9 | 549 | 493.4 | 476.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 38 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 30 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 96 | 99 | 113 | 113 | 103 | 103 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 359 | 328 | 385 | 385 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1450 | 1420 | 1566 | 1566 | 1472 | 1472
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 0 | 0 | 410 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 70 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 377 | 505 | 1234.2 | 1234.2 | 617 | 617 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1370 | 1399 | 3612.2 | 3512.2 | 2480.01 | 2380.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 258 | 322 | 315 | 315 | 315 | 315 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 115 | 105 | 130 | 130 | 125 | 125 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1080 | 1110 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.91 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1927.91 | 2074 | 2487.12 | 2486.12 | 2482.12 | 2481.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 187 | 200 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 203 | 194 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 172 | 193 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 325 | 380 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.2 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1215.85 | 1365.67 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 59.88 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 92 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2259.93 | 2367.67 | 3114.68 | 2948.53 | 3061.89 | 2895.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 53 | 56 | 56 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 164 | 168 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 54 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 189 | 0 | 193.45 | 0 | 193.45 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 483 | 326 | 697.85 | 468 | 696.85 | 467
System Total |  |  |  |  | 27566.2 | 28535.742 | 13686.96 | 14784.67 | 23251.35 | 22676.46 | 20261.4 | 19808.51
Forecast Scenario (05-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14100 |  | 0 |  | 14100
|  |  |  | 1:00 | 13760 |  | 0 |  | 13760
|  |  |  | 2:00 | 13240 |  | 0 |  | 13240
|  |  |  | 3:00 | 12360 |  | 0 |  | 12360
|  |  |  | 4:00 | 11810 |  | 0 |  | 11810
|  |  |  | 5:00 | 11620 |  | 0 |  | 11620
|  |  |  | 6:00 | 11400 |  | 0 |  | 11400
|  |  |  | 7:00 | 11470 |  | 0 |  | 11470
|  |  |  | 8:00 | 11410 |  | 0 |  | 11410
|  |  |  | 9:00 | 11970 |  | 0 |  | 11970
|  |  |  | 10:00 | 12370 |  | 0 |  | 12370
|  |  |  | 11:00 | 12960 |  | 0 |  | 12960
|  |  |  | 12:00 | 13540 |  | 0 |  | 13540
|  |  |  | 13:00 | 13900 |  | 0 |  | 13900
|  |  |  | 14:00 | 13940 |  | 0 |  | 13940
|  |  |  | 15:00 | 14200 |  | 0 |  | 14200
|  |  |  | 16:00 | 13920 |  | 0 |  | 13920
|  |  |  | 17:00 | 13730 |  | 0 |  | 13730
|  |  |  | 18:00 | 13520 |  | 0 |  | 13520
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 14920 |  | 0 |  | 14920
|  |  |  | 19:30 | 15330 |  | 0 |  | 15330
|  |  |  | 20:00 | 15300 |  | 0 |  | 15300
|  |  |  | 21:00 | 15300 |  | 0 |  | 15300
|  |  |  | 22:00 | 15130 |  | 0 |  | 15130
|  |  |  | 23:00 | 15100 |  | 0 |  | 15100
Probable Maximum Temperature: |  |  | 32.90°C
Probable Maximum Demand at Day Peak: |  |  | 13540.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15330.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15330.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 320.97 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:48 hrs on 05-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 04-05-2025 | [28 empty] | Date: | 04-05-2025 | [28 empty] | Date: | 04-05-2025 | [28 empty] | Date: | 04-05-2025 | [28 empty] | Date: | 04-05-2025 | [16 empty] | Date: | 04-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 35 | 17 | 87 | 95 | 0 | 0 | 17 | 0 | 0 | 16 | 400 | 300 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 125 | 24.8 | 22 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 100 | 10 | 0 | 40 | 0 | 23 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1104 | 0 | 35 | 10 | 155 | 0 | 359 | 0 | 47 | 188 | 34 | 115 | 37 | 132 | 14 | 20 | 105 | 40 | 8 | 0 | 39 | 315 | 320 | 360 | 39 | 40 | 0 | 102 | 8 | 0 | 86 | 28 | 0 | 0 | 173 | 0 | 106 | 141 | 32 | 0 | 0 | 12 | 7743.8 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 0 | 1372.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 177 | 0 | 179 | 0 | 394 | 0 | 0 | 0 | 162 | 53 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 115 | 220 | 0 | 221 | 1244 | 0 | 6403.39 | 14147.19 | 79.45
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 35 | 17 | 75 | 131 | 0 | 0 | 0 | 0 | 0 | 16 | 400 | 297 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 125 | 24 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 30 | 575 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1100 | 0 | 35 | 0 | 175 | 0 | 355 | 0 | 44 | 192 | 34 | 115 | 25 | 120 | 9 | 20 | 70 | 39 | 0 | 0 | 39 | 305 | 320 | 358 | 39 | 40 | 0 | 81 | 8 | 0 | 86 | 28 | 0 | 0 | 173 | 0 | 48 | 93 | 32 | 0 | 0 | 12 | 7495 | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 0 | 1305.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 172 | 0 | 169 | 0 | 341 | 0 | 0 | 0 | 165 | 54 | 90 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 221 | 1120 | 0 | 6020.46 | 13515.46 | 79.44
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 35 | 17 | 70 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 301 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 108 | 21.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 68 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 32 | 576 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1008 | 0 | 35 | 0 | 175 | 0 | 355 | 18 | 46 | 197 | 34 | 106 | 25 | 121 | 9 | 20 | 70 | 36 | 0 | 0 | 39 | 310 | 320 | 363 | 39 | 40 | 0 | 81 | 8 | 0 | 86 | 28 | 0 | 0 | 173 | 0 | 48 | 94 | 32 | 0 | 0 | 12 | 7381.5 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 542 | 0 | 1317.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 170 | 0 | 158 | 0 | 345 | 0 | 0 | 0 | 164 | 53 | 70 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 110 | 220 | 0 | 222 | 1100 | 0 | 5835.91 | 13217.41 | 79.44
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 70 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 281 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 90 | 19.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 68 | 0 | 0 | 34 | 0 | 0 | 40 | 0 | 32 | 502 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1006 | 0 | 35 | 0 | 178 | 0 | 355 | 58 | 46 | 195 | 34 | 104 | 25 | 125 | 9 | 20 | 34 | 36 | 0 | 0 | 39 | 310 | 320 | 361 | 39 | 40 | 0 | 82 | 8 | 0 | 86 | 30 | 0 | 0 | 173 | 0 | 48 | 93 | 33 | 0 | 0 | 12 | 7176.5 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 467 | 0 | 1262.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 170 | 0 | 133 | 0 | 344 | 0 | 0 | 0 | 168 | 53 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 110 | 220 | 0 | 222 | 1060 | 0 | 5582.69 | 12759.19 | 79.43
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 17 | 70 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 277 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 90 | 19.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 38 | 0 | 0 | 40 | 0 | 29 | 456 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 35 | 0 | 178 | 0 | 355 | 77 | 47 | 190 | 34 | 90 | 30 | 106 | 9 | 20 | 0 | 34 | 0 | 0 | 0 | 305 | 320 | 361 | 39 | 40 | 0 | 81 | 8 | 0 | 86 | 30 | 0 | 0 | 173 | 0 | 48 | 93 | 33 | 0 | 0 | 12 | 6804.5 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 461 | 0 | 1253.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 171 | 0 | 132 | 0 | 338 | 0 | 0 | 0 | 164 | 53 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 8 | 110 | 220 | 0 | 221 | 1040 | 0 | 5514.64 | 12319.14 | 79.43
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 70 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 279 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 70 | 19.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 60 | 0 | 0 | 40 | 0 | 24 | 455 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 0 | 35 | 0 | 178 | 0 | 355 | 88 | 47 | 194 | 34 | 80 | 40 | 90 | 9 | 20 | 0 | 34 | 0 | 0 | 0 | 315 | 320 | 355 | 39 | 40 | 0 | 83 | 8 | 0 | 86 | 30 | 0 | 0 | 173 | 0 | 48 | 93 | 33 | 0 | 0 | 12 | 6818.5 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 1224.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 167 | 0 | 136 | 0 | 344 | 0 | 0 | 0 | 161 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 110 | 220 | 0 | 220 | 1000 | 0 | 5297.19 | 12115.69 | 79.42
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 70 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 292 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 1 | 52 | 17.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 24 | 0 | 1 | 40 | 0 | 34 | 455 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 900 | 2 | 35 | 0 | 178 | 0 | 355 | 120 | 47 | 203 | 34 | 68 | 50 | 72 | 9 | 20 | 0 | 32 | 0 | 2 | 0 | 310 | 320 | 335 | 39 | 40 | 0 | 84 | 8 | 0 | 86 | 30 | 0 | 0 | 173 | 0 | 48 | 100 | 33 | 0 | 2.36 | 12 | 6780.86 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.63 | 377 | 0 | 1029.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.49 | 155 | 0 | 163 | 0 | 134 | 0 | 357 | 0 | 0.19 | 0 | 161 | 55 | 0 | 1 | 0 | 0 | 0 | 0 | 10 | 0.04 | 0 | 200 | 6 | 115 | 220 | 0 | 221 | 880 | 0 | 5017.87 | 11798.73 | 79.42
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 78 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 290 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 5 | 52 | 22.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 12 | 0 | 1 | 40 | 0 | 33 | 454 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 900 | 3 | 35 | 0 | 178 | 0 | 355 | 180 | 46 | 205 | 34 | 34 | 45 | 17 | 9 | 20 | 0 | 30 | 0 | 18 | 0 | 320 | 320 | 333 | 39 | 40 | 0 | 90 | 8 | 0 | 86 | 30 | 0 | 0 | 173 | 0 | 67 | 123 | 33 | 0 | 11.43 | 12 | 6894.93 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.81 | 377 | 0 | 1021.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 13.22 | 162 | 0 | 162 | 0 | 141 | 0 | 369 | 0 | 0.92 | 0 | 158 | 54 | 0 | 3 | 0 | 0 | 0 | 0.1 | 21 | 0.15 | 0 | 200 | 6 | 115 | 220 | 0 | 222 | 850 | 0 | 5065.91 | 11960.84 | 79.41
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 87 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 305 | 400 | 0 | 0 | 0 | 255 | 0 | 0 | 0 | 52 | 25 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 0 | 11 | 406 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 905 | 11 | 35 | 0 | 178 | 0 | 349 | 215 | 46 | 206 | 33 | 34 | 45 | 16 | 9 | 20 | 0 | 30 | 0 | 19 | 0 | 315 | 320 | 345 | 39 | 40 | 0 | 86 | 8 | 0 | 86 | 30 | 0 | 0 | 173 | 0 | 67 | 122 | 27 | 1 | 24.43 | 12 | 6896.43 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.57 | 377 | 0 | 917.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 21.83 | 161 | 0 | 169 | 0 | 140 | 0 | 378 | 0 | 1.83 | 0 | 158 | 54 | 50 | 13 | 0 | 0 | 0 | 1.2 | 88 | 0.34 | 0 | 200 | 6 | 125 | 220 | 0 | 222 | 805 | 0 | 5080.97 | 11977.4 | 79.41
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 17 | 87 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 304 | 400 | 0 | 0 | 0 | 227 | 0 | 0 | 23 | 52 | 27 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 36 | 0 | 4 | 40 | 0 | 4 | 405 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 900 | 15 | 35 | 0 | 178 | 0 | 348 | 255 | 45 | 199 | 30 | 48 | 45 | 22 | 9 | 20 | 17 | 30 | 0 | 55 | 0 | 315 | 375 | 366 | 37 | 40 | 0 | 100 | 8 | 0 | 83 | 30 | 0 | 0 | 173 | 0 | 67 | 121 | 27 | 1 | 27.76 | 12 | 7209.76 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 378 | 0 | 919.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 38.22 | 181 | 0 | 185 | 0 | 170 | 0 | 394 | 0 | 3.29 | 0 | 156 | 54 | 54 | 22 | 0 | 0 | 0 | 2 | 133 | 0.56 | 0 | 250 | 6 | 115 | 220 | 0 | 222 | 860 | 0 | 5350.73 | 12560.49 | 79.41
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 87 | 110 | 0 | 0 | 25 | 0 | 0 | 0 | 400 | 301 | 400 | 0 | 0 | 0 | 225 | 0 | 0 | 30 | 52 | 25 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 20 | 4 | 40 | 0 | 4 | 500 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1000 | 18 | 35 | 0 | 177 | 0 | 346 | 300 | 43 | 196 | 32 | 78 | 50 | 34 | 9 | 20 | 17 | 30 | 0 | 67 | 0 | 310 | 320 | 376 | 38 | 40 | 0 | 100 | 8 | 0 | 83 | 30 | 0 | 0 | 173 | 0 | 67 | 119 | 27 | 2 | 41.51 | 12 | 7556.51 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 376 | 0 | 917.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 42.45 | 190 | 0 | 193 | 0 | 178 | 0 | 389 | 0 | 4.41 | 0 | 161 | 54 | 54 | 27 | 0 | 0 | 0 | 0.9 | 165 | 0.27 | 0 | 250 | 6 | 115 | 220 | 0 | 221 | 900 | 0 | 5522.83 | 13079.34 | 79.4
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 17 | 98 | 95 | 0 | 0 | 35 | 40 | 0 | 0 | 450 | 292 | 400 | 0 | 0 | 0 | 225 | 0 | 0 | 35 | 52 | 24 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 20 | 4 | 40 | 0 | 4 | 503 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1100 | 18 | 35 | 0 | 88 | 0 | 347 | 345 | 43 | 186 | 32 | 90 | 70 | 34 | 9 | 20 | 17 | 32 | 0 | 73 | 0 | 310 | 320 | 381 | 38 | 40 | 0 | 96 | 8 | 0 | 83 | 30 | 0 | 0 | 173 | 0 | 67 | 119 | 10 | 2 | 51.25 | 12 | 7648.25 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 379 | 0 | 1019.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 57.62 | 184 | 0 | 203 | 0 | 183 | 0 | 325 | 0 | 1.64 | 0 | 162 | 53 | 54 | 30 | 0 | 0 | 0 | 2.6 | 188 | 0.23 | 0 | 250 | 4 | 115 | 220 | 0 | 221 | 945 | 0 | 5714.9 | 13363.15 | 79.39
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 9 | 17 | 112 | 95 | 0 | 0 | 35 | 86 | 0 | 0 | 450 | 291 | 350 | 0 | 17 | 0 | 225 | 0 | 0 | 15 | 52 | 23 | 7 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 68 | 20 | 3 | 40 | 0 | 4 | 503 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1100 | 4 | 35 | 0 | 80 | 0 | 343 | 345 | 47 | 187 | 32 | 97 | 70 | 46 | 8 | 20 | 34 | 36 | 0 | 77 | 0 | 305 | 320 | 359 | 36 | 40 | 0 | 96 | 8 | 0 | 83 | 30 | 0 | 0 | 173 | 0 | 67 | 124 | 10 | 2 | 31.12 | 12 | 7646.12 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 377 | 0 | 1215.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 59.88 | 187 | 0 | 203 | 0 | 172 | 0 | 325 | 0 | 5.2 | 0 | 164 | 53 | 54 | 15 | 0 | 0 | 0 | 8 | 189 | 0.91 | 0 | 250 | 4 | 115 | 220 | 0 | 258 | 1080 | 0 | 6040.84 | 13686.96 | 79.39
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 54 | 17 | 112 | 110 | 5 | 0 | 35 | 100 | 0 | 7 | 450 | 287 | 350 | 0 | 35 | 0 | 225 | 0 | 0 | 11 | 70 | 23 | 14 | 0 | 400 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 68 | 20 | 3 | 40 | 0 | 2 | 501 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1100 | 16 | 35 | 1 | 45 | 0 | 348 | 345 | 46 | 181 | 32 | 115 | 70 | 68 | 9 | 20 | 34 | 38 | 16 | 39 | 23 | 305 | 320 | 335 | 37 | 40 | 0 | 81 | 8 | 0 | 86 | 30 | 0 | 0 | 174 | 0 | 67 | 118 | 10 | 1 | 50.56 | 12 | 7780.56 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 376 | 0 | 1307.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 59.5 | 189 | 0 | 202 | 0 | 175 | 0 | 320 | 0 | 5.13 | 0 | 162 | 53 | 54 | 32 | 0 | 0 | 0 | 6.7 | 173 | 0.37 | 0 | 250 | 5 | 90 | 220 | 0 | 296 | 1082 | 0 | 6047.83 | 13828.39 | 79.38
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 54 | 17 | 112 | 110 | 45 | 0 | 35 | 72 | 0 | 30 | 450 | 300 | 300 | 0 | 17 | 0 | 225 | 0 | 0 | 12 | 70 | 22.5 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 68 | 20 | 0 | 40 | 0 | 2 | 438 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1050 | 15 | 35 | 45 | 45 | 0 | 300 | 345 | 46 | 199 | 32 | 115 | 70 | 68 | 9 | 8 | 34 | 36 | 8 | 20 | 38 | 300 | 320 | 340 | 37 | 40 | 0 | 83 | 8 | 0 | 85 | 30 | 0 | 0 | 174 | 0 | 67 | 118 | 10 | 0 | 25.2 | 12 | 7445.7 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 378 | 0 | 1317.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 21.9 | 178 | 0 | 150 | 0 | 204 | 0 | 351 | 0 | 1.85 | 0 | 160 | 53 | 54 | 23 | 0 | 0 | 0 | 6.4 | 150 | 0.42 | 0 | 200 | 7 | 100 | 180 | 0 | 319 | 980 | 0 | 5808.52 | 13254.22 | 79.38
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 54 | 17 | 112 | 82 | 45 | 0 | 35 | 54 | 0 | 64 | 450 | 291 | 300 | 0 | 35 | 0 | 224 | 0 | 0 | 26 | 35 | 22 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 88 | 50 | 1 | 40 | 0 | 2 | 403 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1000 | 12 | 35 | 50 | 45 | 0 | 347 | 345 | 45 | 190 | 32 | 90 | 70 | 51 | 9 | 8 | 34 | 30 | 8 | 29 | 38 | 310 | 320 | 315 | 38 | 39 | 0 | 100 | 8 | 0 | 86 | 30 | 0 | 0 | 171 | 0 | 45 | 117 | 10 | 1 | 20.9 | 12 | 7394.9 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 376 | 0 | 1313.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 12.86 | 181 | 0 | 194 | 0 | 199 | 0 | 380 | 0 | 1.31 | 0 | 161 | 53 | 90 | 14 | 0 | 0 | 0 | 4.9 | 115 | 0.35 | 0 | 200 | 5 | 100 | 220 | 0 | 322 | 886 | 0 | 5856.71 | 13251.61 | 79.37
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 54 | 17 | 112 | 82 | 45 | 0 | 35 | 54 | 0 | 67 | 450 | 292 | 300 | 0 | 35 | 0 | 225 | 0 | 0 | 15 | 17 | 22.5 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 88 | 50 | 1 | 40 | 0 | 2 | 403 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1000 | 8 | 35 | 50 | 45 | 0 | 346 | 345 | 45 | 188 | 32 | 90 | 80 | 51 | 16 | 8 | 34 | 34 | 8 | 16 | 30 | 310 | 320 | 300 | 38 | 39 | 0 | 97 | 8 | 0 | 86 | 30 | 0 | 0 | 171 | 0 | 45 | 127 | 11 | 0 | 21.44 | 12 | 7326.94 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 376 | 0 | 1268.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 12.44 | 200 | 0 | 195 | 0 | 200 | 0 | 379 | 0 | 1.78 | 0 | 167 | 53 | 52 | 14 | 0 | 0 | 0 | 3.7 | 65 | 0.1 | 0 | 200 | 6 | 100 | 220 | 0 | 323 | 884 | 0 | 5708.23 | 13035.17 | 79.37
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 54 | 17 | 112 | 82 | 30 | 0 | 35 | 35 | 0 | 67 | 450 | 292 | 300 | 0 | 35 | 0 | 224 | 0 | 0 | 6 | 17 | 22 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 100 | 30 | 0 | 40 | 0 | 6 | 404 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1000 | 2 | 35 | 50 | 45 | 0 | 357 | 345 | 45 | 191 | 33 | 90 | 80 | 51 | 37 | 20 | 34 | 34 | 8 | 7 | 30 | 305 | 320 | 302 | 38 | 39 | 0 | 96 | 8 | 0 | 86 | 30 | 0 | 0 | 171 | 0 | 45 | 128 | 11 | 0 | 4.06 | 12 | 7299.06 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 375 | 0 | 1215.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 6.67 | 201 | 0 | 197 | 0 | 140 | 0 | 385 | 0 | 0.5 | 0 | 169 | 53 | 52 | 3 | 0 | 0 | 0 | 0.7 | 35 | 0.12 | 0 | 200 | 6 | 100 | 220 | 0 | 322 | 883 | 0 | 5543.64 | 12842.7 | 79.36
18:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 54 | 17 | 112 | 95 | 30 | 4 | 35 | 35 | 0 | 67 | 370 | 287 | 300 | 0 | 35 | 0 | 225 | 0 | 0 | 1 | 35 | 22 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 100 | 30 | 0 | 40 | 0 | 3 | 405 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 950 | 0 | 35 | 50 | 45 | 0 | 358 | 345 | 50 | 183 | 34 | 90 | 80 | 51 | 37 | 20 | 34 | 34 | 8 | 1 | 30 | 310 | 320 | 338 | 38 | 39 | 0 | 97 | 8 | 0 | 86 | 30 | 0 | 0 | 171 | 0 | 65 | 155 | 11 | 0 | 1.81 | 12 | 7303.81 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.12 | 375 | 10 | 1221.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.15 | 150 | 0 | 150 | 0 | 140 | 0 | 377 | 0 | 0.2 | 0 | 169 | 53 | 52 | 1 | 14 | 0 | 0 | 0.1 | 1 | 0.02 | 0 | 200 | 6 | 90 | 220 | 0 | 320 | 886 | 0 | 5370.52 | 12674.33 | 79.36
19:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 17 | 112 | 115 | 35 | 16 | 35 | 72 | 0 | 84 | 420 | 305 | 460 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 98 | 22 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 100 | 100 | 0 | 40 | 0 | 5 | 575 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1120 | 0 | 43 | 50 | 45 | 0 | 355 | 345 | 48 | 195 | 34 | 95 | 90 | 69 | 38 | 20 | 55 | 40 | 8 | 0 | 0 | 315 | 320 | 328 | 38 | 30 | 0 | 95 | 8 | 0 | 86 | 30 | 0 | 0 | 171 | 10 | 85 | 168 | 11 | 0 | 0 | 12 | 8443 | 885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 17 | 1368.53 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 194 | 0 | 193 | 0 | 403 | 0 | 0 | 0 | 167 | 53 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 9 | 115 | 220 | 0 | 322 | 947 | 0 | 6041.53 | 14484.53 | 79.35
19:30 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 115 | 115 | 60 | 30 | 35 | 54 | 0 | 84 | 420 | 304 | 460 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 110 | 22 | 20 | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 84 | 40 | 0 | 100 | 100 | 0 | 40 | 0 | 8 | 575 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1120 | 0 | 43 | 60 | 45 | 0 | 356 | 345 | 48 | 188 | 34 | 97 | 90 | 120 | 38 | 20 | 114 | 40 | 25 | 0 | 0 | 310 | 320 | 328 | 38 | 30 | 0 | 99 | 8 | 0 | 86 | 30 | 0 | 0 | 171 | 17 | 85 | 168 | 11 | 0 | 0 | 12 | 8618 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 17 | 1365.67 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 194 | 0 | 193 | 0 | 380 | 0 | 0 | 0 | 168 | 53 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 105 | 220 | 0 | 322 | 1110 | 0 | 6166.67 | 14784.67
20:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 115 | 115 | 30 | 30 | 35 | 54 | 0 | 84 | 380 | 302 | 460 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 125 | 22 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 0 | 100 | 100 | 0 | 40 | 0 | 17 | 523 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1085 | 0 | 43 | 66 | 45 | 0 | 356 | 345 | 48 | 182 | 34 | 98 | 90 | 120 | 38 | 20 | 114 | 40 | 20 | 0 | 8 | 300 | 320 | 325 | 38 | 30 | 0 | 96 | 8 | 0 | 86 | 30 | 0 | 0 | 171 | 17 | 85 | 177 | 11 | 0 | 0 | 12 | 8460 | 877 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 17 | 1369.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 193 | 0 | 193 | 0 | 378 | 0 | 0 | 0 | 169 | 53 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 105 | 220 | 0 | 323 | 1094 | 0 | 6078.61 | 14538.61 | 79.35
21:00 | 33 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 115 | 115 | 15 | 50 | 17 | 17 | 0 | 84 | 380 | 306 | 420 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 108 | 21.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 0 | 100 | 70 | 0 | 40 | 0 | 20 | 521 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1082 | 0 | 43 | 60 | 45 | 0 | 356 | 345 | 50 | 182 | 34 | 96 | 90 | 100 | 38 | 20 | 114 | 40 | 25 | 0 | 30 | 300 | 320 | 359 | 38 | 30 | 0 | 95 | 0 | 0 | 86 | 30 | 0 | 18 | 171 | 17 | 85 | 160 | 11 | 0 | 0 | 12 | 8437.5 | 923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 35 | 1365.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 190 | 0 | 193 | 0 | 340 | 0 | 0 | 0 | 170 | 53 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 115 | 220 | 0 | 321 | 1049 | 0 | 6052.33 | 14489.83 | 79.34
22:00 | 16 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 17 | 115 | 115 | 15 | 15 | 17 | 17 | 0 | 84 | 380 | 310 | 420 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 90 | 21.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 0 | 100 | 70 | 0 | 40 | 0 | 25 | 522 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1005 | 0 | 43 | 50 | 45 | 0 | 356 | 345 | 48 | 202 | 34 | 96 | 90 | 100 | 39 | 20 | 94 | 40 | 25 | 0 | 30 | 310 | 320 | 385 | 39 | 30 | 0 | 101 | 0 | 0 | 86 | 30 | 0 | 18 | 171 | 17 | 85 | 145 | 11 | 0 | 0 | 12 | 8319.5 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 17 | 1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 187 | 0 | 190 | 0 | 361 | 0 | 0 | 0 | 171 | 55 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 7 | 115 | 220 | 0 | 322 | 987 | 0 | 5898 | 14217.5 | 79.34
23:00 | 16 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 17 | 115 | 115 | 0 | 15 | 17 | 17 | 0 | 84 | 380 | 300 | 420 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 90 | 21.5 | 20 | 0 | 420 | 0 | 0 | 0 | 0 | 2 | 85 | 40 | 0 | 88 | 40 | 0 | 40 | 0 | 29 | 522 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1007 | 0 | 43 | 50 | 8 | 0 | 356 | 345 | 48 | 199 | 34 | 96 | 90 | 108 | 37 | 20 | 88 | 40 | 25 | 0 | 30 | 310 | 320 | 365 | 38 | 30 | 0 | 101 | 0 | 0 | 86 | 30 | 0 | 18 | 173 | 17 | 85 | 145 | 9 | 0 | 0 | 12 | 8173.5 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 0 | 1353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 183 | 0 | 189 | 0 | 405 | 0 | 0 | 0 | 170 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 115 | 220 | 0 | 322 | 995 | 0 | 5988 | 14161.5 | 79.33
Total KWH | 95072 | 764160 | 402720 | 0 | 0 | 0 | 0 | 0 | 8596800 | 0 | 0 | 733680 | 433440 | 2368224 | 2504160 | 357796 | 161511 | 481234 | 668160 | 0 | 788160 | 9464500 | 7129164 | 9258813 | 0 | 386068 | 0 | 5717175 | 0 | 0 | 184890 | 1729200 | 529800 | 425160 | 0 | 9420909.09 | 0 | 0 | 0 | 0 | 96480 | 679634 | 201952 | 0 | 1761600 | 674880 | 26324 | 960000 | 0 | 373440 | 11563636.36 | 0 | 0 | 0 | 0 | 0 | 3489490 | 0 | 0 | 0 | 24294543 | 124875 | 843568 | 682472 | 2509090 | 0 | 8747700 | 6044000 | 1118400 | 4777000 | 803016 | 2195520 | 1469050 | 1857600 | 438480 | 456910 | 1051080 | 835200 | 198514 | 427382 | 432800 | 7532500 | 7694500 | 8797000 | 899000 | 309303 | 0 | 2213018.2 | 151488 | 0 | 2046720 | 704256 | 0 | 73000 | 4563500 | 101520 | 1536000 | 2973600 | 437760 | 11500 | 298630 | 292800 | 182371527.65 | 22140364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600480 | 10458180 | 118080 | 28504727 | 0 | 0 | 0 | 60768 | 0 | 0 | 0 | 0 | 0 | 519890 | 0 | 357752 | 4395091 | 0 | 4562536 | 0 | 4261664 | 0 | 8873818 | 0 | 30000 | 0 | 4019000 | 1063255 | 1063150 | 193780 | 443308 | 0 | 0 | 40780.2 | 1332000 | 3760.5 | 25920 | 5891000 | 181532 | 2600000 | 5404110 | 0 | 6450264 | 24270545.45 | 0 | 137865755.15 | 320237282.8

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 04-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13686.96 | MW | 12:00 Hr. | Energy Generated |  |  | 320.2373 |  | MKWHr.
| Day Peak Demand |  |  | 13686.96 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.262 |  | MKWHr.
| Evening Peak Generation |  |  | 14784.67 | MW | 19:30 Hr. | Energy Demand |  |  | 320.4993 |  | MKWHr.
| Evening Peak Demand |  |  | 14820.67 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.4 |  | °C
| Minimum Generation of the Day |  |  | 11798.73 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1067.27 |  | MMCFD
| Maximum Generation of the Day |  |  | 14784.67 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.2127 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 50.5423 | 0 | 11.8736 | 0 | 0 | 0.18489 | 0 | 0 | 62.6008 | Gas | 146.8748 | Gas | 518804452.1973
| Chattogram Zone |  |  | 3.8629 | 35.8582 | 3.3181 | 0 | 0.96 | 0.1512 | 0 | 0.09648 | 44.2469 | Coal | 88.0104 | Coal | 584342291.6925
| Cumilla Zone |  |  | 26.7687 | 0 | 6.8565 | 0 | 0 | 0.42738 | 0.8352 | 0 | 34.8878 | HFO | 28.6633 | HFO | 539181774.05
| Mymensingh Zone |  |  | 0.43776 | 0 | 4.9039 | 0 | 0 | 0.31013 | 0 | 0 | 5.6518 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.9843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.9843 | Hydro | 0.96 | Hydro | 96000
| Khulna Zone |  |  | 0 | 10.4582 | 0.11808 | 0 | 0 | 0.60048 | 22.1404 | 0 | 33.3171 | Solar | 4.152 | Solar | 68125444.117
| Barishal Zone |  |  | 8.1856 | 36.6118 | 0.02592 | 0 | 0 | 0.0037605 | 0 | 0 | 44.8271 | Import | 51.4803 | Import | 277585585.9
| Rajshahi Zone |  |  | 22.0931 | 0 | 0.060768 | 0 | 0 | 0.90764 | 28.5047 | 0 | 51.5662 | Wind | 0.09648 | Wind | 1412467.2
| Rangpur Zone |  |  | 0 | 5.0823 | 1.5065 | 0 | 0 | 1.5666 | 0 | 0 | 8.1553
| Total |  |  | 146.8748 | 88.0104 | 28.6633 | 0 | 0.96 | 4.152 | 51.4803 | 0.09648 | 320.2373
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 518804452.1973 |  | Hydro | 96000
|  |  |  | Coal | 584342291.6925 |  | Solar | 68125444.117
|  |  |  | HFO | 539181774.05 |  | Import | 277585585.9
|  |  |  | HSD | 0 |  | Wind | 1412467.2
[5 empty] | Total: | 198,95,48,015 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1404 | Peak Hr Flow | 877.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 34114072.79 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.5047 | Peak Hr Flow | 1365.67 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 662 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8352 | Peak Hr Flow | 40.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 954 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 51.4803 | Peak Hr Flow | 2282.67 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 34 |  | 5355
|  |  |  | Chattogram |  | 0 |  | 1462
|  |  |  | Cumilla |  | 0 |  | 1334
|  |  |  | Mymensingh |  | 0 |  | 1195
|  |  |  | Sylhet |  | 0 |  | 607
|  |  |  | Khulna |  | 0 |  | 1649
|  |  |  | Barishal |  | 0 |  | 431
|  |  |  | Rajshahi |  | 0 |  | 1479
|  |  |  | Rangpur |  | 0 |  | 782
|  |  |  | Total |  | 34 |  | 14294
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:55 | 16:20 | Cumilla(N)-Kachua 132 kV Ckt-2 Scheduled S/D from Kachua 132/33kV end Due to fault find
out in line .
| 08:56 | 16:19 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to Line
checking
| 09:45 | 17:26 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to CB density
monitor and maintenance of local-remote switch
| 09:46 | 17:25 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to CB density
monitor and maintenance of local-remote switch
| 10:56 |  | Jamalpur-Mymensingh 132kV Ckt-1 Scheduled S/D from Jamalpur 132/33kV end Due to Work on
mymensingh grid and from Mymensingh 132/33kV end Due to Density monitor replace.
| 12:00 |  | Day Peak Gen. 13686 MW
|  | 13:01 | Faridpur 132/33kV S/S ATR-2 LT is restored.
|  | 15:18 | Bheramara 230/132kV S/S GTG (NW) is restored.
|  | 15:24 | Bheramara 230/132kV S/S STG (NW) is restored.
| 17:24 | 17:48 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Micom P142 relays Due to 33 kv
(BPBS-2)Feeder Fault
| 19:30 |  | Evening Peak Generation 14784 MW
| 04:41 | 05:08 | Sylhet 132/33kV S/S T2 HT Tripped showing OC -B phase relays Due to fault of 33 KV | [7 empty] | 20.0MW load
|  |  | Amborkhana-1 Feeder | [7 empty] | interrup.
| 04:41 | 05:09 | Sylhet 132/33kV S/S T2 LT Tripped showing OC -B phase relays Due to fault of 33 KV
Amborkhana-1 Feeder
| 06:06 |  | Ashuganj-Brahmanbaria 132kV Ckt-1 Forced S/D from Brahmanbaria 132/33kV end.
| 06:21 |  | Rampura-Ullon-2 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Command by
NLDC
| 06:26 |  | Aminbazar-Kaliakoir 230kV Ckt-1 Forced S/D from Kaliakoir 400/230/132kV end Due to by
NLDC
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 04-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 333 | 8596800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9464500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7129164 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 30 | 161511 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 225 | 5717175 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 95072 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 733680 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 115 | 2504160 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 481234 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 386068 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 529800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 425160 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 402720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 60 | 357796 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 115 | 2368224 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 764160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 84 | 788160 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 668160 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 184890 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 433440 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 9420909.09 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 460 | 9258813 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 110 | 1729200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3028 | 62600796.09
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 0 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 124875 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 147 | 3489490 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 40 | 201952 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 84 | 679634 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1761600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 373440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Engine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26324 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 674880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Engine Problem
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1120 | 24294543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 96480 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 11563636.36 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2214 | 44246854.36
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 4777000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8747700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 6044000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 803016 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1118400 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 2509090 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 843568 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 60 | 682472 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 432800 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 1469050 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1857600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 835200 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 198514 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 456910 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1051080 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 438480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 97 | 2195520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 427382 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1663 | 34887782
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 11 | 437760 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 168 | 2973600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 1536000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 298630 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 292800 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 101520 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 293 | 5651810
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 899000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 309303 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 99 | 2213018.2 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 704256 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 2046720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 171 | 4563500 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 73000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 151488 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7532500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 328 | 8797000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7694500 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1420 | 34984285.2
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 22140364 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 0 | 0 | Line fault
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 118080 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 600480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 505 | 10458180 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1399 | 33317104
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 322 | 6450264 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 25920 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 181532 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 105 | 2600000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1110 | 24270545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5404110 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5891000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3760.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2074 | 44827131.95
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | Engine Problem
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 200 | 4395091 | FGMO
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 194 | 4562536 | FGMO
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 193 | 4261664 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 380 | 8873818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | -
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 60768 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30000 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1365.67 | 28504727 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 357752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 519890 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2367.67 | 51566246
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 53 | 1063255 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 168 | 4019000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 443308 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40780.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 1063150 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 193780 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1332000 | -
Rangpur Area Total |  |  |  |  | 950 | 326 | 8155273.2
Eastern Grid Total |  |  |  |  | 16921.242 | 8618 | 182371527.65
Western Grid Total |  |  |  |  | 11614.5 | 6166.67 | 137865755.15
National Grid Total |  |  |  |  | 28535.742 | 14784.67 | 320237282.8
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 04-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9919.51 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4340.7 | MW
i) Dhaka area |  |  | 5321.27 |  | MW | i) Khulna area |  |  |  | 1649 | MW
ii) Chattogram area |  |  | 1462 |  | MW | ii) Barishal area |  |  |  | 431.1 | MW
iii) Cumilla area |  |  | 1334.24 |  | MW | iii) Rajshahi area |  |  |  | 1478.6 | MW
iv) Mymensingh area |  |  | 1195 |  | MW | iv) Rangpur area |  |  |  | 782 | MW
v) Sylhet area |  |  | 607 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14260.21 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 77 | 19:30 | 133 | Patuakhali | 70.1 | 21:00
2 | AKSML | 20 | 21:00 | 68 | Jaldhaka | 82 | 19:00 | 134 | Payra | 30 | 00:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jamalpur | 135 | 00:00 | 135 | Postogola | 55 | 12:00
4 | Agargaon | 125 | 13:00 | 70 | Jashore | 131 | 13:00 | 136 | Purbachal | 18 | 19:00
5 | Agrabad | 92 | 19:30 | 71 | Jhenaidah | 115 | 00:00 | 137 | Purbasadipur | 127 | 13:00
6 | Amnura | 45 | 20:00 | 72 | Joydebpur | 152 | 19:30 | 138 | Rahanpur | 29 | 00:00
7 | Ashuganj | 99 | 00:00 | 73 | Joypurhat | 73 | 00:00 | 139 | Rahim | 41 | 23:00
8 | BSRM | 198 | 04:00 | 74 | Juldah | 14 | 15:00 | 140 | Rajbari | 73 | 19:00
9 | Bagerhat | 83 | 20:00 | 75 | KSRM | 11 | 19:30 | 141 | Rajendrapur | 137 | 22:00
10 | Bajitpur | 49 | 20:00 | 76 | Kabirpur | 280 | 16:00 | 142 | Rajshahi | 116 | 00:00
11 | Bakulia | 91 | 19:00 | 77 | Kachua | 82 | 19:30 | 143 | Rajshahi-230 | 90 | 13:00
12 | Banani | 38 | 11:00 | 78 | Kallyanpur | 96 | 19:00 | 144 | Ramganj | 112 | 19:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kalurghat | 38 | 16:00 | 145 | Rampur | 40 | 00:00
14 | Barapukuria | 66 | 00:00 | 80 | Kamrangirchar | 68.8 | 13:00 | 146 | Rangamati | 16 | 19:30
15 | Barguna | 20 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 152 | 19:00
16 | Barishal | 95 | 19:00 | 82 | Kasba | 33 | 21:00 | 148 | Ruppur | 7.6 | 11:00
17 | Barishal-230 | 104 | 19:00 | 83 | Kazla | 91 | 01:00 | 149 | SSM | 15 | 06:00
18 | Baroaulia | 56 | 19:30 | 84 | Keranigonj | 76 | 13:00 | 150 | Saidpur | 115 | 14:00
19 | Baroirhat | 70 | 19:30 | 85 | Khagrachori | 30 | 19:00 | 151 | Satkhira | 129 | 00:00
20 | Bashundhara | 184 | 13:00 | 86 | Khulna | 63 | 09:00 | 152 | Satmasjid | 98 | 11:00
21 | BashundharaCement | 12 | 11:00 | 87 | Khulshi | 178 | 19:00 | 153 | Savar | 236 | 12:00
22 | Beanibazar | 74 | 19:00 | 88 | Kishoreganj | 133 | 19:30 | 154 | SevenRings | 7.79 | 03:00
23 | Benapole | 62 | 22:00 | 89 | Kodda | 307 | 18:30 | 155 | ShahCement | 19 | 08:00
24 | Bhaluka | 140 | 12:00 | 90 | Kulaura | 48 | 19:30 | 156 | Shahjadpur | 92 | 19:00
25 | Bhandaria | 50 | 00:00 | 91 | Kurigram | 66 | 19:00 | 157 | Shahjibazar | 115 | 19:00
26 | Bhangura | 41 | 19:00 | 92 | Kushtia | 148 | 00:00 | 158 | Shahmirpur | 57 | 00:00
27 | Bheramara(GK) | 62 | 19:30 | 93 | Lalbag | 65 | 12:00 | 159 | Shariatpur | 77 | 21:00
28 | Bhulta | 240 | 08:00 | 94 | Lalmonirhat | 65 | 19:00 | 160 | Sherpur | 152 | 19:30
29 | Bog-Sherpur | 64 | 00:00 | 95 | MI_Cement | 17.4 | 14:00 | 161 | Shikalbaha | 26 | 15:00
30 | Bogura | 162 | 00:00 | 96 | Madanganj | 50 | 17:00 | 162 | Shitalakhya | 80.4 | 13:00
31 | Borhanuddin | 80 | 00:00 | 97 | Madaripur | 95 | 19:00 | 163 | Sholosohor | 43 | 16:00
32 | Brahmanbaria | 116 | 23:00 | 98 | Madartek | 85.37 | 23:00 | 164 | Shyampur | 160 | 16:00
33 | Cantonment | 127 | 13:00 | 99 | Madunaghat | 53 | 22:00 | 165 | Siddhirganj | 117 | 15:00
34 | Chandina | 16.77 | 15:00 | 100 | Magura | 55 | 19:00 | 166 | Sirajganj | 122 | 19:30
35 | Chandpur | 66 | 22:00 | 101 | Mahasthangarh | 82 | 00:00 | 167 | Sonargaon | 126 | 18:30
36 | Chandraghona | 35 | 19:00 | 102 | Manikganj | 131 | 21:00 | 168 | Sreemongol | 76 | 21:00
37 | Chapai | 70 | 00:00 | 103 | Maniknagar | 72 | 13:00 | 169 | Sreepur | 105 | 19:30
38 | Charsaidpur | 39 | 00:00 | 104 | Matarbari | 49 | 19:00 | 170 | Srinagar | 42.2 | 21:00
39 | Chauddagram | 65 | 19:00 | 105 | Matuail | 72 | 15:00 | 171 | Sunamganj | 60 | 21:00
40 | Chhatak | 40 | 20:00 | 106 | Millgate | 108 | 15:00 | 172 | Sylhet | 51 | 22:00
41 | Chowmuhani | 219 | 20:00 | 107 | Mirpur | 123 | 11:00 | 173 | Sylhet-132 | 137 | 18:30
42 | Chuadanga | 107 | 19:30 | 108 | Mirsorai | 10 | 15:00 | 174 | TK | 33.6 | 23:00
43 | Coxsbazar | 136 | 19:30 | 109 | Mirzapur | 45 | 02:00 | 175 | Tangail | 194 | 19:30
44 | Cumilla(N) | 139 | 21:00 | 110 | Mithapukur | 58 | 19:00 | 176 | Thakurgaon | 102 | 00:00
45 | Cumilla(S) | 166 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 116 | 11:00
46 | Daudkandi | 150 | 21:00 | 112 | Mogbazar | 148.1 | 15:00 | 178 | Ullahpara | 45 | 19:00
47 | Dhaka | 60 | 11:00 | 113 | Mongla | 49 | 19:00 | 179 | Ullon | 42 | 19:30
48 | Dhamrai | 132 | 19:00 | 114 | Motijheel | 40 | 13:00 | 180 | Uttara | 81 | 11:00
49 | Dhanmondi | 149 | 13:00 | 115 | Muktagacha | 34 | 19:00 | 181 | UttaraNew | 46 | 22:00
50 | Dohazari | 99 | 19:30 | 116 | Munshiganj | 102 | 21:00 | 182 | Zigatola | 72 | 13:00
51 | Faridpur | 142 | 20:00 | 117 | Muradnagar | 27 | 18:00
52 | Fatullah | 101 | 12:00 | 118 | Mymensingh | 193 | 20:00
53 | Fenchuganj | 40 | 19:00 | 119 | Naogaon | 136 | 00:00
54 | Feni | 104 | 19:00 | 120 | Narail | 49 | 19:00
55 | GPH | 21 | 03:00 | 121 | Narinda | 77.5 | 13:00
56 | Ghatail | 78 | 19:00 | 122 | Narshingdi | 179 | 20:00
57 | Ghorashal | 17 | 15:00 | 123 | Natore | 153 | 20:00
58 | Ghorashal-230 | 95 | 21:00 | 124 | Nawabganj | 51.8 | 22:00
59 | Goalpara | 36 | 19:30 | 125 | Netrakona | 123 | 19:30
60 | Gollamari | 94 | 00:00 | 126 | New | 86 | 15:00
61 | Gopalganj | 95 | 19:00 | 127 | Niamatpur | 87 | 00:00
62 | Gulshan | 116 | 13:00 | 128 | Noapara | 44 | 19:00
63 | Halishahar | 80.5 | 15:00 | 129 | PHP | 8 | 20:00
64 | HaripurSBU | 162 | 19:30 | 130 | Pabna | 114 | 19:30
65 | Hasnabad | 76 | 20:00 | 131 | Palashbari | 114 | 00:00
66 | Hathazari | 77 | 19:00 | 132 | Panchagarh | 61 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 04-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14147.19 | 0 |  | 14147.19
1:00 | 13515.46 | 0 |  | 13515.46
2:00 | 13217.41 | 0 |  | 13217.41
3:00 | 12759.19 | 0 |  | 12759.19
4:00 | 12319.14 | 0 |  | 12319.14
5:00 | 12115.69 | 0 |  | 12115.69
6:00 | 11798.73 | 0 |  | 11798.73
7:00 | 11960.84 | 0 |  | 11960.84
8:00 | 11977.4 | 0 |  | 11977.4
9:00 | 12560.49 | 0 |  | 12560.49
10:00 | 13079.34 | 0 |  | 13079.34
11:00 | 13363.15 | 0 |  | 13363.15
12:00 | 13686.96 | 0 |  | 13686.96
13:00 | 13828.39 | 0 |  | 13828.39
14:00 | 13254.22 | 0 |  | 13254.22
15:00 | 13251.61 | 50 |  | 13303.61
16:00 | 13035.17 | 55 |  | 13092.17
17:00 | 12842.7 | 57 |  | 12902.7
18:00 | 12674.33 | 55 |  | 12731.33
19:00 | 14484.53 | 34 |  | 14520.53
19:30 | 14784.67 | 34 |  | 14820.67
20:00 | 14538.61 | 0 |  | 14538.61
21:00 | 14489.83 | 0 |  | 14489.83
22:00 | 14217.5 | 0 |  | 14217.5
23:00 | 14161.5 | 11 |  | 14172.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 04-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7743.8 | 6403.39 | 14147.19 | DAILY GENERATION CURVE
00:30 | 7619.4 | 6211.925 | 13831.325
01:00 | 7495 | 6020.46 | 13515.46 | 04-05-2025
01:30 | 7438.25 | 5928.185 | 13366.435
02:00 | 7381.5 | 5835.91 | 13217.41
02:30 | 7279 | 5709.3 | 12988.3
03:00 | 7176.5 | 5582.69 | 12759.19
03:30 | 6990.5 | 5548.665 | 12539.165
04:00 | 6804.5 | 5514.64 | 12319.14
04:30 | 6811.5 | 5405.915 | 12217.415
05:00 | 6818.5 | 5297.19 | 12115.69
05:30 | 6799.68 | 5157.53 | 11957.21
06:00 | 6780.86 | 5017.87 | 11798.73
06:30 | 6837.895 | 5041.89 | 11879.785
07:00 | 6894.93 | 5065.91 | 11960.84
07:30 | 6895.68 | 5073.44 | 11969.12
08:00 | 6896.43 | 5080.97 | 11977.4
08:30 | 7053.095 | 5215.85 | 12268.945
09:00 | 7209.76 | 5350.73 | 12560.49
09:30 | 7383.135 | 5436.78 | 12819.915
10:00 | 7556.51 | 5522.83 | 13079.34
10:30 | 7602.38 | 5618.865 | 13221.245
11:00 | 7648.25 | 5714.9 | 13363.15
11:30 | 7647.185 | 5877.87 | 13525.055
12:00 | 7646.12 | 6040.84 | 13686.96
12:30 | 7713.34 | 6044.335 | 13757.675
13:00 | 7780.56 | 6047.83 | 13828.39
13:30 | 7613.13 | 5928.175 | 13541.305
14:00 | 7445.7 | 5808.52 | 13254.22
14:30 | 7420.3 | 5832.615 | 13252.915
15:00 | 7394.9 | 5856.71 | 13251.61
15:30 | 7360.92 | 5782.47 | 13143.39
16:00 | 7326.94 | 5708.23 | 13035.17
16:30 | 7313 | 5625.935 | 12938.935
17:00 | 7299.06 | 5543.64 | 12842.7
17:30 | 7301.435 | 5457.08 | 12758.515
18:00 | 7303.81 | 5370.52 | 12674.33
18:30 | 7873.405 | 5706.025 | 13579.43
19:00 | 8443 | 6041.53 | 14484.53
19:30 | 8618 | 6166.67 | 14784.67
20:00 | 8460 | 6078.61 | 14538.61
20:30 | 8448.75 | 6065.47 | 14514.22 |  | Executive Engineer
21:00 | 8437.5 | 6052.33 | 14489.83 |  | Network Operation Division
21:30 | 8378.5 | 5975.165 | 14353.665
22:00 | 8319.5 | 5898 | 14217.5
22:30 | 8246.5 | 5943 | 14189.5
23:00 | 8173.5 | 5988 | 14161.5

## En-Curve
QF-LDC-12
Date | 04-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3411 | 2567.8 | 906 | 0 | 40 | 1372.39 | 40 | 4287 | 0 | 370 | 1153 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3352.5 | 2561.9 | 906 | 0 | 39.5 | 1338.925 | 40 | 4202 | 0 | 379 | 1011.5 | 0 | 0 | 0 | 0 | 04-05-2025
01:00 | 3294 | 2556 | 906 | 0 | 39 | 1305.46 | 40 | 4117 | 0 | 388 | 870 | 0 | 0 | 0 | 0
01:30 | 3301.5 | 2560.75 | 913.5 | 0 | 37.5 | 1311.685 | 40 | 4016 | 0 | 371 | 814 | 0 | 0 | 0.5 | 0 | Energy Generated | 320.2373 |  | MKWHr
02:00 | 3309 | 2565.5 | 921 | 0 | 36 | 1317.91 | 40 | 3915 | 0 | 354 | 758 | 0 | 0 | 1 | 0 | Energy not Served | 0.262 |  | MKWHr
02:30 | 3307 | 2556.5 | 921.5 | 0 | 36 | 1290.3 | 40 | 3821.5 | 0 | 345 | 669.5 | 0 | 0 | 1 | 0 | Total Energy Requirement | 320.4993 |  | MKWHr
03:00 | 3305 | 2547.5 | 922 | 0 | 36 | 1262.69 | 40 | 3728 | 0 | 336 | 581 | 0 | 0 | 1 | 0
03:30 | 3307.5 | 2541 | 922 | 0 | 35 | 1258.165 | 40 | 3628 | 0 | 256.5 | 549.5 | 0 | 0 | 1.5 | 0
04:00 | 3310 | 2534.5 | 922 | 0 | 34 | 1253.64 | 40 | 3528 | 0 | 177 | 518 | 0 | 0 | 2 | 0
04:30 | 3329.5 | 2539 | 922 | 0 | 34 | 1238.915 | 40 | 3446.5 | 0 | 167 | 498.5 | 0 | 0 | 2 | 0
05:00 | 3349 | 2543.5 | 922 | 0 | 34 | 1224.19 | 40 | 3365 | 0 | 157 | 479 | 0 | 0 | 2 | 0
05:30 | 3368.5 | 2526 | 922 | 0 | 33 | 1126.855 | 40 | 3307 | 15.355 | 165 | 449.5 | 0 | 0 | 4 | 0
06:00 | 3388 | 2508.5 | 922 | 0 | 32 | 1029.52 | 40 | 3249 | 30.71 | 173 | 420 | 0 | 0 | 6 | 0
06:30 | 3443 | 2517 | 922 | 0 | 31 | 1025.615 | 40 | 3232 | 77.67 | 191 | 394.5 | 0 | 0 | 6 | 0
07:00 | 3498 | 2525.5 | 922 | 0 | 30 | 1021.71 | 40 | 3215 | 124.63 | 209 | 369 | 0 | 0 | 6 | 0
07:30 | 3529.5 | 2518.75 | 898.5 | 0 | 30 | 969.455 | 40 | 3171 | 202.915 | 208.5 | 397.5 | 0 | 0 | 3 | 0
08:00 | 3561 | 2512 | 875 | 0 | 30 | 917.2 | 40 | 3127 | 281.2 | 208 | 426 | 0 | 0 | 0 | 0
08:30 | 3639 | 2539 | 875 | 0 | 30 | 918.43 | 40 | 3176 | 359.015 | 234 | 458 | 0 | 0 | 0.5 | 0
09:00 | 3717 | 2566 | 875 | 0 | 30 | 919.66 | 40 | 3225 | 436.83 | 260 | 490 | 0 | 0 | 1 | 0
09:30 | 3720.5 | 2584.5 | 898.5 | 0 | 30 | 918.73 | 40 | 3343.5 | 487.685 | 249.5 | 546.5 | 0 | 0 | 0.5 | 0
10:00 | 3724 | 2603 | 922 | 0 | 30 | 917.8 | 40 | 3462 | 538.54 | 239 | 603 | 0 | 0 | 0 | 0
10:30 | 3710.5 | 2540 | 922 | 0 | 31 | 968.805 | 40 | 3537.5 | 598.44 | 231.5 | 641.5 | 0 | 0 | 0 | 0
11:00 | 3697 | 2477 | 922 | 0 | 32 | 1019.81 | 40 | 3613 | 658.34 | 224 | 680 | 0 | 0 | 0 | 0
11:30 | 3679 | 2450 | 922.5 | 0 | 34 | 1117.83 | 40 | 3699 | 615.225 | 224 | 743 | 0 | 0 | 0.5 | 0
12:00 | 3661 | 2423 | 923 | 0 | 36 | 1215.85 | 40 | 3785 | 572.11 | 224 | 806 | 0 | 0 | 1 | 0
12:30 | 3638.5 | 2400 | 923 | 0 | 37 | 1261.49 | 40 | 3802.5 | 518.185 | 252 | 876.5 | 0 | 0 | 8.5 | 0
13:00 | 3616 | 2377 | 923 | 0 | 38 | 1307.13 | 40 | 3820 | 464.26 | 280 | 947 | 0 | 0 | 16 | 0
13:30 | 3607.5 | 2274.25 | 922.5 | 0 | 37 | 1312.54 | 40 | 3699 | 395.515 | 265.5 | 973.5 | 0 | 0 | 14 | 0
14:00 | 3599 | 2171.5 | 922 | 0 | 36 | 1317.95 | 40 | 3578 | 326.77 | 251 | 1000 | 0 | 0 | 12 | 0
14:30 | 3648.5 | 2209.25 | 923 | 0 | 33 | 1315.62 | 40 | 3489.5 | 334.545 | 219.5 | 1030 | 0 | 0 | 10 | 25
15:00 | 3698 | 2247 | 924 | 0 | 30 | 1313.29 | 40 | 3401 | 342.32 | 188 | 1060 | 0 | 0 | 8 | 50
15:30 | 3694 | 2243.75 | 924 | 0 | 32 | 1290.75 | 40 | 3403.5 | 282.39 | 175 | 1051 | 0 | 0 | 7 | 52.5
16:00 | 3690 | 2240.5 | 924 | 0 | 34 | 1268.21 | 40 | 3406 | 222.46 | 162 | 1042 | 0 | 0 | 6 | 55
16:30 | 3671 | 2248.25 | 924 | 0 | 34 | 1241.93 | 40 | 3406 | 171.255 | 162 | 1032 | 0 | 0 | 8.5 | 56
17:00 | 3652 | 2256 | 924 | 0 | 34 | 1215.65 | 40 | 3406 | 120.05 | 162 | 1022 | 0 | 0 | 11 | 57
17:30 | 3612 | 2217.5 | 924 | 0 | 34 | 1218.79 | 40 | 3382 | 68.225 | 191 | 1059.5 | 0 | 0 | 11.5 | 56
18:00 | 3572 | 2179 | 924 | 0 | 34 | 1221.93 | 40 | 3358 | 16.4 | 220 | 1097 | 0 | 0 | 12 | 55
18:30 | 3666 | 2375 | 904.5 | 0 | 37 | 1295.23 | 40 | 3677 | 8.2 | 302.5 | 1268 | 0 | 0 | 6 | 44.5
19:00 | 3760 | 2571 | 885 | 0 | 40 | 1368.53 | 40 | 3996 | 0 | 385 | 1439 | 0 | 0 | 0 | 34
19:30 | 3718 | 2573 | 877 | 0 | 40 | 1365.67 | 40 | 4160 | 0 | 426 | 1585 | 0 | 0 | 0 | 34
20:00 | 3715 | 2497 | 877 | 0 | 40 | 1369.61 | 40 | 4064 | 0 | 450 | 1486 | 0 | 0 | 0 | 0
20:30 | 3757 | 2476.75 | 900 | 0 | 40 | 1367.47 | 40 | 4038.5 | 0 | 452.5 | 1442 | 0 | 0 | 0 | 0
21:00 | 3799 | 2456.5 | 923 | 0 | 40 | 1365.33 | 40 | 4013 | 0 | 455 | 1398 | 0 | 0 | 0 | 0
21:30 | 3830.5 | 2466.5 | 922.5 | 0 | 40 | 1358.165 | 40 | 3916.5 | 0 | 446 | 1333.5 | 0 | 0 | 0 | 0
22:00 | 3862 | 2476.5 | 922 | 0 | 40 | 1351 | 40 | 3820 | 0 | 437 | 1269 | 0 | 0 | 0 | 0
22:30 | 3870 | 2456.5 | 921.5 | 0 | 40 | 1352 | 40 | 3852.5 | 0 | 424 | 1232 | 0 | 0 | 1 | 5.5
23:00 | 3878 | 2436.5 | 921 | 0 | 40 | 1353 | 40 | 3885 | 0 | 411 | 1195 | 0 | 0 | 2 | 11
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 04-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 387 | 06:00 | 373 | 12:00 | Payra | 413 | 06:00 | 406 | 19:00
Ashuganj | N/A | N/A | N/A | N/A | Rahanpur | 401 | 09:00 | 389 | 20:00
Bhulta | 396 | 06:00 | 376 | 12:00 | Rampal | 400 | 08:00 | 385 | 19:00
Bibiana | 393 | 07:00 | 385 | 12:00
BIPTC | 399 | 08:00 | 390 | 00:00
Bogura | 387 | 09:00 | 374 | 00:00
Gopalganj | 396 | 06:00 | 383 | 19:00
Kaliakoir | 377 | 07:00 | 362 | 12:00
Madunaghat | 394 | 06:00 | 385 | 13:00
Meghnaghat | 392 | 06:00 | 348 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 06:00 | 216 | 12:00 | Keranigonj | 225 | 06:00 | 214 | 12:00
AKSML | 225 | 06:00 | 219 | 19:00 | Khulna(S) | 230 | 08:00 | 216 | 19:00
Aminbazar | 228 | 08:00 | 216 | 13:00 | Madunaghat | 227 | 06:00 | 221 | 12:00
Ashuganj | 231 | 06:00 | 222 | 12:00 | Madunaghat-400 | 227 | 06:00 | 221 | 13:00
Ashuganj-400 | 231 | 06:00 | 222 | 12:00 | Maniknagar | 224 | 05:00 | 212 | 12:00
Baghabari | 234 | 05:00 | 226 | 20:00 | Meghnaghat | 232 | 05:00 | 221 | 12:00
Barapukuria | 225 | 05:00 | 218 | 13:00 | Meghnaghat-400 | 227 | 06:00 | 2 | 22:00
Barapukuria-230 | 225 | 05:00 | 218 | 13:00 | Mirsorai | 225 | 06:00 | 216 | 13:00
Barishal | 237 | 06:00 | 229 | 19:00 | Rajshahi | 235 | 05:00 | 222 | 12:00
Bheramara | 235 | 18:00 | 222 | 12:00 | Rampal | 228 | 05:00 | 217 | 19:00
Bhulta | 224 | 05:00 | 212 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 05:00 | 218 | 12:00 | Rampura | 224 | 06:00 | 210 | 12:00
BIPTC | 236 | 02:00 | 222 | 12:00 | Shikalbaha | 225 | 08:00 | 220 | 12:00
Bogura | 235 | 18:00 | 227 | 00:00 | Shyampur | 226 | 07:00 | 215 | 12:00
Bogura-400 | 235 | 18:00 | 227 | 13:00 | Siddhirganj | 226 | 06:00 | 214 | 12:00
Borhanuddin | 240 | 04:00 | 236 | 00:00 | Sirajgonj | 240 | 07:00 | 234 | 12:00
BSRM | 225 | 06:00 | 216 | 12:00 | Sreepur | 230 | 16:00 | 220 | 12:00
Cumilla(N) | 222 | 06:00 | 214 | 12:00 | Tongi | 225 | 07:00 | 212 | 11:00
Faridpur | 232 | 06:00 | 224 | 19:00
Fenchuganj | 225 | 18:00 | 220 | 02:00
Ghorashal | 230 | 00:00 | 220 | 11:00
Ghorashal-230 | 226 | 06:00 | 214 | 12:00
Gopalganj | 234 | 06:00 | 226 | 19:00
GPH | 226 | 06:00 | 218 | 12:00
Haripur | 225 | 06:00 | 214 | 12:00
Hasnabad | 223 | 06:00 | 214 | 11:00
Hathazari | 227 | 06:00 | 221 | 12:00
Ishurdi | 236 | 08:00 | 224 | 19:30
Jhenaidah | 230 | 18:00 | 214 | 19:30
Kaliakoir | 232 | 07:00 | 220 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 03:00 | 124 | 12:00 | Madartek | 134 | 06:00 | 124 | 12:00
Agargaon | 134 | 05:00 | 126 | 12:00 | Madunaghat | 130 | 05:00 | 126 | 12:00
Agrabad | 130 | 05:00 | 123 | 11:00 | Magura | 134 | 09:00 | 124 | 19:00
AKS | 126 | 06:00 | 123 | 12:00 | Mahasthangarh | 136 | 18:00 | 129 | 00:00
Aminbazar | 132 | 08:00 | 125 | 10:00 | Manikganj | 130 | 06:00 | 115 | 21:00
Amnura | 136 | 09:00 | 121 | 21:00 | Maniknagar | 132 | 05:00 | 123 | 12:00
Ashuganj | 136 | 07:00 | 132 | 13:00 | Matarbari | 116 | 08:00 | 109 | 19:00
Bagerhat | 132 | 07:00 | 120 | 19:00 | Matuail | 131 | 04:00 | 123.5 | 12:00
Bajitpur | 131 | 05:00 | 124 | 00:00 | Millgate | 131 | 07:00 | 122 | 12:00
Bakulia | 130 | 20:00 | 124 | 12:00 | Mirpur | 131 | 05:00 | 123 | 11:00
Banani | 133 | 04:00 | 122 | 12:00 | Mirzapur | 132 | 08:00 | 125 | 12:00
Bangabhaban | 131 | 03:00 | 123 | 12:00 | Mithapukur | 134 | 18:00 | 121 | 21:00
Barapukuria | 136 | 18:00 | 126 | 07:00 | MI_Cement | 131 | 07:00 | 71 | 18:30
Barguna | 134 | 06:00 | 130 | 00:00 | Modern | 0 | 0:00 | 0 | 0:00
Barishal | 132 | 05:00 | 126 | 00:00 | Mogbazar | 135 | 05:00 | 125 | 12:00
Barishal-230 | 131 | 04:00 | 126 | 19:00 | Mongla | 132 | 08:00 | 119 | 19:00
Baroaulia | 131 | 03:00 | 124 | 12:00 | Motijheel | 131 | 03:00 | 123 | 12:00
Baroirhat | 121 | 20:00 | 115 | 11:00 | Muktagacha | 132 | 08:00 | 125 | 12:00
Bashundhara | 134 | 05:00 | 121 | 13:00 | Munshiganj | 130 | 05:00 | 123 | 11:00
BashundharaCement | 129 | 04:00 | 123 | 12:00 | Muradnagar | 126 | 06:00 | 119 | 12:00
Beanibazar | 129 | 06:00 | 124 | 19:00 | Mymensingh | 135 | 18:00 | 115 | 19:30
Benapole | 132 | 16:00 | 120 | 19:30 | Naogaon | 136 | 18:00 | 125 | 00:00
Bhaluka | 131 | 15:00 | 122 | 12:00 | Narail | 136 | 04:00 | 123 | 19:00
Bhandaria | 125 | 07:00 | 119 | 00:00 | Narinda | 132 | 05:00 | 123 | 12:00
Bhangura | 133 | 05:00 | 127 | 12:00 | Narshingdi | 126 | 07:00 | 116 | 00:00
Bheramara | 136 | 18:00 | 128 | 12:00 | Natore | 135 | 15:00 | 127 | 20:00
Bheramara(GK) | 135 | 18:00 | 127 | 12:00 | Nawabganj | 135 | 06:00 | 127 | 12:00
Bhulta | 124 | 02:00 | 117 | 12:00 | Netrakona | 126 | 15:00 | 113 | 19:00
Bog-Sherpur | 136 | 18:00 | 129 | 12:00 | New | 131 | 04:00 | 122 | 12:00
Bogura | 139 | 18:00 | 132 | 00:00 | Niamatpur | 132 | 06:00 | 127 | 00:00
Bogura-230 | 139 | 18:00 | 132 | 12:00 | Noapara | 135 | 18:00 | 124 | 19:00
Brahmanbaria | 128 | 05:00 | 121 | 00:00 | Pabna | 135 | 15:00 | 128 | 12:00
Cantonment | 134 | 06:00 | 125 | 12:00 | Palashbari | 131 | 18:00 | 124 | 12:00
Chandina | 127 | 18:00 | 121 | 11:00 | Panchagarh | 136 | 19:00 | 117 | 07:00
Chandpur | 124 | 00:00 | 117 | 11:00 | Patuakhali | 134 | 04:00 | 130 | 19:00
Chandraghona | 131 | 06:00 | 127 | 01:00 | Payra | 136 | 06:00 | 133 | 19:30
Chapai | 129 | 18:00 | 123 | 00:00 | PHP | 120 | 06:00 | 115 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 04:00 | 124 | 11:00 | Postogola | 133 | 06:00 | 126 | 11:00
Chauddagram | 121 | 05:00 | 116 | 11:00 | Purbachal | 134 | 05:00 | 124 | 12:00
Chhatak | 129 | 07:00 | 12 | 20:00 | Purbasadipur | 133 | 19:00 | 120 | 14:00
Chowmuhani | 117 | 18:00 | 111 | 11:00 | Rahanpur | 136 | 09:00 | 129 | 00:00
Chuadanga | 133 | 08:00 | 119 | 19:00 | Rahanpur-400 | 133 | 06:00 | 129 | 00:00
Coxsbazar | 120 | 05:00 | 110 | 18:30 | Rahim | 131 | 06:00 | 124 | 13:00
Cumilla(N) | 127 | 06:00 | 122 | 11:00 | Rajbari | 135 | 05:00 | 128 | 19:00
Cumilla(S) | 133 | 04:00 | 118 | 11:00 | Rajendrapur | 132 | 06:00 | 122 | 12:00
Daudkandi | 124 | 00:00 | 116 | 12:00 | Rajshahi | 135 | 15:00 | 128 | 12:00
Dhaka | 134 | 06:00 | 124 | 12:00 | Rajshahi-230 | 136 | 18:00 | 116 | 00:00
Dhamrai | 136 | 04:00 | 128 | 12:00 | Ramganj | 119 | 03:00 | 111 | 11:00
Dhanmondi | 135 | 05:00 | 125 | 12:00 | Rampur | 129 | 03:00 | 123 | 12:00
Dohazari | 125 | 06:00 | 121 | 12:00 | Rampura | 134 | 06:00 | 124 | 12:00
Faridpur | 135 | 04:00 | 130 | 19:30 | Rangamati | 130 | 06:00 | 125 | 12:00
Fatullah | 131 | 05:00 | 125 | 11:00 | Rangpur | 128 | 09:00 | 123 | 13:00
Fenchuganj | 136 | 07:00 | 130 | 01:00 | Ruppur | 138 | 03:00 | 131 | 19:00
Feni | 122 | 22:00 | 116 | 12:00 | Saidpur | 132 | 18:30 | 118 | 07:00
Ghatail | 130 | 04:00 | 121 | 12:00 | Satkhira | 133 | 18:00 | 120 | 19:00
Ghorashal | 134 | 03:00 | 130 | 18:00 | Satmasjid | 134 | 06:00 | 125 | 13:00
Goalpara | 137 | 08:00 | 124 | 19:30 | Savar | 130 | 06:00 | 123 | 11:00
Gollamari | 136 | 07:00 | 127 | 19:30 | SevenRings | 136 | 07:00 | 130 | 12:00
Gopalganj | 135 | 18:00 | 126 | 19:30 | ShahCement | 130 | 04:00 | 124 | 11:00
Gopalganj-400 | 136 | 06:00 | 130 | 19:00 | Shahjadpur | 137 | 03:00 | 132 | 12:00
Gulshan | 134 | 05:00 | 124 | 12:00 | Shahjibazar | 131 | 08:00 | 124 | 00:00
Halishahar | 129 | 05:00 | 123 | 12:00 | Shahmirpur | 130 | 20:00 | 126 | 12:00
Haripur | 131 | 05:00 | 124 | 12:00 | Shariatpur | 134 | 06:00 | 127 | 19:30
HaripurSBU | 131 | 05:00 | 125 | 11:00 | Sherpur | 135 | 18:00 | 124 | 01:00
Hasnabad | 132 | 03:00 | 125 | 12:00 | Shikalbaha | 120 | 04:00 | 115 | 11:00
Hathazari | 132 | 22:00 | 127 | 18:30 | Shikalbaha-230 | 131 | 07:00 | 126 | 13:00
Ishurdi | 139 | 08:00 | 132 | 19:00 | Shitalakhya | 131 | 07:00 | 124 | 11:00
Jaldhaka | 131 | 19:00 | 116 | 07:00 | Sholosohor | 129 | 05:00 | 126 | 12:00
Jamalpur | 138 | 18:00 | 127 | 01:00 | Shyampur | 130 | 01:00 | 124 | 12:00
Jashore | 133 | 18:00 | 121 | 19:30 | Shyampur-230 | 131 | 06:00 | 124 | 12:00
Jhenaidah | 134 | 09:00 | 124 | 19:00 | Siddhirganj | 131 | 05:00 | 124 | 12:00
Jhenaidah-230 | 135 | 09:00 | 124 | 19:30 | Sirajganj | 132 | 17:00 | 125 | 19:30
Joydebpur | 130 | 03:00 | 124 | 12:00 | Sonargaon | 128 | 04:00 | 121 | 12:00
Joypurhat | 133 | 18:00 | 119 | 00:00 | Sreemongol | 131 | 08:00 | 125 | 00:00
Juldah | 131 | 20:00 | 126 | 12:00 | Sreepur | 133 | 16:00 | 126 | 11:00
Kabirpur | 133 | 07:00 | 18 | 22:00 | Srinagar | 136 | 07:00 | 126 | 12:00
Kachua | 123 | 01:00 | 116 | 11:00 | SSM | 132 | 02:00 | 130 | 00:00
Kaliakoir | 139 | 06:00 | 130 | 12:00 | Sunamganj | 127 | 06:00 | 120 | 19:00
Kallyanpur | 132 | 06:00 | 125 | 13:00 | Sylhet | 131 | 07:00 | 126 | 19:00
Kalurghat | 130 | 05:00 | 126 | 11:00 | Sylhet-132 | 130 | 05:00 | 127 | 19:00
Kamrangirchar | 136 | 06:00 | 127 | 11:00 | Tangail | 129 | 08:00 | 122 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 138 | 19:00 | 124 | 14:00
Kasba | 125 | 06:00 | 118 | 11:00 | TK | 131 | 05:00 | 126 | 11:00
Kazla | 132 | 06:00 | 122 | 13:00 | Tongi | 133 | 07:00 | 124 | 11:00
Keranigonj | 136 | 06:00 | 127 | 12:00 | Ullahpara | 134 | 05:00 | 127 | 20:00
Khagrachori | 129 | 06:00 | 124 | 12:00 | Ullon | 134 | 06:00 | 124 | 12:00
Khulna | 135 | 08:00 | 124 | 19:30 | Uttara | 131 | 06:00 | 123 | 11:00
Khulna(S) | 137 | 08:00 | 127 | 19:00 | UttaraNew | 131 | 06:00 | 123 | 11:00
Khulshi | 128 | 22:00 | 122 | 12:00 | Zigatola | 136 | 08:00 | 127 | 12:00
Kishoreganj | 130 | 15:00 | 121 | 19:30
Kodda | 132 | 08:00 | 123 | 10:00
KSRM | 129 | 04:00 | 124 | 12:00
Kulaura | 133 | 06:00 | 129 | 19:00
Kurigram | 132 | 18:00 | 121 | 19:00
Kushtia | 134 | 08:00 | 125 | 19:00
Lalbag | 136 | 07:00 | 126 | 12:00
Lalmonirhat | 127 | 05:00 | 122 | 07:00
Madanganj | 129 | 04:00 | 123 | 12:00
Madaripur | 134 | 05:00 | 128 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division