## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 06-05-2025 | [28 empty] | Date: | 06-05-2025 | [28 empty] | Date: | 06-05-2025 | [28 empty] | Date: | 06-05-2025 | [28 empty] | Date: | 06-05-2025 | [16 empty] | Date: | 06-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 35 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17 | 17 | 115 | 145 | 125 | 0 | 35 | 90 | 0 | 50 | 450 | 303 | 400 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 108 | 18 | 19 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 70 | 20 | 0 | 40 | 0 | 26 | 575 | 0 | 0 | 0 | 8 | 0 | 149 | 0 | 0 | 0 | 1163 | 0 | 43 | 40 | 26 | 0 | 350 | 345 | 51 | 196 | 37 | 115 | 50 | 150 | 11 | 20 | 114 | 46 | 25 | 0 | 30 | 305 | 320 | 373 | 39 | 30 | 0 | 97 | 8 | 0 | 86 | 20 | 0 | 18 | 173 | 54.5 | 48 | 95 | 0 | 0 | 0 | 8 | 8381.5 | 924 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552 | 17 | 1352 | 0 | 0 | 0 | 35 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 139 | 0 | 140 | 0 | 414 | 0 | 0 | 0 | 165 | 53 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 220 | 1150 | 0 | 6098 | 14479.5 | 79.21
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 17 | 115 | 112 | 30 | 0 | 35 | 54 | 0 | 50 | 450 | 290 | 400 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 90 | 19 | 19 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 68 | 0 | 0 | 70 | 20 | 0 | 40 | 0 | 26 | 575 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 1150 | 0 | 43 | 40 | 26 | 0 | 359 | 345 | 51 | 182 | 37 | 115 | 50 | 155 | 9 | 20 | 114 | 42 | 25 | 0 | 30 | 305 | 320 | 357 | 39 | 30 | 0 | 98 | 8 | 0 | 86 | 20 | 0 | 18 | 173 | 54.5 | 49 | 95 | 0 | 0 | 0 | 12 | 8146.5 | 925 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 17 | 1360 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 138 | 0 | 138 | 0 | 414 | 0 | 0 | 0 | 162 | 52 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 220 | 1120 | 0 | 6014 | 14160.5 | 79.2
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17 | 17 | 113 | 112 | 0 | 0 | 17 | 0 | 0 | 50 | 450 | 303 | 400 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 90 | 19 | 19 | 0 | 400 | 0 | 0 | 0 | 0 | 3 | 51 | 0 | 0 | 70 | 20 | 0 | 40 | 0 | 20 | 504 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 1106 | 0 | 43 | 0 | 26 | 0 | 357 | 345 | 51 | 198 | 37 | 115 | 50 | 155 | 9 | 20 | 114 | 40 | 25 | 0 | 30 | 300 | 320 | 381 | 39 | 30 | 0 | 97 | 6 | 0 | 86 | 25 | 0 | 18 | 173 | 22 | 49 | 95 | 0 | 0 | 0 | 12 | 7857 | 924 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519 | 0 | 1319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 135 | 0 | 134 | 0 | 414 | 0 | 0 | 0 | 162 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 11 | 115 | 220 | 0 | 221 | 1050 | 0 | 5872 | 13729 | 79.2
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 17 | 113 | 112 | 0 | 0 | 0 | 0 | 0 | 34 | 450 | 298 | 400 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 70 | 19 | 19 | 0 | 400 | 0 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 70 | 20 | 0 | 40 | 0 | 24 | 504 | 0 | 0 | 0 | 8 | 0 | 150 | 0 | 0 | 0 | 1105 | 0 | 43 | 0 | 26 | 0 | 356 | 345 | 53 | 195 | 37 | 115 | 50 | 155 | 9 | 20 | 114 | 38 | 0 | 0 | 30 | 310 | 320 | 357 | 39 | 30 | 0 | 102 | 6 | 0 | 86 | 25 | 0 | 18 | 173 | 17 | 48 | 95 | 0 | 0 | 0 | 12 | 7733 | 924 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 1272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 135 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 109 | 220 | 0 | 220 | 1050 | 0 | 5563 | 13296 | 79.19
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 99 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 450 | 298 | 400 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 70 | 19 | 19 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 48 | 20 | 0 | 40 | 0 | 24 | 504 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1050 | 0 | 43 | 0 | 26 | 0 | 359 | 345 | 52 | 196 | 37 | 115 | 50 | 155 | 9 | 20 | 70 | 38 | 0 | 0 | 0 | 310 | 320 | 360 | 39 | 30 | 0 | 99 | 6 | 0 | 86 | 25 | 0 | 18 | 173 | 17 | 49 | 95 | 0 | 0 | 0 | 12 | 7494 | 925 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 1179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 144 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 115 | 220 | 0 | 221 | 1000 | 0 | 5444 | 12938 | 79.19
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 88 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 302 | 400 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 19 | 19 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 24 | 503 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 1005 | 0 | 43 | 0 | 26 | 0 | 354 | 345 | 52 | 199 | 37 | 115 | 50 | 136 | 9 | 20 | 70 | 34 | 0 | 0 | 0 | 315 | 320 | 384 | 39 | 30 | 0 | 99 | 6 | 0 | 86 | 25 | 0 | 18 | 173 | 0 | 49 | 95 | 0 | 0 | 0 | 12 | 7198 | 925 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 452 | 0 | 1162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 145 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 109 | 220 | 0 | 221 | 950 | 0 | 5384 | 12582 | 79.18
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 0 | 17 | 79 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 292 | 400 | 0 | 0 | 0 | 225 | 0 | 0 | 2 | 0 | 19 | 19 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 33 | 455 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 950 | 1 | 43 | 0 | 26 | 0 | 350 | 345 | 53 | 191 | 37 | 104 | 50 | 120 | 9 | 20 | 52 | 34 | 0 | 3 | 0 | 305 | 320 | 359 | 39 | 30 | 0 | 98 | 6 | 0 | 86 | 30 | 0 | 18 | 173 | 0 | 49 | 94 | 0 | 0 | 2.36 | 3 | 6997.36 | 925 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 406 | 0 | 1065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.03 | 150 | 0 | 141 | 0 | 0 | 0 | 350 | 0 | 0.19 | 0 | 166 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.04 | 0 | 250 | 8 | 111 | 220 | 0 | 221 | 900 | 0 | 5152.26 | 12149.62 | 79.18
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 82 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 350 | 286 | 340 | 0 | 0 | 0 | 225 | 0 | 0 | 7 | 0 | 18 | 19 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 1 | 40 | 0 | 31 | 456 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 950 | 5 | 43 | 0 | 26 | 0 | 320 | 345 | 53 | 182 | 37 | 72 | 51 | 100 | 9 | 20 | 34 | 30 | 0 | 10 | 0 | 295 | 320 | 350 | 39 | 30 | 0 | 96 | 6 | 0 | 86 | 30 | 0 | 18 | 173 | 0 | 78 | 113 | 0 | 0 | 10.68 | 12 | 6851.68 | 924 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 406 | 0 | 1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 10.89 | 155 | 0 | 143 | 0 | 0 | 0 | 300 | 0 | 0.88 | 0 | 163 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0.15 | 0 | 200 | 7 | 115 | 180 | 0 | 221 | 850 | 0 | 5015.92 | 11867.6 | 79.17
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 17 | 113 | 98 | 0 | 0 | 9 | 0 | 0 | 16 | 320 | 301 | 340 | 0 | 0 | 0 | 225 | 0 | 0 | 15 | 17 | 18 | 19 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 3 | 40 | 0 | 8 | 455 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 900 | 10 | 43 | 0 | 26 | 0 | 351 | 345 | 53 | 195 | 34 | 72 | 50 | 68 | 9 | 20 | 34 | 34 | 0 | 38 | 0 | 310 | 320 | 368 | 39 | 30 | 0 | 97 | 6 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 77 | 113 | 0 | 1 | 21.24 | 12 | 6887.24 | 878 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 407 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 27.7 | 160 | 0 | 168 | 0 | 0 | 0 | 300 | 0 | 2.18 | 0 | 159 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0.32 | 0 | 200 | 7 | 115 | 180 | 0 | 221 | 834 | 0 | 5008.2 | 11895.44 | 79.17
09:00 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 17 | 119 | 96 | 0 | 0 | 11 | 0 | 0 | 16 | 320 | 278 | 380 | 0 | 0 | 0 | 225 | 0 | 0 | 21 | 43 | 17.5 | 18 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 60 | 0 | 4 | 40 | 0 | 3 | 504 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 950 | 15 | 43 | 0 | 26 | 0 | 346 | 345 | 50 | 202 | 33 | 72 | 50 | 68 | 9 | 20 | 34 | 34 | 0 | 50 | 0 | 310 | 320 | 384 | 39 | 30 | 0 | 105 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 77 | 112 | 0 | 1 | 16.73 | 12 | 7168.23 | 869 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.74 | 404 | 0 | 1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 23.79 | 173 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 3.05 | 0 | 161 | 54 | 0 | 4 | 0 | 0 | 0 | 0 | 58 | 0.56 | 0 | 250 | 7 | 115 | 220 | 0 | 221 | 854 | 0 | 5321.14 | 12489.37 | 79.16
10:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 17 | 124 | 96 | 0 | 0 | 29 | 25 | 0 | 16 | 320 | 294 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 28 | 84 | 17.5 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 65 | 0 | 4 | 40 | 0 | 3 | 505 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1000 | 7 | 43 | 0 | 26 | 0 | 342 | 345 | 49 | 197 | 33 | 72 | 50 | 68 | 9 | 20 | 31 | 34 | 0 | 64 | 0 | 310 | 320 | 370 | 38 | 30 | 0 | 103 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 76 | 112 | 0 | 1 | 40.61 | 12 | 7344.11 | 917 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.18 | 383 | 0 | 1069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 17.92 | 170 | 0 | 162 | 0 | 0 | 0 | 414 | 0 | 2.62 | 0 | 167 | 54 | 0 | 6 | 0 | 0 | 0 | 0 | 50 | 0.68 | 0 | 250 | 7 | 115 | 220 | 0 | 220 | 894 | 0 | 5392.4 | 12736.51 | 79.16
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 12 | 17 | 113 | 95 | 15 | 0 | 35 | 35 | 0 | 16 | 320 | 293 | 350 | 0 | 17 | 0 | 227 | 0 | 0 | 32 | 90 | 17.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 1 | 17 | 0 | 0 | 76 | 10 | 5 | 40 | 0 | 2 | 502 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1000 | 11 | 43 | 15 | 26 | 0 | 346 | 345 | 48 | 193 | 33 | 88 | 50 | 91 | 9 | 20 | 30 | 36 | 2 | 67 | 0 | 315 | 320 | 366 | 38 | 30 | 0 | 102 | 6 | 0 | 82 | 30 | 0 | 18 | 174 | 9 | 0 | 0 | 0 | 0 | 8.89 | 12 | 7269.69 | 917 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.28 | 379 | 0 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 15.96 | 168 | 0 | 157 | 0 | 0 | 0 | 350 | 0 | 1.52 | 0 | 170 | 54 | 0 | 29 | 0 | 0 | 0 | 4.6 | 35 | 0.73 | 0 | 280 | 7 | 105 | 220 | 0 | 220 | 924 | 0 | 5384.09 | 12653.78 | 79.15
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 34 | 17 | 113 | 95 | 45 | 0 | 35 | 108 | 0 | 16 | 320 | 281 | 350 | 0 | 35 | 0 | 227 | 0 | 0 | 8 | 90 | 17.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 0 | 76 | 40 | 5 | 40 | 0 | 3 | 500 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1000 | 18 | 43 | 55 | 26 | 0 | 358 | 345 | 46 | 182 | 32 | 101 | 50 | 93 | 13 | 20 | 28 | 38 | 16 | 72 | 16 | 305 | 320 | 310 | 38 | 30 | 0 | 98 | 7 | 0 | 83 | 30 | 0 | 18 | 173 | 17 | 45 | 72 | 0 | 1 | 16.49 | 12 | 7561.29 | 917 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.25 | 377 | 0 | 1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 51.19 | 167 | 0 | 156 | 0 | 0 | 0 | 300 | 0 | 3.09 | 0 | 167 | 54 | 0 | 41 | 0 | 0 | 0 | 6 | 120 | 0.72 | 0 | 280 | 9 | 105 | 220 | 0 | 221 | 908 | 0 | 5480.25 | 13041.54 | 79.15
13:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 54 | 0 | 104 | 15 | 45 | 0 | 35 | 108 | 0 | 16 | 380 | 295 | 360 | 0 | 35 | 0 | 225 | 0 | 0 | 2 | 52 | 17.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 14 | 17 | 0 | 0 | 76 | 40 | 5 | 40 | 0 | 7 | 404 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 0 | 950 | 18 | 43 | 40 | 26 | 0 | 330 | 300 | 50 | 193 | 29 | 93 | 50 | 97 | 9 | 20 | 28 | 36 | 16 | 68 | 16 | 310 | 320 | 385 | 38 | 30 | 0 | 94 | 7 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 45 | 72 | 0 | 1 | 45.26 | 12 | 7322.06 | 917 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.91 | 379 | 0 | 922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 55.46 | 140 | 0 | 148 | 0 | 0 | 0 | 330 | 0 | 4.92 | 0 | 166 | 54 | 0 | 33 | 0 | 0 | 0 | 8 | 202 | 0.71 | 0 | 220 | 8 | 90 | 220 | 0 | 220 | 831 | 0 | 5257 | 12579.06 | 79.14
14:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 54 | 4 | 93 | 15 | 15 | 0 | 35 | 108 | 0 | 16 | 380 | 308 | 360 | 0 | 35 | 0 | 225 | 0 | 0 | 13 | 17 | 17.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 10 | 16.5 | 0 | 0 | 76 | 60 | 1 | 40 | 0 | 5 | 366 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 900 | 17 | 43 | 40 | 26 | 0 | 353 | 320 | 47 | 152 | 32 | 93 | 50 | 105 | 9 | 20 | 52 | 42 | 16 | 61 | 22 | 305 | 320 | 396 | 38 | 29 | 0 | 102 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 45 | 75 | 0 | 2 | 38.73 | 12 | 7258.03 | 917 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.57 | 379 | 0 | 925.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 48.2 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 4.24 | 0 | 165 | 54 | 0 | 30 | 0 | 0 | 0 | 7.4 | 44 | 0.28 | 0 | 220 | 8 | 115 | 220 | 0 | 221 | 798 | 0 | 5170.94 | 12428.97 | 79.14
15:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 44 | 17 | 58 | 64 | 0 | 0 | 35 | 72 | 0 | 16 | 380 | 269 | 300 | 0 | 17 | 0 | 225 | 0 | 0 | 17 | 35 | 18.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 12 | 34 | 0 | 0 | 88 | 30 | 3 | 40 | 0 | 2 | 425 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 950 | 13 | 43 | 20 | 8 | 0 | 355 | 345 | 50 | 181 | 34 | 95 | 50 | 114 | 9 | 0 | 70 | 24 | 18 | 48 | 22 | 300 | 320 | 314 | 38 | 30 | 0 | 100 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 76 | 94 | 0 | 2 | 34.38 | 12 | 7203.18 | 916 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.34 | 381 | 0 | 973.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 27.06 | 157 | 0 | 151 | 0 | 0 | 0 | 370 | 0 | 2.52 | 0 | 164 | 54 | 0 | 27 | 0 | 0 | 0 | 2.6 | 135 | 0.18 | 0 | 307 | 9 | 105 | 220 | 0 | 212 | 855 | 0 | 5394.36 | 12597.54 | 79.13
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 17 | 58 | 64 | 0 | 0 | 35 | 36 | 0 | 0 | 380 | 291 | 300 | 0 | 17 | 0 | 225 | 0 | 0 | 8 | 35 | 18.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 7 | 34 | 0 | 0 | 88 | 30 | 3 | 40 | 0 | 2 | 425 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 950 | 8 | 43 | 10 | 8 | 0 | 355 | 345 | 53 | 190 | 30 | 94 | 50 | 110 | 25 | 5 | 70 | 28 | 25 | 10 | 22 | 310 | 320 | 299 | 38 | 30 | 0 | 101 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 76 | 103 | 0 | 0 | 23.29 | 12 | 7112.09 | 916 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.99 | 379 | 0 | 967.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 21.4 | 161 | 0 | 152 | 0 | 0 | 0 | 414 | 0 | 2.03 | 0 | 164 | 54 | 0 | 13 | 0 | 0 | 0 | 5.2 | 80 | 0.09 | 0 | 307 | 0 | 111 | 220 | 0 | 201 | 890 | 0 | 5265.46 | 12377.55 | 79.13
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 35 | 17 | 58 | 95 | 0 | 0 | 35 | 35 | 0 | 0 | 380 | 307 | 300 | 0 | 17 | 0 | 225 | 0 | 0 | 3 | 52 | 18.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 2 | 34 | 0 | 0 | 100 | 50 | 0 | 40 | 0 | 5 | 426 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 950 | 3 | 43 | 10 | 8 | 0 | 350 | 345 | 55 | 212 | 38 | 82 | 50 | 17 | 36 | 14 | 0 | 36 | 0 | 2 | 22 | 300 | 320 | 346 | 38 | 30 | 0 | 100 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 77 | 110 | 0 | 0 | 12.25 | 12 | 7075.05 | 916 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 379 | 0 | 971.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 5.95 | 161 | 0 | 152 | 0 | 0 | 0 | 414 | 0 | 0.55 | 0 | 164 | 54 | 0 | 7 | 0 | 0 | 0 | 1.1 | 38 | 0.03 | 0 | 307 | 0 | 120 | 220 | 0 | 201 | 892 | 0 | 5179.07 | 12254.12 | 79.12
18:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35 | 17 | 109 | 95 | 0 | 0 | 35 | 72 | 0 | 7 | 380 | 303 | 300 | 0 | 17 | 0 | 225 | 0 | 0 | 0 | 52 | 18.8 | 18 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 50 | 0 | 40 | 0 | 7 | 425 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 950 | 0 | 43 | 10 | 8 | 0 | 354 | 345 | 55 | 202 | 38 | 86 | 50 | 46 | 39 | 14 | 17 | 38 | 7 | 0 | 23 | 305 | 320 | 307 | 38 | 30 | 0 | 104 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 113 | 139 | 0 | 0 | 2.84 | 12 | 7273.64 | 916 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.84 | 379 | 0 | 970.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5.13 | 161 | 0 | 151 | 0 | 0 | 0 | 414 | 0 | 0.44 | 0 | 167 | 54 | 0 | 2 | 0 | 0 | 0 | 0.5 | 8 | 0.02 | 0 | 307 | 7 | 115 | 220 | 0 | 201 | 916 | 0 | 5166.12 | 12439.76 | 79.12
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 40 | 17 | 132 | 103 | 145 | 0 | 35 | 120 | 0 | 12 | 420 | 285 | 420 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 70 | 18.8 | 18 | 0 | 420 | 0 | 0 | 0 | 0 | 2 | 68 | 40 | 0 | 100 | 90 | 0 | 40 | 0 | 2 | 575 | 17 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1107 | 0 | 51 | 83 | 8 | 0 | 355 | 345 | 55 | 195 | 38 | 93 | 50 | 56 | 38 | 14 | 34 | 44 | 16 | 0 | 29 | 300 | 320 | 324 | 38 | 30 | 0 | 101 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 25 | 103 | 141 | 0 | 0 | 0 | 12 | 8326.8 | 869 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 9 | 1191.56 | 0 | 0 | 0 | 6 | 0 | 42 | 10 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 150 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 54 | 60 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 112 | 220 | 0 | 220 | 1100 | 0 | 5753.56 | 14080.36 | 79.11
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 17 | 132 | 119 | 145 | 0 | 35 | 144 | 0 | 16 | 380 | 278 | 400 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 117 | 18.8 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 4 | 68 | 52 | 0 | 100 | 90 | 0 | 40 | 0 | 7 | 570 | 17 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1020 | 0 | 51 | 134 | 8 | 0 | 355 | 345 | 55 | 182 | 38 | 93 | 50 | 86 | 38 | 14 | 34 | 44 | 16 | 0 | 31 | 290 | 320 | 344 | 38 | 30 | 0 | 101 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 35 | 104 | 141 | 0 | 0 | 0 | 12 | 8415.8 | 869 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 18 | 1330.47 | 0 | 0 | 0 | 70 | 0 | 42 | 50 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 149 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 54 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 105 | 220 | 0 | 221 | 1244 | 0 | 6276.47 | 14692.27 | 0
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 385 | 0 | 0 | 54 | 17 | 132 | 130 | 95 | 0 | 35 | 108 | 0 | 16 | 380 | 281 | 400 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 125 | 18.8 | 18 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 68 | 54 | 0 | 100 | 90 | 0 | 40 | 0 | 12 | 500 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1006 | 0 | 51 | 133 | 8 | 0 | 355 | 345 | 55 | 182 | 38 | 94 | 50 | 90 | 39 | 14 | 17 | 38 | 8 | 0 | 31 | 290 | 320 | 315 | 37 | 30 | 0 | 89 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 35 | 104 | 141 | 0 | 0 | 0 | 12 | 8168.8 | 868 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615 | 17 | 1367.55 | 0 | 0 | 0 | 70 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 149 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 157 | 54 | 110 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 105 | 220 | 0 | 220 | 1244 | 0 | 6332.55 | 14501.35 | 79.11
21:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 51 | 17 | 114 | 112 | 45 | 0 | 35 | 72 | 0 | 16 | 380 | 293 | 400 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 108 | 18.8 | 19 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 68 | 54 | 0 | 100 | 60 | 0 | 40 | 0 | 18 | 504 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1005 | 0 | 51 | 80 | 8 | 0 | 355 | 345 | 55 | 183 | 38 | 93 | 50 | 97 | 39 | 18 | 34 | 38 | 9 | 0 | 31 | 295 | 320 | 348 | 37 | 30 | 0 | 86 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 17 | 104 | 141 | 0 | 0 | 0 | 12 | 8012.8 | 917 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 0 | 1356.27 | 0 | 0 | 0 | 70 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 149 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 53 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 105 | 220 | 0 | 220 | 1244 | 0 | 6365.27 | 14378.07 | 79.1
22:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 38 | 17 | 113 | 112 | 0 | 0 | 35 | 108 | 0 | 16 | 320 | 283 | 350 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 108 | 18 | 19 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 68 | 54 | 0 | 100 | 60 | 0 | 40 | 0 | 22 | 505 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1001 | 0 | 51 | 80 | 8 | 0 | 355 | 345 | 55 | 182 | 38 | 93 | 50 | 105 | 39 | 18 | 34 | 40 | 16 | 0 | 33 | 300 | 320 | 348 | 37 | 30 | 0 | 97 | 8 | 0 | 83 | 30 | 0 | 18 | 170 | 17 | 105 | 150 | 0 | 0 | 0 | 12 | 7842 | 916 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 1373 | 0 | 0 | 0 | 70 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 149 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 165 | 54 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 105 | 220 | 0 | 221 | 1120 | 0 | 6285 | 14127 | 79.1
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 42 | 17 | 96 | 112 | 0 | 0 | 35 | 108 | 0 | 16 | 320 | 300 | 350 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 90 | 19 | 19 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 100 | 60 | 0 | 40 | 0 | 29 | 504 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1002 | 0 | 51 | 40 | 8 | 0 | 355 | 345 | 55 | 200 | 38 | 93 | 50 | 104 | 39 | 18 | 34 | 40 | 16 | 0 | 33 | 300 | 320 | 387 | 39 | 30 | 0 | 97 | 8 | 0 | 84 | 30 | 0 | 18 | 171 | 0 | 105 | 150 | 0 | 0 | 0 | 12 | 7716 | 917 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 623 | 0 | 1376 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 153 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 165 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 221 | 1120 | 0 | 6166 | 13882 | 79.09
Total KWH | 0 | 713280 | 378720 | 0 | 0 | 0 | 0 | 0 | 8866800 | 0 | 0 | 605880 | 417600 | 2464128 | 2193600 | 531175 | 0 | 648682 | 1290240 | 0 | 435840 | 8697000 | 7153251 | 8817191 | 0 | 490555 | 0 | 5439084 | 0 | 0 | 140581 | 1461600 | 433200 | 436680 | 0 | 8911818.18 | 0 | 0 | 0 | 0 | 76800 | 842566 | 215040 | 0 | 1861440 | 815040 | 31801 | 964000 | 0 | 357120 | 11476363.64 | 18400 | 0 | 0 | 24881.4 | 0 | 3340640 | 0 | 0 | 0 | 23994543 | 134190 | 1051420 | 874836 | 485091 | 0 | 8715900 | 8268000 | 1248480 | 4763000 | 862920 | 2280000 | 1195100 | 2542080 | 456960 | 397100 | 1206120 | 884160 | 279754 | 507255 | 436464 | 7403500 | 7680500 | 8947000 | 910000 | 678360 | 0 | 2380500 | 169104 | 0 | 2019840 | 678144 | 0 | 435000 | 4567370 | 270360 | 1690800 | 2551200 | 0 | 11000 | 235590 | 288240 | 182050878.22 | 22062545 | 3840768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11112730 | 63840 | 27234546 | 0 | 0 | 0 | 354240 | 0 | 231808 | 43872 | 0 | 0 | 636070 | 0 | 306000 | 3987418 | 0 | 3811782 | 0 | 380855 | 0 | 9470981 | 0 | 22800 | 0 | 3998000 | 1264581 | 526207 | 175800 | 334128 | 0 | 0 | 37895.4 | 789840 | 4305 | 0 | 6589000 | 192798 | 2693000 | 5330360 | 0 | 5235840 | 24277818.18 | 0 | 135009827.58 | 317060705.8

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 07-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-05-2025 | during | 07-05-2025 | during | 07-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 350 | 402 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 380 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 281 | 278 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 227 | 225 | 335 | 335 | 227 | 227 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 16 | 102 | 16 | 16 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 34 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 95 | 119 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 36 | 55 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.8 | 18.8 | 30 | 30 | 21 | 21 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 18 | 18 | 22 | 22 | 19 | 19 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 45 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 132 | 135 | 135 | 135 | 135 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 16 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 360 | 400 | 584 | 584 | 420 | 420 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 350 | 400 | 583 | 583 | 420 | 420 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 117 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2595.8 | 3003.8 | 5235.9 | 5286.9 | 3783.92 | 3767.92
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | -
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 147 | 145 | 145 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 52 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 68 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 7 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 2.02 | 0 | 2.02 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 40 | 90 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1000 | 1020 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 4 | 4 | 3 | 4 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 500 | 570 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1856 | 2113 | 3413.74 | 3402.72 | 3418.74 | 3402.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 182 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 358 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 345 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 38 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 55 | 55 | 55 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 26 | 8 | 195 | 195 | 83 | 83 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 55 | 134 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 16 | 31 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 50 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 93 | 86 | 200 | 200 | 200 | 200 | FGMO
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 16 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 14 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 28 | 34 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 101 | 93 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 72 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1534 | 1574 | 2465.99 | 2400.99 | 2134.55 | 2098.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 06-05-2025 | during | 07-05-2025 | during | 07-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 11 | 11 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 72 | 141 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 104 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 16.49 | 0 | 49.4 | 0 | 49.4 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 163.49 | 292 | 600.5 | 549 | 322 | 342.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 38 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 98 | 101 | 113 | 113 | 113 | 113 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 310 | 344 | 385 | 385 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1412 | 1433 | 1563 | 1563 | 1469 | 1469
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 917 | 869 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 165 | 154 | 410 | 410 | 170 | 170 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 18 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 93.25 | 0 | 89 | 0 | 89 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 377 | 558 | 1234.2 | 1234.2 | 618 | 618 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1552.25 | 1599 | 3603.2 | 3514.2 | 2642.01 | 2553.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 221 | 221 | 315 | 315 | 315 | 315 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 9 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 105 | 105 | 125 | 125 | 125 | 125 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 908 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 280 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.72 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1743.72 | 2107 | 2482.12 | 2481.12 | 2482.12 | 2481.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 42 | 42 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 167 | 161 | 214 | 214 | 195 | 195 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 156 | 149 | 220 | 220 | 185 | 185 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 185 | 185 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 300 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 42 | 94 | 94 | 94 | 94 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.09 | 0 | 5.05 | 0 | 5.05 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1011 | 1330.47 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 51.19 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 90 | 0 | 90 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 1796.28 | 2216.47 | 3098.58 | 2942.53 | 2956.79 | 2800.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 54 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 167 | 160 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6 | 0 | 6.4 | 0 | 6.4 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 41 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 120 | 0 | 185.65 | 0 | 170.16 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 388 | 354 | 675.05 | 453 | 659.56 | 453
System Total |  |  |  |  | 27566.2 | 28535.742 | 13041.54 | 14692.27 | 23138.08 | 22593.46 | 19868.69 | 19368.56
Forecast Scenario (07-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13910 |  | 0 |  | 13910
|  |  |  | 1:00 | 13470 |  | 0 |  | 13470
|  |  |  | 2:00 | 12930 |  | 0 |  | 12930
|  |  |  | 3:00 | 12640 |  | 0 |  | 12640
|  |  |  | 4:00 | 12310 |  | 0 |  | 12310
|  |  |  | 5:00 | 12040 |  | 0 |  | 12040
|  |  |  | 6:00 | 11720 |  | 0 |  | 11720
|  |  |  | 7:00 | 11960 |  | 0 |  | 11960
|  |  |  | 8:00 | 12040 |  | 0 |  | 12040
|  |  |  | 9:00 | 12540 |  | 0 |  | 12540
|  |  |  | 10:00 | 13050 |  | 0 |  | 13050
|  |  |  | 11:00 | 13430 |  | 0 |  | 13430
|  |  |  | 12:00 | 13890 |  | 0 |  | 13890
|  |  |  | 13:00 | 14110 |  | 0 |  | 14110
|  |  |  | 14:00 | 14080 |  | 0 |  | 14080
|  |  |  | 15:00 | 14300 |  | 0 |  | 14300
|  |  |  | 16:00 | 14010 |  | 0 |  | 14010
|  |  |  | 17:00 | 13680 |  | 0 |  | 13680
|  |  |  | 18:00 | 13350 |  | 0 |  | 13350
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15080 |  | 0 |  | 15080
|  |  |  | 19:30 | 15550 |  | 0 |  | 15550
|  |  |  | 20:00 | 15200 |  | 0 |  | 15200
|  |  |  | 21:00 | 15180 |  | 0 |  | 15180
|  |  |  | 22:00 | 14980 |  | 0 |  | 14980
|  |  |  | 23:00 | 14820 |  | 0 |  | 14820
Probable Maximum Temperature: |  |  | 33.90°C
Probable Maximum Demand at Day Peak: |  |  | 13890.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15550.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15550.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 324.72 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:38 hrs on 07-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 06-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13041.54 | MW | 12:00 Hr. | Energy Generated |  |  | 317.0607 |  | MKWHr.
| Day Peak Demand |  |  | 13087.54 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.899 |  | MKWHr.
| Evening Peak Generation |  |  | 14692.27 | MW | 19:30 Hr. | Energy Demand |  |  | 317.9597 |  | MKWHr.
| Evening Peak Demand |  |  | 14725.27 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 11867.6 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1039.7 |  | MMCFD
| Maximum Generation of the Day |  |  | 14692.27 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.248 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 48.755 | 0 | 11.6313 | 0 | 0 | 0.14058 | 0 | 0 | 60.5269 | Gas | 145.0171 | Gas | 511390990.5506
| Chattogram Zone |  |  | 3.6978 | 35.4709 | 3.7774 | 0 | 0.964 | 0.16599 | 0 | 0.0768 | 44.1528 | Coal | 87.9489 | Coal | 593548492.899
| Cumilla Zone |  |  | 26.987 | 0 | 8.0762 | 0 | 0 | 0.50726 | 0.88416 | 0 | 36.4546 | HFO | 29.8396 | HFO | 558671367.318
| Mymensingh Zone |  |  | 0 | 0 | 4.8006 | 0 | 0 | 0.24659 | 0 | 0 | 5.0472 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.8693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.8693 | Hydro | 0.964 | Hydro | 96400
| Khulna Zone |  |  | 3.8408 | 11.1127 | 0.06384 | 0 | 0 | 0 | 22.0625 | 0 | 37.0799 | Solar | 3.0331 | Solar | 47653131.984
| Barishal Zone |  |  | 8.2162 | 36.1027 | 0 | 0 | 0 | 0.004305 | 0 | 0 | 44.3231 | Import | 50.1813 | Import | 268514152.29
| Rajshahi Zone |  |  | 17.651 | 0 | 0.62992 | 0 | 0 | 0.96487 | 27.2345 | 0 | 46.4804 | Wind | 0.0768 | Wind | 1124352
| Rangpur Zone |  |  | 0 | 5.2626 | 0.86033 | 0 | 0 | 1.0035 | 0 | 0 | 7.1265
| Total |  |  | 145.0171 | 87.9489 | 29.8396 | 0 | 0.964 | 3.0331 | 50.1813 | 0.0768 | 317.0607
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 511390990.5506 |  | Hydro | 96400
|  |  |  | Coal | 593548492.899 |  | Solar | 47653131.984
|  |  |  | HFO | 558671367.318 |  | Import | 268514152.29
|  |  |  | HSD | 0 |  | Wind | 1124352
[5 empty] | Total: | 198,09,98,887 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0625 | Peak Hr Flow | 869.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 37836709.17 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.2345 | Peak Hr Flow | 1330.47 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 488 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.88416 | Peak Hr Flow | 44.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1090 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.1813 | Peak Hr Flow | 2243.47 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 32 |  | 5436
|  |  |  | Chattogram |  | 0 |  | 1463
|  |  |  | Cumilla |  | 0 |  | 1220
|  |  |  | Mymensingh |  | 0 |  | 1191
|  |  |  | Sylhet |  | 0 |  | 546
|  |  |  | Khulna |  | 0 |  | 1578
|  |  |  | Barishal |  | 0 |  | 378
|  |  |  | Rajshahi |  | 0 |  | 1427
|  |  |  | Rangpur |  | 0 |  | 888
|  |  |  | Total |  | 32 |  | 14127
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:15 | Bhaluka 132/33kV S/S Transformer- 01 HT is restored.
|  | 08:16 | Bhaluka 132/33kV S/S Transformer- 01 LT is restored.
| 11:38 | 12:05 | Jhenaidah-Magura 132 kV Ckt-2 Tripped from Jhenaidah 132/33kV end showing Distance relay
relays.
| 12:00 | 14:45 | Ghorasal- Ishwardi 230 kV Ckt-1 Tripped from Ishurdi 230/132kV end showing Siemens
Siprotec-7SA87 relays Due to C Phase to ground fault distance -134 Km Zone-1 SOTF and
from Ghorashal 230kV end showing Distance Relay relays Due to Bammbo
| 12:00 |  | Day Peak Generation: 13039 MW.
| 13:05 | 13:17 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing REF 630 relays Due to 33 KV | [7 empty] | 15.0MW load
|  |  | Sharsha Benapole Feeder trip | [7 empty] | interrup.
| 13:30 | 16:24 | Kodda-Rajendrapur 132kV Ckt-1 Project Work S/D from Rajendrapur 132/33kV end Due to
Kodda end Work Purpose
| 13:36 | 16:26 | Rajendrapur 132/33kV S/S MTR-1 HT Scheduled S/D Due to Rajendrapur Substation Metering
Division Work Purpose. Load Share By MTR-1 &MTR-2.
| 13:45 | 13:50 | Sylhet 132/33kV S/S T2 LT Project Work S/D Due to 132 KV T4 X-Former Red Hot Maintenance
Purpose.
| 13:50 | 15:09 | Sylhet 132/33kV S/S T4 LT Project Work S/D Due to 132 KV T4 X-Former Red Hot Maintenance
Purpose.
| 13:50 | 15:09 | Sylhet 132/33kV S/S T4 HT Project Work S/D Due to 132 KV T4 X-Former Red Hot Maintenance
Purpose.
| 14:04 | 15:01 | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing
Distance Relay relays.
| 14:28 | 14:51 | Chandina 132/33kV S/S TR-2 HT Tripped showing Relay AF87T1 Relay AF87T12 K86L1 K86L2
relays.
| 15:12 | 15:15 | Sylhet 132/33kV S/S T2 LT Project Work S/D Due to Maintenance of T4 X-Former.
| 15:13 | 17:17 | GPH 230/33kV S/S BSRM CKT-1 Forced S/D Due to To remove the kite
| 15:21 | 17:16 | BSRM 230/33kV S/S GPH Ispat Ckt. -01 Forced S/D Due to Baro Awlia Substation Emergency
Work.
| 19:30 |  | Evening peak: 14691 MW.
| 20:49 | 21:35 | Chowmuhani 132/33kV S/S TR3-435T LT Scheduled S/D Due to TR-03 33kv side B-phase red hot | [7 empty] | 15.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 20:49 | 21:35 | Chowmuhani 132/33kV S/S TR3-435T HT Scheduled S/D Due to TR-03 33kv side B-phase red hot | [7 empty] | 15.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 05:45 | 07:38 | Mirpur 132/33kV S/S T2 LT Scheduled S/D
| 05:46 | 07:37 | Mirpur 132/33kV S/S T2 HT Scheduled S/D
| 06:00 |  | Min. Gen. 11526 MW
| 06:02 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Forced S/D Due to Hot spot
| 06:03 |  | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Forced S/D Due to Hot spot
| 07:05 | 07:53 | Kishoreganj 132/33kV S/S 33 kV T2 Bus Scheduled S/D Due to PT connection work by PBS | [7 empty] | 20.0MW load
interrup.
| 07:10 |  | Chandina 132/33kV S/S TR-3 HT Tripped showing K861 Lockout Relay 1 K862 Lockout Relay | [7 empty] | 4.11MW load
|  |  | 2 F87T1 F86T2 BCU 1 relays. | [7 empty] | interrup.
| 07:10 |  | Chandina 132/33kV S/S TR-3 LT Tripped showing TR BACKUP RELAY -F51 BCU1 relays. | [7 empty] | 4.11MW load
interrup.
| 07:36 |  | Kaliakoir 400/230/132kV S/S 400kV Bus 1 Scheduled S/D Due to Project Work
| 07:40 |  | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 06-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 402 | 8866800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 8697000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 278 | 7153251 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 225 | 5439084 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 605880 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 119 | 2193600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 648682 | -
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 490555 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18.8 | 433200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 436680 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 378720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 531175 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2464128 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 713280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 435840 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1290240 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 140581 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 417600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 8911818.18 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 8817191 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 117 | 1461600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3003.8 | 60526905.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 24881.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134190 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 964000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 145 | 3340640 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 52 | 215040 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 68 | 842566 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1861440 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 7 | 357120 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 31801 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 815040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 18400 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1020 | 23994543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 4 | 76800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 570 | 11476363.64 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2113 | 44152825.04
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4763000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8715900 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8268000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 38 | 862920 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 55 | 1248480 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 485091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1051420 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 134 | 874836 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 31 | 436464 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 50 | 1195100 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 86 | 2542080 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 44 | 884160 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 16 | 279754 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 397100 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 1206120 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 456960 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 2280000 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 507255 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1574 | 36454640
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 141 | 2551200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1690800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 235590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 288240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 270360 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 292 | 5047190
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 910000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 678360 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 101 | 2380500 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 678144 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 2019840 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 171 | 4567370 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 435000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 169104 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7403500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 344 | 8947000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7680500 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1433 | 35869318
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 869 | 22062545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 154 | 3840768 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 18 | 63840 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 0 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 558 | 11112730 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1599 | 37079883
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 221 | 5235840 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 192798 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 105 | 2693000 | FGMO
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 24277818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5330360 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6589000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4305 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2107 | 44323121.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 161 | 3987418 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 149 | 3811782 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 380855 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9470981 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 231808 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 354240 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 50 | 43872 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22800 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1330.47 | 27234546 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 306000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 636070 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2216.47 | 46480372
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1264581 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3998000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 334128 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37895.4 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 526207 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 175800 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 789840 | -
Rangpur Area Total |  |  |  |  | 950 | 354 | 7126451.4
Eastern Grid Total |  |  |  |  | 16921.242 | 8415.8 | 182050878.22
Western Grid Total |  |  |  |  | 11614.5 | 6276.47 | 135009827.58
National Grid Total |  |  |  |  | 28535.742 | 14692.27 | 317060705.8
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 06-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9823.92 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4272 | MW
i) Dhaka area |  |  | 5403.52 |  | MW | i) Khulna area |  |  |  | 1578.5 | MW
ii) Chattogram area |  |  | 1462.9 |  | MW | ii) Barishal area |  |  |  | 378.5 | MW
iii) Cumilla area |  |  | 1220.5 |  | MW | iii) Rajshahi area |  |  |  | 1427 | MW
iv) Mymensingh area |  |  | 1191 |  | MW | iv) Rangpur area |  |  |  | 888 | MW
v) Sylhet area |  |  | 546 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14095.92 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 80 | 19:00 | 133 | Patuakhali | 75.5 | 00:00
2 | AKSML | 25.2 | 19:00 | 68 | Jaldhaka | 66 | 19:00 | 134 | Payra | 30 | 00:00
3 | Aftabnagar | 38 | 12:00 | 69 | Jamalpur | 136 | 19:30 | 135 | Postogola | 60 | 13:00
4 | Agargaon | 136 | 12:00 | 70 | Jashore | 130 | 00:00 | 136 | Purbachal | 20 | 00:00
5 | Agrabad | 100 | 15:00 | 71 | Jhenaidah | 113 | 00:00 | 137 | Purbasadipur | 117 | 19:30
6 | Amnura | 33 | 19:30 | 72 | Joydebpur | 162 | 12:00 | 138 | Rahanpur | 25 | 22:00
7 | Ashuganj | 136.5 | 01:00 | 73 | Joypurhat | 61 | 00:00 | 139 | Rahim | 54 | 15:00
8 | BSRM | 193 | 17:00 | 74 | Juldah | 18 | 22:00 | 140 | Rajbari | 76 | 19:30
9 | Bagerhat | 89 | 19:00 | 75 | KSRM | 13 | 12:00 | 141 | Rajendrapur | 138 | 12:00
10 | Bajitpur | 50 | 00:00 | 76 | Kabirpur | 276 | 12:00 | 142 | Rajshahi | 111 | 19:30
11 | Bakulia | 99 | 16:00 | 77 | Kachua | 85 | 00:00 | 143 | Rajshahi-230 | 82 | 21:00
12 | Banani | 42 | 12:00 | 78 | Kallyanpur | 105 | 00:00 | 144 | Ramganj | 114 | 00:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 44 | 12:00 | 145 | Rampur | 44 | 23:00
14 | Barapukuria | 65 | 07:00 | 80 | Kamrangirchar | 71.4 | 13:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 20 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 151 | 19:00
16 | Barishal | 108 | 13:00 | 82 | Kasba | 35 | 00:00 | 148 | Ruppur | 7 | 15:00
17 | Barishal-230 | 102 | 00:00 | 83 | Kazla | 94 | 00:00 | 149 | SSM | 10 | 04:00
18 | Baroaulia | 63 | 11:00 | 84 | Keranigonj | 77 | 00:00 | 150 | Saidpur | 104 | 20:00
19 | Baroirhat | 70 | 15:00 | 85 | Khagrachori | 30 | 19:00 | 151 | Satkhira | 136 | 01:00
20 | Bashundhara | 201 | 12:00 | 86 | Khulna | 69 | 13:00 | 152 | Satmasjid | 104 | 12:00
21 | BashundharaCement | 12 | 01:00 | 87 | Khulshi | 184 | 12:00 | 153 | Savar | 226 | 15:00
22 | Beanibazar | 72 | 19:00 | 88 | Kishoreganj | 134 | 19:30 | 154 | SevenRings | 14.6 | 17:00
23 | Benapole | 64 | 00:00 | 89 | Kodda | 310 | 21:00 | 155 | ShahCement | 30 | 20:00
24 | Bhaluka | 157 | 19:30 | 90 | Kulaura | 45 | 20:00 | 156 | Shahjadpur | 90 | 19:00
25 | Bhandaria | 51 | 00:00 | 91 | Kurigram | 58 | 19:30 | 157 | Shahjibazar | 115 | 00:00
26 | Bhangura | 40 | 20:00 | 92 | Kushtia | 148 | 13:00 | 158 | Shahmirpur | 57 | 19:00
27 | Bheramara(GK) | 62 | 19:00 | 93 | Lalbag | 70 | 12:00 | 159 | Shariatpur | 82 | 00:00
28 | Bhulta | 231 | 09:00 | 94 | Lalmonirhat | 57 | 19:00 | 160 | Sherpur | 134 | 19:30
29 | Bog-Sherpur | 68 | 19:00 | 95 | MI_Cement | 17.5 | 04:00 | 161 | Shikalbaha | 23 | 19:00
30 | Bogura | 153 | 00:00 | 96 | Madanganj | 52 | 00:00 | 162 | Shitalakhya | 92.2 | 13:00
31 | Borhanuddin | 86 | 00:00 | 97 | Madaripur | 107 | 00:00 | 163 | Sholosohor | 47 | 19:00
32 | Brahmanbaria | 132 | 00:00 | 98 | Madartek | 90.88 | 00:00 | 164 | Shyampur | 186 | 12:00
33 | Cantonment | 142 | 12:00 | 99 | Madunaghat | 53 | 19:00 | 165 | Siddhirganj | 124 | 12:00
34 | Chandina | 15.27 | 19:00 | 100 | Magura | 60 | 00:00 | 166 | Sirajganj | 130 | 20:00
35 | Chandpur | 70 | 01:00 | 101 | Mahasthangarh | 74 | 19:30 | 167 | Sonargaon | 122 | 05:00
36 | Chandraghona | 36 | 19:00 | 102 | Manikganj | 132 | 00:00 | 168 | Sreemongol | 76 | 00:00
37 | Chapai | 63 | 22:00 | 103 | Maniknagar | 86 | 10:00 | 169 | Sreepur | 108 | 11:00
38 | Charsaidpur | 40 | 00:00 | 104 | Matarbari | 50 | 20:00 | 170 | Srinagar | 47 | 00:00
39 | Chauddagram | 70 | 00:00 | 105 | Matuail | 70 | 12:00 | 171 | Sunamganj | 54 | 23:00
40 | Chhatak | 36 | 00:00 | 106 | Millgate | 120 | 12:00 | 172 | Sylhet | 44 | 01:00
41 | Chowmuhani | 210 | 00:00 | 107 | Mirpur | 139 | 12:00 | 173 | Sylhet-132 | 121 | 19:30
42 | Chuadanga | 106 | 00:00 | 108 | Mirsorai | 11 | 15:00 | 174 | TK | 34 | 19:00
43 | Coxsbazar | 134 | 23:00 | 109 | Mirzapur | 46 | 09:00 | 175 | Tangail | 184 | 19:30
44 | Cumilla(N) | 148 | 00:00 | 110 | Mithapukur | 53 | 20:00 | 176 | Thakurgaon | 99 | 20:00
45 | Cumilla(S) | 171 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 120 | 00:00
46 | Daudkandi | 147 | 00:00 | 112 | Mogbazar | 146.4 | 11:00 | 178 | Ullahpara | 48 | 19:30
47 | Dhaka | 62 | 12:00 | 113 | Mongla | 36 | 12:00 | 179 | Ullon | 38 | 00:00
48 | Dhamrai | 142 | 18:30 | 114 | Motijheel | 42 | 12:00 | 180 | Uttara | 96 | 12:00
49 | Dhanmondi | 138.7 | 12:00 | 115 | Muktagacha | 35 | 19:00 | 181 | UttaraNew | 50 | 12:00
50 | Dohazari | 103 | 01:00 | 116 | Munshiganj | 107 | 00:00 | 182 | Zigatola | 74 | 12:00
51 | Faridpur | 161 | 00:00 | 117 | Muradnagar | 27 | 00:00
52 | Fatullah | 110 | 12:00 | 118 | Mymensingh | 190 | 01:00
53 | Fenchuganj | 44 | 19:00 | 119 | Naogaon | 110 | 21:00
54 | Feni | 116 | 19:30 | 120 | Narail | 52.5 | 00:00
55 | GPH | 16 | 08:00 | 121 | Narinda | 82 | 12:00
56 | Ghatail | 76 | 19:00 | 122 | Narshingdi | 183 | 00:00
57 | Ghorashal | 16 | 00:00 | 123 | Natore | 143 | 21:00
58 | Ghorashal-230 | 98 | 00:00 | 124 | Nawabganj | 55.8 | 00:00
59 | Goalpara | 42 | 00:00 | 125 | Netrakona | 125 | 19:30
60 | Gollamari | 94 | 12:00 | 126 | New | 91 | 12:00
61 | Gopalganj | 96 | 00:00 | 127 | Niamatpur | 65 | 22:00
62 | Gulshan | 130 | 12:00 | 128 | Noapara | 43 | 00:00
63 | Halishahar | 75 | 16:00 | 129 | PHP | 8 | 02:00
64 | HaripurSBU | 170 | 16:00 | 130 | Pabna | 117 | 21:00
65 | Hasnabad | 81 | 00:00 | 131 | Palashbari | 112 | 19:30
66 | Hathazari | 83 | 19:00 | 132 | Panchagarh | 49 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 06-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14479.5 | 96 |  | 14579.82
1:00 | 14160.5 | 96 |  | 14260.5
2:00 | 13729 | 82 |  | 13814.69
3:00 | 13296 | 80 |  | 13380
4:00 | 12938 | 74 |  | 13015
5:00 | 12582 | 84 |  | 12670
6:00 | 12149.62 | 77 |  | 12229.62
7:00 | 11867.6 | 33 |  | 11901.6
8:00 | 11895.44 | 25 |  | 11921.44
9:00 | 12489.37 | 23 |  | 12513.37
10:00 | 12736.51 | 45 |  | 12783.51
11:00 | 12653.78 | 44 |  | 12699.78
12:00 | 13041.54 | 44 |  | 13087.54
13:00 | 12579.06 | 38 |  | 12619.06
14:00 | 12428.97 | 0 |  | 12428.97
15:00 | 12597.54 | 0 |  | 12597.54
16:00 | 12377.55 | 0 |  | 12377.55
17:00 | 12254.12 | 0 |  | 12254.12
18:00 | 12439.76 | 0 |  | 12439.76
19:00 | 14080.36 | 34 |  | 14116.36
19:30 | 14692.27 | 32 |  | 14725.27
20:00 | 14501.35 | 24 |  | 14526.35
21:00 | 14378.07 | 0 |  | 14378.07
22:00 | 14127 | 0 |  | 14127
23:00 | 13882 | 0 |  | 13882
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 06-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8381.5 | 6098 | 14479.5 | DAILY GENERATION CURVE
00:30 | 8264 | 6056 | 14320
01:00 | 8146.5 | 6014 | 14160.5 | 06-05-2025
01:30 | 8001.75 | 5943 | 13944.75
02:00 | 7857 | 5872 | 13729
02:30 | 7795 | 5717.5 | 13512.5
03:00 | 7733 | 5563 | 13296
03:30 | 7613.5 | 5503.5 | 13117
04:00 | 7494 | 5444 | 12938
04:30 | 7346 | 5414 | 12760
05:00 | 7198 | 5384 | 12582
05:30 | 7097.68 | 5268.13 | 12365.81
06:00 | 6997.36 | 5152.26 | 12149.62
06:30 | 6924.52 | 5084.09 | 12008.61
07:00 | 6851.68 | 5015.92 | 11867.6
07:30 | 6869.46 | 5012.06 | 11881.52
08:00 | 6887.24 | 5008.2 | 11895.44
08:30 | 7027.735 | 5164.67 | 12192.405
09:00 | 7168.23 | 5321.14 | 12489.37
09:30 | 7256.17 | 5356.77 | 12612.94
10:00 | 7344.11 | 5392.4 | 12736.51
10:30 | 7306.9 | 5388.245 | 12695.145
11:00 | 7269.69 | 5384.09 | 12653.78
11:30 | 7415.49 | 5432.17 | 12847.66
12:00 | 7561.29 | 5480.25 | 13041.54
12:30 | 7441.675 | 5368.625 | 12810.3
13:00 | 7322.06 | 5257 | 12579.06
13:30 | 7290.045 | 5213.97 | 12504.015
14:00 | 7258.03 | 5170.94 | 12428.97
14:30 | 7230.605 | 5282.65 | 12513.255
15:00 | 7203.18 | 5394.36 | 12597.54
15:30 | 7157.635 | 5329.91 | 12487.545
16:00 | 7112.09 | 5265.46 | 12377.55
16:30 | 7093.57 | 5222.265 | 12315.835
17:00 | 7075.05 | 5179.07 | 12254.12
17:30 | 7174.345 | 5172.595 | 12346.94
18:00 | 7273.64 | 5166.12 | 12439.76
18:30 | 7800.22 | 5459.84 | 13260.06
19:00 | 8326.8 | 5753.56 | 14080.36
19:30 | 8415.8 | 6276.47 | 14692.27
20:00 | 8168.8 | 6332.55 | 14501.35
20:30 | 8090.8 | 6348.91 | 14439.71 |  | Executive Engineer
21:00 | 8012.8 | 6365.27 | 14378.07 |  | Network Operation Division
21:30 | 7927.4 | 6325.135 | 14252.535
22:00 | 7842 | 6285 | 14127
22:30 | 7779 | 6225.5 | 14004.5
23:00 | 7716 | 6166 | 13882

## En-Curve
QF-LDC-12
Date | 06-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3649 | 2483 | 924 | 0 | 46 | 1352 | 40 | 4185 | 0 | 437 | 1363.5 | 0 | 0 | 0 | 96 | DAILY ENERGY CURVE
00:30 | 3649.5 | 2477.5 | 924.5 | 0 | 44 | 1356 | 40 | 4162 | 0 | 381 | 1285 | 0 | 0 | 0.5 | 96 | 06-05-2025
01:00 | 3650 | 2472 | 925 | 0 | 42 | 1360 | 40 | 4139 | 0 | 325 | 1206.5 | 0 | 0 | 1 | 96
01:30 | 3714 | 2471.5 | 924.5 | 0 | 41 | 1339.5 | 40 | 4030 | 0 | 316.5 | 1065.75 | 0 | 0 | 2 | 89 | Energy Generated | 317.0607 |  | MKWHr
02:00 | 3778 | 2471 | 924 | 0 | 40 | 1319 | 40 | 3921 | 0 | 308 | 925 | 0 | 0 | 3 | 82 | Energy not Served | 0.899 |  | MKWHr
02:30 | 3706.5 | 2479 | 924 | 0 | 39 | 1295.5 | 40 | 3857.5 | 0 | 289.5 | 876 | 0 | 0 | 5.5 | 81 | Total Energy Requirement | 317.9597 |  | MKWHr
03:00 | 3635 | 2487 | 924 | 0 | 38 | 1272 | 40 | 3794 | 0 | 271 | 827 | 0 | 0 | 8 | 80
03:30 | 3643 | 2485 | 924.5 | 0 | 38 | 1225.5 | 40 | 3742 | 0 | 240.5 | 774.5 | 0 | 0 | 4 | 77
04:00 | 3651 | 2483 | 925 | 0 | 38 | 1179 | 40 | 3690 | 0 | 210 | 722 | 0 | 0 | 0 | 74
04:30 | 3664.5 | 2417 | 925 | 0 | 36 | 1170.5 | 40 | 3643.5 | 0 | 175 | 688.5 | 0 | 0 | 0 | 79
05:00 | 3678 | 2351 | 925 | 0 | 34 | 1162 | 40 | 3597 | 0 | 140 | 655 | 0 | 0 | 0 | 84
05:30 | 3632.5 | 2344.5 | 925 | 0 | 34 | 1113.5 | 40 | 3499 | 14.31 | 140 | 623 | 0 | 0 | 0 | 80.5
06:00 | 3587 | 2338 | 925 | 0 | 34 | 1065 | 40 | 3401 | 28.62 | 140 | 591 | 0 | 0 | 0 | 77
06:30 | 3538 | 2277 | 924.5 | 0 | 32 | 1064 | 40 | 3350.5 | 62.61 | 140 | 580 | 0 | 0 | 0 | 55
07:00 | 3489 | 2216 | 924 | 0 | 30 | 1063 | 40 | 3300 | 96.6 | 140 | 569 | 0 | 0 | 0 | 33
07:30 | 3537 | 2183.5 | 901 | 0 | 32 | 1038.5 | 40 | 3265 | 163.52 | 148.5 | 572.5 | 0 | 0 | 0 | 29
08:00 | 3585 | 2151 | 878 | 0 | 34 | 1014 | 40 | 3230 | 230.44 | 157 | 576 | 0 | 0 | 0 | 25
08:30 | 3670 | 2178.75 | 873.5 | 0 | 34 | 1037.5 | 40 | 3314 | 259.655 | 193.5 | 591.5 | 0 | 0 | 0 | 24
09:00 | 3755 | 2206.5 | 869 | 0 | 34 | 1061 | 40 | 3398 | 288.87 | 230 | 607 | 0 | 0 | 0 | 23
09:30 | 3737 | 2218 | 893 | 0 | 34 | 1065 | 40 | 3435.5 | 307.44 | 251.5 | 631.5 | 0 | 0 | 0 | 34
10:00 | 3719 | 2229.5 | 917 | 0 | 34 | 1069 | 40 | 3473 | 326.01 | 273 | 656 | 0 | 0 | 0 | 45
10:30 | 3676 | 2229.65 | 917 | 0 | 35 | 1042 | 40 | 3501 | 349.495 | 275.5 | 629 | 0 | 0 | 0.5 | 44.5
11:00 | 3633 | 2229.8 | 917 | 0 | 36 | 1015 | 40 | 3529 | 372.98 | 278 | 602 | 0 | 0 | 1 | 44
11:30 | 3568 | 2218.3 | 917 | 0 | 37 | 1013 | 40 | 3518 | 458.36 | 286 | 786.5 | 0 | 0 | 5.5 | 44
12:00 | 3503 | 2206.8 | 917 | 0 | 38 | 1011 | 40 | 3507 | 543.74 | 294 | 971 | 0 | 0 | 10 | 44
12:30 | 3491 | 2252.8 | 917 | 0 | 37 | 966.5 | 40 | 3365.5 | 563 | 217.5 | 948 | 0 | 0 | 12 | 41
13:00 | 3479 | 2298.8 | 917 | 0 | 36 | 922 | 40 | 3224 | 582.26 | 141 | 925 | 0 | 0 | 14 | 38
13:30 | 3544.5 | 2304.8 | 917 | 0 | 39 | 923.625 | 40 | 3163.5 | 499.34 | 126.25 | 934 | 0 | 0 | 12 | 19
14:00 | 3610 | 2310.8 | 917 | 0 | 42 | 925.25 | 40 | 3103 | 416.42 | 111.5 | 943 | 0 | 0 | 10 | 0
14:30 | 3589.5 | 2239.8 | 916.5 | 0 | 33 | 949.455 | 40 | 3225.5 | 440.75 | 153.75 | 914 | 0 | 0 | 11 | 0
15:00 | 3569 | 2168.8 | 916 | 0 | 24 | 973.66 | 40 | 3348 | 465.08 | 196 | 885 | 0 | 0 | 12 | 0
15:30 | 3589 | 2184.8 | 916 | 0 | 26 | 970.705 | 40 | 3359 | 337.54 | 192 | 863 | 0 | 0 | 9.5 | 0
16:00 | 3609 | 2200.8 | 916 | 0 | 28 | 967.75 | 40 | 3370 | 210 | 188 | 841 | 0 | 0 | 7 | 0
16:30 | 3648.5 | 2210.3 | 916 | 0 | 32 | 969.445 | 40 | 3371.5 | 145.59 | 212 | 766 | 0 | 0 | 4.5 | 0
17:00 | 3688 | 2219.8 | 916 | 0 | 36 | 971.14 | 40 | 3373 | 81.18 | 236 | 691 | 0 | 0 | 2 | 0
17:30 | 3661 | 2226.8 | 916 | 0 | 37 | 970.665 | 40 | 3386 | 53.475 | 254 | 801 | 0 | 0 | 1 | 0
18:00 | 3634 | 2233.8 | 916 | 0 | 38 | 970.19 | 40 | 3399 | 25.77 | 272 | 911 | 0 | 0 | 0 | 0
18:30 | 3629.5 | 2333.8 | 892.5 | 0 | 41 | 1080.875 | 40 | 3682.5 | 12.885 | 346 | 1200 | 0 | 0 | 1 | 17
19:00 | 3625 | 2433.8 | 869 | 0 | 44 | 1191.56 | 40 | 3966 | 0 | 420 | 1489 | 0 | 0 | 2 | 34
19:30 | 3676 | 2341.8 | 869 | 0 | 44 | 1330.47 | 40 | 4134 | 0 | 497 | 1756 | 0 | 0 | 4 | 32
20:00 | 3608 | 2336.8 | 868 | 0 | 38 | 1367.55 | 40 | 4103 | 0 | 518 | 1622 | 0 | 0 | 0 | 24
20:30 | 3634 | 2349.3 | 892.5 | 0 | 38 | 1361.91 | 40 | 4108.5 | 0 | 491.5 | 1524 | 0 | 0 | 0 | 12
21:00 | 3660 | 2361.8 | 917 | 0 | 38 | 1356.27 | 40 | 4114 | 0 | 465 | 1426 | 0 | 0 | 0 | 0
21:30 | 3658.5 | 2286.4 | 916.5 | 0 | 39 | 1364.635 | 40 | 4054.5 | 0 | 466 | 1427 | 0 | 0 | 0 | 0
22:00 | 3657 | 2211 | 916 | 0 | 40 | 1373 | 40 | 3995 | 0 | 467 | 1428 | 0 | 0 | 0 | 0
22:30 | 3681 | 2225 | 916.5 | 0 | 40 | 1374.5 | 40 | 3995.5 | 0 | 415 | 1317 | 0 | 0 | 0 | 0
23:00 | 3705 | 2239 | 917 | 0 | 40 | 1376 | 40 | 3996 | 0 | 363 | 1206 | 0 | 0 | 0 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 06-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 06:00 | 374 | 11:00 | Payra | 412 | 07:00 | 406 | 00:00
Ashuganj | 398 | 6:00 | 380 | 11:00 | Rahanpur | 409 | 08:00 | 393 | 00:00
Bhulta | 393 | 06:00 | 378 | 10:00 | Rampal | 400 | 15:00 | 386 | 00:00
Bibiana | 392 | 02:00 | 388 | 01:00
BIPTC | 399 | 08:00 | 388 | 00:00
Bogura | 395 | 08:00 | 377 | 00:00
Gopalganj | 394 | 06:00 | 384 | 00:00
Kaliakoir | 374 | 04:00 | 365 | 11:00
Madunaghat | 394 | 06:00 | 388 | 00:00
Meghnaghat | 389 | 06:00 | 380 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 07:00 | 215 | 11:00 | Keranigonj | 222 | 06:00 | 214 | 10:00
AKSML | 231 | 16:00 | 223 | 12:00 | Khulna(S) | 231 | 15:00 | 218 | 00:00
Aminbazar | 224 | 05:00 | 217 | 10:00 | Madunaghat | 231 | 05:00 | 226 | 11:00
Ashuganj | 233 | 09:00 | 222 | 11:00 | Madunaghat-400 | 233 | 06:00 | 227 | 12:00
Ashuganj-400 | 233 | 09:00 | 222 | 11:00 | Maniknagar | 221 | 01:00 | 213 | 10:00
Baghabari | 235 | 05:00 | 227 | 20:00 | Meghnaghat | 230 | 05:00 | 221 | 10:00
Barapukuria | 230 | 07:00 | 219 | 01:00 | Meghnaghat-400 | 225 | 06:00 | 218 | 10:00
Barapukuria-230 | 230 | 07:00 | 219 | 01:00 | Mirsorai | 228 | 08:00 | 220 | 11:00
Barishal | 237 | 15:00 | 229 | 00:00 | Rajshahi | 235 | 05:00 | 224 | 21:00
Bheramara | 234 | 04:00 | 225 | 21:00 | Rampal | 230 | 15:00 | 217 | 00:00
Bhulta | 223 | 06:00 | 214 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 06:00 | 220 | 10:00 | Rampura | 222 | 06:00 | 212 | 10:00
BIPTC | 236 | 04:00 | 225 | 21:00 | Shikalbaha | 230 | 16:00 | 225 | 12:00
Bogura | 238 | 07:00 | 229 | 00:00 | Shyampur | 223 | 07:00 | 215 | 10:00
Bogura-400 | 239 | 08:00 | 229 | 01:00 | Siddhirganj | 222 | 07:00 | 215 | 09:00
Borhanuddin | 242 | 15:00 | 235 | 00:00 | Sirajgonj | 239 | 11:00 | 235 | 23:00
BSRM | 225 | 05:00 | 220 | 12:00 | Sreepur | 228 | 13:00 | 222 | 09:00
Cumilla(N) | 222 | 15:00 | 215 | 10:00 | Tongi | 224 | 04:00 | 212 | 15:00
Faridpur | 235 | 18:00 | 223 | 00:00
Fenchuganj | 225 | 14:00 | 217 | 02:00
Ghorashal | 230 | 00:00 | 225 | 14:00
Ghorashal-230 | 223 | 04:00 | 215 | 10:00
Gopalganj | 234 | 15:00 | 226 | 00:00
GPH | 226 | 07:00 | 223 | 00:00
Haripur | 222 | 04:00 | 217 | 09:00
Hasnabad | 223 | 06:00 | 214 | 11:00
Hathazari | 232 | 18:00 | 227 | 00:00
Ishurdi | 236 | 08:00 | 227 | 21:00
Jhenaidah | 229 | 14:00 | 217 | 00:00
Kaliakoir | 229 | 04:00 | 222 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 05:00 | 126 | 11:00 | Madartek | 133 | 03:00 | 126 | 10:00
Agargaon | 131 | 04:00 | 125 | 10:00 | Madunaghat | 132 | 06:00 | 129 | 10:00
Agrabad | 130 | 03:00 | 126 | 09:00 | Magura | 135 | 13:00 | 125 | 00:00
AKS | 129 | 17:00 | 126 | 00:00 | Mahasthangarh | 139 | 08:00 | 130 | 01:00
Aminbazar | 130 | 22:00 | 124 | 09:00 | Manikganj | 150 | 15:00 | 115 | 09:00
Amnura | 137 | 04:00 | 124 | 19:30 | Maniknagar | 130 | 04:00 | 123 | 10:00
Ashuganj | 136 | 13:00 | 133 | 10:00 | Matarbari | 119 | 16:00 | 112 | 00:00
Bagerhat | 136 | 15:00 | 119 | 00:00 | Matuail | 129.1 | 06:00 | 124 | 10:00
Bajitpur | 133 | 13:00 | 127 | 00:00 | Millgate | 129 | 02:00 | 122 | 09:00
Bakulia | 131 | 16:00 | 128 | 09:00 | Mirpur | 128 | 13:00 | 122 | 10:00
Banani | 134 | 05:00 | 125 | 11:00 | Mirzapur | 133 | 04:00 | 129 | 14:00
Bangabhaban | 130 | 05:00 | 122 | 12:00 | Mithapukur | 138 | 08:00 | 127 | 01:00
Barapukuria | 140 | 07:00 | 130 | 02:00 | MI_Cement | 129 | 06:00 | 123 | 10:00
Barguna | 134 | 06:00 | 130 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 15:00 | 125 | 00:00 | Mogbazar | 135 | 03:00 | 125 | 11:00
Barishal-230 | 132 | 15:00 | 125 | 00:00 | Mongla | 136 | 15:00 | 121 | 00:00
Baroaulia | 132 | 18:00 | 129 | 01:00 | Motijheel | 130 | 05:00 | 122 | 12:00
Baroirhat | 128 | 16:00 | 117 | 12:00 | Muktagacha | 137 | 12:00 | 118 | 11:00
Bashundhara | 134 | 03:00 | 121 | 09:00 | Munshiganj | 128 | 06:00 | 122 | 10:00
BashundharaCement | 128 | 05:00 | 123 | 11:00 | Muradnagar | 127 | 15:00 | 120 | 10:00
Beanibazar | 130 | 06:00 | 126 | 00:00 | Mymensingh | 138 | 12:00 | 116 | 11:00
Benapole | 133 | 15:00 | 120 | 00:00 | Naogaon | 138 | 07:00 | 129 | 00:00
Bhaluka | 132 | 12:00 | 123 | 16:00 | Narail | 137 | 13:00 | 124 | 00:00
Bhandaria | 129 | 16:00 | 116 | 00:00 | Narinda | 130 | 04:00 | 123 | 10:00
Bhangura | 134 | 04:00 | 129 | 20:00 | Narshingdi | 128 | 16:00 | 117 | 00:00
Bheramara | 137 | 15:00 | 131 | 00:00 | Natore | 136 | 08:00 | 129 | 21:00
Bheramara(GK) | 137 | 15:00 | 130 | 00:00 | Nawabganj | 133 | 06:00 | 126 | 11:00
Bhulta | 123 | 05:00 | 118 | 10:00 | Netrakona | 126 | 12:00 | 116 | 16:00
Bog-Sherpur | 139 | 11:00 | 132 | 00:00 | New | 129 | 05:00 | 122 | 11:00
Bogura | 141 | 07:00 | 134 | 01:00 | Niamatpur | 135 | 06:00 | 129 | 21:00
Bogura-230 | 141 | 08:00 | 134 | 00:00 | Noapara | 135 | 14:00 | 124 | 00:00
Brahmanbaria | 129 | 07:00 | 123 | 00:00 | Pabna | 136 | 10:00 | 129 | 21:00
Cantonment | 132 | 06:00 | 124 | 11:00 | Palashbari | 137 | 08:00 | 125 | 1:00
Chandina | 130 | 16:00 | 122 | 10:00 | Panchagarh | 139 | 22:00 | 122 | 02:00
Chandpur | 136 | 16:00 | 120 | 10:00 | Patuakhali | 134 | 07:00 | 130 | 00:00
Chandraghona | 133 | 06:00 | 129 | 00:00 | Payra | 136 | 18:00 | 133 | 00:00
Chapai | 133 | 09:00 | 126 | 00:00 | PHP | 128 | 16:00 | 116 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 03:00 | 123 | 11:00 | Postogola | 131 | 06:00 | 126 | 10:00
Chauddagram | 131 | 16:00 | 117 | 10:00 | Purbachal | 134 | 04:00 | 125 | 11:00
Chhatak | 129 | 05:00 | 123 | 00:00 | Purbasadipur | 136 | 07:00 | 122 | 00:00
Chowmuhani | 130 | 16:00 | 112 | 23:00 | Rahanpur | 136 | 08:00 | 131 | 00:00
Chuadanga | 132 | 06:00 | 120 | 00:00 | Rahanpur-400 | 136 | 07:00 | 131 | 00:00
Coxsbazar | 117 | 09:00 | 112 | 00:00 | Rahim | 129 | 04:00 | 124 | 10:00
Cumilla(N) | 130 | 15:00 | 122 | 10:00 | Rajbari | 135 | 14:00 | 127 | 00:00
Cumilla(S) | 132 | 04:00 | 120 | 10:00 | Rajendrapur | 134 | 13:00 | 121 | 11:00
Daudkandi | 125 | 16:00 | 118 | 00:00 | Rajshahi | 136 | 05:00 | 130 | 00:00
Dhaka | 134 | 04:00 | 126 | 10:00 | Rajshahi-230 | 136 | 08:00 | 119 | 22:00
Dhamrai | 134 | 13:00 | 129 | 09:00 | Ramganj | 133 | 16:00 | 112 | 12:00
Dhanmondi | 134 | 04:00 | 124 | 11:00 | Rampur | 130 | 03:00 | 126 | 09:00
Dohazari | 129 | 18:00 | 126 | 05:00 | Rampura | 134 | 04:00 | 126 | 10:00
Faridpur | 136 | 15:00 | 130 | 00:00 | Rangamati | 132 | 06:00 | 128 | 10:00
Fatullah | 130 | 06:00 | 124 | 10:00 | Rangpur | 139 | 08:00 | 124 | 01:00
Fenchuganj | 135 | 19:30 | 131 | 01:00 | Ruppur | 139 | 12:00 | 132 | 21:00
Feni | 130 | 16:00 | 115 | 10:00 | Saidpur | 138 | 07:00 | 124 | 12:00
Ghatail | 136 | 12:00 | 120 | 11:00 | Satkhira | 136 | 16:00 | 119 | 00:00
Ghorashal | 134 | 08:00 | 132 | 00:00 | Satmasjid | 132 | 06:00 | 124 | 11:00
Goalpara | 139 | 15:00 | 126 | 00:00 | Savar | 130 | 03:00 | 121 | 09:00
Gollamari | 138 | 15:00 | 128 | 00:00 | SevenRings | 136 | 13:00 | 129 | 10:00
Gopalganj | 136 | 14:00 | 127 | 00:00 | ShahCement | 129 | 04:00 | 123 | 11:00
Gopalganj-400 | 136 | 15:00 | 130 | 00:00 | Shahjadpur | 137 | 03:00 | 133 | 19:00
Gulshan | 134 | 06:00 | 126 | 10:00 | Shahjibazar | 132 | 14:00 | 124 | 00:00
Halishahar | 130 | 03:00 | 125 | 12:00 | Shahmirpur | 132 | 17:00 | 129 | 01:00
Haripur | 129 | 04:00 | 125 | 09:00 | Shariatpur | 135 | 15:00 | 126 | 00:00
HaripurSBU | 129 | 04:00 | 124 | 12:00 | Sherpur | 137 | 12:00 | 122 | 00:00
Hasnabad | 131 | 04:00 | 125 | 11:00 | Shikalbaha | 121 | 06:00 | 118 | 00:00
Hathazari | 135 | 18:00 | 129 | 23:00 | Shikalbaha-230 | 133 | 17:00 | 129 | 12:00
Ishurdi | 139 | 04:00 | 132 | 23:00 | Shitalakhya | 129 | 06:00 | 123 | 10:00
Jaldhaka | 138 | 07:00 | 121 | 13:00 | Sholosohor | 132 | 06:00 | 129 | 00:00
Jamalpur | 140 | 18:00 | 124 | 11:00 | Shyampur | 129 | 19:00 | 124 | 10:00
Jashore | 134 | 15:00 | 121 | 00:00 | Shyampur-230 | 129 | 04:00 | 124 | 10:00
Jhenaidah | 135 | 15:00 | 125 | 00:00 | Siddhirganj | 130 | 05:00 | 125 | 11:00
Jhenaidah-230 | 135 | 18:00 | 126 | 00:00 | Sirajganj | 137 | 11:00 | 128 | 19:30
Joydebpur | 134 | 13:00 | 124 | 12:00 | Sonargaon | 126 | 00:00 | 121 | 09:00
Joypurhat | 135 | 07:00 | 126 | 00:00 | Sreemongol | 132 | 14:00 | 125 | 00:00
Juldah | 132 | 01:00 | 130 | 00:00 | Sreepur | 134 | 12:00 | 127 | 16:00
Kabirpur | 139 | 12:00 | 117 | 11:00 | Srinagar | 133 | 06:00 | 127 | 11:00
Kachua | 132 | 16:00 | 119 | 10:00 | SSM | 132 | 00:00 | 128 | 10:00
Kaliakoir | 139 | 04:00 | 132 | 09:00 | Sunamganj | 128 | 05:00 | 123 | 00:00
Kallyanpur | 129 | 14:00 | 124 | 10:00 | Sylhet | 131 | 07:00 | 127 | 01:00
Kalurghat | 132 | 03:00 | 129 | 12:00 | Sylhet-132 | 131 | 03:00 | 128 | 23:00
Kamrangirchar | 133 | 05:00 | 126 | 11:00 | Tangail | 135 | 12:00 | 125 | 07:00
Kaptai | 135 | 18:00 | 132 | 14:00 | Thakurgaon | 140 | 21:00 | 124 | 02:00
Kasba | 128 | 15:00 | 118 | 10:00 | TK | 132 | 05:00 | 130 | 00:00
Kazla | 130 | 06:00 | 123 | 11:00 | Tongi | 131 | 04:00 | 125 | 09:00
Keranigonj | 133 | 04:00 | 127 | 11:00 | Ullahpara | 136 | 11:00 | 129 | 19:30
Khagrachori | 131 | 18:00 | 126 | 12:00 | Ullon | 134 | 04:00 | 125 | 11:00
Khulna | 137 | 15:00 | 125 | 00:00 | Uttara | 128 | 05:00 | 121 | 10:00
Khulna(S) | 139 | 15:00 | 128 | 00:00 | UttaraNew | 128 | 06:00 | 121 | 11:00
Khulshi | 130 | 06:00 | 125 | 10:00 | Zigatola | 133 | 05:00 | 127 | 11:00
Kishoreganj | 131 | 12:00 | 123 | 19:00
Kodda | 137 | 12:00 | 123 | 11:00
KSRM | 134 | 16:00 | 128 | 08:00
Kulaura | 134 | 07:00 | 131 | 00:00
Kurigram | 138 | 08:00 | 122 | 18:00
Kushtia | 135 | 15:00 | 127 | 00:00
Lalbag | 133 | 06:00 | 126 | 11:00
Lalmonirhat | 136 | 08:00 | 122 | 18:00
Madanganj | 128 | 05:00 | 123 | 11:00
Madaripur | 137 | 15:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division