## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 08-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-05-2025 | during | 08-05-2025 | during | 08-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 401 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 360 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 292 | 282 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 10 | 40 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 230 | 315 | 335 | 335 | 226 | 226 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 49 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 95 | 143 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 20 | 30 | 30 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 20 | 22 | 22 | 19 | 19 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 0 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 107 | 131 | 135 | 135 | 135 | 135 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 48 | 68 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 350 | 584 | 584 | 420 | 420 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 300 | 350 | 583 | 583 | 420 | 420 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2698 | 3338 | 5257.9 | 5319.9 | 3595.13 | 3657.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 144 | 145 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 42 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 47 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 68 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 70 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 13 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 4.74 | 0 | 4.74 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 13 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1001 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 0 | 3 | 6 | 3 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 454 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1818 | 2396 | 3413.46 | 3405.72 | 3418.46 | 3405.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 209 | 188 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 334 | 344 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 345 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 36 | 35 | 46.94 | 46.94 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 46 | 46 | 55 | 55 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 16 | 195 | 195 | 26 | 26 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 86 | 115 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 16 | 38 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 148 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 70 | 72 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 69 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1539 | 1736.2 | 2468.99 | 2400.99 | 2056.55 | 2017.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 07-05-2025 | during | 08-05-2025 | during | 08-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 121 | 137 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 68 | 112 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 36.18 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 42 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 256.18 | 303 | 601.1 | 549 | 311.6 | 331.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 36 | 38 | 38 | 36 | 36 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 98 | 100 | 113 | 113 | 103 | 103 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 25 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 83 | 84 | 84 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 172 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 7 | 8 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 391 | 343 | 385 | 385 | 352 | 352 | FGMO
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1489 | 1445 | 1554 | 1554 | 1474 | 1474
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 923 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 164 | 178 | 410 | 410 | 185 | 185 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 87 | 0 | 100 | 0 | 100 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 507 | 620 | 1234.2 | 1234.2 | 618 | 618 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1681 | 1713 | 3614.2 | 3514.2 | 2668.01 | 2568.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 220 | 261 | 315 | 315 | 315 | 315 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 3 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 115 | 115 | 125 | 125 | 125 | 125 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1091 | 1225 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.71 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1956.71 | 2155 | 2482.12 | 2481.12 | 2482.12 | 2481.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 49 | 42 | 42 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 178 | 175 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 170 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 32 | 32 | 32 | 32 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 16 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 94 | 94 | 94 | 94 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 106 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 95 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.01 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1347.54 | 1159 | 1364.58 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.41 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 110 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3393.2 | 2064.42 | 2541.58 | 3110.68 | 2944.53 | 3057.89 | 2891.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 51 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 168 | 163 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 107 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.4 | 0 | 6.8 | 0 | 6.8 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 35 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 198 | 0 | 196.89 | 0 | 196.89 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 460.4 | 436 | 700.69 | 467 | 700.69 | 467
System Total |  |  |  |  | 27566.2 | 28535.742 | 13962.71 | 16063.78 | 23203.14 | 22636.46 | 19764.45 | 19293.77
Forecast Scenario (08-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14100 |  | 0 |  | 14100
|  |  |  | 1:00 | 13410 |  | 0 |  | 13410
|  |  |  | 2:00 | 13040 |  | 0 |  | 13040
|  |  |  | 3:00 | 12720 |  | 0 |  | 12720
|  |  |  | 4:00 | 12400 |  | 0 |  | 12400
|  |  |  | 5:00 | 12170 |  | 0 |  | 12170
|  |  |  | 6:00 | 11820 |  | 0 |  | 11820
|  |  |  | 7:00 | 12110 |  | 0 |  | 12110
|  |  |  | 8:00 | 12170 |  | 0 |  | 12170
|  |  |  | 9:00 | 12840 |  | 0 |  | 12840
|  |  |  | 10:00 | 13380 |  | 0 |  | 13380
|  |  |  | 11:00 | 13820 |  | 0 |  | 13820
|  |  |  | 12:00 | 14300 |  | 0 |  | 14300
|  |  |  | 13:00 | 14670 |  | 0 |  | 14670
|  |  |  | 14:00 | 14610 |  | 0 |  | 14610
|  |  |  | 15:00 | 14700 |  | 0 |  | 14700
|  |  |  | 16:00 | 14690 |  | 0 |  | 14690
|  |  |  | 17:00 | 14440 |  | 0 |  | 14440
|  |  |  | 18:00 | 13960 |  | 0 |  | 13960
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15460 |  | 0 |  | 15460
|  |  |  | 19:30 | 15900 |  | 0 |  | 15900
|  |  |  | 20:00 | 15600 |  | 0 |  | 15600
|  |  |  | 21:00 | 15500 |  | 0 |  | 15500
|  |  |  | 22:00 | 15300 |  | 0 |  | 15300
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 37.60°C
Probable Maximum Demand at Day Peak: |  |  | 14300.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15900.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15900.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 332.41 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:33 hrs on 08-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 07-05-2025 | [28 empty] | Date: | 07-05-2025 | [28 empty] | Date: | 07-05-2025 | [28 empty] | Date: | 07-05-2025 | [28 empty] | Date: | 07-05-2025 | [16 empty] | Date: | 07-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1347.540 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17 | 17 | 96 | 132 | 0 | 0 | 35 | 108 | 0 | 16 | 320 | 294 | 350 | 0 | 35 | 0 | 225 | 0 | 0 | 0 | 90 | 19 | 19 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 100 | 60 | 0 | 40 | 0 | 30 | 503 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1006 | 0 | 51 | 10 | 8 | 0 | 355 | 345 | 55 | 189 | 38 | 93 | 50 | 121 | 15 | 18 | 52 | 40 | 16 | 0 | 33 | 305 | 320 | 351 | 39 | 30 | 0 | 102 | 8 | 0 | 84 | 28 | 0 | 18 | 171 | 0 | 105 | 150 | 0 | 0 | 0 | 12 | 7668 | 917 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 0 | 1356 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 153 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 166 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 105 | 220 | 0 | 219 | 1120 | 0 | 6134 | 13802 | 79.09
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 92 | 132 | 0 | 0 | 35 | 108 | 0 | 0 | 320 | 299 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 52 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 30 | 0 | 40 | 0 | 32 | 500 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1007 | 0 | 51 | 0 | 8 | 0 | 355 | 345 | 55 | 197 | 37 | 94 | 50 | 100 | 9 | 18 | 52 | 38 | 0 | 0 | 33 | 310 | 320 | 311 | 39 | 30 | 0 | 87 | 8 | 0 | 84 | 28 | 0 | 18 | 172 | 0 | 47 | 94 | 0 | 0 | 0 | 12 | 7297 | 916 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 157 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 54 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 105 | 220 | 0 | 220 | 1120 | 0 | 5821 | 13118 | 79.08
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 87 | 132 | 0 | 0 | 35 | 108 | 0 | 0 | 320 | 299 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 52 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 30 | 0 | 40 | 0 | 30 | 502 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1004 | 0 | 51 | 0 | 8 | 0 | 355 | 345 | 55 | 196 | 37 | 94 | 50 | 96 | 9 | 18 | 52 | 36 | 0 | 0 | 33 | 310 | 320 | 307 | 39 | 30 | 0 | 85 | 6 | 0 | 84 | 28 | 0 | 18 | 172 | 0 | 48 | 94 | 0 | 0 | 0 | 12 | 7270 | 916 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 421 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 158 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 167 | 54 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 105 | 220 | 0 | 222 | 1000 | 0 | 5474 | 12744 | 79.08
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 17 | 87 | 132 | 0 | 0 | 35 | 108 | 0 | 0 | 320 | 299 | 350 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 52 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 100 | 30 | 0 | 40 | 0 | 30 | 503 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 8 | 0 | 355 | 345 | 55 | 194 | 37 | 93 | 50 | 99 | 9 | 18 | 52 | 36 | 0 | 0 | 33 | 305 | 320 | 312 | 39 | 30 | 0 | 89 | 6 | 0 | 84 | 30 | 0 | 18 | 172 | 10 | 48 | 94 | 0 | 0 | 0 | 12 | 7191 | 916 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 155 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 167 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 115 | 220 | 0 | 221 | 900 | 0 | 5231 | 12422 | 79.07
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 17 | 87 | 132 | 0 | 0 | 17 | 72 | 0 | 0 | 320 | 302 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 52 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 30 | 0 | 40 | 0 | 31 | 407 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 8 | 0 | 355 | 345 | 55 | 202 | 37 | 94 | 50 | 100 | 9 | 18 | 52 | 34 | 0 | 0 | 33 | 315 | 320 | 335 | 39 | 30 | 0 | 96 | 6 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 48 | 94 | 0 | 0 | 0 | 12 | 7076 | 917 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 145 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 169 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 115 | 220 | 0 | 220 | 900 | 0 | 5027 | 12103 | 79.07
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 80 | 98 | 0 | 0 | 17 | 72 | 0 | 0 | 320 | 300 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 35 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 12 | 0 | 40 | 0 | 32 | 406 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 902 | 0 | 51 | 0 | 8 | 0 | 355 | 345 | 55 | 194 | 34 | 68 | 50 | 93 | 9 | 18 | 52 | 34 | 0 | 0 | 33 | 310 | 320 | 320 | 39 | 30 | 0 | 98 | 6 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 48 | 94 | 0 | 0 | 0 | 12 | 6908 | 917 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 411 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 141 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 170 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 9 | 115 | 220 | 0 | 221 | 840 | 0 | 4966 | 11874 | 79.06
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 68 | 118 | 0 | 0 | 17 | 72 | 0 | 0 | 320 | 300 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 2 | 35 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 32 | 405 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 806 | 1 | 51 | 0 | 8 | 0 | 322 | 345 | 55 | 216 | 37 | 50 | 50 | 68 | 9 | 18 | 34 | 28 | 0 | 5 | 33 | 310 | 320 | 355 | 39 | 30 | 0 | 103 | 6 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 48 | 94 | 0 | 0 | 2.6 | 12 | 6761.6 | 916 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.67 | 412 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.99 | 163 | 0 | 147 | 0 | 0 | 0 | 414 | 0 | 0.2 | 0 | 170 | 53 | 0 | 2 | 0 | 0 | 0 | 0 | 10 | 0.03 | 0 | 200 | 9 | 115 | 220 | 0 | 221 | 700 | 0 | 4764.89 | 11526.49 | 79.06
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 80 | 117 | 0 | 0 | 23 | 72 | 0 | 0 | 320 | 298 | 350 | 0 | 0 | 0 | 225 | 0 | 0 | 7 | 35 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 1 | 40 | 0 | 21 | 405 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 903 | 5 | 51 | 0 | 8 | 0 | 323 | 345 | 55 | 195 | 37 | 50 | 50 | 66 | 9 | 20 | 34 | 30 | 0 | 17 | 33 | 300 | 320 | 310 | 39 | 30 | 0 | 101 | 6 | 0 | 84 | 30 | 0 | 18 | 172 | 17 | 68 | 122 | 0 | 0 | 10.73 | 12 | 6839.73 | 916 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.47 | 412 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 9.89 | 164 | 0 | 147 | 0 | 0 | 0 | 414 | 0 | 0.94 | 0 | 170 | 53 | 0 | 7 | 0 | 0 | 0 | 1.7 | 38 | 0.15 | 0 | 250 | 6 | 115 | 220 | 0 | 221 | 775 | 0 | 4973.15 | 11812.88 | 79.05
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 85 | 116 | 0 | 0 | 35 | 108 | 0 | 0 | 400 | 300 | 300 | 0 | 0 | 0 | 225 | 0 | 0 | 14 | 35 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 2 | 40 | 0 | 2 | 405 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 900 | 10 | 51 | 0 | 8 | 0 | 353 | 300 | 55 | 204 | 34 | 50 | 50 | 60 | 9 | 8 | 34 | 28 | 0 | 34 | 32 | 305 | 320 | 345 | 39 | 30 | 0 | 92 | 6 | 0 | 84 | 20 | 0 | 18 | 172 | 17 | 68 | 122 | 0 | 1 | 23.96 | 12 | 6884.96 | 869 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.11 | 413 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 23.93 | 171 | 0 | 171 | 0 | 0 | 0 | 414 | 0 | 2.01 | 0 | 167 | 53 | 0 | 15 | 0 | 0 | 0 | 3.7 | 84 | 0.31 | 0 | 250 | 6 | 106 | 180 | 0 | 221 | 798 | 0 | 4987.06 | 11872.02 | 79.05
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 17 | 94 | 115 | 0 | 0 | 35 | 72 | 0 | 0 | 400 | 289 | 300 | 0 | 0 | 0 | 226 | 0 | 0 | 21 | 35 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 20 | 4 | 40 | 0 | 2 | 407 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 900 | 15 | 51 | 0 | 8 | 0 | 354 | 345 | 53 | 196 | 34 | 50 | 50 | 68 | 9 | 8 | 34 | 30 | 0 | 50 | 32 | 305 | 320 | 363 | 39 | 30 | 0 | 101 | 6 | 0 | 81 | 30 | 0 | 18 | 173 | 17 | 68 | 122 | 0 | 1 | 36.95 | 12 | 7094.95 | 869 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 409 | 0 | 929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 35.44 | 177 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 3.12 | 0 | 167 | 53 | 0 | 24 | 0 | 0 | 0 | 5.5 | 134 | 0.47 | 0 | 307 | 6 | 115 | 220 | 0 | 221 | 914 | 0 | 5449.53 | 12544.48 | 79.04
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 17 | 104 | 95 | 0 | 0 | 35 | 35 | 0 | 0 | 400 | 289 | 300 | 0 | 0 | 0 | 226 | 0 | 0 | 28 | 70 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 20 | 2 | 40 | 0 | 2 | 457 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1000 | 17 | 51 | 0 | 8 | 0 | 350 | 345 | 50 | 190 | 34 | 50 | 50 | 65 | 9 | 8 | 34 | 32 | 0 | 62 | 25 | 300 | 320 | 364 | 38 | 30 | 0 | 101 | 6 | 0 | 81 | 30 | 0 | 18 | 173 | 17 | 68 | 122 | 0 | 1 | 45.94 | 12 | 7253.94 | 922 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 450 | 0 | 1105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 42.31 | 177 | 0 | 169 | 0 | 0 | 0 | 414 | 0 | 3.75 | 0 | 167 | 53 | 0 | 32 | 0 | 0 | 0 | 4.3 | 142 | 0.65 | 0 | 307 | 6 | 107 | 220 | 0 | 221 | 1037 | 0 | 5833.01 | 13086.95 | 79.04
11:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 19 | 17 | 104 | 95 | 0 | 0 | 35 | 35 | 0 | 35 | 400 | 288 | 300 | 0 | 0 | 0 | 230 | 0 | 0 | 31 | 70 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 20 | 5 | 40 | 0 | 2 | 455 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 1000 | 14 | 51 | 28 | 8 | 0 | 345 | 345 | 46 | 199 | 34 | 52 | 50 | 82 | 9 | 15 | 34 | 34 | 0 | 67 | 25 | 305 | 320 | 362 | 38 | 30 | 0 | 101 | 7 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 68 | 120 | 0 | 2 | 46.59 | 12 | 7426.59 | 922 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 457 | 0 | 1169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 40.78 | 178 | 0 | 157 | 0 | 0 | 0 | 414 | 0 | 3.28 | 0 | 168 | 53 | 0 | 34 | 0 | 0 | 0 | 6.2 | 166 | 0.68 | 0 | 307 | 6 | 110 | 220 | 0 | 214 | 1094 | 0 | 6062.94 | 13489.53 | 79.03
12:00 | 16 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 107 | 95 | 95 | 10 | 35 | 35 | 0 | 48 | 400 | 292 | 300 | 0 | 35 | 0 | 230 | 0 | 0 | 32 | 70 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 1 | 68 | 0 | 0 | 70 | 20 | 3 | 38 | 0 | 2 | 454 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1001 | 18 | 51 | 86 | 8 | 0 | 334 | 345 | 46 | 209 | 36 | 70 | 70 | 100 | 9 | 20 | 34 | 36 | 0 | 69 | 16 | 300 | 320 | 391 | 38 | 30 | 0 | 98 | 7 | 0 | 84 | 30 | 0 | 18 | 173 | 17 | 68 | 121 | 0 | 2 | 36.18 | 12 | 7800.18 | 923 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 507 | 0 | 1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 36.41 | 178 | 0 | 164 | 0 | 0 | 0 | 414 | 0 | 3.01 | 0 | 168 | 52 | 0 | 35 | 0 | 0 | 0 | 7.4 | 198 | 0.71 | 0 | 307 | 3 | 115 | 220 | 0 | 220 | 1091 | 0 | 6162.53 | 13962.71 | 79.02
13:00 | 16 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 0 | 131 | 95 | 210 | 55 | 35 | 72 | 0 | 51 | 300 | 282 | 300 | 0 | 35 | 0 | 280 | 0 | 0 | 30 | 108 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 5 | 68 | 0 | 0 | 70 | 20 | 4 | 38 | 0 | 2 | 504 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1050 | 17 | 51 | 110 | 8 | 0 | 341 | 345 | 48 | 184 | 36 | 74 | 70 | 110 | 9 | 20 | 55 | 38 | 0 | 64 | 16 | 305 | 320 | 337 | 38 | 30 | 0 | 100 | 7 | 0 | 83 | 30 | 0 | 18 | 173 | 17 | 68 | 123 | 0 | 2 | 45.41 | 12 | 8071.41 | 922 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 561 | 0 | 1317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 31.52 | 176 | 0 | 170 | 0 | 0 | 0 | 350 | 0 | 4.63 | 0 | 165 | 53 | 0 | 34 | 0 | 0 | 0 | 7.8 | 182 | 0.63 | 0 | 307 | 8 | 105 | 180 | 0 | 220 | 1100 | 0 | 6256.58 | 14327.99 | 79.01
14:00 | 16 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 48 | 0 | 132 | 127 | 294 | 55 | 35 | 72 | 0 | 51 | 300 | 284 | 270 | 0 | 35 | 0 | 310 | 0 | 0 | 27 | 108 | 20 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 10 | 66 | 0 | 0 | 70 | 20 | 4 | 38 | 0 | 2 | 505 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1050 | 16 | 51 | 113 | 8 | 0 | 300 | 300 | 50 | 185 | 35 | 75 | 70 | 131 | 9 | 20 | 70 | 38 | 0 | 58 | 31 | 305 | 320 | 352 | 38 | 30 | 0 | 93 | 0 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 76 | 112 | 0 | 2 | 29.69 | 12 | 8113.69 | 922 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 559 | 0 | 1317.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 26.2 | 176 | 0 | 170 | 0 | 0 | 0 | 320 | 0 | 5.24 | 0 | 168 | 52 | 0 | 31 | 0 | 0 | 0 | 7.3 | 175 | 0.65 | 0 | 285 | 9 | 115 | 180 | 0 | 220 | 1050 | 0 | 6135.58 | 14249.27 | 79
15:00 | 16 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 38 | 0 | 130 | 126 | 293 | 55 | 35 | 72 | 0 | 51 | 300 | 293 | 270 | 0 | 35 | 0 | 308 | 0 | 0 | 21 | 108 | 18 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 8 | 72 | 0 | 0 | 70 | 20 | 3 | 40 | 0 | 2 | 505 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1050 | 13 | 51 | 103 | 8 | 0 | 330 | 340 | 48 | 204 | 21 | 75 | 70 | 148 | 9 | 20 | 101 | 38 | 0 | 44 | 31 | 310 | 320 | 374 | 38 | 30 | 0 | 101 | 0 | 0 | 83 | 30 | 0 | 17 | 173 | 17 | 67 | 115 | 0 | 1 | 28.97 | 12 | 8210.97 | 926 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 560 | 0 | 1323.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 35.42 | 176 | 0 | 168 | 0 | 0 | 0 | 370 | 0 | 3.26 | 0 | 166 | 53 | 30 | 25 | 0 | 0 | 0 | 3.8 | 137 | 0.34 | 0 | 250 | 9 | 115 | 220 | 0 | 219 | 1050 | 0 | 6117.37 | 14328.34 | 78.99
16:00 | 33 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 393 | 0 | 0 | 54 | 12 | 127 | 126 | 293 | 55 | 35 | 90 | 0 | 66 | 330 | 292 | 300 | 0 | 35 | 0 | 308 | 0 | 0 | 15 | 108 | 18 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 5 | 67 | 0 | 0 | 70 | 20 | 2 | 40 | 0 | 2 | 504 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 1050 | 8 | 51 | 105 | 8 | 0 | 330 | 340 | 45 | 208 | 21 | 92 | 70 | 148 | 25 | 20 | 103 | 34 | 0 | 25 | 31 | 315 | 320 | 373 | 37 | 30 | 0 | 100 | 7 | 0 | 82 | 30 | 0 | 16 | 172 | 17 | 86 | 115 | 0 | 1 | 18.67 | 12 | 8355.67 | 926 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 560 | 0 | 1272.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 23.19 | 176 | 0 | 168 | 0 | 0 | 0 | 360 | 0 | 2.03 | 0 | 169 | 53 | 35 | 15 | 0 | 0 | 0 | 4 | 77 | 0.33 | 0 | 265 | 9 | 115 | 220 | 0 | 221 | 1045 | 0 | 5974.26 | 14329.93 | 78.99
17:00 | 32 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 44 | 17 | 130 | 126 | 245 | 55 | 35 | 90 | 0 | 67 | 330 | 287 | 300 | 0 | 17 | 0 | 314 | 0 | 0 | 7 | 108 | 19 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 67 | 0 | 0 | 70 | 20 | 1 | 40 | 0 | 2 | 503 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1050 | 3 | 51 | 112 | 8 | 0 | 332 | 345 | 44 | 205 | 25 | 87 | 70 | 131 | 36 | 20 | 87 | 38 | 0 | 12 | 38 | 310 | 320 | 355 | 37 | 30 | 0 | 100 | 8 | 0 | 82 | 30 | 0 | 16 | 172 | 17 | 86 | 118 | 0 | 0 | 8.82 | 12 | 8235.82 | 926 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 518 | 0 | 1271.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 10.37 | 175 | 0 | 168 | 0 | 0 | 0 | 414 | 0 | 0.9 | 0 | 172 | 52 | 35 | 7 | 0 | 0 | 0 | 1.9 | 40 | 0.15 | 0 | 265 | 8 | 115 | 220 | 0 | 220 | 1048 | 0 | 5875.03 | 14110.85 | 78.97
18:00 | 32 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 35 | 17 | 130 | 127 | 210 | 55 | 35 | 90 | 0 | 68 | 330 | 284 | 300 | 0 | 17 | 0 | 306 | 0 | 0 | 1 | 108 | 19 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 2 | 73 | 0 | 0 | 70 | 20 | 0 | 40 | 0 | 2 | 455 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 1050 | 0 | 51 | 118 | 8 | 0 | 332 | 345 | 44 | 194 | 29 | 73 | 70 | 136 | 37 | 20 | 61 | 38 | 0 | 1 | 38 | 320 | 320 | 348 | 36 | 30 | 0 | 91 | 8 | 0 | 82 | 30 | 0 | 16 | 172 | 17 | 102 | 134 | 0 | 0 | 0.62 | 10 | 8084.62 | 926 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 509 | 0 | 1219.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.9 | 175 | 0 | 169 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 167 | 52 | 35 | 1 | 0 | 0 | 0 | 0.3 | 7 | 0.02 | 0 | 280 | 8 | 100 | 180 | 0 | 219 | 1002 | 0 | 5582.35 | 13666.97 | 78.96
19:00 | 65 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 39 | 17 | 131 | 127 | 245 | 55 | 35 | 162 | 0 | 68 | 330 | 296 | 300 | 0 | 35 | 0 | 309 | 0 | 0 | 0 | 160 | 20 | 20 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 95 | 40 | 0 | 100 | 70 | 0 | 40 | 0 | 3 | 576 | 0 | 0 | 0 | 0 | 5 | 144 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 8 | 0 | 338 | 345 | 45 | 195 | 35 | 72 | 70 | 140 | 38 | 20 | 78 | 44 | 1 | 0 | 38 | 315 | 320 | 373 | 36 | 30 | 0 | 96 | 8 | 0 | 83 | 25 | 0 | 18 | 172 | 20 | 112 | 146 | 0 | 0 | 0 | 6 | 8843 | 913 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 555 | 15 | 1363.67 | 0 | 0 | 0 | 19 | 0 | 74 | 50 | 17 | 0 | 0 | 22 | 0 | 176 | 0 | 169 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 150 | 52 | 112 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 262 | 1063 | 0 | 6316.67 | 15159.67 | 78.95
19:30 | 81 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 54 | 17 | 131 | 143 | 294 | 55 | 35 | 162 | 0 | 68 | 360 | 285 | 300 | 0 | 35 | 0 | 311 | 0 | 0 | 0 | 160 | 20 | 20 | 0 | 300 | 0 | 15 | 0 | 0 | 0 | 102 | 45 | 17 | 100 | 88 | 0 | 40 | 1 | 6 | 575 | 17 | 0 | 0 | 8 | 21 | 144 | 0 | 0 | 0 | 1224 | 0 | 51 | 116 | 16 | 0 | 342 | 345 | 46 | 197 | 35 | 72 | 70 | 146 | 38 | 20 | 114 | 44 | 52.2 | 0 | 38 | 315 | 320 | 359 | 36 | 30 | 0 | 98 | 8 | 0 | 83 | 25 | 0 | 18 | 172 | 35 | 112 | 137 | 0 | 0 | 0 | 12 | 9190.2 | 880 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 614 | 35 | 1369.22 | 0 | 45 | 0 | 108 | 0 | 93 | 108 | 25 | 0 | 0 | 22 | 0 | 175 | 0 | 169 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 52 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 261 | 1240 | 0 | 6826.22 | 16016.42 | 78.95
20:00 | 49 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 131 | 143 | 294 | 40 | 35 | 162 | 0 | 68 | 360 | 282 | 350 | 0 | 35 | 0 | 315 | 0 | 0 | 0 | 160 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 102 | 47 | 0 | 100 | 88 | 0 | 40 | 13 | 13 | 575 | 0 | 0 | 0 | 8 | 42 | 144 | 0 | 0 | 0 | 1224 | 0 | 51 | 115 | 16 | 0 | 344 | 345 | 46 | 188 | 35 | 72 | 70 | 148 | 38 | 20 | 114 | 44 | 52.2 | 0 | 38 | 310 | 320 | 343 | 36 | 30 | 0 | 100 | 8 | 0 | 83 | 25 | 0 | 18 | 172 | 42 | 112 | 137 | 0 | 0 | 0 | 12 | 9218.2 | 880 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 35 | 1364.58 | 0 | 49 | 0 | 106 | 0 | 93 | 95 | 37 | 16 | 0 | 22 | 0 | 175 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 51 | 115 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 115 | 220 | 0 | 261 | 1225 | 0 | 6845.58 | 16063.78 | 78.94
21:00 | 24 | 52 | 10 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 131 | 143 | 225 | 0 | 35 | 162 | 0 | 68 | 360 | 297 | 350 | 0 | 35 | 0 | 314 | 0 | 0 | 0 | 160 | 20 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 102 | 47 | 0 | 100 | 88 | 0 | 40 | 34 | 16 | 575 | 0 | 0 | 0 | 0 | 51 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 16 | 0 | 343 | 345 | 45 | 198 | 32 | 72 | 70 | 146 | 38 | 20 | 114 | 44 | 52.2 | 0 | 39 | 310 | 320 | 343 | 36 | 30 | 0 | 100 | 8 | 0 | 83 | 25 | 0 | 18 | 170 | 54.5 | 112 | 138 | 0 | 0 | 0 | 12 | 9154.7 | 927 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619 | 53 | 1363.17 | 0 | 35 | 0 | 112 | 0 | 93 | 70 | 29 | 16 | 0 | 22 | 0 | 175 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 115 | 220 | 0 | 261 | 1244 | 0 | 6895.17 | 16049.87 | 78.93
22:00 | 24 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 131 | 143 | 160 | 0 | 35 | 162 | 0 | 68 | 320 | 303 | 300 | 0 | 35 | 0 | 315 | 0 | 0 | 0 | 160 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 102 | 47 | 0 | 100 | 50 | 0 | 40 | 17 | 10 | 575 | 0 | 0 | 0 | 0 | 34 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 122 | 16 | 0 | 347 | 345 | 44 | 195 | 33 | 78 | 70 | 145 | 38 | 20 | 114 | 46 | 34 | 0 | 37 | 305 | 320 | 385 | 36 | 30 | 0 | 96 | 8 | 0 | 83 | 25 | 0 | 18 | 168 | 50 | 113 | 137 | 0 | 0 | 0 | 12 | 8905 | 927 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 60 | 1366.78 | 0 | 51 | 0 | 113 | 0 | 93 | 50 | 29 | 34 | 0 | 22 | 0 | 175 | 0 | 172 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 161 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 115 | 220 | 0 | 260 | 1244 | 0 | 6851.78 | 15756.78 | 78.92
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 398 | 0 | 0 | 54 | 17 | 131 | 144 | 160 | 0 | 35 | 162 | 0 | 68 | 320 | 300 | 300 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 160 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 102 | 47 | 0 | 100 | 0 | 0 | 40 | 0 | 28 | 575 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 16 | 0 | 336 | 345 | 47 | 210 | 33 | 93 | 70 | 168 | 38 | 20 | 114 | 48 | 16 | 0 | 39 | 315 | 320 | 378 | 36 | 30 | 0 | 103 | 8 | 0 | 83 | 25 | 0 | 18 | 168 | 17 | 113 | 136 | 0 | 0 | 0 | 12 | 8769 | 926 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 71 | 1364.55 | 0 | 50 | 0 | 113 | 0 | 93 | 50 | 29 | 34 | 0 | 22 | 0 | 176 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 125 | 220 | 0 | 261 | 1244 | 0 | 6943.55 | 15712.55 | 78.91
Total KWH | 324144 | 739200 | 402720 | 0 | 0 | 0 | 0 | 0 | 9208800 | 0 | 0 | 669960 | 389160 | 2668752 | 2932800 | 2859862 | 455516 | 825254 | 2335680 | 0 | 806400 | 8237000 | 7100393 | 7778636 | 0 | 431322 | 0 | 6392957 | 0 | 0 | 220023 | 2175600 | 482400 | 488520 | 0 | 7993181.82 | 8782 | 8029 | 0 | 0 | 40320 | 1138682 | 229632 | 7724 | 2043840 | 682560 | 31918 | 960000 | 95300 | 355200 | 11658181.82 | 1672 | 0 | 0 | 6813 | 184836 | 3486465 | 0 | 0 | 0 | 24763634 | 134190 | 1187752 | 1507127 | 267636 | 0 | 8513000 | 8226000 | 1185600 | 4879000 | 815904 | 1815360 | 1435520 | 2769600 | 446880 | 423380 | 1666680 | 891840 | 215170 | 514991 | 772496 | 7487000 | 7642900 | 8883000 | 895000 | 667920 | 0 | 2344745 | 157176 | 0 | 1993920 | 683904 | 0 | 425000 | 4556040 | 484200 | 1819200 | 2810400 | 0 | 14100 | 335750 | 288240 | 190778490.64 | 22142545 | 4040352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1286640 | 12312730 | 299520 | 27807273 | 0 | 232361 | 0 | 592320 | 0 | 486208 | 403776 | 128202 | 111154 | 806690 | 111507 | 354752 | 4146273 | 0 | 4142100 | 0 | 0 | 0 | 9621527 | 0 | 30600 | 0 | 4061000 | 1164218 | 848463 | 241167 | 598492 | 0 | 0 | 52654.8 | 1339200 | 5055 | 71424 | 6785000 | 201703 | 2730000 | 5328380 | 0 | 5490360 | 25362909.09 | 0 | 143336555.89 | 334115046.53

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 07-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13962.71 | MW | 12:00 Hr. | Energy Generated |  |  | 334.115 |  | MKWHr.
| Day Peak Demand |  |  | 14001.38 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.744 |  | MKWHr.
| Evening Peak Generation |  |  | 16063.78 | MW | 20:00 Hr. | Energy Demand |  |  | 334.859 |  | MKWHr.
| Evening Peak Demand |  |  | 16133.78 | MW | 20:00 Hr. | Maximum Temperature |  |  | 35.7 |  | °C
| Minimum Generation of the Day |  |  | 11526.49 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1042.24 |  | MMCFD
| Maximum Generation of the Day |  |  | 16063.78 | MW | 20:00 Hr. | Production Cost per KWHr |  |  | 6.755 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 47.6819 | 0 | 18.0164 | 0 | 0 | 0.22002 | 0 | 0 | 65.9183 | Gas | 144.4043 | Gas | 509237289.8994
| Chattogram Zone |  |  | 3.8417 | 36.4218 | 4.4079 | 0 | 0.96 | 0.16611 | 0 | 0.04032 | 45.8378 | Coal | 91.598 | Coal | 617332807.8245
| Cumilla Zone |  |  | 26.9338 | 0 | 9.1933 | 0 | 0 | 0.51499 | 0.89184 | 0 | 37.5339 | HFO | 40.903 | HFO | 768976593.64
| Mymensingh Zone |  |  | 0 | 0 | 5.402 | 0 | 0 | 0.34985 | 0 | 0 | 5.7519 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7366 | Hydro | 0.96 | Hydro | 96000
| Khulna Zone |  |  | 4.0404 | 12.3127 | 0.29952 | 0 | 0 | 1.2866 | 22.1425 | 0 | 40.0818 | Solar | 5.3677 | Solar | 87693194.558
| Barishal Zone |  |  | 8.2601 | 37.6383 | 0.071424 | 0 | 0 | 0.005055 | 0 | 0 | 45.9748 | Import | 50.8417 | Import | 273009174.87
| Rajshahi Zone |  |  | 17.9099 | 0 | 2.0655 | 0 | 0 | 1.192 | 27.8073 | 0 | 48.9747 | Wind | 0.04032 | Wind | 590284.8
| Rangpur Zone |  |  | 0 | 5.2252 | 1.447 | 0 | 0 | 1.633 | 0 | 0 | 8.3052
| Total |  |  | 144.4043 | 91.598 | 40.903 | 0 | 0.96 | 5.3677 | 50.8417 | 0.04032 | 334.115
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 509237289.8994 |  | Hydro | 96000
|  |  |  | Coal | 617332807.8245 |  | Solar | 87693194.558
|  |  |  | HFO | 768976593.64 |  | Import | 273009174.87
|  |  |  | HSD | 0 |  | Wind | 590284.8
[5 empty] | Total: | 225,69,35,345 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1425 | Peak Hr Flow | 880.00 MW at 20:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36328600.06 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.8073 | Peak Hr Flow | 1364.58 MW at 20:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 571 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.89184 | Peak Hr Flow | 44.00 MW at 20:00 hrs.
Maximum Power Flow: |  |  | MW: | 884 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.8417 | Peak Hr Flow | 2288.58 MW at 20:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (20:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 18 |  | 5614
|  |  |  | Chattogram |  | 0 |  | 1521
|  |  |  | Cumilla |  | 10 |  | 1473
|  |  |  | Mymensingh |  | 25 |  | 1286
|  |  |  | Sylhet |  | 0 |  | 641
|  |  |  | Khulna |  | 0 |  | 1883
|  |  |  | Barishal |  | 0 |  | 466
|  |  |  | Rajshahi |  | 0 |  | 1650
|  |  |  | Rangpur |  | 14 |  | 1038
|  |  |  | Total |  | 67 |  | 15572
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:04 | Chandina 132/33kV S/S TR-3 HT is restored.
|  | 08:05 | Chandina 132/33kV S/S TR-3 LT is restored.
| 09:09 | 11:19 | Sherpur 132/33kV S/S Transformer- 01 HT Scheduled S/D
| 09:12 | 11:19 | Sherpur 132/33kV S/S Transformer- 01 LT Scheduled S/D
| 09:21 | 15:18 | Barishal 230/132kV S/S Gopalgonj CKT-1 Scheduled S/D Due to Line differential and
teleprotection establishment work.
| 09:22 | 15:19 | Gopalganj 400/132kV S/S 230kV Barisal CKT-01 Project Work S/D
| 09:38 | 12:32 | Bashundhara-Tongi 132 kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Emergency
maintenance work
| 10:35 | 12:33 | Narshingdi 132/33kV S/S T-1 LT Forced S/D Due to T-1 ট্রান্সফরমারের ৩৩ কেভি Bushing (
Y-Phase) টার্মিনাল পয়েন্টে Oil Leakage হওয়ায়
| 10:35 | 12:33 | Narshingdi 132/33kV S/S T-1 HT Forced S/D Due to T-1 ট্রান্সফরমারের ৩৩ কেভি Bushing (
Y-Phase) টার্মিনাল পয়েন্টে Oil Leakage হওয়ায়
| 11:12 | 14:05 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to High
Temperature maintenance of Gantry Clam-T
|  | 12:33 | Narshingdi 132/33kV S/S T-1 HT is restored.
|  | 12:33 | Narshingdi 132/33kV S/S T-1 HT is restored.
|  | 12:58 | Kaliakoir 400/230/132kV S/S 400kV Bus 1 is restored.
| 13:13 | 15:20 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end. | [7 empty] | 50.0MW load
interrup. Manikganj
132/33kV end
| 13:17 | 15:27 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Scheduled S/D | [7 empty] | 50.0MW load
interrup.
| 13:33 | 15:00 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to Red hot appeared in | [7 empty] | 45.0MW load
|  |  | bus coupler between 33kv Bus section 02 and 03 | [7 empty] | interrup.
| 13:34 | 14:58 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to Red hot appeared in | [7 empty] | 45.0MW load
|  |  | bus coupler between 33kv Bus section 02 and 03 | [7 empty] | interrup.
| 13:58 | 19:37 | Ghorasal- Ishwardi 230 kV Ckt-1 Scheduled S/D from Ishurdi 230/132kV end Due to Request
by NLDC
|  | 14:55 | BIPTC S/S 20DF24 is restored.
| 15:23 | 17:41 | Benapole 132/33kV S/S Transformer-1(406T) LT Scheduled S/D Due to 33 KV feeder | [7 empty] | 25.0MW load
|  |  | maintenance work of pbs | [7 empty] | interrup.
| 15:24 | 17:40 | Benapole 132/33kV S/S Transformer-1(406T) HT Scheduled S/D Due to 33 KV feeder | [7 empty] | 25.0MW load
|  |  | maintenance work of pbs | [7 empty] | interrup.
| 15:27 | 18:47 | Gopalganj 400/132kV S/S 230kV Barisal CKT-02 Project Work S/D
| 15:28 | 18:47 | Barishal 230/132kV S/S Gopalgonj CKT-2 Scheduled S/D Due to Line differential and
teleprotection work
| 15:34 | 16:45 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to 33 KV side Red hot at Anondoh Bazar | [7 empty] | 45.0MW load
|  |  | feeder | [7 empty] | interrup.
| 15:34 | 16:48 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to 33 kv side red hot at Anondoh Bazar | [7 empty] | 45.0MW load
|  |  | feeder | [7 empty] | interrup.
| 16:31 | 17:40 | Munshiganj 132/33kV S/S Transformer-2 LT Forced S/D Due to 33 kv incoming -02 Isolator | [7 empty] | 55.0MW load
|  |  | Maintenance due to Red Hot | [7 empty] | interrup.
|  | 17:23 | Rangpur-Saidpur 132kV Ckt-1 is restored.
| 17:40 | 18:03 | Fatullah-Shyampur(New) 132 kV Ckt-2 Tripped from Fatullah 132/33kV end showing Relay
details: Main-1 general trip, Comm. Distance Carrier Send, Dist. Zone 1 trip
relays Due to None
|  | 18:45 | Gopalganj 400/132kV S/S 400kV Bus-01 is restored.
| 18:51 | 19:52 | Kodda 132/33kV S/S Tr-5 (446T) LT Scheduled S/D Due to 33 KV Feeder Fault
| 18:51 | 19:50 | Kodda 132/33kV S/S Tr-5 (446T) HT Scheduled S/D Due to 33 KV Feeder Fault
| 20:00 |  | Evening Peak Generation: 16063 MW.
| 21:25 | 22:43 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Forced S/D from Rangpur 132/33kV end Due | [7 empty] | 26.0MW load
|  |  | to teamparature high | [7 empty] | interrup. Rangpur
132/33kV end
| 21:35 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Tripped showing OC/EF relays Due to Flashing | [7 empty] | 55.0MW load
interrup.
| 23:41 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to Red hot maintenance | [7 empty] | 30.0MW load
interrup.
| 05:18 |  | Kodda-Rajendrapur 132kV Ckt-1 Forced S/D from Rajendrapur 132/33kV end Due to For kodda
ckt-1 red hot maintenance work in DS at kodda sub-station
| 07:47 |  | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 07-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9208800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 360 | 8237000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 282 | 7100393 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 40 | 455516 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 315 | 6392957 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 49 | 324144 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 669960 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 2932800 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 825254 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 431322 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 20 | 482400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 488520 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 0 | 402720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2859862 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2668752 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 739200 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 68 | 806400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2335680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 220023 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 389160 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 7993181.82 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 350 | 7778636 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2175600 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3338 | 65918280.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | -
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 6813 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 134190 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 960000 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 144 | 3486465 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 42 | 184836 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 47 | 229632 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 1138682 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2043840 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 13 | 355200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 31918 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 8029 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 7724 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 13 | 95300 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 682560 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 8782 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 1672 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 24763634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 40320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 11658181.82 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2396 | 45837778.82
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 4879000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 344 | 8513000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8226000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 815904 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 1185600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 267636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1187752 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 115 | 1507127 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 38 | 772496 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1435520 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 148 | 2769600 | FGMO
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 44 | 891840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 215170 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 423380 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1666680 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 446880 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 1815360 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 514991 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1736.2 | 37533936
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 137 | 2810400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 112 | 1819200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 335750 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 288240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 42 | 484200 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 303 | 5751890
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 895000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 667920 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 2344745 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 25 | 683904 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1993920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 172 | 4556040 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 425000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 157176 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7487000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 343 | 8883000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7642900 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1445 | 35736605
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 22142545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 178 | 4040352 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 299520 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 1286640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 620 | 12312730 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1713 | 40081787
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 261 | 5490360 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 71424 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 201703 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 115 | 2730000 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1225 | 25362909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5328380 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6785000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5055 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2155 | 45974831.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 49 | 232361 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 37 | 128202 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 175 | 4146273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 170 | 4142100 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9621527 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 111507 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 16 | 111154 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 486208 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 106 | 592320 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 403776 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 30600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1347.54 | 1364.58 | 27807273 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 354752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 806690 | -
Rajshahi Area Total |  |  |  |  | 3393.2 | 2541.58 | 48974743
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1164218 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 163 | 4061000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 107 | 598492 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 52654.8 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 848463 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 241167 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1339200 | -
Rangpur Area Total |  |  |  |  | 950 | 436 | 8305194.8
Eastern Grid Total |  |  |  |  | 16921.242 | 9218.2 | 190778490.64
Western Grid Total |  |  |  |  | 11614.5 | 6845.58 | 143336555.89
National Grid Total |  |  |  |  | 28535.742 | 16063.78 | 334115046.53
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 07-05-2025
Zone Total Scenario at Evening Peak Hour (20:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10482.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5024 | MW
i) Dhaka area |  |  | 5596.2 |  | MW | i) Khulna area |  |  |  | 1883.3 | MW
ii) Chattogram area |  |  | 1521.4 |  | MW | ii) Barishal area |  |  |  | 466.5 | MW
iii) Cumilla area |  |  | 1462.93 |  | MW | iii) Rajshahi area |  |  |  | 1650.2 | MW
iv) Mymensingh area |  |  | 1261 |  | MW | iv) Rangpur area |  |  |  | 1024 | MW
v) Sylhet area |  |  | 641 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15506.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 85 | 19:00 | 133 | Patuakhali | 83 | 22:00
2 | AKSML | 23 | 10:00 | 68 | Jaldhaka | 81 | 19:30 | 134 | Payra | 34 | 22:00
3 | Aftabnagar | 38 | 18:30 | 69 | Jamalpur | 146 | 19:30 | 135 | Postogola | 59 | 13:00
4 | Agargaon | 137 | 13:00 | 70 | Jashore | 149 | 19:00 | 136 | Purbachal | 20 | 21:00
5 | Agrabad | 102 | 18:30 | 71 | Jhenaidah | 137 | 20:00 | 137 | Purbasadipur | 133 | 19:30
6 | Amnura | 39 | 20:00 | 72 | Joydebpur | 163 | 16:00 | 138 | Rahanpur | 30 | 22:00
7 | Ashuganj | 125 | 22:00 | 73 | Joypurhat | 71 | 23:00 | 139 | Rahim | 49 | 18:00
8 | BSRM | 179 | 20:00 | 74 | Juldah | 18 | 00:00 | 140 | Rajbari | 85 | 19:00
9 | Bagerhat | 92 | 23:00 | 75 | KSRM | 16 | 23:00 | 141 | Rajendrapur | 147 | 19:30
10 | Bajitpur | 55 | 20:00 | 76 | Kabirpur | 284 | 11:00 | 142 | Rajshahi | 127 | 22:00
11 | Bakulia | 105 | 19:30 | 77 | Kachua | 93 | 19:30 | 143 | Rajshahi-230 | 92 | 21:00
12 | Banani | 40.8 | 15:00 | 78 | Kallyanpur | 108 | 19:00 | 144 | Ramganj | 120 | 21:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kalurghat | 44 | 19:00 | 145 | Rampur | 45 | 23:00
14 | Barapukuria | 69 | 21:00 | 80 | Kamrangirchar | 69 | 12:00 | 146 | Rangamati | 18 | 19:30
15 | Barguna | 24 | 23:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 159 | 19:00
16 | Barishal | 110 | 13:00 | 82 | Kasba | 36 | 20:00 | 148 | Ruppur | 7.8 | 11:00
17 | Barishal-230 | 108 | 20:00 | 83 | Kazla | 105 | 16:00 | 149 | SSM | 9 | 00:00
18 | Baroaulia | 85.5 | 16:00 | 84 | Keranigonj | 83 | 19:00 | 150 | Saidpur | 122 | 19:30
19 | Baroirhat | 65 | 19:00 | 85 | Khagrachori | 32 | 19:30 | 151 | Satkhira | 144 | 22:00
20 | Bashundhara | 184 | 14:00 | 86 | Khulna | 81 | 20:00 | 152 | Satmasjid | 108 | 19:00
21 | BashundharaCement | 13 | 00:00 | 87 | Khulshi | 178 | 17:00 | 153 | Savar | 236 | 15:00
22 | Beanibazar | 80 | 20:00 | 88 | Kishoreganj | 146 | 22:00 | 154 | SevenRings | 20.71 | 18:00
23 | Benapole | 72 | 19:00 | 89 | Kodda | 302 | 10:00 | 155 | ShahCement | 29 | 11:00
24 | Bhaluka | 169 | 21:00 | 90 | Kulaura | 51 | 19:00 | 156 | Shahjadpur | 101 | 20:00
25 | Bhandaria | 57 | 22:00 | 91 | Kurigram | 70 | 19:30 | 157 | Shahjibazar | 117 | 22:00
26 | Bhangura | 48 | 19:30 | 92 | Kushtia | 166 | 22:00 | 158 | Shahmirpur | 58 | 18:30
27 | Bheramara(GK) | 68 | 20:00 | 93 | Lalbag | 71 | 13:00 | 159 | Shariatpur | 89 | 22:00
28 | Bhulta | 237 | 10:00 | 94 | Lalmonirhat | 66 | 19:30 | 160 | Sherpur | 162 | 19:00
29 | Bog-Sherpur | 74 | 19:00 | 95 | MI_Cement | 18.1 | 17:00 | 161 | Shikalbaha | 31 | 19:00
30 | Bogura | 182 | 23:00 | 96 | Madanganj | 52 | 20:00 | 162 | Shitalakhya | 88.7 | 15:00
31 | Borhanuddin | 93 | 23:00 | 97 | Madaripur | 112 | 19:30 | 163 | Sholosohor | 49 | 19:00
32 | Brahmanbaria | 136 | 21:00 | 98 | Madartek | 94.06 | 23:00 | 164 | Shyampur | 184 | 13:00
33 | Cantonment | 140 | 13:00 | 99 | Madunaghat | 54 | 19:00 | 165 | Siddhirganj | 120 | 12:00
34 | Chandina | 20.44 | 13:00 | 100 | Magura | 71 | 19:30 | 166 | Sirajganj | 142 | 22:00
35 | Chandpur | 74 | 21:00 | 101 | Mahasthangarh | 84 | 19:30 | 167 | Sonargaon | 122 | 02:00
36 | Chandraghona | 38 | 19:30 | 102 | Manikganj | 127 | 19:30 | 168 | Sreemongol | 80 | 22:00
37 | Chapai | 72 | 21:00 | 103 | Maniknagar | 86 | 13:00 | 169 | Sreepur | 114 | 19:30
38 | Charsaidpur | 39 | 23:00 | 104 | Matarbari | 53 | 20:00 | 170 | Srinagar | 48.9 | 22:00
39 | Chauddagram | 73 | 18:30 | 105 | Matuail | 68 | 10:00 | 171 | Sunamganj | 63 | 20:00
40 | Chhatak | 37 | 21:00 | 106 | Millgate | 122 | 14:00 | 172 | Sylhet | 47 | 19:00
41 | Chowmuhani | 233 | 19:00 | 107 | Mirpur | 140 | 19:30 | 173 | Sylhet-132 | 129 | 18:30
42 | Chuadanga | 119 | 19:30 | 108 | Mirsorai | 11 | 15:00 | 174 | TK | 35.4 | 19:00
43 | Coxsbazar | 138 | 22:00 | 109 | Mirzapur | 46 | 18:30 | 175 | Tangail | 204 | 19:00
44 | Cumilla(N) | 149 | 21:00 | 110 | Mithapukur | 66 | 19:00 | 176 | Thakurgaon | 111 | 20:00
45 | Cumilla(S) | 186 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 125 | 15:00
46 | Daudkandi | 160 | 21:00 | 112 | Mogbazar | 157.2 | 17:00 | 178 | Ullahpara | 46 | 19:00
47 | Dhaka | 62 | 13:00 | 113 | Mongla | 44 | 19:00 | 179 | Ullon | 40 | 19:30
48 | Dhamrai | 138 | 09:00 | 114 | Motijheel | 40 | 13:00 | 180 | Uttara | 91 | 15:00
49 | Dhanmondi | 157 | 13:00 | 115 | Muktagacha | 41 | 19:00 | 181 | UttaraNew | 52 | 23:00
50 | Dohazari | 106 | 21:00 | 116 | Munshiganj | 116 | 19:00 | 182 | Zigatola | 83 | 19:30
51 | Faridpur | 167 | 19:30 | 117 | Muradnagar | 29 | 18:30
52 | Fatullah | 108 | 12:00 | 118 | Mymensingh | 220 | 20:00
53 | Fenchuganj | 49 | 19:00 | 119 | Naogaon | 137 | 21:00
54 | Feni | 126 | 19:30 | 120 | Narail | 58 | 19:00
55 | GPH | 7 | 13:00 | 121 | Narinda | 81 | 13:00
56 | Ghatail | 80 | 19:00 | 122 | Narshingdi | 185 | 22:00
57 | Ghorashal | 17 | 18:00 | 123 | Natore | 167 | 22:00
58 | Ghorashal-230 | 96 | 22:00 | 124 | Nawabganj | 62.4 | 22:00
59 | Goalpara | 32 | 00:00 | 125 | Netrakona | 128 | 21:00
60 | Gollamari | 100 | 23:00 | 126 | New | 88.5 | 16:00
61 | Gopalganj | 107.8 | 20:00 | 127 | Niamatpur | 81 | 22:00
62 | Gulshan | 124 | 13:00 | 128 | Noapara | 49 | 20:00
63 | Halishahar | 84.5 | 09:00 | 129 | PHP | 8 | 11:00
64 | HaripurSBU | 184 | 15:00 | 130 | Pabna | 130 | 19:30
65 | Hasnabad | 86 | 23:00 | 131 | Palashbari | 128 | 21:00
66 | Hathazari | 87 | 19:30 | 132 | Panchagarh | 62 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 07-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13802 | 0 |  | 13802
1:00 | 13118 | 0 |  | 13118
2:00 | 12744 | 0 |  | 12744
3:00 | 12422 | 0 |  | 12422
4:00 | 12103 | 0 |  | 12103
5:00 | 11874 | 0 |  | 11874
6:00 | 11526.49 | 0 |  | 11526.49
7:00 | 11812.88 | 0 |  | 11812.88
8:00 | 11872.02 | 0 |  | 11872.02
9:00 | 12544.48 | 0 |  | 12544.48
10:00 | 13086.95 | 0 |  | 13086.95
11:00 | 13489.53 | 36 |  | 13527.53
12:00 | 13962.71 | 37 |  | 14001.38
13:00 | 14327.99 | 48 |  | 14377.99
14:00 | 14249.27 | 60 |  | 14312.27
15:00 | 14328.34 | 72 |  | 14403.34
16:00 | 14329.93 | 59 |  | 14391.93
17:00 | 14110.85 | 32 |  | 14143.85
18:00 | 13666.97 | 33 |  | 13700.97
19:00 | 15159.67 | 39 |  | 15200.67
19:30 | 16016.42 | 53 |  | 16071.42
20:00 | 16063.78 | 67 |  | 16133.78
21:00 | 16049.87 | 49 |  | 16100.87
22:00 | 15756.78 | 109 |  | 15870.78
23:00 | 15712.55 | 103 |  | 15820.55
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 07-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7668 | 6134 | 13802 | DAILY GENERATION CURVE
00:30 | 7482.5 | 5977.5 | 13460
01:00 | 7297 | 5821 | 13118 | 07-05-2025
01:30 | 7283.5 | 5647.5 | 12931
02:00 | 7270 | 5474 | 12744
02:30 | 7230.5 | 5352.5 | 12583
03:00 | 7191 | 5231 | 12422
03:30 | 7133.5 | 5129 | 12262.5
04:00 | 7076 | 5027 | 12103
04:30 | 6992 | 4996.5 | 11988.5
05:00 | 6908 | 4966 | 11874
05:30 | 6834.8 | 4865.445 | 11700.245
06:00 | 6761.6 | 4764.89 | 11526.49
06:30 | 6800.665 | 4869.02 | 11669.685
07:00 | 6839.73 | 4973.15 | 11812.88
07:30 | 6862.345 | 4980.105 | 11842.45
08:00 | 6884.96 | 4987.06 | 11872.02
08:30 | 6989.955 | 5218.295 | 12208.25
09:00 | 7094.95 | 5449.53 | 12544.48
09:30 | 7174.445 | 5641.27 | 12815.715
10:00 | 7253.94 | 5833.01 | 13086.95
10:30 | 7340.265 | 5947.975 | 13288.24
11:00 | 7426.59 | 6062.94 | 13489.53
11:30 | 7613.385 | 6112.735 | 13726.12
12:00 | 7800.18 | 6162.53 | 13962.71
12:30 | 7935.795 | 6209.555 | 14145.35
13:00 | 8071.41 | 6256.58 | 14327.99
13:30 | 8092.55 | 6196.08 | 14288.63
14:00 | 8113.69 | 6135.58 | 14249.27
14:30 | 8162.33 | 6126.475 | 14288.805
15:00 | 8210.97 | 6117.37 | 14328.34
15:30 | 8283.32 | 6045.815 | 14329.135
16:00 | 8355.67 | 5974.26 | 14329.93
16:30 | 8295.745 | 5924.645 | 14220.39
17:00 | 8235.82 | 5875.03 | 14110.85
17:30 | 8160.22 | 5728.69 | 13888.91
18:00 | 8084.62 | 5582.35 | 13666.97
18:30 | 8463.81 | 5949.51 | 14413.32
19:00 | 8843 | 6316.67 | 15159.67
19:30 | 9190.2 | 6826.22 | 16016.42
20:00 | 9218.2 | 6845.58 | 16063.78
20:30 | 9186.45 | 6870.375 | 16056.825 |  | Executive Engineer
21:00 | 9154.7 | 6895.17 | 16049.87 |  | Network Operation Division
21:30 | 9029.85 | 6873.475 | 15903.325
22:00 | 8905 | 6851.78 | 15756.78
22:30 | 8837 | 6897.665 | 15734.665
23:00 | 8769 | 6943.55 | 15712.55

## En-Curve
QF-LDC-12
Date | 07-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3671 | 2244 | 917 | 0 | 40 | 1356 | 40 | 3997 | 0 | 375 | 1162 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3652.5 | 2243 | 916.5 | 0 | 39 | 1285 | 40 | 3965 | 0 | 325.5 | 993.5 | 0 | 0 | 0 | 0 | 07-05-2025
01:00 | 3634 | 2242 | 916 | 0 | 38 | 1214 | 40 | 3933 | 0 | 276 | 825 | 0 | 0 | 0 | 0
01:30 | 3630 | 2239 | 916 | 0 | 37 | 1167 | 40 | 3805 | 0 | 276 | 821 | 0 | 0 | 0 | 0 | Energy Generated | 334.115 |  | MKWHr
02:00 | 3626 | 2236 | 916 | 0 | 36 | 1120 | 40 | 3677 | 0 | 276 | 817 | 0 | 0 | 0 | 0 | Energy not Served | 0.744 |  | MKWHr
02:30 | 3635.5 | 2235 | 916 | 0 | 36 | 1072 | 40 | 3567 | 0 | 276 | 805.5 | 0 | 0 | 0 | 0 | Total Energy Requirement | 334.859 |  | MKWHr
03:00 | 3645 | 2234 | 916 | 0 | 36 | 1024 | 40 | 3457 | 0 | 276 | 794 | 0 | 0 | 0 | 0
03:30 | 3667 | 2244.5 | 916.5 | 0 | 35 | 972.5 | 40 | 3356.5 | 0 | 259 | 771.5 | 0 | 0 | 0 | 0
04:00 | 3689 | 2255 | 917 | 0 | 34 | 921 | 40 | 3256 | 0 | 242 | 749 | 0 | 0 | 0 | 0
04:30 | 3659 | 2253 | 917 | 0 | 34 | 919 | 40 | 3230 | 0 | 216.5 | 720 | 0 | 0 | 0 | 0
05:00 | 3629 | 2251 | 917 | 0 | 34 | 917 | 40 | 3204 | 0 | 191 | 691 | 0 | 0 | 0 | 0
05:30 | 3655 | 2253.5 | 916.5 | 0 | 31 | 867.5 | 40 | 3085.5 | 16.745 | 201 | 633.5 | 0 | 0 | 0 | 0
06:00 | 3681 | 2256 | 916 | 0 | 28 | 818 | 40 | 2967 | 33.49 | 211 | 576 | 0 | 0 | 0 | 0
06:30 | 3636.5 | 2243 | 916 | 0 | 29 | 820 | 40 | 3078 | 88.685 | 210.5 | 608 | 0 | 0 | 0 | 0
07:00 | 3592 | 2230 | 916 | 0 | 30 | 822 | 40 | 3189 | 143.88 | 210 | 640 | 0 | 0 | 0 | 0
07:30 | 3575 | 2183.5 | 892.5 | 0 | 29 | 825 | 40 | 3198 | 226.95 | 209 | 663.5 | 0 | 0 | 0 | 0
08:00 | 3558 | 2137 | 869 | 0 | 28 | 828 | 40 | 3207 | 310.02 | 208 | 687 | 0 | 0 | 0 | 0
08:30 | 3634 | 2153.5 | 869 | 0 | 29 | 878.5 | 40 | 3292.5 | 390.75 | 233.5 | 687.5 | 0 | 0 | 0 | 0
09:00 | 3710 | 2170 | 869 | 0 | 30 | 929 | 40 | 3378 | 471.48 | 259 | 688 | 0 | 0 | 0 | 0
09:30 | 3689 | 2166 | 895.5 | 0 | 31 | 1017 | 40 | 3535 | 506.215 | 263 | 673 | 0 | 0 | 0 | 0
10:00 | 3668 | 2162 | 922 | 0 | 32 | 1105 | 40 | 3692 | 540.95 | 267 | 658 | 0 | 0 | 0 | 0
10:30 | 3695.5 | 2167.5 | 922 | 0 | 33 | 1137 | 40 | 3720 | 577.74 | 284 | 711.5 | 0 | 0 | 0 | 18
11:00 | 3723 | 2173 | 922 | 0 | 34 | 1169 | 40 | 3748 | 614.53 | 301 | 765 | 0 | 0 | 0 | 36
11:30 | 3763 | 2172 | 922.5 | 0 | 35 | 1164 | 39 | 3774 | 626.12 | 318 | 912 | 0 | 0 | 0.5 | 36.5
12:00 | 3803 | 2171 | 923 | 0 | 36 | 1159 | 38 | 3800 | 637.71 | 335 | 1059 | 0 | 0 | 1 | 37
12:30 | 3760.5 | 2102.5 | 922.5 | 0 | 37 | 1238 | 38 | 3880 | 625.85 | 345 | 1193 | 0 | 0 | 3 | 42.5
13:00 | 3718 | 2034 | 922 | 0 | 38 | 1317 | 38 | 3960 | 613.99 | 355 | 1327 | 0 | 0 | 5 | 48
13:30 | 3687.5 | 2014.5 | 922 | 0 | 38 | 1317.095 | 38 | 3924.5 | 585.535 | 369 | 1385 | 0 | 0 | 7.5 | 54
14:00 | 3657 | 1995 | 922 | 0 | 38 | 1317.19 | 38 | 3889 | 557.08 | 383 | 1443 | 0 | 0 | 10 | 60
14:30 | 3708 | 2024 | 924 | 0 | 38 | 1320.37 | 39 | 3871 | 507.435 | 380.5 | 1467.5 | 0 | 0 | 9 | 66
15:00 | 3759 | 2053 | 926 | 0 | 38 | 1323.55 | 40 | 3853 | 457.79 | 378 | 1492 | 0 | 0 | 8 | 72
15:30 | 3770 | 2086 | 926 | 0 | 36 | 1298.13 | 40 | 3860 | 367.005 | 379.5 | 1560 | 0 | 0 | 6.5 | 65.5
16:00 | 3781 | 2119 | 926 | 0 | 34 | 1272.71 | 40 | 3867 | 276.22 | 381 | 1628 | 0 | 0 | 5 | 59
16:30 | 3809.5 | 2114 | 926 | 0 | 36 | 1272.21 | 40 | 3847.5 | 199.68 | 384.5 | 1585.5 | 0 | 0 | 5.5 | 45.5
17:00 | 3838 | 2109 | 926 | 0 | 38 | 1271.71 | 40 | 3828 | 123.14 | 388 | 1543 | 0 | 0 | 6 | 32
17:30 | 3789 | 2088 | 926 | 0 | 38 | 1245.42 | 40 | 3781 | 70.99 | 384 | 1522.5 | 0 | 0 | 4 | 32.5
18:00 | 3740 | 2067 | 926 | 0 | 38 | 1219.13 | 40 | 3734 | 18.84 | 380 | 1502 | 0 | 0 | 2 | 33
18:30 | 3799 | 2096.5 | 919.5 | 0 | 41 | 1291.4 | 40 | 3961.5 | 9.42 | 493.5 | 1760.5 | 0 | 0 | 1 | 36
19:00 | 3858 | 2126 | 913 | 0 | 44 | 1363.67 | 40 | 4189 | 0 | 607 | 2019 | 0 | 0 | 0 | 39
19:30 | 3856 | 2159 | 880 | 0 | 44 | 1369.22 | 40 | 4436 | 0 | 725 | 2507.2 | 0 | 0 | 0 | 53
20:00 | 3838 | 2260 | 880 | 0 | 44 | 1364.58 | 40 | 4426 | 0 | 743 | 2468.2 | 0 | 0 | 0 | 67
20:30 | 3843.5 | 2268.5 | 903.5 | 0 | 44 | 1363.875 | 40 | 4434 | 0 | 737.5 | 2421.95 | 0 | 0 | 0 | 58
21:00 | 3849 | 2277 | 927 | 0 | 44 | 1363.17 | 40 | 4442 | 0 | 732 | 2375.7 | 0 | 0 | 0 | 49
21:30 | 3836 | 2202.5 | 927 | 0 | 45 | 1364.975 | 40 | 4442.5 | 0 | 742 | 2303.35 | 0 | 0 | 0 | 79
22:00 | 3823 | 2128 | 927 | 0 | 46 | 1366.78 | 40 | 4443 | 0 | 752 | 2231 | 0 | 0 | 0 | 109
22:30 | 3852.5 | 2145.5 | 926.5 | 0 | 47 | 1365.665 | 40 | 4445 | 0 | 744 | 2168.5 | 0 | 0 | 0 | 106
23:00 | 3882 | 2163 | 926 | 0 | 48 | 1364.55 | 40 | 4447 | 0 | 736 | 2106 | 0 | 0 | 0 | 103
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 07-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 391 | 05:00 | 372 | 11:00 | Payra | 414 | 05:00 | 404 | 17:00
Ashuganj | 403 | 7:00 | 382 | 10:00 | Rahanpur | 407 | 05:00 | 393 | 13:00
Bhulta | 398 | 05:00 | 377 | 12:00 | Rampal | 402 | 04:00 | 382 | 19:30
Bibiana | 395 | 05:00 | 386 | 12:00
BIPTC | 397 | 04:00 | 387 | 16:00
Bogura | 391 | 05:00 | 375 | 13:00
Gopalganj | 400 | 05:00 | 379 | 23:00
Kaliakoir | 381 | 04:00 | 364 | 11:00
Madunaghat | 396 | 05:00 | 388 | 11:00
Meghnaghat | 395 | 05:00 | 377 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 229 | 05:00 | 214 | 11:00 | Keranigonj | 227 | 05:00 | 213 | 11:00
AKSML | 233 | 05:00 | 223 | 12:00 | Khulna(S) | 233 | 05:00 | 210 | 19:30
Aminbazar | 230 | 04:00 | 216 | 11:00 | Madunaghat | 233 | 06:00 | 227 | 10:00
Ashuganj | 232 | 05:00 | 222 | 11:00 | Madunaghat-400 | 233 | 04:00 | 228 | 11:00
Ashuganj-400 | 232 | 05:00 | 222 | 11:00 | Maniknagar | 224 | 04:00 | 212 | 11:00
Baghabari | 233 | 05:00 | 225 | 11:00 | Meghnaghat | 230 | 06:00 | 220 | 12:00
Barapukuria | 225 | 03:00 | 218 | 12:00 | Meghnaghat-400 | 228 | 05:00 | 217 | 11:00
Barapukuria-230 | 225 | 03:00 | 218 | 12:00 | Mirsorai | 229 | 06:00 | 218 | 11:00
Barishal | 239 | 05:00 | 228 | 11:00 | Rajshahi | 233 | 04:00 | 220 | 12:00
Bheramara | 234 | 04:00 | 221 | 12:00 | Rampal | 231 | 05:00 | 214 | 19:30
Bhulta | 226 | 04:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 04:00 | 218 | 23:00 | Rampura | 226 | 05:00 | 210 | 11:00
BIPTC | 237 | 05:00 | 221 | 12:00 | Shikalbaha | 231 | 05:00 | 224 | 12:00
Bogura | 237 | 05:00 | 227 | 13:00 | Shyampur | 227 | 04:00 | 214 | 11:00
Bogura-400 | 237 | 05:00 | 227 | 13:00 | Siddhirganj | 225 | 06:00 | 215 | 11:00
Borhanuddin | 242 | 08:00 | 233 | 23:00 | Sirajgonj | 240 | 04:00 | 234 | 11:00
BSRM | 229 | 05:00 | 220 | 11:00 | Sreepur | 230 | 04:00 | 220 | 11:00
Cumilla(N) | 224 | 06:00 | 215 | 11:00 | Tongi | 222 | 07:00 | 210 | 16:00
Faridpur | 235 | 05:00 | 223 | 12:00
Fenchuganj | 227 | 06:00 | 219 | 21:00
Ghorashal | 230 | 00:00 | 225 | 14:00
Ghorashal-230 | 227 | 05:00 | 214 | 11:00
Gopalganj | 236 | 05:00 | 223 | 23:00
GPH | 230 | 04:00 | 223 | 11:00
Haripur | 226 | 05:00 | 214 | 11:00
Hasnabad | 224 | 04:00 | 214 | 11:00
Hathazari | 231 | 07:00 | 225 | 11:00
Ishurdi | 237 | 05:00 | 224 | 12:00
Jhenaidah | 232 | 05:00 | 212 | 21:00
Kaliakoir | 233 | 05:00 | 221 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 04:00 | 127 | 10:00 | Madartek | 136 | 06:00 | 126 | 11:00
Agargaon | 135 | 05:00 | 124 | 11:00 | Madunaghat | 133 | 06:00 | 129 | 10:00
Agrabad | 131 | 05:00 | 126 | 10:00 | Magura | 136 | 04:00 | 119 | 19:00
AKS | 130 | 06:00 | 125 | 15:00 | Mahasthangarh | 136 | 05:00 | 129 | 13:00
Aminbazar | 133 | 05:00 | 125 | 10:00 | Manikganj | 133 | 09:00 | 114 | 11:00
Amnura | 136 | 05:00 | 124 | 13:00 | Maniknagar | 132 | 04:00 | 122 | 11:00
Ashuganj | 137 | 08:00 | 132 | 23:00 | Matarbari | 125 | 19:00 | 110 | 13:00
Bagerhat | 134 | 05:00 | 116 | 19:30 | Matuail | 131 | 04:00 | 123.7 | 11:00
Bajitpur | 133 | 05:00 | 125 | 19:00 | Millgate | 131 | 03:00 | 120 | 11:00
Bakulia | 133 | 19:00 | 128 | 13:00 | Mirpur | 133 | 05:00 | 121 | 11:00
Banani | 135 | 05:00 | 125 | 11:00 | Mirzapur | 135 | 05:00 | 128 | 11:00
Bangabhaban | 132 | 04:00 | 122 | 11:00 | Mithapukur | 132 | 04:00 | 124 | 12:00
Barapukuria | 136 | 03:00 | 129 | 14:00 | MI_Cement | 131 | 04:00 | 123.2 | 11:00
Barguna | 136 | 01:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 05:00 | 123 | 23:00 | Mogbazar | 136 | 04:00 | 125 | 11:00
Barishal-230 | 133 | 04:00 | 123 | 19:30 | Mongla | 134 | 06:00 | 117 | 19:30
Baroaulia | 132 | 00:00 | 126 | 15:00 | Motijheel | 132 | 04:00 | 122 | 11:00
Baroirhat | 125 | 07:00 | 118 | 12:00 | Muktagacha | 134 | 09:00 | 123 | 19:00
Bashundhara | 136 | 04:00 | 117 | 12:00 | Munshiganj | 130 | 05:00 | 122 | 10:00
BashundharaCement | 129 | 05:00 | 123 | 10:00 | Muradnagar | 127 | 07:00 | 120 | 11:00
Beanibazar | 129 | 05:00 | 123 | 20:00 | Mymensingh | 135 | 09:00 | 114 | 18:30
Benapole | 134 | 05:00 | 115 | 19:00 | Naogaon | 135 | 05:00 | 127 | 13:00
Bhaluka | 130 | 06:00 | 122 | 12:00 | Narail | 137 | 05:00 | 117 | 19:30
Bhandaria | 129 | 06:00 | 115 | 19:30 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 133 | 04:00 | 126 | 19:30 | Narshingdi | 128 | 09:00 | 116 | 11:00
Bheramara | 138 | 04:00 | 131 | 12:00 | Natore | 134 | 08:00 | 127 | 19:30
Bheramara(GK) | 136 | 04:00 | 131 | 12:00 | Nawabganj | 136 | 05:00 | 125 | 11:00
Bhulta | 123 | 05:00 | 117 | 11:00 | Netrakona | 125 | 04:00 | 111 | 21:00
Bog-Sherpur | 137 | 05:00 | 130 | 12:00 | New | 133 | 04:00 | 122 | 10:00
Bogura | 139 | 05:00 | 133 | 12:00 | Niamatpur | 134 | 05:00 | 128 | 13:00
Bogura-230 | 140 | 05:00 | 133 | 12:00 | Noapara | 137 | 04:00 | 120 | 19:30
Brahmanbaria | 130 | 06:00 | 121 | 22:00 | Pabna | 136 | 05:00 | 126 | 19:30
Cantonment | 135 | 05:00 | 123 | 12:00 | Palashbari | 130 | 03:00 | 122 | 19:00
Chandina | 128 | 05:00 | 122 | 12:00 | Panchagarh | 134 | 21:00 | 119 | 12:00
Chandpur | 124 | 18:30 | 120 | 00:00 | Patuakhali | 135 | 05:00 | 129 | 20:00
Chandraghona | 133 | 03:00 | 129 | 13:00 | Payra | 138 | 08:00 | 132 | 23:00
Chapai | 131 | 06:00 | 124 | 13:00 | PHP | 123 | 07:00 | 116 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 06:00 | 124 | 10:00 | Postogola | 133 | 04:00 | 125 | 11:00
Chauddagram | 123 | 06:00 | 117 | 12:00 | Purbachal | 136 | 04:00 | 125 | 11:00
Chhatak | 130 | 07:00 | 120 | 22:00 | Purbasadipur | 128 | 17:00 | 116 | 13:00
Chowmuhani | 117 | 07:00 | 112 | 13:00 | Rahanpur | 135 | 04:00 | 130 | 13:00
Chuadanga | 133 | 05:00 | 116 | 19:30 | Rahanpur-400 | 136 | 05:00 | 130 | 19:00
Coxsbazar | 123 | 18:30 | 112 | 00:00 | Rahim | 131 | 07:00 | 124 | 11:00
Cumilla(N) | 128 | 06:00 | 122 | 12:00 | Rajbari | 137 | 05:00 | 125 | 19:30
Cumilla(S) | 133 | 03:00 | 120 | 11:00 | Rajendrapur | 134 | 18:30 | 121 | 11:00
Daudkandi | 125 | 05:00 | 119 | 11:00 | Rajshahi | 134 | 06:00 | 127 | 12:00
Dhaka | 137 | 04:00 | 126 | 11:00 | Rajshahi-230 | 134 | 03:00 | 117 | 13:00
Dhamrai | 136 | 03:00 | 127 | 11:00 | Ramganj | 118 | 07:00 | 112 | 01:00
Dhanmondi | 137 | 05:00 | 126 | 11:00 | Rampur | 132 | 05:00 | 125 | 15:00
Dohazari | 130 | 19:00 | 120 | 13:00 | Rampura | 136 | 04:00 | 125 | 11:00
Faridpur | 137 | 06:00 | 128 | 19:30 | Rangamati | 133 | 07:00 | 128 | 11:00
Fatullah | 132 | 04:00 | 124 | 11:00 | Rangpur | 132 | 03:00 | 123 | 12:00
Fenchuganj | 135 | 06:00 | 130 | 20:00 | Ruppur | 138 | 04:00 | 131 | 19:30
Feni | 122 | 18:00 | 115 | 01:00 | Saidpur | 133 | 04:00 | 119 | 14:00
Ghatail | 131 | 08:00 | 122 | 19:00 | Satkhira | 135 | 05:00 | 116 | 19:30
Ghorashal | 136 | 04:00 | 131 | 22:00 | Satmasjid | 134 | 05:00 | 124 | 11:00
Goalpara | 138 | 05:00 | 124 | 19:30 | Savar | 132 | 04:00 | 120 | 11:00
Gollamari | 139 | 05:00 | 124 | 19:30 | SevenRings | 136 | 04:00 | 129 | 11:00
Gopalganj | 137 | 05:00 | 124 | 19:30 | ShahCement | 131 | 06:00 | 124 | 10:00
Gopalganj-400 | 138 | 05:00 | 129 | 19:30 | Shahjadpur | 137 | 03:00 | 131 | 19:30
Gulshan | 136 | 05:00 | 125 | 11:00 | Shahjibazar | 132 | 07:00 | 123 | 22:00
Halishahar | 131 | 03:00 | 126 | 11:00 | Shahmirpur | 133 | 05:00 | 129 | 12:00
Haripur | 131 | 04:00 | 124 | 11:00 | Shariatpur | 135 | 04:00 | 123 | 19:30
HaripurSBU | 131 | 04:00 | 124 | 11:00 | Sherpur | 135 | 00:00 | 121 | 19:00
Hasnabad | 134 | 05:00 | 125 | 12:00 | Shikalbaha | 122 | 03:00 | 117 | 15:00
Hathazari | 134 | 09:00 | 129 | 11:00 | Shikalbaha-230 | 134 | 07:00 | 129 | 12:00
Ishurdi | 139 | 04:00 | 130 | 19:30 | Shitalakhya | 131 | 04:00 | 123.2 | 11:00
Jaldhaka | 130 | 05:00 | 118 | 14:00 | Sholosohor | 133 | 04:00 | 129 | 11:00
Jamalpur | 138 | 00:00 | 125 | 19:00 | Shyampur | 131 | 05:00 | 123 | 11:00
Jashore | 135 | 04:00 | 116 | 19:30 | Shyampur-230 | 132 | 05:00 | 121 | 11:00
Jhenaidah | 135 | 06:00 | 121 | 19:30 | Siddhirganj | 131 | 04:00 | 124 | 11:00
Jhenaidah-230 | 137 | 05:00 | 121 | 19:30 | Sirajganj | 132 | 04:00 | 126 | 19:30
Joydebpur | 140 | 18:00 | 126 | 00:00 | Sonargaon | 126 | 01:00 | 122 | 09:00
Joypurhat | 133 | 05:00 | 124 | 13:00 | Sreemongol | 132 | 06:00 | 124 | 19:00
Juldah | 132 | 01:00 | 129 | 11:00 | Sreepur | 134 | 05:00 | 127 | 11:00
Kabirpur | 139 | 18:00 | 116 | 11:00 | Srinagar | 137 | 05:00 | 126 | 11:00
Kachua | 123 | 04:00 | 119 | 01:00 | SSM | 133 | 18:00 | 129 | 13:00
Kaliakoir | 140 | 04:00 | 126 | 01:00 | Sunamganj | 128 | 06:00 | 119 | 19:30
Kallyanpur | 132 | 05:00 | 123 | 11:00 | Sylhet | 131 | 07:00 | 125 | 19:00
Kalurghat | 133 | 06:00 | 129 | 10:00 | Sylhet-132 | 131 | 06:00 | 126 | 23:00
Kamrangirchar | 136 | 05:00 | 125 | 11:00 | Tangail | 130 | 04:00 | 124 | 12:00
Kaptai | 135 | 4:00 | 132 | 11:00 | Thakurgaon | 136 | 21:00 | 121 | 12:00
Kasba | 127 | 07:00 | 119 | 12:00 | TK | 133 | 08:00 | 129 | 15:00
Kazla | 132 | 05:00 | 122 | 11:00 | Tongi | 131 | 07:00 | 125 | 11:00
Keranigonj | 136 | 04:00 | 126 | 11:00 | Ullahpara | 135 | 04:00 | 128 | 12:00
Khagrachori | 132 | 07:00 | 126 | 13:00 | Ullon | 136 | 04:00 | 125 | 11:00
Khulna | 137 | 05:00 | 123 | 20:00 | Uttara | 132 | 05:00 | 120 | 12:00
Khulna(S) | 139 | 05:00 | 124 | 19:30 | UttaraNew | 132 | 04:00 | 121 | 11:00
Khulshi | 131 | 04:00 | 125 | 15:00 | Zigatola | 136 | 05:00 | 125 | 13:00
Kishoreganj | 131 | 05:00 | 119 | 19:00
Kodda | 136 | 04:00 | 122 | 11:00
KSRM | 132 | 01:00 | 128 | 13:00
Kulaura | 134 | 08:00 | 128 | 23:00
Kurigram | 130 | 22:00 | 119 | 17:00
Kushtia | 136 | 04:00 | 125 | 19:30
Lalbag | 136 | 05:00 | 125 | 11:00
Lalmonirhat | 129 | 04:00 | 121 | 12:00
Madanganj | 130 | 07:00 | 123 | 10:00
Madaripur | 136 | 05:00 | 126 | 19:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division