## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 08-05-2025 | [28 empty] | Date: | 08-05-2025 | [28 empty] | Date: | 08-05-2025 | [28 empty] | Date: | 08-05-2025 | [28 empty] | Date: | 08-05-2025 | [16 empty] | Date: | 08-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 54 | 17 | 131 | 144 | 195 | 0 | 35 | 162 | 0 | 60 | 320 | 298 | 350 | 0 | 35 | 0 | 278 | 0 | 0 | 0 | 160 | 21 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 102 | 47 | 0 | 100 | 0 | 0 | 40 | 0 | 29 | 576 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 16 | 0 | 348 | 345 | 48 | 188 | 35 | 93 | 70 | 172 | 15 | 20 | 114 | 46 | 52.2 | 0 | 39 | 315 | 320 | 330 | 38 | 30 | 0 | 102 | 8 | 0 | 83 | 25 | 0 | 18 | 169 | 17 | 104 | 129 | 0 | 0 | 0 | 12 | 8794.2 | 927 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 75 | 1360.35 | 0 | 50 | 0 | 113 | 0 | 93 | 70 | 28 | 34 | 0 | 22 | 0 | 177 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 115 | 220 | 0 | 260 | 1244 | 0 | 6951.35 | 15745.55 | 78.9
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 131 | 144 | 195 | 0 | 35 | 162 | 0 | 51 | 320 | 304 | 300 | 0 | 17 | 0 | 286 | 0 | 0 | 0 | 160 | 21.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 47 | 0 | 100 | 0 | 0 | 40 | 0 | 30 | 575 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 16 | 0 | 330 | 345 | 50 | 194 | 36 | 94 | 81 | 150 | 9 | 20 | 114 | 44 | 52.2 | 0 | 39 | 305 | 320 | 356 | 38 | 30 | 0 | 89 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 17 | 48 | 94 | 0 | 0 | 0 | 12 | 8533.7 | 927 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621 | 90 | 1370.74 | 0 | 0 | 0 | 113 | 0 | 40 | 0 | 0 | 8 | 0 | 0 | 0 | 177 | 0 | 175 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 163 | 51 | 115 | 0 | 113 | 0 | 0 | 3.7 | 0 | 0 | 16 | 290 | 11 | 115 | 220 | 0 | 261 | 1200 | 0 | 6578.44 | 15112.14 | 78.89
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 38 | 17 | 131 | 112 | 0 | 0 | 35 | 162 | 0 | 16 | 320 | 291 | 300 | 0 | 17 | 0 | 276 | 0 | 0 | 0 | 160 | 22 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 47 | 0 | 100 | 0 | 0 | 40 | 0 | 30 | 576 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 20 | 16 | 0 | 320 | 345 | 51 | 186 | 36 | 94 | 80 | 152 | 9 | 20 | 114 | 42 | 52.2 | 0 | 39 | 305 | 320 | 329 | 38 | 30 | 0 | 81 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 0 | 48 | 92 | 0 | 0 | 0 | 12 | 8069.2 | 927 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 93 | 1371.94 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 176 | 0 | 176 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 165 | 51 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 280 | 11 | 115 | 220 | 0 | 260 | 1200 | 0 | 6502.94 | 14572.14 | 78.88
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 35 | 17 | 95 | 96 | 0 | 0 | 35 | 162 | 0 | 0 | 320 | 303 | 300 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 30 | 576 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 16 | 0 | 320 | 345 | 51 | 203 | 36 | 93 | 80 | 156 | 8 | 20 | 114 | 42 | 52.2 | 0 | 39 | 310 | 320 | 358 | 38 | 30 | 0 | 86 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 0 | 48 | 92 | 0 | 0 | 0 | 12 | 7995.2 | 927 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 0 | 1321.54 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 176 | 0 | 184 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 160 | 51 | 35 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 16 | 250 | 11 | 115 | 220 | 0 | 262 | 1200 | 0 | 6017.54 | 14012.74 | 78.87
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 0 | 17 | 68 | 96 | 0 | 0 | 35 | 162 | 0 | 0 | 320 | 301 | 300 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 142 | 21.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 80 | 0 | 0 | 40 | 0 | 30 | 502 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 16 | 0 | 320 | 345 | 52 | 203 | 36 | 93 | 80 | 165 | 9 | 20 | 114 | 40 | 52.2 | 0 | 0 | 315 | 320 | 360 | 38 | 30 | 0 | 91 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 0 | 48 | 92 | 0 | 0 | 0 | 12 | 7712.7 | 927 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 0 | 1316.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 177 | 0 | 185 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 160 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 250 | 11 | 115 | 220 | 0 | 262 | 1200 | 0 | 5933.49 | 13646.19 | 78.86
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 17 | 70 | 96 | 0 | 0 | 35 | 162 | 0 | 0 | 320 | 300 | 300 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 142 | 22 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 76 | 0 | 0 | 40 | 0 | 31 | 503 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1103 | 0 | 51 | 0 | 16 | 0 | 320 | 345 | 52 | 198 | 33 | 93 | 80 | 165 | 9 | 20 | 114 | 30 | 52.2 | 0 | 0 | 305 | 320 | 325 | 38 | 30 | 0 | 89 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 48 | 92 | 0 | 0 | 0 | 12 | 7631.2 | 926 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 554 | 0 | 1311.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 180 | 0 | 185 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 161 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 250 | 11 | 115 | 220 | 0 | 261 | 1100 | 0 | 5834.11 | 13465.31 | 78.85
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 54 | 96 | 0 | 0 | 35 | 162 | 0 | 0 | 320 | 303 | 300 | 0 | 0 | 0 | 298 | 0 | 0 | 2 | 142 | 21.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 32 | 505 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1019 | 1 | 51 | 0 | 16 | 0 | 320 | 345 | 53 | 206 | 33 | 94 | 80 | 136 | 9 | 20 | 114 | 40 | 52.2 | 4 | 0 | 280 | 320 | 360 | 38 | 30 | 0 | 85 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 48 | 91 | 0 | 0 | 2.43 | 12 | 7511.13 | 926 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.22 | 447 | 0 | 1158.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 2.23 | 186 | 0 | 170 | 0 | 0 | 0 | 220 | 0 | 0.2 | 0 | 162 | 51 | 0 | 1 | 0 | 0 | 0 | 0.3 | 10 | 0.04 | 0 | 250 | 9 | 115 | 220 | 0 | 261 | 1000 | 0 | 5414.57 | 12925.7 | 78.84
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 61 | 96 | 0 | 0 | 35 | 162 | 0 | 0 | 320 | 294 | 300 | 0 | 0 | 0 | 275 | 0 | 0 | 7 | 142 | 21.5 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 48 | 0 | 1 | 40 | 0 | 32 | 503 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1011 | 5 | 51 | 0 | 16 | 0 | 333 | 345 | 53 | 191 | 36 | 93 | 80 | 136 | 9 | 20 | 88 | 36 | 25 | 18 | 0 | 295 | 320 | 347 | 38 | 30 | 0 | 86 | 0 | 0 | 83 | 25 | 0 | 18 | 171 | 0 | 76 | 99 | 0 | 0 | 12 | 12 | 7489.5 | 926 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.14 | 411 | 0 | 1159.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11.21 | 188 | 0 | 165 | 0 | 0 | 0 | 300 | 0 | 0.88 | 0 | 165 | 51 | 0 | 6 | 0 | 0 | 0 | 1.7 | 41 | 0.15 | 0 | 250 | 8 | 115 | 220 | 0 | 262 | 900 | 0 | 5443.18 | 12932.68 | 78.83
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 17 | 87 | 96 | 0 | 0 | 35 | 162 | 0 | 0 | 320 | 302 | 300 | 0 | 0 | 0 | 295 | 0 | 0 | 15 | 108 | 20.9 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 48 | 0 | 3 | 40 | 0 | 7 | 457 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 900 | 10 | 51 | 0 | 16 | 0 | 332 | 345 | 52 | 205 | 36 | 93 | 80 | 126 | 9 | 20 | 70 | 34 | 25 | 35 | 0 | 310 | 320 | 385 | 39 | 30 | 0 | 84 | 0 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 78 | 108 | 0 | 1 | 25.1 | 12 | 7415 | 879 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.26 | 411 | 0 | 1159.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 27.56 | 190 | 0 | 181 | 0 | 0 | 0 | 250 | 0 | 2.32 | 0 | 160 | 51 | 0 | 13 | 0 | 0 | 0 | 3.5 | 87 | 0.17 | 0 | 200 | 8 | 115 | 220 | 0 | 263 | 900 | 0 | 5431.91 | 12846.91 | 78.82
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 17 | 85 | 112 | 0 | 0 | 35 | 162 | 0 | 0 | 380 | 287 | 300 | 0 | 0 | 0 | 286 | 0 | 0 | 22 | 108 | 20 | 21 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 48 | 0 | 3 | 40 | 0 | 2 | 455 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1005 | 16 | 51 | 0 | 16 | 0 | 342 | 345 | 49 | 193 | 36 | 94 | 80 | 132 | 9 | 20 | 70 | 36 | 25 | 47 | 0 | 300 | 320 | 370 | 38 | 30 | 0 | 96 | 0 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 77 | 108 | 0 | 2 | 37.42 | 12 | 7623.42 | 878 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.11 | 408 | 0 | 1161.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 39.07 | 190 | 0 | 189 | 0 | 0 | 0 | 300 | 0 | 3.28 | 0 | 156 | 51 | 0 | 21 | 0 | 0 | 0 | 4.3 | 124 | 0.5 | 0 | 250 | 7 | 115 | 220 | 0 | 263 | 900 | 0 | 5639.13 | 13262.55 | 78.81
10:00 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 17 | 86 | 128 | 0 | 0 | 35 | 162 | 0 | 0 | 380 | 295 | 280 | 0 | 0 | 0 | 290 | 0 | 0 | 27 | 108 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 1 | 102 | 0 | 0 | 50 | 0 | 4 | 40 | 0 | 2 | 502 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1105 | 19 | 51 | 0 | 16 | 0 | 334 | 345 | 48 | 207 | 36 | 93 | 80 | 127 | 8 | 20 | 70 | 36 | 25 | 63 | 0 | 305 | 320 | 387 | 39 | 30 | 0 | 102 | 0 | 0 | 80 | 30 | 0 | 18 | 172 | 0 | 77 | 101 | 0 | 2 | 46.02 | 12 | 7849.02 | 925 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.76 | 407 | 0 | 1260.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 48.75 | 189 | 0 | 186 | 0 | 0 | 0 | 300 | 0 | 4.2 | 0 | 158 | 51 | 0 | 27 | 0 | 0 | 0 | 6.4 | 156 | 0.62 | 0 | 250 | 7 | 115 | 220 | 0 | 263 | 930 | 0 | 5882.17 | 13731.19 | 78.8
11:00 | 16 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 27 | 17 | 96 | 125 | 100 | 1 | 35 | 162 | 0 | 4 | 320 | 290 | 280 | 0 | 35 | 0 | 283 | 0 | 0 | 31 | 108 | 20 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 11 | 102 | 0 | 0 | 76 | 20 | 4 | 40 | 0 | 2 | 501 | 21 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1104 | 18 | 51 | 28 | 16 | 0 | 336 | 345 | 47 | 193 | 29 | 93 | 80 | 131 | 8 | 20 | 70 | 38 | 30 | 68 | 0 | 300 | 320 | 337 | 37 | 30 | 0 | 101 | 0 | 0 | 80 | 30 | 0 | 18 | 173 | 8 | 76 | 110 | 0 | 2 | 49.85 | 12 | 8030.85 | 925 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7 | 450 | 0 | 1317.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 55.45 | 190 | 0 | 166 | 0 | 0 | 0 | 414 | 0 | 4.78 | 0 | 162 | 50 | 0 | 20 | 0 | 0 | 0 | 7.4 | 179 | 0.68 | 0 | 307 | 0 | 115 | 180 | 0 | 261 | 1070 | 0 | 6240.21 | 14271.06 | 78.79
12:00 | 16 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 54 | 17 | 113 | 125 | 146 | 15 | 35 | 162 | 0 | 26 | 320 | 293 | 280 | 0 | 35 | 0 | 302 | 0 | 0 | 32 | 130 | 19.5 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 6 | 102 | 0 | 0 | 76 | 20 | 4 | 39 | 0 | 3 | 503 | 65 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1150 | 18 | 51 | 86 | 16 | 0 | 331 | 340 | 44 | 205 | 35 | 94 | 90 | 143 | 9 | 20 | 98 | 40 | 52.2 | 70 | 0 | 310 | 320 | 335 | 38 | 30 | 0 | 105 | 0 | 0 | 82 | 30 | 0 | 18 | 173 | 35 | 76 | 102 | 0 | 2 | 50.07 | 12 | 8462.77 | 926 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.53 | 504 | 0 | 1354.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 57.94 | 186 | 0 | 150 | 0 | 0 | 0 | 414 | 0 | 4.88 | 0 | 162 | 50 | 0 | 23 | 0 | 0 | 0 | 6.1 | 190 | 0.72 | 0 | 307 | 0 | 115 | 180 | 0 | 262 | 1100 | 0 | 6371.23 | 14834 | 78.78
13:00 | 16 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 54 | 17 | 124 | 124 | 293 | 50 | 35 | 162 | 0 | 44 | 320 | 290 | 280 | 0 | 35 | 0 | 300 | 0 | 0 | 27 | 160 | 19.5 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 12 | 102 | 0 | 0 | 76 | 20 | 4 | 40 | 0 | 10 | 503 | 108 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 1154 | 17 | 51 | 100 | 16 | 0 | 329 | 330 | 43 | 202 | 34 | 94 | 90 | 144 | 8 | 13 | 114 | 40 | 43 | 67 | 23 | 305 | 320 | 385 | 37 | 30 | 0 | 102 | 0 | 0 | 81 | 30 | 0 | 18 | 173 | 35 | 75 | 110 | 0 | 2 | 47.58 | 12 | 8813.08 | 925 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.77 | 502 | 0 | 1353.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 56.56 | 182 | 0 | 165 | 0 | 0 | 0 | 350 | 0 | 4.77 | 0 | 163 | 49 | 0 | 33 | 0 | 0 | 0 | 7.6 | 188 | 0.69 | 0 | 307 | 8 | 100 | 220 | 0 | 260 | 1080 | 0 | 6318.93 | 15132.01 | 78.77
14:00 | 16 | 17 | 31 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 35 | 17 | 128 | 108 | 293 | 55 | 35 | 162 | 0 | 50 | 380 | 282 | 280 | 0 | 35 | 0 | 296 | 0 | 0 | 26 | 160 | 19 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 15 | 83 | 0 | 0 | 89 | 20 | 4 | 40 | 0 | 4 | 575 | 108 | 0 | 0 | 0 | 0 | 142 | 0 | 0 | 0 | 1224 | 16 | 51 | 105 | 16 | 0 | 325 | 335 | 41 | 205 | 31 | 93 | 90 | 147 | 8 | 19 | 114 | 42 | 43 | 57 | 23 | 310 | 320 | 360 | 37 | 30 | 0 | 98 | 0 | 0 | 80 | 30 | 0 | 18 | 173 | 35 | 75 | 110 | 0 | 2 | 41.59 | 12 | 8909.59 | 926 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.53 | 596 | 0 | 1343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 49.64 | 179 | 0 | 167 | 0 | 0 | 0 | 350 | 0 | 4.29 | 0 | 163 | 51 | 30 | 29 | 0 | 0 | 0 | 6.8 | 120 | 0.57 | 0 | 307 | 8 | 100 | 180 | 0 | 260 | 1000 | 0 | 6219.83 | 15129.42 | 78.76
15:00 | 16 | 17 | 31 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 35 | 17 | 126 | 107 | 294 | 55 | 35 | 162 | 0 | 50 | 350 | 285 | 280 | 0 | 35 | 0 | 299 | 0 | 0 | 22 | 160 | 19 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 95 | 0 | 0 | 89 | 42 | 3 | 40 | 0 | 2 | 522 | 108 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0 | 1150 | 12 | 51 | 107 | 16 | 0 | 325 | 335 | 42 | 206 | 27 | 92 | 80 | 147 | 8 | 19 | 114 | 44 | 52.2 | 42 | 23 | 310 | 320 | 335 | 37 | 30 | 0 | 100 | 0 | 0 | 80 | 30 | 0 | 18 | 172 | 35 | 74 | 108 | 0 | 2 | 25.74 | 12 | 8725.94 | 925 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.03 | 618 | 0 | 1369 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 27.63 | 176 | 0 | 167 | 0 | 0 | 0 | 414 | 0 | 1.84 | 0 | 161 | 51 | 42 | 23 | 5 | 0 | 0 | 3.7 | 131 | 0.46 | 0 | 307 | 10 | 115 | 220 | 0 | 256 | 1015 | 0 | 6347.66 | 15073.6 | 78.75
16:00 | 32 | 17 | 31 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35 | 17 | 119 | 122 | 294 | 55 | 35 | 162 | 0 | 49 | 300 | 299 | 280 | 0 | 35 | 0 | 296 | 0 | 0 | 11 | 160 | 19 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 95 | 0 | 0 | 89 | 88 | 2 | 40 | 0 | 2 | 455 | 108 | 0 | 0 | 4 | 0 | 141 | 0 | 0 | 0 | 1150 | 8 | 51 | 107 | 16 | 0 | 326 | 335 | 37 | 204 | 33 | 72 | 80 | 154 | 24 | 19 | 114 | 42 | 52.2 | 29 | 23 | 305 | 320 | 335 | 37 | 30 | 0 | 98 | 8 | 0 | 79 | 30 | 0 | 18 | 172 | 35 | 74 | 99 | 0 | 1 | 13.13 | 12 | 8625.33 | 925 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.46 | 358 | 15 | 1364 | 0 | 0 | 0 | 32 | 0 | 0 | 25 | 0 | 0 | 23 | 0 | 10.16 | 173 | 0 | 167 | 0 | 0 | 0 | 414 | 0 | 1.27 | 0 | 165 | 51 | 74 | 14 | 45 | 0 | 0 | 1.9 | 84 | 0.19 | 6 | 307 | 9 | 115 | 220 | 0 | 213 | 1140 | 0 | 6168.98 | 14794.31 | 78.74
17:00 | 50 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 35 | 17 | 109 | 137 | 294 | 55 | 35 | 162 | 0 | 50 | 300 | 292 | 280 | 0 | 35 | 0 | 275 | 0 | 0 | 5 | 160 | 19 | 19 | 0 | 300 | 10 | 15 | 1 | 0 | 12 | 101 | 35 | 0 | 100 | 100 | 1 | 40 | 9 | 2 | 406 | 160 | 0 | 0 | 14 | 14 | 142 | 0 | 0 | 0 | 1050 | 3 | 51 | 107 | 16 | 0 | 320 | 300 | 37 | 190 | 33 | 77 | 90 | 165 | 36 | 19 | 114 | 40 | 52.2 | 4 | 23 | 305 | 320 | 300 | 37 | 30 | 0 | 89 | 8 | 0 | 80 | 30 | 0 | 18 | 171 | 0 | 74 | 118 | 0 | 1 | 6.71 | 12 | 8512.91 | 926 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.27 | 0 | 60 | 1294 | 0 | 43 | 0 | 106 | 0 | 0 | 100 | 0 | 8 | 17 | 10 | 13.97 | 173 | 0 | 167 | 0 | 0 | 0 | 300 | 0 | 1.25 | 0 | 167 | 51 | 115 | 6 | 113 | 0 | 0 | 1.2 | 41 | 0.13 | 48 | 307 | 0 | 94 | 180 | 0 | 212 | 1195 | 17 | 5951.82 | 14464.73 | 78.73
18:00 | 72 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 35 | 17 | 112 | 137 | 294 | 55 | 35 | 162 | 0 | 50 | 300 | 296 | 280 | 0 | 35 | 0 | 278 | 0 | 0 | 1 | 160 | 18 | 18 | 0 | 300 | 17 | 15 | 30 | 0 | 7 | 101 | 38 | 0 | 100 | 100 | 0 | 40 | 17 | 6 | 406 | 54 | 0 | 0 | 25.5 | 17 | 143 | 0 | 0 | 0 | 1007 | 0 | 51 | 110 | 8 | 0 | 280 | 300 | 37 | 192 | 33 | 72 | 90 | 166 | 38 | 19 | 70 | 40 | 52.2 | 1 | 27 | 310 | 320 | 309 | 37 | 30 | 0 | 82 | 8 | 0 | 80 | 30 | 0 | 18 | 171 | 7 | 101 | 135 | 0 | 0 | 2.14 | 12 | 8443.84 | 926 | 168 | 0 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.69 | 0 | 70 | 1266 | 0 | 49 | 0 | 70 | 5 | 93 | 35 | 19 | 8 | 5 | 15 | 2.55 | 174 | 0 | 167 | 0 | 0 | 0 | 300 | 0 | 0.22 | 0 | 166 | 50 | 70 | 1 | 113 | 0 | 0 | 0.4 | 8 | 0 | 48 | 250 | 0 | 100 | 180 | 0 | 221 | 1115 | 17 | 5723.86 | 14167.7 | 78.72
19:00 | 98 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 35 | 17 | 119 | 140 | 294 | 55 | 35 | 162 | 0 | 50 | 300 | 288 | 300 | 0 | 35 | 0 | 298 | 0 | 0 | 0 | 160 | 19 | 18 | 0 | 300 | 17 | 16 | 61 | 0 | 5 | 102 | 44 | 0 | 100 | 100 | 0 | 40 | 17 | 14 | 575 | 108 | 0 | 0 | 25.5 | 20 | 145 | 0 | 0 | 0 | 1225 | 0 | 51 | 118 | 8 | 0 | 333 | 345 | 45 | 207 | 34 | 72 | 80 | 179 | 38 | 20 | 114 | 46 | 52.2 | 0 | 31 | 315 | 320 | 333 | 36 | 30 | 0 | 94 | 8 | 0 | 82 | 28 | 0 | 18 | 171 | 54 | 101 | 137 | 0 | 0 | 0 | 12 | 9291.7 | 923 | 169 | 0 | 33 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1358 | 0 | 48 | 0 | 85 | 5 | 93 | 113 | 27 | 25 | 0 | 20 | 0 | 173 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 74 | 307 | 0 | 115 | 220 | 0 | 261 | 1153 | 27 | 6386 | 15677.7 | 78.71
19:30 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 17 | 119 | 142 | 294 | 55 | 35 | 162 | 0 | 50 | 300 | 294 | 300 | 0 | 35 | 0 | 284 | 0 | 0 | 0 | 160 | 19 | 18 | 0 | 300 | 17 | 15 | 63 | 0 | 14 | 102 | 66 | 0 | 100 | 100 | 0 | 40 | 34 | 5 | 575 | 160 | 0 | 0 | 25.5 | 40 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 126 | 8 | 0 | 337 | 345 | 45 | 193 | 34 | 93 | 80 | 166 | 38 | 20 | 114 | 44 | 52.2 | 0 | 31 | 315 | 320 | 305 | 37 | 30 | 0 | 99 | 8 | 0 | 82 | 25 | 0 | 18 | 171 | 35 | 102 | 138 | 0 | 0 | 0 | 12 | 9310.7 | 879 | 168 | 0 | 31 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 1362 | 0 | 48 | 0 | 113 | 5 | 93 | 113 | 27 | 43 | 0 | 20 | 0 | 173 | 0 | 172 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 0 | 108 | 220 | 0 | 262 | 1220 | 43 | 6499 | 15809.7
20:00 | 98 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 35 | 17 | 132 | 144 | 294 | 55 | 35 | 162 | 0 | 50 | 300 | 271 | 300 | 0 | 35 | 0 | 266 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 300 | 0 | 0 | 63 | 0 | 8 | 102 | 70 | 0 | 100 | 100 | 0 | 40 | 17 | 14 | 575 | 160 | 0 | 0 | 25.5 | 26 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 8 | 0 | 354 | 345 | 47 | 181 | 34 | 90 | 80 | 171 | 38 | 20 | 114 | 44 | 52.2 | 0 | 31 | 305 | 320 | 305 | 36 | 30 | 0 | 97 | 8 | 0 | 82 | 30 | 0 | 18 | 171 | 44 | 102 | 138 | 0 | 0 | 0 | 12 | 9239.7 | 879 | 168 | 0 | 31 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 1371 | 0 | 48 | 0 | 113 | 5 | 93 | 113 | 36 | 43 | 0 | 20 | 0 | 173 | 0 | 172 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 164 | 52 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 2 | 105 | 220 | 0 | 290 | 1230 | 45 | 6507 | 15746.7 | 78.7
21:00 | 98 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 35 | 17 | 132 | 143 | 294 | 55 | 35 | 162 | 0 | 50 | 350 | 304 | 300 | 0 | 35 | 0 | 283 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 300 | 0 | 0 | 62 | 0 | 1 | 102 | 70 | 0 | 100 | 100 | 0 | 40 | 0 | 20 | 575 | 160 | 0 | 0 | 25.5 | 10 | 145 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 8 | 0 | 342 | 345 | 48 | 199 | 36 | 94 | 80 | 167 | 39 | 20 | 114 | 42 | 52.2 | 0 | 31 | 300 | 320 | 335 | 36 | 30 | 0 | 99 | 8 | 0 | 82 | 28 | 0 | 18 | 171 | 36 | 102 | 138 | 0 | 0 | 0 | 12 | 9345.7 | 925 | 168 | 0 | 31 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 1360 | 0 | 49 | 0 | 113 | 5 | 93 | 113 | 36 | 43 | 0 | 15 | 0 | 174 | 0 | 172 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 163 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 2 | 115 | 220 | 0 | 374 | 1244 | 100 | 6691 | 16036.7 | 78.69
22:00 | 50 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 35 | 17 | 129 | 143 | 294 | 55 | 35 | 162 | 0 | 50 | 300 | 282 | 300 | 0 | 35 | 0 | 255 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 300 | 0 | 0 | 58 | 0 | 0 | 102 | 70 | 0 | 100 | 100 | 0 | 40 | 0 | 19 | 576 | 160 | 0 | 0 | 25.5 | 4 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 8 | 0 | 354 | 345 | 50 | 183 | 36 | 93 | 70 | 170 | 39 | 20 | 114 | 44 | 52.2 | 0 | 31 | 310 | 320 | 300 | 36 | 30 | 0 | 98 | 8 | 0 | 82 | 28 | 0 | 18 | 173 | 35 | 102 | 148 | 0 | 0 | 0 | 12 | 9217.7 | 925 | 164 | 0 | 31 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 1367 | 0 | 49 | 0 | 113 | 5 | 93 | 113 | 36 | 43 | 0 | 15 | 0 | 174 | 0 | 171 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 5 | 105 | 220 | 0 | 434 | 1244 | 100 | 6809 | 16026.7 | 78.68
23:00 | 34 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 131 | 143 | 294 | 40 | 35 | 162 | 0 | 50 | 300 | 294 | 300 | 0 | 35 | 0 | 278 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 300 | 0 | 0 | 46 | 0 | 0 | 102 | 70 | 0 | 89 | 100 | 0 | 40 | 0 | 28 | 576 | 35 | 0 | 0 | 25.5 | 5 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 8 | 0 | 346 | 345 | 51 | 194 | 36 | 94 | 70 | 164 | 39 | 20 | 114 | 46 | 52.2 | 0 | 31 | 305 | 320 | 345 | 36 | 30 | 0 | 84 | 8 | 0 | 82 | 28 | 0 | 18 | 173 | 35 | 102 | 137 | 0 | 0 | 0 | 12 | 9095.7 | 925 | 163 | 0 | 31 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 1375 | 0 | 49 | 0 | 113 | 12 | 93 | 113 | 36 | 43 | 0 | 15 | 0 | 169 | 0 | 169 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 164 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 6 | 125 | 220 | 0 | 453 | 1244 | 100 | 6824 | 15919.7 | 78.67
Total KWH | 659232 | 748800 | 475200 | 0 | 0 | 0 | 0 | 0 | 8863200 | 0 | 0 | 688320 | 432360 | 2590272 | 2903040 | 3924469 | 661799 | 889683 | 3908160 | 0 | 729600 | 8029500 | 7007389 | 7140909 | 0 | 573377 | 0 | 6907530 | 0 | 0 | 223156 | 3566400 | 472800 | 466200 | 0 | 7821818.18 | 75273 | 55200 | 323520 | 0 | 116640 | 2409346 | 521469 | 0 | 2006400 | 984000 | 32762 | 985900 | 87800 | 387840 | 12436363.64 | 1396727 | 0 | 0 | 183897 | 132981 | 3476516 | 0 | 0 | 0 | 27239997 | 138105 | 1133152 | 1727927 | 351273 | 0 | 8291000 | 8216000 | 1129440 | 4789000 | 820080 | 2161920 | 1918850 | 3689760 | 440160 | 462050 | 2464680 | 971520 | 1107648 | 498600 | 459280 | 7440500 | 7685000 | 8550000 | 885000 | 667560 | 0 | 2233718 | 112056 | 0 | 1954560 | 698112 | 0 | 435000 | 3549890 | 509400 | 1837200 | 2664000 | 0 | 16200 | 368410 | 292080 | 203204976.82 | 22244363 | 4466304 | 0 | 161760 | 214144 | 0 | 0 | 0 | 0 | 0 | 0 | 725760 | 8174545 | 921600 | 31461564 | 0 | 394819 | 0 | 1270464 | 38549 | 651312 | 863424 | 210804 | 287702 | 784230 | 122054 | 412504 | 4340727 | 0 | 4358445 | 0 | 0 | 0 | 8273309 | 0 | 34560 | 0 | 3967000 | 1234472 | 1274625 | 222659 | 1201929 | 0 | 0 | 51516.24 | 1391040 | 5047.5 | 719520 | 6742000 | 157664 | 2657000 | 5286970 | 0 | 6784776 | 27458909.09 | 444000 | 150012070.83 | 353217047.65

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 09-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-05-2025 | during | 09-05-2025 | during | 09-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 360 | 343 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 350 | 450 | 450 | 400 | 400 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 293 | 304 | 335 | 335 | 331.5 | 331.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 302 | 283 | 335 | 335 | 315 | 315 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 98 | 16 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 125 | 143 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19.5 | 18 | 30 | 30 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 21 | 18 | 22 | 22 | 21 | 21 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 40 | 17 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 146 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 132 | 135 | 135 | 135 | 135 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 50 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 26 | 50 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 32 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 300 | 584 | 584 | 350 | 350 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 280 | 300 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 130 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2891.5 | 3201 | 5267.9 | 5319.9 | 3760.61 | 3820.61
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 39 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 143 | 145 | 145 | 150 | 150 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 10 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 70 | 56 | 80 | 56 | 80 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 102 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 76 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 20 | 30 | 34 | 30 | 34 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 62 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 3.46 | 0 | 3.46 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 65 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1150 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 6 | 1 | 5 | 3 | 5 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 503 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2129 | 2634.5 | 3425.18 | 3432.72 | 3430.18 | 3432.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 205 | 199 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 331 | 342 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 345 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 35 | 36 | 46.94 | 46.94 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 48 | 55 | 55 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 86 | 127 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 31 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 80 | 163 | 163 | 163 | 163 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 143 | 167 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 24.5 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 39 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 94 | 94 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1724.2 | 1795.2 | 2465.99 | 2400.99 | 2315.55 | 2279.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 08-05-2025 | during | 09-05-2025 | during | 09-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 102 | 138 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 76 | 102 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.07 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 36 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 277.07 | 288 | 601.1 | 549 | 311.6 | 331.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 38 | 36 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 105 | 99 | 113 | 113 | 103 | 103 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 28 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 341 | 341 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 335 | 335 | 385 | 385 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1441 | 1427 | 1553 | 1553 | 1510 | 1510
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 926 | 925 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 31 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 41 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 185 | 168 | 410 | 410 | 212 | 212 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 103 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 98.53 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 504 | 0 | 1234.2 | 1234.2 | 618 | 618 | U2 Reserve Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1713.53 | 1268 | 3612.2 | 3514.2 | 2693.01 | 2595.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 262 | 374 | 315 | 315 | 315 | 315 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 96 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 0 | 2 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 115 | 115 | 125 | 125 | 125 | 125 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1100 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.72 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1964.72 | 2458 | 2482.12 | 2481.12 | 2482.12 | 2481.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 49 | 47 | 47 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 5 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 36 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 186 | 174 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 172 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 350 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 15 | 22 | 22 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 93 | 93 | 93 | 93 | 93 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.88 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1354.06 | 1360 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.94 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 95 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 2261.88 | 2523 | 3104.73 | 2938.53 | 3046.94 | 2880.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 51 | 52 | 52 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 162 | 163 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.1 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 190 | 0 | 189.51 | 0 | 189.51 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 431.1 | 442 | 690.11 | 464 | 693.11 | 467
System Total |  |  |  |  | 27566.2 | 28624.082 | 14834 | 16036.7 | 23202.33 | 22653.46 | 20243.12 | 19798.25
Forecast Scenario (09-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15700 |  | 0 |  | 15700
|  |  |  | 1:00 | 15390 |  | 0 |  | 15390
|  |  |  | 2:00 | 15010 |  | 0 |  | 15010
|  |  |  | 3:00 | 14570 |  | 0 |  | 14570
|  |  |  | 4:00 | 14170 |  | 0 |  | 14170
|  |  |  | 5:00 | 13800 |  | 0 |  | 13800
|  |  |  | 6:00 | 13180 |  | 0 |  | 13180
|  |  |  | 7:00 | 12990 |  | 0 |  | 12740
|  |  |  | 8:00 | 12840 |  | 0 |  | 12540
|  |  |  | 9:00 | 13260 |  | 0 |  | 12390
|  |  |  | 10:00 | 13770 |  | 0 |  | 12270
|  |  |  | 11:00 | 14320 |  | 0 |  | 12670
|  |  |  | 12:00 | 14890 |  | 0 |  | 13220
|  |  |  | 13:00 | 15180 |  | 0 |  | 13680
|  |  |  | 14:00 | 15210 |  | 0 |  | 13220
|  |  |  | 15:00 | 15220 |  | 0 |  | 13640
|  |  |  | 16:00 | 14980 |  | 0 |  | 13490
|  |  |  | 17:00 | 14670 |  | 0 |  | 12890
|  |  |  | 18:00 | 14220 |  | 0 |  | 12430
|  |  |  | 18:30 | 14900 |  | 0 |  | 13300
|  |  |  | 19:00 | 15760 |  | 0 |  | 14370
|  |  |  | 19:30 | 16000 |  | 0 |  | 15280
|  |  |  | 20:00 | 16000 |  | 0 |  | 15130
|  |  |  | 21:00 | 16170 |  | 0 |  | 15390
|  |  |  | 22:00 | 15800 |  | 0 |  | 15340
|  |  |  | 23:00 | 15700 |  | 0 |  | 15300
Probable Maximum Temperature: |  |  | 36.00°C
Probable Maximum Demand at Day Peak: |  |  | 13220.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15390.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16170.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 351.00 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:03 hrs on 09-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 08-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14834 | MW | 12:00 Hr. | Energy Generated |  |  | 353.217 |  | MKWHr.
| Day Peak Demand |  |  | 14898.79 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.151 |  | MKWHr.
| Evening Peak Generation |  |  | 16036.7 | MW | 21:00 Hr. | Energy Demand |  |  | 355.368 |  | MKWHr.
| Evening Peak Demand |  |  | 16170.7 | MW | 21:00 Hr. | Maximum Temperature |  |  | 38 |  | °C
| Minimum Generation of the Day |  |  | 12846.91 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1034.05 |  | MMCFD
| Maximum Generation of the Day |  |  | 16036.7 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.3093 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 46.7093 | 0 | 22.7507 | 0 | 0 | 0.22316 | 0 | 0 | 69.6832 | Gas | 141.4364 | Gas | 499417499.8006
| Chattogram Zone |  |  | 3.8644 | 39.6764 | 8.1766 | 0 | 0.9859 | 0.17087 | 0 | 0.11664 | 52.9907 | Coal | 94.0381 | Coal | 622743599.0645
| Cumilla Zone |  |  | 27.1108 | 0 | 12.0514 | 0 | 0 | 0.4986 | 0.97152 | 0 | 40.6323 | HFO | 57.0581 | HFO | 1076971341.26
| Mymensingh Zone |  |  | 0 | 0 | 5.3027 | 0 | 0 | 0.38461 | 0 | 0 | 5.6873 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.2114 | Hydro | 0.9859 | Hydro | 98590
| Khulna Zone |  |  | 4.4663 | 8.1745 | 1.2975 | 0 | 0 | 0.72576 | 22.2444 | 0 | 36.9085 | Solar | 4.9045 | Solar | 79958934.6014
| Barishal Zone |  |  | 8.1016 | 40.9857 | 1.1635 | 0 | 0 | 0.0050475 | 0 | 0 | 50.2559 | Import | 54.6774 | Import | 300865000.35
| Rajshahi Zone |  |  | 16.9725 | 0 | 3.8391 | 0 | 0 | 1.2313 | 31.4616 | 0 | 53.5045 | Wind | 0.11664 | Wind | 1707609.6
| Rangpur Zone |  |  | 0 | 5.2015 | 2.4766 | 0 | 0 | 1.6652 | 0 | 0 | 9.3432
| Total |  |  | 141.4364 | 94.0381 | 57.0581 | 0 | 0.9859 | 4.9045 | 54.6774 | 0.11664 | 353.217
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 499417499.8006 |  | Hydro | 98590
|  |  |  | Coal | 622743599.0645 |  | Solar | 79958934.6014
|  |  |  | HFO | 1076971341.26 |  | Import | 300865000.35
|  |  |  | HSD | 0 |  | Wind | 1707609.6
[5 empty] | Total: | 258,17,62,574 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2444 | Peak Hr Flow | 925.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35588581.89 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.4616 | Peak Hr Flow | 1360.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 580 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.97152 | Peak Hr Flow | 42.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 894 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.6774 | Peak Hr Flow | 2327.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 50 |  | 5677
|  |  |  | Chattogram |  | 0 |  | 1564
|  |  |  | Cumilla |  | 10 |  | 1478
|  |  |  | Mymensingh |  | 68 |  | 1337
|  |  |  | Sylhet |  | 0 |  | 595
|  |  |  | Khulna |  | 0 |  | 1875
|  |  |  | Barishal |  | 0 |  | 356
|  |  |  | Rajshahi |  | 0 |  | 1706
|  |  |  | Rangpur |  | 0 |  | 1006
|  |  |  | Total |  | 128 |  | 15594
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Ashuganj 450 MW CCPP(North) GT |  |  | 240 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Ashuganj 450 MW CCPP(North) ST |  |  | 120 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Baghabari 100 MW GTPP |  |  | 100 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Barapukuria TPP Unit-2 |  |  | 85 | 4 | Kushiara 163 MW CCPP (KP) ST |  |  | 54
|  | 5 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 660 |  |  |  | Total | 489.09
|  |  |  | Total Unavailable Capacity |  |  |  | 1149.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:12 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 HT is restored.
|  | 08:16 | Aminbazar 400/230/132kV S/S 230/132kv Tr-01 LT is restored.
|  | 08:23 | Aminbazar 400/230/132kV S/S 132 kv Bus 01 is restored.
| 08:50 | 14:44 | Siddhirganj-Siddhirganj (Orion)132kV Ckt-1 Tripped from Siddhirganj 132/33kV end showing
DEF,E/F,GT,O/C relays Due to E/F,
| 08:50 | 11:48 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Tripped showing LBB Initiation,86 relays Due to
Dutchbangla Line fault
|  | 09:57 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT is restored.
|  | 09:58 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT is restored.
| 11:41 | 12:25 | Baghabari-Bangura 132 kV Ckt-1 Tripped from Bhangura 132/33kV end showing TCS 1 R Y B | [7 empty] | 37.0MW load
|  |  | Phase relays Due to Bagabari side trip | [7 empty] | interrup. Bhangura
132/33kV end
| 11:43 | 12:12 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing Over current
Earth fault. relays.
| 13:31 | 14:34 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 13:32 | 14:34 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D | [7 empty] | 15.0MW load
interrup.
| 13:51 | 17:27 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to High
Temperature maintenance of Gantry Clam-T
| 13:52 | 14:58 | Rajendrapur 132/33kV S/S MTR-2 LT Scheduled S/D Due to For 33 KV incomer -2 meter
installation work by metering division
| 13:52 | 14:57 | Rajendrapur 132/33kV S/S MTR-2 HT Scheduled S/D Due to For 33 KV incomer -2 meter
installation work by metering division
|  | 14:25 | Kodda-Rajendrapur 132kV Ckt-1 is restored.
| 14:59 | 21:08 | Siddhirganj-Siddhirganj (Orion)132kV Ckt-1 Forced S/D from Siddhirganj 132/33kV end Due
to Y Ph Lope Disconnect
| 15:06 | 15:46 | Rajendrapur 132/33kV S/S MTR-3 LT Scheduled S/D Due to For 33 KV incomer -3 meter
installation work by metering division
| 15:07 | 15:45 | Rajendrapur 132/33kV S/S MTR-3 HT Scheduled S/D Due to For 33 KV incomer -3 meter
installation work by metering division
| 15:09 |  | Shyampur 230/132 kV to Shyampur 132/33 kV S/S ckt-1 and 2 tripped showing distance relay. | [7 empty] | 156MW load
interrup.
| 15:09 | 18:32 | Shyampur-Shyampur(New) 132kV Ckt-2 Tripped from Shyampur 132/33kV end showing Distance | [7 empty] | 80.0MW load
|  |  | relay relays Due to None | [7 empty] | interrup. Shyampur
132/33kV end
| 15:11 | 15:55 | Shyampur-Shyampur(New) 132kV Ckt-1 Tripped from Shyampur 132/33kV end showing O/C relays. | [7 empty] | 80.0MW load
interrup. Shyampur
132/33kV end
| 15:55 |  | Shyampur 230/132 kV to Shyampur 132/33 kV S/S ckt-1 switched on.
|  | 15:56 | Gopalganj 400/132kV S/S 400kV Bus-02 is restored.
| 16:01 |  | Rampal 1320 MW (BIFPCL) Shutdown with remarks:- U1
| 16:40 | 17:39 | Hathazari 230/132/33kV S/S T-01 HT Forced S/D
| 16:40 | 17:39 | Hathazari 230/132/33kV S/S T-01 LT Forced S/D
| 17:54 | 18:36 | Bogura 132/33kV S/S Transformer-1 LT Tripped showing O/C E/F &33 KV LOCKOUT OPERATED. | [7 empty] | 50.0MW load
|  |  | relays Due to DEW TO TALORA 33KV & PURAN BOGURA 33KV FEEDER FAULT. | [7 empty] | interrup.
| 17:54 | 18:36 | Bogura 132/33kV S/S Transformer-2 LT Tripped showing O/C, E/F & 33KV LOCKOUT OPERATED. | [7 empty] | 50.0MW load
|  |  | relays Due to DEW TO TALORA 33KV & PURAN BOGURA 33KV FEEDER FAULT.. | [7 empty] | interrup.
| 18:32 |  | Shyampur 230/132 kV to Shyampur 132/33 kV S/S ckt-2 switched on.
| 21:00 |  | Evening peak generation 16036 MW.
| 21:21 | 22:41 | Madunaghat 132/33kV S/S TR-2(517T) LT Scheduled S/D Due to Maintenance work by BPDB | [7 empty] | 10.0MW load
|  |  | Mohora. | [7 empty] | interrup.
| 21:23 | 22:41 | Madunaghat 132/33kV S/S TR-2(517T) HT Scheduled S/D Due to Maintenance work by PDB. | [7 empty] | 10.0MW load
interrup.
| 04:33 |  | Sikalbaha-TKCL 132kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing Main1
Protection relay FN1 relays.
| 05:11 |  | Sikalbaha 132 kv bus-1 tripped showing bus differential ( bus-2 under shutdown for long
days) and Hathazari - Baroaulia line-1 & 2 tripped showing O/C. As a result, about 635 MW
interruption occurred under Baroaulia, Sitalpur Steel Mill, KSRM, Kulsi, Rampur, Agrabad,
Julda, Dohazari, Sikalbaha, Coxbazar & Matarbari S/S from 05:11 to 5:42 hrs
| 05:11 | 07:21 | Dohazari-Sikalbaha 132 kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing FN-6
relays.
| 05:11 |  | Shahmirpur-Sikalbaha 132kV Ckt-2 Tripped from Shikalbaha 230/132kV end showing FN-6
relays.
| 05:11 |  | Juldah-Sikalbaha 132kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing FN-6 relays. | [7 empty] | 1.0MW load
interrup.
Shikalbaha
230/132kV end
| 05:11 | 05:46 | Khulshi 132/33kV S/S 405T (T1) LT Tripped showing Under Frequency Relay relays Due to | [7 empty] | 50.0MW load
|  |  | 132kV Grid power failure. | [7 empty] | interrup.
| 05:11 | 05:46 | Khulshi 132/33kV S/S 415T (T2) LT Tripped showing Under Frequency relays Due to 132kV | [7 empty] | 47.0MW load
|  |  | Grid power failure. | [7 empty] | interrup.
| 05:11 | 05:42 | Baroaulia-Hathazari 132 kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing MCGG | [7 empty] | 40.0MW load
|  |  | relays Due to over current | [7 empty] | interrup. Hathazari
230/132/33kV end
| 05:11 |  | Shikalbaha 230/132kV S/S ATR 01 LT Tripped showing FN-6 relays.
| 05:11 | 05:42 | Baroaulia-Hathazari 132 kV Ckt-2 Tripped from Hathazari 230/132/33kV end showing Mcgg | [7 empty] | 40.0MW load
|  |  | relays Due to over current | [7 empty] | interrup. Hathazari
230/132/33kV end
| 05:11 |  | Shikalbaha 230/132kV S/S ATR 02 LT Tripped showing FN-6 relays.
| 05:11 |  | Bakulia-Sikalbaha 132 kV Ckt-2 Tripped from Shikalbaha 230/132kV end showing FN-6 relays.
| 05:11 | 07:19 | Bakulia-Sikalbaha 132 kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing FN-6 relays.
| 05:11 |  | Dohazari-Sikalbaha 132 kV Ckt-2 Tripped from Shikalbaha 230/132kV end showing FN-6
relays.
| 05:11 |  | Shikalbaha 230/132kV S/S Interconnection-1 Tripped showing FN-6 relays.
| 05:11 |  | Shahmirpur-Sikalbaha 132kV Ckt-1 Tripped from Shikalbaha 230/132kV end showing FN-6
relays.
| 06:00 |  | Min. Gen. 12002 MW
| 06:16 |  | Mirpur 132/33kV S/S T2 LT Scheduled S/D
| 06:17 | 07:44 | Mirpur 132/33kV S/S T2 HT Scheduled S/D
| 06:21 |  | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to 33kV Bus maintenance | [7 empty] | 50.0MW load
interrup.
| 06:27 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33kV Bus maintenance | [7 empty] | 95.0MW load
interrup.
| 06:27 |  | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to 33kv Bus maintenance | [7 empty] | 95.0MW load
interrup.
| 06:49 |  | Siddhirganj CCPP 335 MW was shutdown due to air-inlet filter maintenance.
| 07:02 |  | Rampal 1320 MW (BIFPCL) unit-2 was sync.
| 07:02 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
| 07:08 |  | Baghabari-Ishurdi 230 kV Ckt-1 Project Work S/D from Ishurdi 230/132kV end.
| 07:09 |  | Baghabari-Ishurdi 230 kV Ckt-2 Project Work S/D from Ishurdi 230/132kV end.
| 07:22 |  | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to hotspot maintenance | [7 empty] | 10.0MW load
interrup.
| 07:22 |  | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to hotspot maintenance | [7 empty] | 10.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 08-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 343 | 8863200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8029500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7007389 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 661799 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 283 | 6907530 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 98 | 659232 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 688320 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 2903040 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 889683 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 573377 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 472800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 466200 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 475200 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 3924469 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 132 | 2590272 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 748800 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 50 | 729600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3908160 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 223156 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432360 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 7821818.18 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 300 | 7140909 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 3566400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3201 | 69683214.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 183897 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 138105 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 985900 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 145 | 3476516 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 10 | 132981 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 70 | 521469 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 2409346 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 2006400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 387840 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 62 | 323520 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 32762 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 55200 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 87800 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 984000 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 75273 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 1396727 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27239997 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 116640 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 575 | 12436363.64 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2634.5 | 52990736.64
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 199 | 4789000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 342 | 8291000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8216000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 820080 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 48 | 1129440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 351273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1133152 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 127 | 1727927 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 31 | 459280 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1918850 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 167 | 3689760 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 42 | 971520 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1107648 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 462050 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2464680 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 39 | 440160 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 2161920 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 498600 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1795.2 | 40632340
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 16200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 138 | 2664000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1837200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 368410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 292080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 36 | 509400 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 288 | 5687290
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 885000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 667560 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 99 | 2233718 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 28 | 698112 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1954560 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 171 | 3549890 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 435000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 112056 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7440500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 8550000 | FGMO
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7685000 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 1427 | 34211396
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 925 | 22244363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 31 | 161760 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 41 | 214144 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 168 | 4466304 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 103 | 921600 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 725760 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 0 | 8174545 | U2 Reserve Shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1268 | 36908476
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 374 | 6784776 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 96 | 719520 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 2 | 157664 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 115 | 2657000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27458909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5286970 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 444000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6742000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 5047.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2458 | 50255886.59
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 49 | 394819 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 5 | 38549 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 36 | 210804 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 174 | 4340727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 172 | 4358445 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 8273309 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 15 | 122054 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 287702 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 651312 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1270464 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 863424 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 34560 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1360 | 31461564 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 412504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 784230 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2523 | 53504467
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1234472 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 163 | 3967000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1201929 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 51516.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1274625 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 222659 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1391040 | -
Rangpur Area Total |  |  |  |  | 950 | 442 | 9343241.24
Eastern Grid Total |  |  |  |  | 16921.242 | 9345.7 | 203204976.82
Western Grid Total |  |  |  |  | 11702.84 | 6691 | 150012070.83
National Grid Total |  |  |  |  | 28624.082 | 16036.7 | 353217047.65
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 08-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10523.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4943.1 | MW
i) Dhaka area |  |  | 5627.09 |  | MW | i) Khulna area |  |  |  | 1875 | MW
ii) Chattogram area |  |  | 1564 |  | MW | ii) Barishal area |  |  |  | 356.5 | MW
iii) Cumilla area |  |  | 1468.5 |  | MW | iii) Rajshahi area |  |  |  | 1705.6 | MW
iv) Mymensingh area |  |  | 1269 |  | MW | iv) Rangpur area |  |  |  | 1006 | MW
v) Sylhet area |  |  | 595 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15466.69 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 94 | 19:30 | 133 | Patuakhali | 81 | 00:00
2 | AKSML | 19 | 00:00 | 68 | Jaldhaka | 85 | 19:00 | 134 | Payra | 34 | 00:00
3 | Aftabnagar | 40 | 13:00 | 69 | Jamalpur | 140 | 21:00 | 135 | Postogola | 60 | 13:00
4 | Agargaon | 150 | 15:00 | 70 | Jashore | 151 | 21:00 | 136 | Purbachal | 22 | 19:00
5 | Agrabad | 104 | 18:30 | 71 | Jhenaidah | 140 | 21:00 | 137 | Purbasadipur | 137 | 21:00
6 | Amnura | 47 | 22:00 | 72 | Joydebpur | 165 | 12:00 | 138 | Rahanpur | 33 | 23:00
7 | Ashuganj | 100 | 00:00 | 73 | Joypurhat | 76 | 19:30 | 139 | Rahim | 56 | 02:00
8 | BSRM | 207 | 15:00 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 90 | 19:30
9 | Bagerhat | 92 | 00:00 | 75 | KSRM | 25 | 16:00 | 141 | Rajendrapur | 151 | 19:30
10 | Bajitpur | 58 | 20:00 | 76 | Kabirpur | 279 | 09:00 | 142 | Rajshahi | 131 | 21:00
11 | Bakulia | 105 | 19:30 | 77 | Kachua | 89 | 00:00 | 143 | Rajshahi-230 | 99 | 23:00
12 | Banani | 45.6 | 15:00 | 78 | Kallyanpur | 105 | 16:00 | 144 | Ramganj | 116 | 03:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 46 | 12:00 | 145 | Rampur | 46 | 18:30
14 | Barapukuria | 75 | 21:00 | 80 | Kamrangirchar | 72.5 | 19:00 | 146 | Rangamati | 18 | 18:30
15 | Barguna | 24 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 165 | 19:00
16 | Barishal | 114 | 15:00 | 82 | Kasba | 38 | 22:00 | 148 | Ruppur | 8 | 15:00
17 | Barishal-230 | 102 | 00:00 | 83 | Kazla | 105 | 12:00 | 149 | SSM | 9 | 02:00
18 | Baroaulia | 72 | 11:00 | 84 | Keranigonj | 83 | 19:30 | 150 | Saidpur | 115 | 21:00
19 | Baroirhat | 78 | 19:30 | 85 | Khagrachori | 32 | 19:00 | 151 | Satkhira | 143 | 22:00
20 | Bashundhara | 214 | 14:00 | 86 | Khulna | 82 | 00:00 | 152 | Satmasjid | 114 | 16:00
21 | BashundharaCement | 13 | 12:00 | 87 | Khulshi | 192 | 17:00 | 153 | Savar | 240 | 16:00
22 | Beanibazar | 79 | 19:00 | 88 | Kishoreganj | 141 | 00:00 | 154 | SevenRings | 19.77 | 19:30
23 | Benapole | 70 | 21:00 | 89 | Kodda | 308 | 18:00 | 155 | ShahCement | 30 | 10:00
24 | Bhaluka | 183 | 19:00 | 90 | Kulaura | 51 | 21:00 | 156 | Shahjadpur | 99 | 22:00
25 | Bhandaria | 55.4 | 00:00 | 91 | Kurigram | 60 | 20:00 | 157 | Shahjibazar | 116 | 00:00
26 | Bhangura | 52 | 19:00 | 92 | Kushtia | 169 | 21:00 | 158 | Shahmirpur | 58 | 00:00
27 | Bheramara(GK) | 70 | 19:00 | 93 | Lalbag | 72 | 13:00 | 159 | Shariatpur | 86 | 00:00
28 | Bhulta | 235 | 22:00 | 94 | Lalmonirhat | 60 | 19:30 | 160 | Sherpur | 166 | 21:00
29 | Bog-Sherpur | 78 | 19:30 | 95 | MI_Cement | 18.1 | 00:00 | 161 | Shikalbaha | 28 | 19:00
30 | Bogura | 185 | 22:00 | 96 | Madanganj | 56 | 16:00 | 162 | Shitalakhya | 86.3 | 15:00
31 | Borhanuddin | 92 | 00:00 | 97 | Madaripur | 109 | 22:00 | 163 | Sholosohor | 52 | 18:30
32 | Brahmanbaria | 137 | 22:00 | 98 | Madartek | 93.72 | 23:00 | 164 | Shyampur | 194 | 12:00
33 | Cantonment | 150 | 13:00 | 99 | Madunaghat | 60 | 19:00 | 165 | Siddhirganj | 120 | 16:00
34 | Chandina | 16.6 | 20:00 | 100 | Magura | 69 | 19:30 | 166 | Sirajganj | 130 | 21:00
35 | Chandpur | 76 | 00:00 | 101 | Mahasthangarh | 92 | 19:30 | 167 | Sonargaon | 134 | 19:00
36 | Chandraghona | 38 | 19:00 | 102 | Manikganj | 136 | 23:00 | 168 | Sreemongol | 83 | 19:00
37 | Chapai | 76 | 23:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 110 | 19:00
38 | Charsaidpur | 40 | 00:00 | 104 | Matarbari | 55 | 19:30 | 170 | Srinagar | 46.68 | 22:00
39 | Chauddagram | 75 | 19:30 | 105 | Matuail | 74 | 12:00 | 171 | Sunamganj | 60 | 19:00
40 | Chhatak | 37 | 00:00 | 106 | Millgate | 127 | 15:00 | 172 | Sylhet | 46 | 00:00
41 | Chowmuhani | 233 | 20:00 | 107 | Mirpur | 146 | 19:00 | 173 | Sylhet-132 | 132 | 20:00
42 | Chuadanga | 123 | 23:00 | 108 | Mirsorai | 11 | 16:00 | 174 | TK | 36.5 | 22:00
43 | Coxsbazar | 142 | 19:30 | 109 | Mirzapur | 50 | 19:00 | 175 | Tangail | 194 | 18:30
44 | Cumilla(N) | 159 | 22:00 | 110 | Mithapukur | 64 | 23:00 | 176 | Thakurgaon | 108 | 21:00
45 | Cumilla(S) | 180 | 13:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 128 | 10:00
46 | Daudkandi | 153 | 20:00 | 112 | Mogbazar | 170.7 | 15:00 | 178 | Ullahpara | 49 | 19:00
47 | Dhaka | 68 | 13:00 | 113 | Mongla | 43 | 12:00 | 179 | Ullon | 40 | 00:00
48 | Dhamrai | 144 | 14:00 | 114 | Motijheel | 41 | 11:00 | 180 | Uttara | 110 | 14:00
49 | Dhanmondi | 166 | 13:00 | 115 | Muktagacha | 42 | 19:00 | 181 | UttaraNew | 53 | 14:00
50 | Dohazari | 112 | 21:00 | 116 | Munshiganj | 112 | 00:00 | 182 | Zigatola | 82 | 00:00
51 | Faridpur | 168 | 23:00 | 117 | Muradnagar | 32 | 21:00
52 | Fatullah | 109 | 12:00 | 118 | Mymensingh | 228 | 20:00
53 | Fenchuganj | 50 | 20:00 | 119 | Naogaon | 145 | 23:00
54 | Feni | 119 | 19:30 | 120 | Narail | 62 | 19:30
55 | GPH | 98 | 23:00 | 121 | Narinda | 88 | 13:00
56 | Ghatail | 86 | 19:00 | 122 | Narshingdi | 185 | 00:00
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 176 | 19:30
58 | Ghorashal-230 | 103 | 23:00 | 124 | Nawabganj | 60.1 | 20:00
59 | Goalpara | 28 | 00:00 | 125 | Netrakona | 130 | 18:30
60 | Gollamari | 100 | 00:00 | 126 | New | 94 | 12:00
61 | Gopalganj | 102.3 | 19:00 | 127 | Niamatpur | 88 | 22:00
62 | Gulshan | 142 | 15:00 | 128 | Noapara | 50 | 22:00
63 | Halishahar | 79 | 15:00 | 129 | PHP | 9 | 08:00
64 | HaripurSBU | 185 | 00:00 | 130 | Pabna | 137 | 19:30
65 | Hasnabad | 86 | 00:00 | 131 | Palashbari | 143 | 20:00
66 | Hathazari | 88 | 18:00 | 132 | Panchagarh | 65 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 08-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15745.55 | 72 |  | 15820.79
1:00 | 15112.14 | 137 |  | 15255.31
2:00 | 14572.14 | 123 |  | 14701.14
3:00 | 14012.74 | 74 |  | 14089.74
4:00 | 13646.19 | 53 |  | 13701.19
5:00 | 13465.31 | 33 |  | 13499.31
6:00 | 12925.7 | 45 |  | 12972.7
7:00 | 12932.68 | 57 |  | 12992.68
8:00 | 12846.91 | 0 |  | 12846.91
9:00 | 13262.55 | 0 |  | 13262.55
10:00 | 13731.19 | 40 |  | 13773.19
11:00 | 14271.06 | 52 |  | 14325.4
12:00 | 14834 | 62 |  | 14898.79
13:00 | 15132.01 | 55 |  | 15189.49
14:00 | 15129.42 | 80 |  | 15213.42
15:00 | 15073.6 | 143 |  | 15222.6
16:00 | 14794.31 | 180 |  | 14982.31
17:00 | 14464.73 | 199 |  | 14672.69
18:00 | 14167.7 | 53 |  | 14222.7
19:00 | 15677.7 | 79 |  | 15760.7
19:30 | 15809.7 | 182 |  | 15999.7
20:00 | 15746.7 | 243 |  | 16000.7
21:00 | 16036.7 | 128 |  | 16170.7
22:00 | 16026.7 | 118 |  | 16149.7
23:00 | 15919.7 | 125 |  | 16050.7
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 08-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8794.2 | 6951.35 | 15745.55 | DAILY GENERATION CURVE
00:30 | 8663.95 | 6764.895 | 15428.845
01:00 | 8533.7 | 6578.44 | 15112.14 | 08-05-2025
01:30 | 8301.45 | 6540.69 | 14842.14
02:00 | 8069.2 | 6502.94 | 14572.14
02:30 | 8032.2 | 6260.24 | 14292.44
03:00 | 7995.2 | 6017.54 | 14012.74
03:30 | 7853.95 | 5975.515 | 13829.465
04:00 | 7712.7 | 5933.49 | 13646.19
04:30 | 7671.95 | 5883.8 | 13555.75
05:00 | 7631.2 | 5834.11 | 13465.31
05:30 | 7571.165 | 5624.34 | 13195.505
06:00 | 7511.13 | 5414.57 | 12925.7
06:30 | 7500.315 | 5428.875 | 12929.19
07:00 | 7489.5 | 5443.18 | 12932.68
07:30 | 7452.25 | 5437.545 | 12889.795
08:00 | 7415 | 5431.91 | 12846.91
08:30 | 7519.21 | 5535.52 | 13054.73
09:00 | 7623.42 | 5639.13 | 13262.55
09:30 | 7736.22 | 5760.65 | 13496.87
10:00 | 7849.02 | 5882.17 | 13731.19
10:30 | 7939.935 | 6061.19 | 14001.125
11:00 | 8030.85 | 6240.21 | 14271.06
11:30 | 8246.81 | 6305.72 | 14552.53
12:00 | 8462.77 | 6371.23 | 14834
12:30 | 8637.925 | 6345.08 | 14983.005
13:00 | 8813.08 | 6318.93 | 15132.01
13:30 | 8861.335 | 6269.38 | 15130.715
14:00 | 8909.59 | 6219.83 | 15129.42
14:30 | 8817.765 | 6283.745 | 15101.51
15:00 | 8725.94 | 6347.66 | 15073.6
15:30 | 8675.635 | 6258.32 | 14933.955
16:00 | 8625.33 | 6168.98 | 14794.31
16:30 | 8569.12 | 6060.4 | 14629.52
17:00 | 8512.91 | 5951.82 | 14464.73
17:30 | 8478.375 | 5837.84 | 14316.215
18:00 | 8443.84 | 5723.86 | 14167.7
18:30 | 8867.77 | 6054.93 | 14922.7
19:00 | 9291.7 | 6386 | 15677.7
19:30 | 9310.7 | 6499 | 15809.7
20:00 | 9239.7 | 6507 | 15746.7
20:30 | 9292.7 | 6599 | 15891.7 |  | Executive Engineer
21:00 | 9345.7 | 6691 | 16036.7 |  | Network Operation Division
21:30 | 9281.7 | 6750 | 16031.7
22:00 | 9217.7 | 6809 | 16026.7
22:30 | 9156.7 | 6816.5 | 15973.2
23:00 | 9095.7 | 6824 | 15919.7

## En-Curve
QF-LDC-12
Date | 08-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3775 | 2263 | 927 | 0 | 46 | 1360.35 | 40 | 4447 | 0 | 727 | 2160.2 | 0 | 0 | 0 | 72 | DAILY ENERGY CURVE
00:30 | 3727.5 | 2216.25 | 927 | 0 | 45 | 1365.545 | 40 | 4416 | 1.85 | 642 | 2047.7 | 0 | 0 | 0 | 104.5 | 08-05-2025
01:00 | 3680 | 2169.5 | 927 | 0 | 44 | 1370.74 | 40 | 4385 | 3.7 | 557 | 1935.2 | 0 | 0 | 0 | 137
01:30 | 3659 | 2159.75 | 927 | 0 | 43 | 1371.34 | 40 | 4380.5 | 1.85 | 521 | 1738.7 | 0 | 0 | 0 | 130 | Energy Generated | 353.217 |  | MKWHr
02:00 | 3638 | 2150 | 927 | 0 | 42 | 1371.94 | 40 | 4376 | 0 | 485 | 1542.2 | 0 | 0 | 0 | 123 | Energy not Served | 2.151 |  | MKWHr
02:30 | 3667 | 2161 | 927 | 0 | 42 | 1346.74 | 40 | 4326 | 0 | 444.5 | 1338.2 | 0 | 0 | 0 | 98.5 | Total Energy Requirement | 355.368 |  | MKWHr
03:00 | 3696 | 2172 | 927 | 0 | 42 | 1321.54 | 40 | 4276 | 0 | 404 | 1134.2 | 0 | 0 | 0 | 74
03:30 | 3709.5 | 2176.25 | 927 | 0 | 41 | 1319.015 | 40 | 4179.5 | 0 | 384.5 | 1052.7 | 0 | 0 | 0 | 63.5
04:00 | 3723 | 2180.5 | 927 | 0 | 40 | 1316.49 | 40 | 4083 | 0 | 365 | 971.2 | 0 | 0 | 0 | 53
04:30 | 3697.5 | 2174.75 | 926.5 | 0 | 35 | 1313.8 | 40 | 4033 | 0 | 365 | 970.2 | 0 | 0 | 0 | 43
05:00 | 3672 | 2169 | 926 | 0 | 30 | 1311.11 | 40 | 3983 | 0 | 365 | 969.2 | 0 | 0 | 0 | 33
05:30 | 3661 | 2155.75 | 926 | 0 | 35 | 1234.845 | 40 | 3839 | 18.21 | 365 | 920.7 | 0 | 0 | 0 | 39
06:00 | 3650 | 2142.5 | 926 | 0 | 40 | 1158.58 | 40 | 3695 | 36.42 | 365 | 872.2 | 0 | 0 | 0 | 45
06:30 | 3674 | 2141.5 | 926 | 0 | 38 | 1158.84 | 40 | 3624 | 95.25 | 365 | 866.6 | 0 | 0 | 0 | 51
07:00 | 3698 | 2140.5 | 926 | 0 | 36 | 1159.1 | 40 | 3553 | 154.08 | 365 | 861 | 0 | 0 | 0 | 57
07:30 | 3716.5 | 2137.7 | 902.5 | 0 | 35 | 1159.1 | 40 | 3447.5 | 237.995 | 348 | 865.5 | 0 | 0 | 0 | 28.5
08:00 | 3735 | 2134.9 | 879 | 0 | 34 | 1159.1 | 40 | 3342 | 321.91 | 331 | 870 | 0 | 0 | 0 | 0
08:30 | 3756.5 | 2151.95 | 878.5 | 0 | 35 | 1160.485 | 40 | 3415 | 393.795 | 351.5 | 872 | 0 | 0 | 0 | 0
09:00 | 3778 | 2169 | 878 | 0 | 36 | 1161.87 | 40 | 3488 | 465.68 | 372 | 874 | 0 | 0 | 0 | 0
09:30 | 3785.5 | 2158 | 901.5 | 0 | 36 | 1211.155 | 40 | 3577 | 522.215 | 396.5 | 868.5 | 0 | 0 | 0.5 | 20
10:00 | 3793 | 2147 | 925 | 0 | 36 | 1260.44 | 40 | 3666 | 578.75 | 421 | 863 | 0 | 0 | 1 | 40
10:30 | 3792.5 | 2087.5 | 925 | 0 | 37 | 1288.82 | 40 | 3785.5 | 596.305 | 423 | 1019.5 | 0 | 0 | 6 | 46
11:00 | 3792 | 2028 | 925 | 0 | 38 | 1317.2 | 40 | 3905 | 613.86 | 425 | 1176 | 0 | 0 | 11 | 52
11:30 | 3796 | 2036.25 | 925.5 | 0 | 39 | 1335.63 | 39.5 | 3971.5 | 633.05 | 436 | 1331.6 | 0 | 0 | 8.5 | 57
12:00 | 3800 | 2044.5 | 926 | 0 | 40 | 1354.06 | 39 | 4038 | 652.24 | 447 | 1487.2 | 0 | 0 | 6 | 62
12:30 | 3783.5 | 2062 | 925.5 | 0 | 40 | 1353.8 | 39.5 | 4028 | 643.605 | 470 | 1628.1 | 0 | 0 | 9 | 58.5
13:00 | 3767 | 2079.5 | 925 | 0 | 40 | 1353.54 | 40 | 4018 | 634.97 | 493 | 1769 | 0 | 0 | 12 | 55
13:30 | 3745.5 | 2084.25 | 925.5 | 0 | 41 | 1348.27 | 40 | 4097 | 586.195 | 457.5 | 1792 | 0 | 0 | 13.5 | 67.5
14:00 | 3724 | 2089 | 926 | 0 | 42 | 1343 | 40 | 4176 | 537.42 | 422 | 1815 | 0 | 0 | 15 | 80
14:30 | 3746 | 2096 | 925.5 | 0 | 43 | 1356 | 40 | 4128 | 484.41 | 427.5 | 1839.1 | 0 | 0 | 16 | 111.5
15:00 | 3768 | 2103 | 925 | 0 | 44 | 1369 | 40 | 4080 | 431.4 | 433 | 1863.2 | 0 | 0 | 17 | 143
15:30 | 3759.5 | 2082 | 925 | 0 | 43 | 1366.5 | 40 | 3959.5 | 338.755 | 440.5 | 1962.7 | 0 | 0 | 16.5 | 161.5
16:00 | 3751 | 2061 | 925 | 0 | 42 | 1364 | 40 | 3839 | 246.11 | 448 | 2062.2 | 0 | 0 | 16 | 180
16:30 | 3630 | 2029 | 925.5 | 0 | 41 | 1329 | 40 | 3613.5 | 180.82 | 502 | 2324.7 | 0 | 0 | 14 | 189.5
17:00 | 3509 | 1997 | 926 | 0 | 40 | 1294 | 40 | 3388 | 115.53 | 556 | 2587.2 | 0 | 0 | 12 | 199
17:30 | 3497 | 1995 | 926 | 0 | 40 | 1280 | 40 | 3301.5 | 71.265 | 644 | 2511.95 | 0 | 0 | 9.5 | 126
18:00 | 3485 | 1993 | 926 | 0 | 40 | 1266 | 40 | 3215 | 27 | 732 | 2436.7 | 0 | 0 | 7 | 53
18:30 | 3638.5 | 2037.5 | 924.5 | 0 | 43 | 1312 | 40 | 3475.5 | 13.5 | 767 | 2665.2 | 0 | 0 | 6 | 66
19:00 | 3792 | 2082 | 923 | 0 | 46 | 1358 | 40 | 3736 | 0 | 802 | 2893.7 | 0 | 0 | 5 | 79
19:30 | 3685 | 2084 | 879 | 0 | 44 | 1362 | 40 | 3802 | 0 | 831 | 3068.7 | 0 | 0 | 14 | 182
20:00 | 3609 | 2061 | 879 | 0 | 44 | 1371 | 40 | 3842 | 0 | 859 | 3033.7 | 0 | 0 | 8 | 243
20:30 | 3649.5 | 2104.5 | 902 | 0 | 43 | 1365.5 | 40 | 3890 | 0 | 852 | 3040.7 | 0 | 0 | 4.5 | 185.5
21:00 | 3690 | 2148 | 925 | 0 | 42 | 1360 | 40 | 3938 | 0 | 845 | 3047.7 | 0 | 0 | 1 | 128
21:30 | 3705.5 | 2118.5 | 925 | 0 | 43 | 1363.5 | 40 | 3969 | 0 | 845 | 3021.7 | 0 | 0 | 0.5 | 123
22:00 | 3721 | 2089 | 925 | 0 | 44 | 1367 | 40 | 4000 | 0 | 845 | 2995.7 | 0 | 0 | 0 | 118
22:30 | 3747 | 2091 | 925 | 0 | 45 | 1371 | 40 | 4009.5 | 0 | 843.5 | 2901.2 | 0 | 0 | 0 | 121.5
23:00 | 3773 | 2093 | 925 | 0 | 46 | 1375 | 40 | 4019 | 0 | 842 | 2806.7 | 0 | 0 | 0 | 125
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 08-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 07:00 | 337 | 18:00 | Payra | 413 | 08:00 | 405 | 00:00
Ashuganj | 397 | 7:00 | 377 | 14:00 | Rahanpur | 401 | 08:00 | 390 | 13:00
Bhulta | 392 | 07:00 | 373 | 12:00 | Rampal | 397 | 07:00 | 376 | 21:00
Bibiana | 392 | 08:00 | 385 | 12:00
BIPTC | 398 | 23:00 | 385 | 16:00
Bogura | 387 | 18:00 | 373 | 13:00
Gopalganj | 394 | 07:00 | 379 | 00:00
Kaliakoir | 374 | 07:00 | 364 | 10:00
Madunaghat | 395 | 08:00 | 386 | 14:00
Meghnaghat | 388 | 06:00 | 376 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 06:00 | 212 | 12:00 | Keranigonj | 222 | 06:00 | 211 | 12:00
AKSML | 235 | 19:30 | 222 | 11:00 | Khulna(S) | 228 | 08:00 | 212 | 22:00
Aminbazar | 226 | 04:00 | 214 | 12:00 | Madunaghat | 235 | 17:00 | 227 | 00:00
Ashuganj | 229 | 07:00 | 221 | 10:00 | Madunaghat-400 | 236 | 18:00 | 227 | 11:00
Ashuganj-400 | 229 | 07:00 | 221 | 10:00 | Maniknagar | 221 | 06:00 | 210 | 12:00
Baghabari | 233 | 06:00 | 224 | 15:00 | Meghnaghat | 230 | 04:00 | 220 | 11:00
Barapukuria | 226 | 17:00 | 216 | 13:00 | Meghnaghat-400 | 225 | 06:00 | 215 | 11:00
Barapukuria-230 | 226 | 17:00 | 216 | 13:00 | Mirsorai | 234 | 20:00 | 220 | 11:00
Barishal | 236 | 20:00 | 226 | 00:00 | Rajshahi | 233 | 06:00 | 219 | 13:00
Bheramara | 234 | 06:00 | 222 | 13:00 | Rampal | 227 | 08:00 | 211 | 23:00
Bhulta | 222 | 06:00 | 210 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 05:00 | 219 | 00:00 | Rampura | 222 | 07:00 | 208 | 12:00
BIPTC | 236 | 07:00 | 221 | 22:00 | Shikalbaha | 233 | 18:00 | 224 | 11:00
Bogura | 235 | 18:00 | 225 | 13:00 | Shyampur | 223 | 07:00 | 212 | 12:00
Bogura-400 | 236 | 18:00 | 226 | 13:00 | Siddhirganj | 223 | 05:00 | 218 | 17:00
Borhanuddin | 241 | 18:00 | 233 | 00:00 | Sirajgonj | 240 | 16:00 | 136 | 01:00
BSRM | 231 | 19:30 | 219 | 10:00 | Sreepur | 226 | 05:00 | 219 | 10:00
Cumilla(N) | 222 | 17:00 | 214 | 10:00 | Tongi | 222 | 07:00 | 208 | 11:00
Faridpur | 230 | 06:00 | 221 | 00:00
Fenchuganj | 227 | 08:00 | 218 | 23:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 223 | 07:00 | 213 | 10:00
Gopalganj | 232 | 07:00 | 224 | 00:00
GPH | 232 | 17:00 | 222 | 11:00
Haripur | 222 | 06:00 | 212 | 12:00
Hasnabad | 222 | 04:00 | 212 | 12:00
Hathazari | 235 | 17:00 | 225 | 00:00
Ishurdi | 235 | 05:00 | 223 | 15:00
Jhenaidah | 229 | 06:00 | 211 | 23:00
Kaliakoir | 228 | 07:00 | 220 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 05:00 | 124 | 12:00 | Madartek | 133 | 06:00 | 122 | 12:00
Agargaon | 132 | 06:00 | 122 | 12:00 | Madunaghat | 135 | 17:00 | 129 | 00:00
Agrabad | 133 | 16:00 | 126 | 14:00 | Magura | 134 | 07:00 | 118 | 22:00
AKS | 130 | 06:00 | 125 | 11:00 | Mahasthangarh | 135 | 17:00 | 127 | 12:00
Aminbazar | 134 | 05:00 | 122 | 12:00 | Manikganj | 131 | 19:30 | 115 | 10:00
Amnura | 140 | 20:00 | 122 | 13:00 | Maniknagar | 130 | 05:00 | 120 | 12:00
Ashuganj | 135 | 06:00 | 132 | 15:00 | Matarbari | 123 | 07:00 | 112 | 00:00
Bagerhat | 130 | 08:00 | 120 | 12:00 | Matuail | 129 | 06:00 | 122 | 12:00
Bajitpur | 130 | 05:00 | 125 | 00:00 | Millgate | 131 | 20:00 | 121 | 10:00
Bakulia | 135 | 17:00 | 128 | 00:00 | Mirpur | 129 | 05:00 | 120 | 12:00
Banani | 133 | 06:00 | 122 | 12:00 | Mirzapur | 133 | 09:00 | 126 | 12:00
Bangabhaban | 130 | 06:00 | 120 | 12:00 | Mithapukur | 132 | 02:00 | 122 | 12:00
Barapukuria | 137 | 17:00 | 128 | 13:00 | MI_Cement | 131 | 18:00 | 122 | 10:00
Barguna | 136 | 21:00 | 129 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 134 | 20:00 | 123 | 00:00 | Mogbazar | 135 | 04:00 | 33 | 08:00
Barishal-230 | 133 | 20:00 | 124 | 00:00 | Mongla | 131 | 20:00 | 119 | 12:00
Baroaulia | 134 | 19:30 | 127 | 11:00 | Motijheel | 130 | 06:00 | 120 | 12:00
Baroirhat | 126 | 17:00 | 117 | 15:00 | Muktagacha | 133 | 09:00 | 124 | 19:00
Bashundhara | 134 | 07:00 | 120 | 10:00 | Munshiganj | 128 | 06:00 | 121 | 12:00
BashundharaCement | 128 | 01:00 | 121 | 12:00 | Muradnagar | 127 | 18:00 | 119 | 10:00
Beanibazar | 134 | 08:00 | 123 | 00:00 | Mymensingh | 135 | 09:00 | 111 | 19:00
Benapole | 129 | 05:00 | 116 | 22:00 | Naogaon | 135 | 18:00 | 126 | 12:00
Bhaluka | 130 | 05:00 | 122 | 12:00 | Narail | 133 | 08:00 | 120 | 22:00
Bhandaria | 130 | 10:00 | 117 | 13:00 | Narinda | 130 | 05:00 | 120 | 12:00
Bhangura | 133 | 17:00 | 126 | 13:00 | Narshingdi | 123 | 07:00 | 116 | 00:00
Bheramara | 138 | 06:00 | 130 | 22:00 | Natore | 134 | 08:00 | 126 | 13:00
Bheramara(GK) | 138 | 07:00 | 130 | 22:00 | Nawabganj | 133 | 07:00 | 124 | 12:00
Bhulta | 123 | 08:00 | 118 | 10:00 | Netrakona | 121 | 06:00 | 111 | 19:00
Bog-Sherpur | 136 | 18:00 | 129 | 12:00 | New | 132 | 20:00 | 122 | 09:00
Bogura | 139 | 17:00 | 131 | 12:00 | Niamatpur | 133 | 07:00 | 127 | 21:00
Bogura-230 | 139 | 17:00 | 131 | 13:00 | Noapara | 135 | 06:00 | 121 | 21:00
Brahmanbaria | 127 | 18:00 | 121 | 00:00 | Pabna | 134 | 05:00 | 127 | 13:00
Cantonment | 132 | 07:00 | 122 | 12:00 | Palashbari | 130 | 17:00 | 120 | 13:00
Chandina | 129 | 18:00 | 122 | 12:00 | Panchagarh | 138 | 16:00 | 119 | 12:00
Chandpur | 132 | 17:00 | 120 | 00:00 | Patuakhali | 137 | 21:00 | 129 | 00:00
Chandraghona | 134 | 17:00 | 128 | 13:00 | Payra | 135 | 06:00 | 133 | 00:00
Chapai | 130 | 03:00 | 123 | 21:00 | PHP | 127 | 17:00 | 116 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 20:00 | 122 | 10:00 | Postogola | 131 | 06:00 | 124 | 12:00
Chauddagram | 125 | 17:00 | 115 | 22:00 | Purbachal | 133 | 05:00 | 122 | 12:00
Chhatak | 131 | 06:00 | 120 | 00:00 | Purbasadipur | 130 | 16:00 | 115 | 13:00
Chowmuhani | 125 | 17:00 | 110 | 00:00 | Rahanpur | 133 | 05:00 | 129 | 13:00
Chuadanga | 134 | 07:00 | 115 | 22:00 | Rahanpur-400 | 133 | 05:00 | 129 | 13:00
Coxsbazar | 121 | 18:00 | 112 | 00:00 | Rahim | 128 | 05:00 | 123 | 10:00
Cumilla(N) | 128 | 17:00 | 122 | 10:00 | Rajbari | 133 | 07:00 | 126 | 00:00
Cumilla(S) | 133 | 03:00 | 120 | 12:00 | Rajendrapur | 130 | 05:00 | 122 | 12:00
Daudkandi | 125 | 18:00 | 117 | 12:00 | Rajshahi | 134 | 05:00 | 126 | 13:00
Dhaka | 133 | 05:00 | 124 | 12:00 | Rajshahi-230 | 135 | 06:00 | 115 | 22:00
Dhamrai | 137 | 15:00 | 127 | 10:00 | Ramganj | 128 | 17:00 | 112 | 00:00
Dhanmondi | 133 | 04:00 | 124 | 12:00 | Rampur | 133 | 17:00 | 125 | 13:00
Dohazari | 132 | 17:00 | 122 | 14:00 | Rampura | 133 | 05:00 | 123 | 12:00
Faridpur | 135 | 08:00 | 128 | 00:00 | Rangamati | 133 | 17:00 | 127 | 14:00
Fatullah | 129 | 05:00 | 122 | 12:00 | Rangpur | 131 | 17:00 | 120 | 13:00
Fenchuganj | 135 | 07:00 | 130 | 00:00 | Ruppur | 138 | 07:00 | 130 | 22:00
Feni | 125 | 18:00 | 115 | 17:00 | Saidpur | 132 | 02:00 | 120 | 12:00
Ghatail | 129 | 09:00 | 121 | 12:00 | Satkhira | 130 | 07:00 | 116 | 22:00
Ghorashal | 136 | 01:00 | 129 | 15:00 | Satmasjid | 131 | 06:00 | 113 | 14:00
Goalpara | 135 | 09:00 | 124 | 22:00 | Savar | 130 | 06:00 | 121 | 12:00
Gollamari | 135 | 08:00 | 126 | 13:00 | SevenRings | 135 | 07:00 | 132 | 05:00
Gopalganj | 133 | 06:00 | 126 | 00:00 | ShahCement | 129 | 20:00 | 122 | 10:00
Gopalganj-400 | 135 | 07:00 | 129 | 00:00 | Shahjadpur | 136 | 05:00 | 131 | 13:00
Gulshan | 134 | 07:00 | 123 | 12:00 | Shahjibazar | 129 | 07:00 | 123 | 00:00
Halishahar | 131 | 06:00 | 125 | 12:00 | Shahmirpur | 136 | 17:00 | 128 | 13:00
Haripur | 129 | 06:00 | 122 | 12:00 | Shariatpur | 133 | 19:30 | 124 | 00:00
HaripurSBU | 128 | 04:00 | 123 | 10:00 | Sherpur | 131 | 19:30 | 122 | 01:00
Hasnabad | 130 | 03:00 | 125 | 11:00 | Shikalbaha | 125 | 17:00 | 117 | 11:00
Hathazari | 138 | 17:00 | 129 | 00:00 | Shikalbaha-230 | 136 | 18:00 | 129 | 00:00
Ishurdi | 139 | 09:00 | 131 | 22:00 | Shitalakhya | 131 | 18:00 | 122 | 10:00
Jaldhaka | 130 | 17:00 | 118 | 13:00 | Sholosohor | 134 | 17:00 | 128 | 00:00
Jamalpur | 138 | 09:00 | 126 | 01:00 | Shyampur | 128 | 01:00 | 125 | 00:00
Jashore | 131 | 08:00 | 118 | 22:00 | Shyampur-230 | 129 | 06:00 | 122 | 12:00
Jhenaidah | 135 | 08:00 | 121 | 22:00 | Siddhirganj | 129 | 05:00 | 123 | 11:00
Jhenaidah-230 | 135 | 07:00 | 122 | 22:00 | Sirajganj | 132 | 01:00 | 126 | 15:00
Joydebpur | 136 | 08:00 | 123 | 15:00 | Sonargaon | 127 | 04:00 | 120 | 10:00
Joypurhat | 130 | 05:00 | 121 | 22:00 | Sreemongol | 130 | 06:00 | 124 | 00:00
Juldah | 136 | 17:00 | 128 | 12:00 | Sreepur | 131 | 05:00 | 126 | 10:00
Kabirpur | 136 | 09:00 | 117 | 10:00 | Srinagar | 133 | 05:00 | 124 | 13:00
Kachua | 129 | 17:00 | 119 | 00:00 | SSM | 136 | 18:00 | 130 | 02:00
Kaliakoir | 136 | 02:00 | 132 | 12:00 | Sunamganj | 131 | 06:00 | 119 | 23:00
Kallyanpur | 130 | 05:00 | 122 | 12:00 | Sylhet | 134 | 07:00 | 125 | 00:00
Kalurghat | 134 | 17:00 | 129 | 11:00 | Sylhet-132 | 132 | 07:00 | 126 | 00:00
Kamrangirchar | 133 | 06:00 | 125 | 10:00 | Tangail | 128 | 09:00 | 121 | 18:30
Kaptai | 135 | 8:00 | 130 | 15:00 | Thakurgaon | 138 | 16:00 | 120 | 12:00
Kasba | 127 | 18:00 | 119 | 10:00 | TK | 135 | 19:00 | 129 | 10:00
Kazla | 129 | 06:00 | 120 | 13:00 | Tongi | 133 | 19:30 | 126 | 09:00
Keranigonj | 133 | 06:00 | 125 | 12:00 | Ullahpara | 133 | 03:00 | 127 | 13:00
Khagrachori | 132 | 17:00 | 126 | 15:00 | Ullon | 133 | 05:00 | 123 | 12:00
Khulna | 133 | 08:00 | 123 | 22:00 | Uttara | 129 | 06:00 | 120 | 12:00
Khulna(S) | 135 | 08:00 | 125 | 22:00 | UttaraNew | 130 | 05:00 | 120 | 12:00
Khulshi | 132 | 17:00 | 125 | 11:00 | Zigatola | 133 | 06:00 | 124 | 12:00
Kishoreganj | 128 | 07:00 | 120 | 14:00
Kodda | 136 | 09:00 | 122 | 15:00
KSRM | 135 | 18:00 | 127 | 12:00
Kulaura | 134 | 07:00 | 129 | 00:00
Kurigram | 131 | 17:00 | 118 | 12:00
Kushtia | 135 | 06:00 | 126 | 22:00
Lalbag | 133 | 07:00 | 123 | 12:00
Lalmonirhat | 129 | 00:00 | 120 | 12:00
Madanganj | 128 | 01:00 | 121 | 12:00
Madaripur | 133 | 20:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division