## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 10-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-05-2025 | during | 10-05-2025 | during | 10-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 397 | 400 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 350 | 450 | 450 | 340 | 340 | Allocation limit by Titas Gas
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 286 | 282 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 140 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 251 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 98 | 16 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 1 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 80 | 125 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 1 | 23 | 30 | 30 | 30 | 30 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 20 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 278 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 95 | 128 | 135 | 135 | 135 | 135 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 50 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 80 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 34 | 0 | 34 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 300 | 584 | 584 | 300 | 300 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 280 | 350 | 583 | 583 | 300 | 300 | Allocation limit by Titas Gas
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2341 | 3241 | 5267.9 | 5319.9 | 3335.62 | 3395.62
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 139 | 146 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 85 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 73 | 72 | 72 | 56 | 80 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 51 | 85 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 61 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 0 | 26 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 70 | 70 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.45 | 0 | 4.45 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 5 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 1 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 94 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 144 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1055 | 1226 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 3 | 0 | 8 | 12 | 8 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 501 | 450 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2010 | 2655.5 | 3418.17 | 3419.72 | 3364.17 | 3389.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 196 | 185 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 345 | 345 | 345 | 345 | 345 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 34 | 46.94 | 46.94 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 47 | 44 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 155 | 163 | 195 | 195 | 195 | 195 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 122 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 30 | 30 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 90 | 183 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 42 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 1 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 19 | 20 | 20.83 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 93 | 93 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1299 | 1612.2 | 2467.32 | 2405.99 | 2249.55 | 2213.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 09-05-2025 | during | 10-05-2025 | during | 10-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 22 | 157.5 | 157.5 | 22 | 22 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 119 | 152 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 64 | 102 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47.66 | 0 | 49.9 | 0 | 49.9 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 43.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 244.66 | 331.5 | 601 | 549 | 333.5 | 353.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 37 | 36 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 29 | 30 | 30 | 30 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 82 | 12 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 80 | 83 | 83 | 83 | 83 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 172 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 340 | 290 | 385 | 385 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 0 | 320 | 320 | 0 | 0 | Machine tripped
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1419 | 989 | 1603 | 1603 | 1191 | 1191
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 925 | 920 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 31 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 43 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 170 | 213 | 410 | 410 | 212 | 212 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 51 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 96.78 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 424 | 618 | 617.1 | 617.1 | 618 | 618 | U#1 Under Shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1615.78 | 1876 | 2995.1 | 2897.1 | 2693.01 | 2595.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 451 | 401 | 620 | 620 | 620 | 620 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 115 | 125 | 125 | 113 | 113 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1010 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.69 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 2055.69 | 2298 | 2787.12 | 2786.12 | 2775.12 | 2774.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 48 | 47 | 47 | 42 | 42 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 25 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 179 | 191 | 214 | 214 | 225 | 225 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 191 | 220 | 220 | 170 | 170 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 15 | 15 | 15 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 93 | 93 | 100 | 100 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.58 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1172 | 1365.69 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 54.64 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 111 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 2106.22 | 2645.69 | 3086.73 | 2920.53 | 2794.94 | 2628.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 52 | 50 | 55 | 55 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 159 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 27 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 179 | 0 | 175.54 | 0 | 175.54 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 468.6 | 437 | 679.14 | 467 | 679.14 | 467
System Total |  |  |  |  | 27566.2 | 28624.082 | 13559.95 | 16085.89 | 22905.48 | 22368.36 | 19416.05 | 19008.26
Forecast Scenario (10-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15800 |  | 0 |  | 15800
|  |  |  | 1:00 | 15450 |  | 0 |  | 15450
|  |  |  | 2:00 | 14920 |  | 0 |  | 14920
|  |  |  | 3:00 | 14510 |  | 0 |  | 14510
|  |  |  | 4:00 | 14170 |  | 0 |  | 14170
|  |  |  | 5:00 | 14040 |  | 0 |  | 14040
|  |  |  | 6:00 | 13620 |  | 0 |  | 13620
|  |  |  | 7:00 | 13420 |  | 0 |  | 13420
|  |  |  | 8:00 | 13280 |  | 0 |  | 13280
|  |  |  | 9:00 | 13120 |  | 0 |  | 13120
|  |  |  | 10:00 | 13040 |  | 0 |  | 13040
|  |  |  | 11:00 | 13220 |  | 0 |  | 13220
|  |  |  | 12:00 | 13800 |  | 0 |  | 13800
|  |  |  | 13:00 | 14260 |  | 0 |  | 14260
|  |  |  | 14:00 | 14340 |  | 0 |  | 14340
|  |  |  | 15:00 | 14750 |  | 0 |  | 14750
|  |  |  | 16:00 | 15060 |  | 0 |  | 15060
|  |  |  | 17:00 | 15159 |  | 0 |  | 15159
|  |  |  | 18:00 | 14600 |  | 0 |  | 14600
|  |  |  | 18:30 | 15000 |  | 0 |  | 15000
|  |  |  | 19:00 | 15580 |  | 0 |  | 15580
|  |  |  | 19:30 | 16300 |  | 0 |  | 16300
|  |  |  | 20:00 | 16380 |  | 0 |  | 16380
|  |  |  | 21:00 | 16500 |  | 0 |  | 16500
|  |  |  | 22:00 | 16450 |  | 0 |  | 16450
|  |  |  | 23:00 | 15970 |  | 0 |  | 15970
Probable Maximum Temperature: |  |  | 37.90°C
Probable Maximum Demand at Day Peak: |  |  | 13800.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 351.439 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:30 hrs on 10-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 09-05-2025 | [28 empty] | Date: | 09-05-2025 | [28 empty] | Date: | 09-05-2025 | [28 empty] | Date: | 09-05-2025 | [28 empty] | Date: | 09-05-2025 | [16 empty] | Date: | 09-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [16 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 33 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 17 | 131 | 143 | 294 | 40 | 35 | 162 | 0 | 50 | 300 | 284 | 300 | 0 | 35 | 0 | 253 | 0 | 0 | 0 | 160 | 18 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 102 | 70 | 0 | 89 | 100 | 0 | 40 | 0 | 30 | 575 | 35 | 0 | 0 | 25 | 5 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 8 | 0 | 354 | 345 | 49 | 188 | 36 | 93 | 70 | 182 | 12 | 20 | 114 | 46 | 52.2 | 0 | 31 | 315 | 320 | 299 | 37 | 30 | 0 | 89 | 8 | 0 | 82 | 28 | 0 | 18 | 172 | 35 | 102 | 147 | 0 | 0 | 0 | 8 | 8961.2 | 925 | 155 | 0 | 31 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 1371 | 0 | 49 | 0 | 113 | 16 | 93 | 113 | 36 | 43 | 0 | 0 | 0 | 171 | 0 | 166 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 159 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 5 | 105 | 220 | 0 | 453 | 1244 | 100 | 6807 | 15768.2 | 78.66
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 47 | 17 | 131 | 110 | 294 | 0 | 35 | 162 | 0 | 35 | 300 | 278 | 300 | 0 | 35 | 0 | 250 | 0 | 0 | 0 | 160 | 18 | 17 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 98 | 70 | 0 | 76 | 100 | 0 | 40 | 0 | 30 | 575 | 0 | 0 | 0 | 25.5 | 9 | 145 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 8 | 0 | 354 | 345 | 51 | 191 | 36 | 93 | 70 | 161 | 9 | 20 | 114 | 44 | 52.2 | 0 | 32 | 300 | 320 | 303 | 38 | 30 | 0 | 79 | 8 | 0 | 82 | 28 | 0 | 18 | 172 | 17 | 46 | 92 | 0 | 0 | 0 | 11 | 8590.7 | 926 | 150 | 0 | 31 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 1358 | 0 | 49 | 0 | 113 | 15 | 93 | 35 | 35 | 16 | 0 | 0 | 0 | 170 | 0 | 163 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 96 | 307 | 7 | 105 | 180 | 0 | 452 | 1244 | 119 | 6663 | 15253.7 | 78.65
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 54 | 17 | 112 | 96 | 145 | 0 | 35 | 162 | 0 | 16 | 300 | 293 | 300 | 0 | 35 | 0 | 255 | 0 | 0 | 0 | 160 | 18 | 18 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 50 | 24 | 0 | 76 | 100 | 0 | 40 | 0 | 22 | 576 | 0 | 0 | 0 | 0 | 2 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 8 | 0 | 354 | 345 | 52 | 203 | 36 | 94 | 70 | 166 | 9 | 20 | 114 | 40 | 16 | 0 | 32 | 305 | 320 | 300 | 38 | 30 | 0 | 80 | 8 | 0 | 82 | 28 | 0 | 18 | 172 | 17 | 46 | 92 | 0 | 0 | 0 | 12 | 8252 | 926 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 1367 | 0 | 0 | 0 | 113 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 161 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 6 | 105 | 180 | 0 | 453 | 1244 | 150 | 6358 | 14610 | 78.64
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 17 | 112 | 96 | 45 | 0 | 35 | 162 | 0 | 16 | 300 | 297 | 300 | 0 | 35 | 0 | 278 | 0 | 0 | 0 | 160 | 18.5 | 18 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 76 | 76 | 0 | 40 | 0 | 29 | 577 | 0 | 0 | 0 | 0 | 6 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 8 | 0 | 354 | 345 | 52 | 203 | 36 | 93 | 80 | 165 | 9 | 20 | 114 | 40 | 16 | 0 | 32 | 300 | 320 | 312 | 38 | 30 | 0 | 82 | 8 | 0 | 82 | 28 | 0 | 18 | 173 | 0 | 46 | 92 | 0 | 0 | 0 | 12 | 8127.5 | 925 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1365 | 0 | 0 | 0 | 113 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 162 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 51 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 105 | 180 | 0 | 453 | 1244 | 54 | 6067 | 14194.5 | 78.63
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 46 | 17 | 112 | 96 | 15 | 0 | 0 | 144 | 0 | 16 | 300 | 294 | 300 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 160 | 18.5 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 76 | 76 | 0 | 40 | 0 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 132 | 8 | 0 | 353 | 345 | 52 | 216 | 36 | 93 | 81 | 174 | 9 | 20 | 114 | 38 | 16 | 0 | 32 | 315 | 320 | 304 | 38 | 30 | 0 | 83 | 8 | 0 | 82 | 28 | 0 | 18 | 172 | 0 | 46 | 92 | 0 | 0 | 0 | 12 | 8022.5 | 926 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1367 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 161 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 159 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 109 | 180 | 0 | 453 | 1244 | 17 | 5865 | 13887.5 | 78.62
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 112 | 96 | 0 | 0 | 0 | 108 | 0 | 0 | 300 | 305 | 300 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 35 | 19 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 76 | 60 | 0 | 40 | 0 | 33 | 575 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 8 | 0 | 354 | 345 | 54 | 215 | 36 | 93 | 80 | 120 | 9 | 20 | 103 | 32 | 0 | 0 | 32 | 300 | 320 | 306 | 38 | 30 | 0 | 81 | 8 | 0 | 82 | 28 | 0 | 18 | 172 | 0 | 46 | 92 | 0 | 0 | 0 | 12 | 7687 | 926 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1375 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 162 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 162 | 50 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 111 | 220 | 0 | 452 | 1244 | 0 | 5785 | 13472 | 78.61
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 112 | 96 | 0 | 0 | 0 | 72 | 0 | 0 | 300 | 273 | 250 | 0 | 0 | 0 | 255 | 0 | 0 | 2 | 35 | 19.5 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 451 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 1010 | 0 | 51 | 123 | 8 | 0 | 300 | 300 | 51 | 180 | 36 | 93 | 80 | 106 | 9 | 20 | 60 | 36 | 0 | 4 | 32 | 285 | 320 | 290 | 38 | 30 | 0 | 83 | 8 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 46 | 92 | 0 | 0 | 2.69 | 12 | 6756.19 | 926 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1260 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.71 | 150 | 0 | 168 | 0 | 0 | 0 | 280 | 0 | 0.23 | 0 | 162 | 50 | 0 | 1 | 0 | 0 | 0 | 0.3 | 9 | 0.02 | 0 | 200 | 6 | 90 | 220 | 0 | 452 | 1080 | 0 | 5246.26 | 12002.45 | 78.6
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 17 | 112 | 96 | 0 | 0 | 0 | 72 | 0 | 0 | 300 | 304 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 35 | 16 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 1000 | 0 | 51 | 130 | 8 | 0 | 347 | 300 | 49 | 206 | 36 | 94 | 80 | 108 | 9 | 20 | 52 | 34 | 0 | 17 | 32 | 310 | 320 | 303 | 38 | 30 | 0 | 85 | 8 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 65 | 120 | 0 | 0 | 8.52 | 12 | 6696.52 | 926 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 1213 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11.17 | 150 | 0 | 176 | 0 | 0 | 0 | 350 | 0 | 0.87 | 0 | 162 | 50 | 0 | 6 | 0 | 0 | 0 | 1.2 | 40 | 0.11 | 0 | 200 | 6 | 100 | 220 | 0 | 454 | 1050 | 0 | 5359.35 | 12055.87 | 78.59
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 107 | 96 | 0 | 0 | 0 | 72 | 0 | 0 | 300 | 278 | 250 | 0 | 0 | 0 | 0 | 99 | 0 | 15 | 17 | 19 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 36 | 3 | 40 | 0 | 0 | 403 | 0 | 0 | 22 | 0 | 0 | 147 | 0 | 0 | 0 | 1000 | 0 | 51 | 128 | 8 | 0 | 354 | 300 | 49 | 181 | 37 | 92 | 80 | 107 | 9 | 20 | 52 | 32 | 0 | 21 | 32 | 295 | 320 | 290 | 38 | 30 | 0 | 80 | 8 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 66 | 122 | 0 | 1 | 22.43 | 12 | 6834.43 | 877 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 73 | 0 | 1119 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 23.47 | 150 | 0 | 175 | 0 | 0 | 0 | 350 | 0 | 1.89 | 0 | 162 | 50 | 0 | 14 | 0 | 0 | 0 | 4.1 | 80 | 0.26 | 0 | 200 | 6 | 90 | 220 | 0 | 451 | 1030 | 0 | 5378.72 | 12213.15 | 78.58
09:00 | 0 | 34 | 9 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 17 | 95 | 96 | 0 | 0 | 0 | 54 | 0 | 0 | 350 | 300 | 250 | 0 | 0 | 0 | 0 | 135 | 0 | 23 | 17 | 19 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 75 | 3 | 40 | 0 | 0 | 367 | 0 | 0 | 45 | 0 | 0 | 142 | 0 | 0 | 0 | 952 | 15 | 51 | 125 | 48 | 0 | 167 | 300 | 49 | 204 | 36 | 93 | 80 | 106 | 9 | 19 | 52 | 30 | 0 | 50 | 32 | 300 | 320 | 345 | 38 | 30 | 0 | 85 | 8 | 0 | 80 | 30 | 0 | 18 | 173 | 0 | 66 | 121 | 0 | 1 | 34.58 | 12 | 6934.58 | 877 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 131 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 35.98 | 150 | 0 | 174 | 0 | 0 | 0 | 350 | 0 | 3.08 | 0 | 166 | 51 | 0 | 23 | 0 | 0 | 0 | 5.1 | 120 | 0.11 | 0 | 200 | 7 | 100 | 220 | 0 | 453 | 900 | 0 | 5288.27 | 12222.85 | 78.57
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 17 | 95 | 31 | 0 | 0 | 17 | 54 | 0 | 0 | 450 | 288 | 350 | 0 | 0 | 0 | 0 | 138 | 0 | 27 | 17 | 19 | 20 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 88 | 4 | 40 | 0 | 0 | 367 | 0 | 0 | 50 | 0 | 0 | 142 | 0 | 0 | 0 | 900 | 17 | 51 | 30 | 147 | 0 | 0 | 345 | 50 | 201 | 35 | 93 | 80 | 111 | 9 | 19 | 17 | 36 | 0 | 61 | 32 | 310 | 320 | 325 | 38 | 30 | 0 | 91 | 8 | 0 | 80 | 30 | 0 | 18 | 173 | 0 | 65 | 121 | 0 | 2 | 43.72 | 12 | 6975.72 | 924 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 245 | 0 | 1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 45.79 | 169 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 3.86 | 0 | 166 | 50 | 0 | 28 | 0 | 0 | 0 | 6.7 | 160 | 0.63 | 0 | 274 | 5 | 100 | 180 | 0 | 453 | 898 | 0 | 5707.98 | 12683.7 | 78.56
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 17 | 95 | 31 | 0 | 0 | 17 | 54 | 0 | 0 | 450 | 286 | 320 | 0 | 0 | 0 | 0 | 138 | 0 | 30 | 17 | 17 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 4 | 17 | 0 | 0 | 61 | 88 | 4 | 40 | 0 | 0 | 455 | 0 | 0 | 50 | 0 | 0 | 141 | 0 | 0 | 0 | 1000 | 17 | 51 | 10 | 157 | 0 | 0 | 345 | 50 | 188 | 31 | 80 | 90 | 97 | 9 | 19 | 17 | 38 | 0 | 66 | 31 | 315 | 320 | 340 | 38 | 30 | 0 | 83 | 8 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 65 | 120 | 0 | 2 | 46.16 | 12 | 7080.16 | 924 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.91 | 342 | 0 | 1060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 53.05 | 179 | 0 | 173 | 0 | 0 | 0 | 414 | 0 | 4.51 | 0 | 170 | 51 | 0 | 33 | 0 | 0 | 0 | 7.5 | 180 | 0.67 | 0 | 307 | 7 | 90 | 180 | 0 | 451 | 960 | 0 | 5955.64 | 13035.8 | 78.55
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 1 | 17 | 95 | 80 | 15 | 0 | 35 | 80 | 0 | 0 | 450 | 286 | 280 | 0 | 17 | 0 | 0 | 140 | 0 | 31 | 52 | 1 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 3 | 51 | 0 | 0 | 61 | 88 | 4 | 40 | 0 | 0 | 501 | 0 | 0 | 50 | 0 | 0 | 139 | 0 | 0 | 0 | 1055 | 18 | 51 | 20 | 155 | 0 | 0 | 340 | 47 | 196 | 32 | 93 | 90 | 90 | 8 | 19 | 17 | 42 | 1 | 68 | 30 | 300 | 320 | 340 | 37 | 29 | 0 | 82 | 8 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 64 | 119 | 0 | 2 | 47.66 | 12 | 7313.66 | 925 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.78 | 424 | 0 | 1172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 0 | 54.64 | 179 | 0 | 171 | 0 | 0 | 0 | 414 | 0 | 4.58 | 0 | 169 | 52 | 27 | 34 | 0 | 0 | 0 | 7.6 | 179 | 0.69 | 0 | 307 | 7 | 100 | 180 | 0 | 451 | 1010 | 0 | 6246.29 | 13559.95 | 78.54
13:00 | 16 | 34 | 15 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 17 | 17 | 100 | 93 | 95 | 7 | 35 | 60 | 0 | 14 | 400 | 278 | 280 | 0 | 35 | 0 | 0 | 189 | 0 | 0 | 52 | 19 | 20 | 0 | 300 | 0 | 0 | 0 | 0 | 14 | 50 | 0 | 0 | 88 | 88 | 4 | 40 | 0 | 0 | 550 | 0 | 0 | 50 | 0 | 0 | 139 | 0 | 0 | 0 | 1100 | 18 | 51 | 55 | 153 | 0 | 0 | 340 | 47 | 190 | 32 | 93 | 90 | 93 | 8 | 19 | 52 | 44 | 16 | 64 | 30 | 310 | 320 | 300 | 37 | 29 | 0 | 90 | 8 | 0 | 80 | 28 | 0 | 16 | 174 | 19 | 64 | 119 | 0 | 2 | 46.24 | 12 | 7642.24 | 925 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.82 | 430 | 0 | 1269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 53.14 | 176 | 0 | 170 | 0 | 0 | 0 | 300 | 0 | 4.7 | 0 | 168 | 51 | 35 | 28 | 0 | 0 | 0 | 7.3 | 182 | 0.6 | 0 | 258 | 10 | 90 | 180 | 0 | 451 | 1100 | 0 | 6256.56 | 13898.8 | 78.53
14:00 | 16 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 35 | 17 | 121 | 93 | 45 | 15 | 35 | 162 | 0 | 20 | 350 | 286 | 280 | 0 | 35 | 0 | 0 | 181 | 0 | 26 | 52 | 21 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 18 | 48 | 0 | 0 | 88 | 88 | 4 | 40 | 0 | 0 | 452 | 0 | 0 | 50 | 0 | 0 | 139 | 0 | 0 | 0 | 1005 | 16 | 51 | 50 | 155 | 0 | 0 | 335 | 45 | 205 | 32 | 93 | 90 | 114 | 26 | 19 | 17 | 44 | 8 | 57 | 31 | 310 | 320 | 369 | 35 | 29 | 0 | 87 | 8 | 0 | 79 | 30 | 0 | 16 | 172 | 35 | 64 | 113 | 0 | 2 | 38.36 | 12 | 7567.36 | 925 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.09 | 463 | 0 | 1225.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 48.08 | 140 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 4.16 | 0 | 163 | 50 | 35 | 29 | 0 | 0 | 0 | 4.5 | 159 | 0.19 | 0 | 200 | 11 | 100 | 220 | 0 | 452 | 1000 | 0 | 6069.51 | 13636.87 | 78.52
15:00 | 16 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 35 | 17 | 120 | 75 | 45 | 15 | 35 | 144 | 0 | 27 | 300 | 291 | 450 | 0 | 35 | 0 | 20 | 132 | 0 | 20 | 52 | 21 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 20 | 48 | 0 | 0 | 83 | 88 | 3 | 40 | 0 | 10 | 500 | 0 | 0 | 50 | 0 | 0 | 138 | 0 | 0 | 0 | 1105 | 12 | 51 | 50 | 152 | 0 | 0 | 335 | 45 | 202 | 31 | 93 | 90 | 135 | 27 | 19 | 52 | 44 | 10 | 44 | 28 | 320 | 320 | 324 | 35 | 30 | 0 | 99 | 8 | 0 | 79 | 28 | 0 | 16 | 171 | 0 | 64 | 113 | 0 | 2 | 32.3 | 12 | 7744.3 | 924 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 458 | 0 | 1216.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 35.98 | 177 | 0 | 161 | 0 | 0 | 0 | 414 | 0 | 3.1 | 0 | 163 | 50 | 35 | 23 | 0 | 0 | 0 | 3.6 | 112 | 0.46 | 0 | 280 | 10 | 115 | 220 | 0 | 451 | 1061 | 0 | 6244.82 | 13989.12 | 78.51
16:00 | 32 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 386 | 0 | 0 | 35 | 17 | 119 | 75 | 45 | 30 | 35 | 162 | 0 | 33 | 300 | 240 | 505 | 0 | 35 | 0 | 32 | 86 | 0 | 13 | 52 | 21 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 17 | 48 | 0 | 0 | 75 | 100 | 1 | 40 | 0 | 10 | 370 | 0 | 0 | 50 | 0 | 0 | 138 | 0 | 0 | 0 | 1100 | 7 | 51 | 50 | 178 | 0 | 0 | 340 | 43 | 184 | 31 | 77 | 90 | 127 | 27 | 19 | 52 | 42 | 52.2 | 22 | 22 | 310 | 0 | 290 | 35 | 29 | 0 | 40 | 8 | 0 | 79 | 28 | 0 | 16 | 169 | 0 | 63 | 108 | 0 | 1 | 22.44 | 12 | 7172.64 | 924 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.69 | 567 | 0 | 1346.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 21.49 | 184 | 0 | 170 | 0 | 0 | 0 | 350 | 0 | 2.01 | 0 | 166 | 51 | 35 | 16 | 0 | 0 | 0 | 3.5 | 83 | 0.19 | 0 | 307 | 11 | 105 | 220 | 0 | 450 | 1135 | 0 | 6403.79 | 13576.43 | 78.5
17:00 | 50 | 17 | 15 | 0 | 0 | 0 | 0 | 0 | 383 | 0 | 0 | 35 | 17 | 101 | 75 | 45 | 55 | 35 | 162 | 0 | 44 | 300 | 240 | 505 | 0 | 35 | 0 | 225 | 0 | 0 | 6 | 66 | 21.5 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 13 | 50 | 17 | 0 | 75 | 100 | 1 | 40 | 0 | 18 | 372 | 0 | 0 | 50 | 0 | 0 | 142 | 0 | 0 | 0 | 1000 | 3 | 51 | 50 | 105 | 0 | 0 | 335 | 42 | 205 | 31 | 93 | 90 | 127 | 36 | 19 | 52 | 38 | 52.2 | 7 | 22 | 300 | 0 | 323 | 35 | 28 | 0 | 13 | 8 | 0 | 76 | 30 | 0 | 16 | 170 | 34 | 64 | 110 | 0 | 0 | 9.93 | 12 | 7216.63 | 924 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.21 | 543 | 0 | 1367.13 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 21 | 0 | 9.55 | 185 | 0 | 178 | 0 | 0 | 0 | 380 | 0 | 0.82 | 0 | 168 | 51 | 35 | 7 | 0 | 0 | 0 | 1.7 | 37 | 0.04 | 0 | 200 | 11 | 115 | 220 | 0 | 399 | 1040 | 0 | 6121.45 | 13338.08 | 78.49
18:00 | 65 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 35 | 17 | 98 | 76 | 45 | 55 | 35 | 162 | 0 | 50 | 300 | 240 | 300 | 0 | 35 | 0 | 225 | 0 | 0 | 1 | 90 | 21.5 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 2 | 51 | 48 | 0 | 88 | 100 | 0 | 40 | 0 | 18 | 330 | 0 | 0 | 50 | 0 | 0 | 145 | 0 | 0 | 0 | 1000 | 0 | 51 | 50 | 105 | 0 | 0 | 340 | 43 | 188 | 32 | 94 | 90 | 120 | 37 | 19 | 52 | 38 | 52.2 | 1 | 22 | 305 | 0 | 310 | 35 | 30 | 0 | 16 | 8 | 0 | 32 | 30 | 0 | 16 | 171 | 52 | 91 | 139 | 0 | 0 | 1.76 | 12 | 7051.46 | 925 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 549 | 0 | 1361.12 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 4 | 0 | 1.74 | 140 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0.15 | 0 | 167 | 51 | 35 | 1 | 0 | 0 | 0 | 0.3 | 7 | 0 | 0 | 200 | 11 | 105 | 220 | 0 | 401 | 1040 | 0 | 5898.31 | 12949.77 | 78.48
19:00 | 98 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 42 | 17 | 110 | 140 | 145 | 55 | 35 | 162 | 0 | 50 | 350 | 295 | 350 | 0 | 35 | 0 | 279 | 0 | 0 | 0 | 125 | 22 | 20 | 0 | 300 | 4 | 0 | 0 | 0 | 6 | 85 | 76 | 0 | 88 | 100 | 0 | 40 | 2 | 19 | 365 | 54 | 0 | 50 | 4 | 4 | 144 | 0 | 0 | 0 | 1225 | 0 | 51 | 67 | 167 | 0 | 0 | 340 | 43 | 206 | 32 | 93 | 90 | 146 | 36 | 19 | 88 | 46 | 52.2 | 0 | 22 | 320 | 0 | 325 | 35 | 30 | 0 | 14 | 8 | 0 | 80 | 30 | 0 | 16 | 170 | 52.5 | 92 | 147 | 0 | 0 | 0 | 12 | 8181.7 | 908 | 203 | 0 | 15 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 0 | 1369.32 | 0 | 41 | 0 | 32 | 5 | 45 | 30 | 15 | 0 | 0 | 7 | 0 | 160 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 51 | 112 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 401 | 1130 | 0 | 6657.32 | 14839.02 | 78.47
19:30 | 98 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 54 | 17 | 120 | 140 | 220 | 55 | 35 | 162 | 0 | 50 | 350 | 300 | 350 | 0 | 35 | 0 | 268 | 0 | 0 | 0 | 160 | 22 | 20 | 0 | 300 | 17 | 0 | 0 | 0 | 8 | 85 | 73 | 0 | 88 | 100 | 0 | 40 | 24 | 27 | 402 | 108 | 0 | 50 | 10 | 51 | 145 | 0 | 0 | 0 | 1226 | 0 | 51 | 105 | 167 | 0 | 0 | 345 | 43 | 204 | 32 | 93 | 90 | 177 | 36 | 19 | 114 | 46 | 52.2 | 0 | 22 | 320 | 0 | 322 | 36 | 30 | 0 | 14 | 8 | 0 | 80 | 30 | 0 | 16 | 170 | 54.5 | 92 | 149 | 10 | 0 | 0 | 12 | 8610.7 | 887 | 205 | 0 | 36 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 8 | 1362.39 | 0 | 48 | 0 | 100 | 5 | 80 | 108 | 28 | 0 | 0 | 15 | 0 | 190 | 0 | 190 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 138 | 50 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 402 | 1244 | 0 | 7024.39 | 15635.09
20:00 | 98 | 52 | 15 | 0 | 0 | 0 | 0 | 0 | 392 | 0 | 0 | 54 | 17 | 123 | 124 | 274 | 55 | 35 | 162 | 0 | 50 | 350 | 300 | 350 | 0 | 35 | 0 | 265 | 0 | 0 | 0 | 160 | 23 | 20 | 0 | 300 | 17 | 0 | 0 | 0 | 7 | 85 | 73 | 0 | 88 | 100 | 0 | 40 | 56 | 27 | 450 | 108 | 0 | 50 | 16 | 55 | 145 | 0 | 0 | 0 | 1224 | 0 | 51 | 102 | 165 | 0 | 0 | 345 | 43 | 195 | 33 | 94 | 90 | 169 | 37 | 19 | 114 | 48 | 52.2 | 0 | 22 | 310 | 0 | 322 | 36 | 30 | 0 | 10 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 52.5 | 92 | 150 | 22 | 0 | 0 | 12 | 8716.7 | 887 | 210 | 0 | 31 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 620 | 18 | 1362.8 | 0 | 48 | 0 | 105 | 20 | 85 | 110 | 36 | 16 | 0 | 15 | 0 | 190 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 115 | 50 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 401 | 1244 | 0 | 7075.8 | 15792.5 | 78.46
21:00 | 98 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 54 | 17 | 128 | 125 | 278 | 55 | 35 | 162 | 0 | 50 | 350 | 282 | 350 | 0 | 35 | 0 | 251 | 0 | 0 | 0 | 160 | 23 | 20 | 0 | 300 | 17 | 5 | 0 | 0 | 0 | 85 | 73 | 1 | 88 | 100 | 0 | 40 | 94 | 26 | 450 | 144 | 0 | 50 | 25.5 | 85 | 146 | 0 | 0 | 0 | 1226 | 0 | 51 | 122 | 163 | 0 | 0 | 345 | 44 | 185 | 34 | 93 | 90 | 183 | 38 | 20 | 114 | 48 | 52.2 | 0 | 30 | 315 | 0 | 290 | 36 | 30 | 0 | 12 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 43.5 | 102 | 152 | 22 | 0 | 0 | 12 | 8829.2 | 920 | 213 | 0 | 31 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 51 | 1365.69 | 0 | 48 | 0 | 113 | 25 | 90 | 113 | 37 | 43 | 0 | 15 | 0 | 191 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 159 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 401 | 1244 | 0 | 7256.69 | 16085.89 | 78.45
22:00 | 50 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 131 | 125 | 293 | 55 | 35 | 162 | 0 | 50 | 330 | 297 | 300 | 0 | 35 | 0 | 286 | 0 | 0 | 0 | 160 | 23 | 21 | 0 | 300 | 52 | 32 | 0 | 0 | 0 | 85 | 73 | 35 | 87 | 100 | 0 | 40 | 88 | 33 | 400 | 150 | 0 | 50 | 25.5 | 87 | 144 | 0 | 0 | 0 | 1226 | 0 | 51 | 123 | 173 | 0 | 0 | 340 | 46 | 208 | 34 | 93 | 90 | 180 | 38 | 20 | 114 | 50 | 52.2 | 0 | 30 | 315 | 0 | 356 | 36 | 30 | 0 | 16 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 54 | 102 | 152 | 22 | 0 | 0 | 12 | 8941.7 | 831 | 213 | 0 | 31 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 53 | 1364.35 | 0 | 40 | 0 | 113 | 26 | 91 | 113 | 35 | 43 | 0 | 15 | 0 | 194 | 0 | 191 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 166 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 415 | 1244 | 0 | 7180.35 | 16122.05 | 78.44
23:00 | 32 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 130 | 125 | 293 | 55 | 35 | 162 | 0 | 32 | 330 | 290 | 270 | 0 | 35 | 0 | 314 | 0 | 0 | 0 | 160 | 23.5 | 0 | 0 | 300 | 96 | 32 | 0 | 0 | 0 | 85 | 73 | 51 | 87 | 100 | 0 | 40 | 88 | 37 | 400 | 160 | 0 | 50 | 25.5 | 87 | 146 | 0 | 0 | 0 | 1225 | 0 | 51 | 127 | 180 | 0 | 0 | 350 | 47 | 204 | 34 | 93 | 90 | 192 | 38 | 20 | 114 | 52 | 52.2 | 0 | 31 | 325 | 0 | 321 | 36 | 29 | 0 | 16 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 47 | 102 | 153 | 21 | 0 | 0 | 12 | 8933.2 | 831 | 213 | 0 | 31 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 80 | 1361.45 | 0 | 42 | 0 | 113 | 22 | 93 | 113 | 35 | 43 | 0 | 15 | 0 | 194 | 0 | 191 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 166 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 453 | 1244 | 5 | 7231.45 | 16164.65 | 78.43
Total KWH | 613008 | 690240 | 299040 | 0 | 0 | 0 | 0 | 0 | 9252000 | 0 | 0 | 734400 | 431640 | 2729088 | 2244480 | 2388404 | 544717 | 623456 | 3031200 | 0 | 533760 | 8234000 | 6911040 | 7677273 | 0 | 559067 | 0 | 3897665 | 1340000 | 0 | 227162 | 2218800 | 457200 | 441720 | 0 | 7533636.36 | 298582 | 90327 | 0 | 0 | 109920 | 1106954 | 585792 | 125020 | 1654080 | 1949760 | 32520 | 952560 | 433236 | 353760 | 10807272.73 | 694182 | 0 | 833760 | 145661.4 | 449963 | 3393789 | 0 | 0 | 0 | 26623634 | 114615 | 1183212 | 2293309 | 2325091 | 0 | 3285400 | 8148000 | 1144320 | 4841000 | 822888 | 2213760 | 2010000 | 3319680 | 478800 | 450860 | 1761300 | 987840 | 607339 | 499727 | 695808 | 7509000 | 4963700 | 8069000 | 881000 | 663480 | 0 | 1433945 | 185136 | 0 | 1870080 | 688896 | 0 | 408000 | 4550920 | 523440 | 1610400 | 2820000 | 76800 | 15400 | 356060 | 290400 | 188352375.49 | 21968000 | 4353984 | 0 | 179040 | 217600 | 0 | 0 | 0 | 0 | 0 | 0 | 692640 | 7869091 | 491040 | 30757322 | 0 | 293009 | 0 | 1261152 | 119625 | 89744 | 697056 | 214550 | 186605 | 817450 | 68529 | 394496 | 4171364 | 0 | 4352600 | 0 | 0 | 0 | 8985890 | 0 | 33600 | 0 | 3944000 | 1154182 | 1189504 | 243768 | 1033180 | 0 | 0 | 53550.24 | 1386720 | 4675 | 172224 | 6567000 | 207485 | 2573000 | 5129490 | 0 | 10545454 | 27594181.82 | 460800 | 150473601.06 | 338825976.55

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 09-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13559.95 | MW | 12:00 Hr. | Energy Generated |  |  | 338.826 |  | MKWHr.
| Day Peak Demand |  |  | 13559.95 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.256 |  | MKWHr.
| Evening Peak Generation |  |  | 16085.89 | MW | 21:00 Hr. | Energy Demand |  |  | 341.082 |  | MKWHr.
| Evening Peak Demand |  |  | 16201.89 | MW | 21:00 Hr. | Maximum Temperature |  |  | 39.9 |  | °C
| Minimum Generation of the Day |  |  | 12002.45 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 987.74 |  | MMCFD
| Maximum Generation of the Day |  |  | 16164.65 | MW | 23:00 Hr. | Production Cost per KWHr |  |  | 7.0466 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 45.7445 | 0 | 17.6413 | 0 | 0 | 0.22716 | 0 | 0 | 63.613 | Gas | 134.7766 | Gas | 482221995.3512
| Chattogram Zone |  |  | 3.7475 | 37.4309 | 8.3673 | 0 | 0.95256 | 0.14713 | 0 | 0.10992 | 50.7554 | Coal | 95.1048 | Coal | 603471202.491
| Cumilla Zone |  |  | 24.2108 | 0 | 11.37 | 0 | 0 | 0.49973 | 0.98784 | 0 | 37.0683 | HFO | 49.2965 | HFO | 925663529.508
| Mymensingh Zone |  |  | 0.0768 | 0 | 5.2442 | 0 | 0 | 0.37146 | 0 | 0 | 5.6925 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.2232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.2232 | Hydro | 0.95256 | Hydro | 95256
| Khulna Zone |  |  | 4.354 | 7.8691 | 0.88768 | 0 | 0 | 0.69264 | 21.968 | 0 | 35.7714 | Solar | 4.8724 | Solar | 79409515.2564
| Barishal Zone |  |  | 7.91 | 44.7066 | 0.63302 | 0 | 0 | 0.004675 | 0 | 0 | 53.2543 | Import | 53.7132 | Import | 295096106.68
| Rajshahi Zone |  |  | 17.5099 | 0 | 2.9303 | 0 | 0 | 1.2455 | 30.7573 | 0 | 52.443 | Wind | 0.10992 | Wind | 1609228.8
| Rangpur Zone |  |  | 0 | 5.0982 | 2.2227 | 0 | 0 | 1.684 | 0 | 0 | 9.0049
| Total |  |  | 134.7766 | 95.1048 | 49.2965 | 0 | 0.95256 | 4.8724 | 53.7132 | 0.10992 | 338.826
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 482221995.3512 |  | Hydro | 95256
|  |  |  | Coal | 603471202.491 |  | Solar | 79409515.2564
|  |  |  | HFO | 925663529.508 |  | Import | 295096106.68
|  |  |  | HSD | 0 |  | Wind | 1609228.8
[5 empty] | Total: | 238,75,66,834 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.968 | Peak Hr Flow | 920.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35253545.51 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.7573 | Peak Hr Flow | 1365.69 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 596 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.98784 | Peak Hr Flow | 48.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 796 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.7132 | Peak Hr Flow | 2333.69 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 35 |  | 5393
|  |  |  | Chattogram |  | 0 |  | 1558
|  |  |  | Cumilla |  | 10 |  | 1494
|  |  |  | Mymensingh |  | 60 |  | 1285
|  |  |  | Sylhet |  | 0 |  | 637
|  |  |  | Khulna |  | 0 |  | 1893
|  |  |  | Barishal |  | 0 |  | 482
|  |  |  | Rajshahi |  | 0 |  | 1766
|  |  |  | Rangpur |  | 6 |  | 1053
|  |  |  | Total |  | 111 |  | 15561
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 735.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:02 | Bakulia-Sikalbaha 132 kV Ckt-2 is restored.
|  | 08:09 | Shikalbaha 230/132kV S/S ATR 01 LT is restored.
|  | 08:11 | Shikalbaha 230/132kV S/S ATR 02 LT is restored.
|  | 08:14 | Shikalbaha 230/132kV S/S Interconnection-1 is restored.
| 08:34 | 10:38 | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to 33 kV Nikra feeder red hot
maintenance
| 08:35 | 10:37 | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to 33 kV Nikra feeder red hot
maintenance
|  | 08:49 | Juldah-Sikalbaha 132kV Ckt-1 is restored.
| 08:50 | 09:10 | Kishoreganj 132/33kV S/S Tr-3 (424T) HT Forced S/D Due to 33Kv T-3 Bus Shutdown due to | [7 empty] | 30.0MW load
|  |  | Pakundia feeder incoming bus loop change | [7 empty] | interrup.
| 08:59 |  | Halishahar 132/33kV S/S 423T(TR-3) HT Project Work S/D Due to ESPNER project work
| 09:13 | 13:23 | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Project Work S/D Due to 132kV Jumper out in
Halishahar Sub-station end.
| 09:18 | 13:21 | Halishahar-Julda 132kV Ckt-1 Project Work S/D from Juldah 132/33kV end Due to The jumper
of the halishahar line from juldha to khulsi line is open
|  | 09:20 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
|  | 09:20 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
| 09:34 | 10:56 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot maintenance
| 09:34 | 10:56 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot maintenance
| 09:35 | 00:06 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) LT Scheduled S/D Due to Changing the
Relay RET 670 of Main 1 protection unit FP1 of Transformer-2.
| 09:36 | 00:06 | Maniknagar 230/132kV S/S Auto Transformer-02 (715T) HT Scheduled S/D Due to Changing the
Relay RET 670 of Main1 protection unit FP1 of Transformer-2.
| 09:45 | 00:06 | Maniknagar-Siddhirganj 230kV Ckt-2 Scheduled S/D from Siddhirganj 230/132kV end Due to
Emergency maintenance work
| 09:45 | 14:10 | New Tongi S/S T1(403T) HT Scheduled S/D Due to 33kv cable laying work
| 09:59 | 12:19 | Siddhirganj 230/132kV S/S 335MW EGCB 1 Scheduled S/D Due to Emergency maintenceance work
| 10:10 | 12:05 | Magura 132/33kV S/S T-3 (425T) LT Scheduled S/D Due to Feeder maintenance by PBS. | [7 empty] | 22.0MW load
interrup.
| 10:11 | 12:02 | Magura 132/33kV S/S T-3 (425T) HT Scheduled S/D Due to Feeder maintenance by PBS. | [7 empty] | 22.0MW load
interrup.
| 10:58 | 11:12 | Juldah-Sikalbaha 132kV Ckt-1 Tripped from Juldah 132/33kV end showing relay trip relays.
|  | 11:13 | Kabirpur 132/33kV S/S XFR, T-I HT is restored.
|  | 11:13 | Kabirpur 132/33kV S/S XFR, T-2 HT is restored.
|  | 11:24 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
| 11:34 | 13:43 | Halishahar 132/33kV S/S 415T(TR-2) HT Project Work S/D Due to Due to secondary 33 kv
cable connection.
| 11:35 | 12:10 | Bagerhat-Bhandaria 132 kV Ckt-1 Tripped from Bagerhat 132/33kV end showing E/F (B,E)
relays Due to Unknown
| 12:04 | 18:33 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-2 Scheduled S/D from Rangpur 132/33kV end
Due to Due to B phase CT change
| 12:17 |  | BIPTC S/S 20DF24 Tripped showing 21R relays Due to Tripped by impedance 21R
| 12:28 | 13:57 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 LT Tripped showing 132kv side Control Panel
signal 1. General Trip Realy Panel signal 1. General Trip relays.
| 12:28 | 13:56 | Aminbazar 400/230/132kV S/S 230/132kv Tr-03 HT Tripped showing 230kv Side Control Panel
signal 1. Diff. Protection Trip 2. General Trip Realy Panel signal 1. General
Trip 2. Diff. Trip R Phase 3. Diff. Trip Y Phase relays Due to None
| 13:51 |  | Day Peak Generation = 13556 MW at 12:00 hr.
| 14:48 |  | Borhanuddin 230/33KV Transformer S/D. | [7 empty] | 55MW load interrup.
| 15:24 |  | Bibiyana South 400 MW Tripped with remarks:- gt
| 16:14 | 17:41 | Gopalganj 132/33kV S/S T2 LT Forced S/D Due to Section Ds clamp maintenance | [7 empty] | 30.0MW load
interrup.
| 16:15 | 17:40 | Gopalganj 132/33kV S/S T2 HT Forced S/D Due to Section Ds Clamp maintenance | [7 empty] | 30.0MW load
interrup.
|  | 17:26 | Baghabari-Ishurdi 230 kV Ckt-2 is restored.
|  | 17:26 | Baghabari-Ishurdi 230 kV Ckt-1 is restored.
| 18:38 |  | Borhanuddin 230/33KV Transformer S/D Withdraw. | [7 empty] | 55MW load interrup.
| 05:37 |  | Gallamari- Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end.
| 05:37 |  | Gallamari- Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end.
| 05:40 |  | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end Due to None | [7 empty] | 50.0MW load
interrup. Khulna(S)
230/132kV end
| 05:40 |  | Khulna (S)-Satkhira 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. | [7 empty] | 50.0MW load
interrup. Khulna(S)
230/132kV end
| 05:51 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end.
| 05:56 |  | Khulna(S) 230/132kV S/S TR-1 HT Scheduled S/D
| 05:56 |  | Khulna(S) 230/132kV S/S TR-2 HT Scheduled S/D
| 05:56 |  | Khulna(S) 230/132kV S/S TR-3 LT Scheduled S/D
| 05:57 |  | Khulna(S) 230/132kV S/S TR-3 HT Scheduled S/D
| 06:05 |  | Khulna(S) 230/132kV S/S 132 KV Main Bus Scheduled S/D Due to Red hot maintenance work | [7 empty] | 100.0MW load
interrup.
| 06:10 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna (C) end Due to Red hot
maintenance.
| 06:34 |  | Haripur 412 MW CCPP Shutdown with remarks:- ST
| 06:47 |  | Haripur 412 MW CCPP Shutdown with remarks:- GT
| 07:00 |  | Minimum Generation 13359 MW.
| 07:30 |  | Gopalganj 132/33kV S/S T1 LT Scheduled S/D Due to Maintenances
| 07:31 |  | Gopalganj 132/33kV S/S T1 HT Scheduled S/D Due to Maintenance
| 07:40 |  | Chauddagram 132/33kV S/S 132 kv T-2 LT Scheduled S/D Due to Red-hot Maintenance. | [7 empty] | 27.0MW load
interrup.
| 07:40 |  | Chauddagram 132/33kV S/S 132 kv T-2 HT Scheduled S/D Due to Red-hot maintenance. | [7 empty] | 27.0MW load
interrup.
| 07:46 |  | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Project Work S/D from BIPTC end. and from
Jhenaidah 230/132kV end Due to Energy meter change
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 09-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 400 | 9252000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8234000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 282 | 6911040 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 544717 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 1340000 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 251 | 3897665 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 98 | 613008 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 734400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 125 | 2244480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 623456 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 559067 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 23 | 457200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 441720 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 299040 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 278 | 2388404 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 128 | 2729088 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 690240 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 50 | 533760 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3031200 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 227162 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 431640 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 7533636.36 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 350 | 7677273 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2218800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3241 | 63612996.36
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 145661.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114615 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 833760 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 952560 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3393789 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 449963 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 73 | 585792 | Engine Problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 85 | 1106954 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 1654080 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 26 | 353760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 32520 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 5 | 90327 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 1 | 125020 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 94 | 433236 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1949760 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 298582 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 144 | 694182 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1226 | 26623634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 109920 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 450 | 10807272.73 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2655.5 | 50755388.13
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 185 | 4841000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 3285400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8148000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 822888 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 44 | 1144320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 163 | 2325091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1183212 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 122 | 2293309 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 30 | 695808 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2010000 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 183 | 3319680 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 48 | 987840 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 607339 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 450860 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1761300 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 478800 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 2213760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 499727 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1612.2 | 37068334
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 22 | 76800 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 152 | 2820000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1610400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 356060 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 290400 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 43.5 | 523440 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 331.5 | 5692500
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 881000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 663480 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 12 | 1433945 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 688896 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1870080 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 172 | 4550920 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 408000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 185136 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7509000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 290 | 8069000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 4963700 | -
Sylhet Area Total |  |  |  |  | 2368.568 | 989 | 31223157
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 920 | 21968000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 31 | 179040 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 43 | 217600 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 213 | 4353984 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 51 | 491040 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 692640 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 618 | 7869091 | Rampal U# 1 is out of bar due to maintenance work
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1876 | 35771395
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 401 | 10545454 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 172224 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 207485 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 115 | 2573000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27594181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5129490 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 460800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6567000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4675 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2298 | 53254309.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 48 | 293009 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 25 | 119625 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 37 | 214550 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 191 | 4171364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 191 | 4352600 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8985890 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 15 | 68529 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 186605 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 89744 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1261152 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 697056 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1365.69 | 30757322 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 394496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 817450 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2645.69 | 52442992
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1154182 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 159 | 3944000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 1033180 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 53550.24 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1189504 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 243768 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1386720 | -
Rangpur Area Total |  |  |  |  | 950 | 437 | 9004904.24
Eastern Grid Total |  |  |  |  | 16921.242 | 8829.2 | 188352375.49
Western Grid Total |  |  |  |  | 11702.84 | 7256.69 | 150473601.06
National Grid Total |  |  |  |  | 28624.082 | 16085.89 | 338825976.55
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 09-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10261.44 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5187.5 | MW
i) Dhaka area |  |  | 5357.62 |  | MW | i) Khulna area |  |  |  | 1893 | MW
ii) Chattogram area |  |  | 1557.5 |  | MW | ii) Barishal area |  |  |  | 481.5 | MW
iii) Cumilla area |  |  | 1484.32 |  | MW | iii) Rajshahi area |  |  |  | 1766 | MW
iv) Mymensingh area |  |  | 1225 |  | MW | iv) Rangpur area |  |  |  | 1047 | MW
v) Sylhet area |  |  | 637 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15448.94 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 86 | 19:00 | 133 | Patuakhali | 79.2 | 23:00
2 | AKSML | 12 | 05:00 | 68 | Jaldhaka | 88 | 20:00 | 134 | Payra | 38 | 21:00
3 | Aftabnagar | 42 | 19:30 | 69 | Jamalpur | 134 | 21:00 | 135 | Postogola | 55 | 00:00
4 | Agargaon | 140 | 23:00 | 70 | Jashore | 151 | 21:00 | 136 | Purbachal | 22 | 22:00
5 | Agrabad | 98 | 23:00 | 71 | Jhenaidah | 144 | 20:00 | 137 | Purbasadipur | 141 | 00:00
6 | Amnura | 49 | 21:00 | 72 | Joydebpur | 144 | 03:00 | 138 | Rahanpur | 33 | 22:00
7 | Ashuganj | 121 | 23:00 | 73 | Joypurhat | 83 | 23:00 | 139 | Rahim | 50 | 02:00
8 | BSRM | 195 | 01:00 | 74 | Juldah | 17 | 23:00 | 140 | Rajbari | 92 | 19:00
9 | Bagerhat | 89 | 20:00 | 75 | KSRM | 24 | 18:30 | 141 | Rajendrapur | 144 | 00:00
10 | Bajitpur | 57 | 21:00 | 76 | Kabirpur | 267 | 00:00 | 142 | Rajshahi | 131 | 21:00
11 | Bakulia | 101 | 23:00 | 77 | Kachua | 98 | 21:00 | 143 | Rajshahi-230 | 101 | 22:00
12 | Banani | 36 | 19:00 | 78 | Kallyanpur | 114 | 23:00 | 144 | Ramganj | 122 | 22:00
13 | Bangabhaban | 5 | 15:00 | 79 | Kalurghat | 36 | 00:00 | 145 | Rampur | 49 | 23:00
14 | Barapukuria | 72 | 22:00 | 80 | Kamrangirchar | 63 | 00:00 | 146 | Rangamati | 19 | 19:00
15 | Barguna | 30 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 164 | 19:30
16 | Barishal | 109 | 13:00 | 82 | Kasba | 43 | 23:00 | 148 | Ruppur | 6 | 11:00
17 | Barishal-230 | 98 | 23:00 | 83 | Kazla | 97 | 01:00 | 149 | SSM | 6 | 03:00
18 | Baroaulia | 64 | 22:00 | 84 | Keranigonj | 79 | 00:00 | 150 | Saidpur | 110 | 19:30
19 | Baroirhat | 77 | 19:00 | 85 | Khagrachori | 38 | 19:00 | 151 | Satkhira | 144 | 00:00
20 | Bashundhara | 202 | 23:00 | 86 | Khulna | 78 | 13:00 | 152 | Satmasjid | 108 | 19:00
21 | BashundharaCement | 12 | 00:00 | 87 | Khulshi | 187 | 20:00 | 153 | Savar | 198 | 12:00
22 | Beanibazar | 81 | 19:00 | 88 | Kishoreganj | 155 | 21:00 | 154 | SevenRings | 19.26 | 04:00
23 | Benapole | 72 | 00:00 | 89 | Kodda | 297 | 08:00 | 155 | ShahCement | 29 | 01:00
24 | Bhaluka | 164 | 00:00 | 90 | Kulaura | 52 | 19:00 | 156 | Shahjadpur | 94 | 00:00
25 | Bhandaria | 54 | 22:00 | 91 | Kurigram | 71 | 19:00 | 157 | Shahjibazar | 119 | 23:00
26 | Bhangura | 52 | 19:00 | 92 | Kushtia | 160 | 23:00 | 158 | Shahmirpur | 64 | 00:00
27 | Bheramara(GK) | 71 | 23:00 | 93 | Lalbag | 64 | 00:00 | 159 | Shariatpur | 91 | 22:00
28 | Bhulta | 230 | 00:00 | 94 | Lalmonirhat | 68 | 19:30 | 160 | Sherpur | 150 | 22:00
29 | Bog-Sherpur | 78 | 00:00 | 95 | MI_Cement | 17.5 | 23:00 | 161 | Shikalbaha | 28 | 00:00
30 | Bogura | 196 | 23:00 | 96 | Madanganj | 54 | 00:00 | 162 | Shitalakhya | 68 | 21:00
31 | Borhanuddin | 101 | 21:00 | 97 | Madaripur | 121 | 22:00 | 163 | Sholosohor | 48 | 23:00
32 | Brahmanbaria | 134 | 01:00 | 98 | Madartek | 102.85 | 23:00 | 164 | Shyampur | 170 | 02:00
33 | Cantonment | 136 | 21:00 | 99 | Madunaghat | 58 | 19:30 | 165 | Siddhirganj | 108 | 12:00
34 | Chandina | 20.34 | 22:00 | 100 | Magura | 71 | 22:00 | 166 | Sirajganj | 122 | 21:00
35 | Chandpur | 69 | 00:00 | 101 | Mahasthangarh | 96 | 23:00 | 167 | Sonargaon | 123 | 00:00
36 | Chandraghona | 40 | 19:00 | 102 | Manikganj | 138 | 00:00 | 168 | Sreemongol | 84 | 21:00
37 | Chapai | 78 | 23:00 | 103 | Maniknagar | 76 | 00:00 | 169 | Sreepur | 102 | 00:00
38 | Charsaidpur | 46 | 19:30 | 104 | Matarbari | 54 | 23:00 | 170 | Srinagar | 52.24 | 21:00
39 | Chauddagram | 77 | 23:00 | 105 | Matuail | 66 | 00:00 | 171 | Sunamganj | 64 | 19:00
40 | Chhatak | 39 | 22:00 | 106 | Millgate | 103 | 00:00 | 172 | Sylhet | 47 | 22:00
41 | Chowmuhani | 243 | 23:00 | 107 | Mirpur | 141.5 | 00:00 | 173 | Sylhet-132 | 128 | 19:00
42 | Chuadanga | 126 | 23:00 | 108 | Mirsorai | 10 | 19:30 | 174 | TK | 35 | 00:00
43 | Coxsbazar | 136 | 00:00 | 109 | Mirzapur | 52 | 12:00 | 175 | Tangail | 184 | 12:00
44 | Cumilla(N) | 172 | 21:00 | 110 | Mithapukur | 70 | 19:00 | 176 | Thakurgaon | 112 | 21:00
45 | Cumilla(S) | 182 | 22:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 121 | 00:00
46 | Daudkandi | 160 | 19:30 | 112 | Mogbazar | 132.2 | 15:00 | 178 | Ullahpara | 52 | 23:00
47 | Dhaka | 30 | 12:00 | 113 | Mongla | 40 | 00:00 | 179 | Ullon | 59 | 21:00
48 | Dhamrai | 142 | 22:00 | 114 | Motijheel | 37 | 19:00 | 180 | Uttara | 97 | 16:00
49 | Dhanmondi | 131 | 20:00 | 115 | Muktagacha | 44 | 19:30 | 181 | UttaraNew | 58 | 23:00
50 | Dohazari | 113 | 22:00 | 116 | Munshiganj | 118 | 21:00 | 182 | Zigatola | 82 | 20:00
51 | Faridpur | 171 | 22:00 | 117 | Muradnagar | 33 | 22:00
52 | Fatullah | 92 | 00:00 | 118 | Mymensingh | 226 | 19:00
53 | Fenchuganj | 51 | 19:30 | 119 | Naogaon | 159 | 21:00
54 | Feni | 120 | 23:00 | 120 | Narail | 62 | 22:00
55 | GPH | 94 | 07:00 | 121 | Narinda | 58 | 00:00
56 | Ghatail | 74 | 08:00 | 122 | Narshingdi | 190 | 01:00
57 | Ghorashal | 16 | 21:00 | 123 | Natore | 177 | 22:00
58 | Ghorashal-230 | 102 | 00:00 | 124 | Nawabganj | 68 | 22:00
59 | Goalpara | 26 | 00:00 | 125 | Netrakona | 130 | 03:00
60 | Gollamari | 102 | 00:00 | 126 | New | 75.8 | 00:00
61 | Gopalganj | 108 | 21:00 | 127 | Niamatpur | 95 | 22:00
62 | Gulshan | 104 | 15:00 | 128 | Noapara | 47 | 00:00
63 | Halishahar | 51 | 15:00 | 129 | PHP | 7 | 02:00
64 | HaripurSBU | 177 | 00:00 | 130 | Pabna | 131 | 21:00
65 | Hasnabad | 85 | 23:00 | 131 | Palashbari | 139 | 22:00
66 | Hathazari | 85 | 22:00 | 132 | Panchagarh | 65 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 09-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15768.2 | 107 |  | 15880.2
1:00 | 15253.7 | 159 |  | 15419.7
2:00 | 14610 | 153 |  | 14770
3:00 | 14194.5 | 149 |  | 14350.5
4:00 | 13887.5 | 127 |  | 14020.5
5:00 | 13472 | 94 |  | 13570
6:00 | 12002.45 | 67 |  | 12072.45
7:00 | 12055.87 | 44 |  | 12101.87
8:00 | 12213.15 | 0 |  | 12213.15
9:00 | 12222.85 | 0 |  | 12222.85
10:00 | 12683.7 | 0 |  | 12683.7
11:00 | 13035.8 | 0 |  | 13035.8
12:00 | 13559.95 | 0 |  | 13559.95
13:00 | 13898.8 | 99 |  | 14001.8
14:00 | 13636.87 | 91 |  | 13731.87
15:00 | 13989.12 | 109 |  | 14103.12
16:00 | 13576.43 | 121 |  | 13702.43
17:00 | 13338.08 | 139 |  | 13483.08
18:00 | 12949.77 | 98 |  | 13051.77
19:00 | 14839.02 | 202 |  | 15050.02
19:30 | 15635.09 | 159 |  | 15801.09
20:00 | 15792.5 | 123 |  | 15921.5
21:00 | 16085.89 | 111 |  | 16201.89
22:00 | 16122.05 | 104 |  | 16231.05
23:00 | 16164.65 | 159 |  | 16330.65
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 09-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8961.2 | 6807 | 15768.2 | DAILY GENERATION CURVE
00:30 | 8775.95 | 6735 | 15510.95
01:00 | 8590.7 | 6663 | 15253.7 | 09-05-2025
01:30 | 8421.35 | 6510.5 | 14931.85
02:00 | 8252 | 6358 | 14610
02:30 | 8189.75 | 6212.5 | 14402.25
03:00 | 8127.5 | 6067 | 14194.5
03:30 | 8075 | 5966 | 14041
04:00 | 8022.5 | 5865 | 13887.5
04:30 | 7854.75 | 5825 | 13679.75
05:00 | 7687 | 5785 | 13472
05:30 | 7221.595 | 5515.63 | 12737.225
06:00 | 6756.19 | 5246.26 | 12002.45
06:30 | 6726.355 | 5302.805 | 12029.16
07:00 | 6696.52 | 5359.35 | 12055.87
07:30 | 6765.475 | 5369.035 | 12134.51
08:00 | 6834.43 | 5378.72 | 12213.15
08:30 | 6884.505 | 5333.495 | 12218
09:00 | 6934.58 | 5288.27 | 12222.85
09:30 | 6955.15 | 5498.125 | 12453.275
10:00 | 6975.72 | 5707.98 | 12683.7
10:30 | 7027.94 | 5831.81 | 12859.75
11:00 | 7080.16 | 5955.64 | 13035.8
11:30 | 7196.91 | 6100.965 | 13297.875
12:00 | 7313.66 | 6246.29 | 13559.95
12:30 | 7477.95 | 6251.425 | 13729.375
13:00 | 7642.24 | 6256.56 | 13898.8
13:30 | 7604.8 | 6163.035 | 13767.835
14:00 | 7567.36 | 6069.51 | 13636.87
14:30 | 7655.83 | 6157.165 | 13812.995
15:00 | 7744.3 | 6244.82 | 13989.12
15:30 | 7458.47 | 6324.305 | 13782.775
16:00 | 7172.64 | 6403.79 | 13576.43
16:30 | 7194.635 | 6262.62 | 13457.255
17:00 | 7216.63 | 6121.45 | 13338.08
17:30 | 7134.045 | 6009.88 | 13143.925
18:00 | 7051.46 | 5898.31 | 12949.77
18:30 | 7616.58 | 6277.815 | 13894.395
19:00 | 8181.7 | 6657.32 | 14839.02
19:30 | 8610.7 | 7024.39 | 15635.09
20:00 | 8716.7 | 7075.8 | 15792.5
20:30 | 8772.95 | 7166.245 | 15939.195 |  | Executive Engineer
21:00 | 8829.2 | 7256.69 | 16085.89 |  | Network Operation Division
21:30 | 8885.45 | 7218.52 | 16103.97
22:00 | 8941.7 | 7180.35 | 16122.05
22:30 | 8937.45 | 7205.9 | 16143.35
23:00 | 8933.2 | 7231.45 | 16164.65

## En-Curve
QF-LDC-12
Date | 09-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3710 | 2096 | 925 | 0 | 46 | 1371 | 40 | 4013 | 0 | 814 | 2753.2 | 0 | 0 | 0 | 107 | DAILY ENERGY CURVE
00:30 | 3691.5 | 2062.5 | 925.5 | 0 | 45 | 1364.5 | 40 | 4014 | 0 | 787 | 2580.95 | 0 | 0 | 0 | 133 | 09-05-2025
01:00 | 3673 | 2029 | 926 | 0 | 44 | 1358 | 40 | 4015 | 0 | 760 | 2408.7 | 0 | 0 | 0 | 159
01:30 | 3673.5 | 2036 | 926 | 0 | 42 | 1362.5 | 40 | 4015.5 | 0 | 620 | 2216.35 | 0 | 0 | 0 | 156 | Energy Generated | 338.826 |  | MKWHr
02:00 | 3674 | 2043 | 926 | 0 | 40 | 1367 | 40 | 4016 | 0 | 480 | 2024 | 0 | 0 | 0 | 153 | Energy not Served | 2.256 |  | MKWHr
02:30 | 3695 | 2047.25 | 925.5 | 0 | 40 | 1366 | 40 | 4016.5 | 0 | 460 | 1812 | 0 | 0 | 0 | 151 | Total Energy Requirement | 341.082 |  | MKWHr
03:00 | 3716 | 2051.5 | 925 | 0 | 40 | 1365 | 40 | 4017 | 0 | 440 | 1600 | 0 | 0 | 0 | 149
03:30 | 3718 | 2059.5 | 925.5 | 0 | 39 | 1366 | 40 | 4014.5 | 0 | 393.5 | 1485 | 0 | 0 | 0 | 138
04:00 | 3720 | 2067.5 | 926 | 0 | 38 | 1367 | 40 | 4012 | 0 | 347 | 1370 | 0 | 0 | 0 | 127
04:30 | 3688.5 | 2086.75 | 926 | 0 | 35 | 1371 | 40 | 4013 | 0 | 284.5 | 1235 | 0 | 0 | 0 | 110.5
05:00 | 3657 | 2106 | 926 | 0 | 32 | 1375 | 40 | 4014 | 0 | 222 | 1100 | 0 | 0 | 0 | 94
05:30 | 3511 | 2041.25 | 926 | 0 | 34 | 1317.5 | 40 | 3709.5 | 14.475 | 205 | 938.5 | 0 | 0 | 0 | 80.5
06:00 | 3365 | 1976.5 | 926 | 0 | 36 | 1260 | 40 | 3405 | 28.95 | 188 | 777 | 0 | 0 | 0 | 67
06:30 | 3355 | 2002.75 | 926 | 0 | 35 | 1236.5 | 40 | 3363 | 81.41 | 188 | 801.5 | 0 | 0 | 0 | 55.5
07:00 | 3345 | 2029 | 926 | 0 | 34 | 1213 | 40 | 3321 | 133.87 | 188 | 826 | 0 | 0 | 0 | 44
07:30 | 3389 | 2008 | 901.5 | 0 | 33 | 1166 | 40 | 3345 | 209.01 | 179 | 864 | 0 | 0 | 0 | 22
08:00 | 3433 | 1987 | 877 | 0 | 32 | 1119 | 40 | 3369 | 284.15 | 170 | 902 | 0 | 0 | 0 | 0
08:30 | 3398 | 2046.5 | 877 | 0 | 31 | 1062.5 | 40 | 3294.5 | 373 | 179 | 916.5 | 0 | 0 | 0 | 0
09:00 | 3363 | 2106 | 877 | 0 | 30 | 1006 | 40 | 3220 | 461.85 | 188 | 931 | 0 | 0 | 0 | 0
09:30 | 3333 | 2262 | 900.5 | 0 | 33 | 1033.5 | 40 | 3286.5 | 520.275 | 159 | 885.5 | 0 | 0 | 0 | 0
10:00 | 3303 | 2418 | 924 | 0 | 36 | 1061 | 40 | 3353 | 578.7 | 130 | 840 | 0 | 0 | 0 | 0
10:30 | 3305 | 2382 | 924 | 0 | 37 | 1060.5 | 40 | 3544.5 | 610.75 | 138 | 816 | 0 | 0 | 2 | 0
11:00 | 3307 | 2346 | 924 | 0 | 38 | 1060 | 40 | 3736 | 642.8 | 146 | 792 | 0 | 0 | 4 | 0
11:30 | 3311.5 | 2303.5 | 924.5 | 0 | 40 | 1116 | 40 | 3852.5 | 650.875 | 204.5 | 851 | 0 | 0 | 3.5 | 0
12:00 | 3316 | 2261 | 925 | 0 | 42 | 1172 | 40 | 3969 | 658.95 | 263 | 910 | 0 | 0 | 3 | 0
12:30 | 3250 | 2253 | 925 | 0 | 43 | 1220.5 | 40 | 4038.5 | 633.375 | 268.5 | 1049 | 0 | 0 | 8.5 | 49.5
13:00 | 3184 | 2245 | 925 | 0 | 44 | 1269 | 40 | 4108 | 607.8 | 274 | 1188 | 0 | 0 | 14 | 99
13:30 | 3215 | 2240.5 | 925 | 0 | 44 | 1247.245 | 40 | 3946.5 | 587.59 | 265 | 1241 | 0 | 0 | 16 | 95
14:00 | 3246 | 2236 | 925 | 0 | 44 | 1225.49 | 40 | 3785 | 567.38 | 256 | 1294 | 0 | 0 | 18 | 91
14:30 | 3280.5 | 2312.5 | 924.5 | 0 | 44 | 1221.085 | 40 | 3926.5 | 501.91 | 245.5 | 1297.5 | 0 | 0 | 19 | 100
15:00 | 3315 | 2389 | 924 | 0 | 44 | 1216.68 | 40 | 4068 | 436.44 | 235 | 1301 | 0 | 0 | 20 | 109
15:30 | 3083.5 | 2369 | 924 | 0 | 43 | 1281.795 | 40 | 4107 | 347.88 | 232 | 1336.1 | 0 | 0 | 18.5 | 115
16:00 | 2852 | 2349 | 924 | 0 | 42 | 1346.91 | 40 | 4146 | 259.32 | 229 | 1371.2 | 0 | 0 | 17 | 121
16:30 | 2957.5 | 2298.75 | 924 | 0 | 40 | 1357.02 | 40 | 3959.5 | 182.785 | 262.5 | 1420.2 | 0 | 0 | 15 | 130
17:00 | 3063 | 2248.5 | 924 | 0 | 38 | 1367.13 | 40 | 3773 | 106.25 | 296 | 1469.2 | 0 | 0 | 13 | 139
17:30 | 2959.5 | 2128.5 | 924.5 | 0 | 38 | 1364.125 | 40 | 3755.5 | 62.1 | 345 | 1519.2 | 0 | 0 | 7.5 | 118.5
18:00 | 2856 | 2008.5 | 925 | 0 | 38 | 1361.12 | 40 | 3738 | 17.95 | 394 | 1569.2 | 0 | 0 | 2 | 98
18:30 | 3004.5 | 2148.75 | 916.5 | 0 | 42 | 1365.22 | 40 | 3994.5 | 8.975 | 524 | 1845.95 | 0 | 0 | 4 | 150
19:00 | 3153 | 2289 | 908 | 0 | 46 | 1369.32 | 40 | 4251 | 0 | 654 | 2122.7 | 0 | 0 | 6 | 202
19:30 | 3206 | 2302 | 887 | 0 | 46 | 1362.39 | 40 | 4387 | 0 | 779 | 2617.7 | 0 | 0 | 8 | 159
20:00 | 3209 | 2287 | 887 | 0 | 48 | 1362.8 | 40 | 4411 | 0 | 801 | 2739.7 | 0 | 0 | 7 | 123
20:30 | 3190 | 2281 | 903.5 | 0 | 48 | 1364.245 | 40 | 4433 | 0 | 815.5 | 2860.45 | 0 | 0 | 3.5 | 117
21:00 | 3171 | 2275 | 920 | 0 | 48 | 1365.69 | 40 | 4455 | 0 | 830 | 2981.2 | 0 | 0 | 0 | 111
21:30 | 3230.5 | 2259.5 | 875.5 | 0 | 49 | 1365.02 | 40 | 4440.5 | 0 | 824 | 3019.95 | 0 | 0 | 0 | 107.5
22:00 | 3290 | 2244 | 831 | 0 | 50 | 1364.35 | 40 | 4426 | 0 | 818 | 3058.7 | 0 | 0 | 0 | 104
22:30 | 3281 | 2226.25 | 831 | 0 | 51 | 1362.9 | 40 | 4445 | 0 | 810 | 3096.2 | 0 | 0 | 0 | 131.5
23:00 | 3272 | 2208.5 | 831 | 0 | 52 | 1361.45 | 40 | 4464 | 0 | 802 | 3133.7 | 0 | 0 | 0 | 159
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 09-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 386 | 08:00 | 370 | 15:00 | Payra | 411 | 08:00 | 405 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Rahanpur | 402 | 10:00 | 393 | 00:00
Bhulta | 396 | 08:00 | 373 | 12:00 | Rampal | 397 | 09:00 | 375 | 02:00
Bibiana | 393 | 08:00 | 382 | 16:00
BIPTC | 399 | 09:00 | 387 | 00:00
Bogura | 386 | 10:00 | 375 | 13:00
Gopalganj | 394 | 08:00 | 379 | 02:00
Kaliakoir | 379 | 08:00 | 362 | 16:00
Madunaghat | 400 | 09:00 | 388 | 02:00
Meghnaghat | 391 | 08:00 | 374 | 16:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 08:00 | 215 | 15:00 | Keranigonj | 224 | 08:00 | 214 | 16:00
AKSML | 235 | 06:00 | 222 | 00:00 | Khulna(S) | 228 | 09:00 | 213 | 02:00
Aminbazar | 226 | 08:00 | 217 | 12:00 | Madunaghat | 238 | 08:00 | 228 | 03:00
Ashuganj | 233 | 08:00 | 222 | 17:00 | Madunaghat-400 | 238 | 07:00 | 228 | 03:00
Ashuganj-400 | 233 | 08:00 | 222 | 17:00 | Maniknagar | 223 | 08:00 | 211 | 12:00
Baghabari | 232 | 07:00 | 228 | 00:00 | Meghnaghat | 231 | 08:00 | 222 | 12:00
Barapukuria | 222 | 01:00 | 218 | 13:00 | Meghnaghat-400 | 226 | 08:00 | 217 | 16:00
Barapukuria-230 | 222 | 01:00 | 218 | 13:00 | Mirsorai | 233 | 21:00 | 221 | 02:00
Barishal | 236 | 08:00 | 228 | 22:00 | Rajshahi | 234 | 09:00 | 224 | 12:00
Bheramara | 235 | 08:00 | 225 | 02:00 | Rampal | 227 | 09:00 | 213 | 03:00
Bhulta | 224 | 08:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 06:00 | 216 | 16:00 | Rampura | 224 | 08:00 | 212 | 12:00
BIPTC | 236 | 08:00 | 222 | 12:00 | Shikalbaha | 239 | 08:00 | 226 | 03:00
Bogura | 233 | 08:00 | 227 | 13:00 | Shyampur | 224 | 08:00 | 215 | 16:00
Bogura-400 | 234 | 10:00 | 228 | 13:00 | Siddhirganj | 226 | 08:00 | 216 | 15:00
Borhanuddin | 241 | 08:00 | 234 | 21:00 | Sirajgonj | 239 | 09:00 | 235 | 01:00
BSRM | 232 | 23:00 | 221 | 02:00 | Sreepur | 228 | 06:00 | 222 | 00:00
Cumilla(N) | 225 | 08:00 | 215 | 12:00 | Tongi | 224 | 19:30 | 213 | 15:00
Faridpur | 233 | 08:00 | 222 | 22:00
Fenchuganj | 226 | 09:00 | 218 | 02:00
Ghorashal | 230 | 01:00 | 225 | 00:00
Ghorashal-230 | 226 | 08:00 | 216 | 12:00
Gopalganj | 233 | 08:00 | 225 | 02:00
GPH | 235 | 06:00 | 224 | 02:00
Haripur | 224 | 08:00 | 215 | 12:00
Hasnabad | 224 | 08:00 | 215 | 15:00
Hathazari | 239 | 05:00 | 227 | 16:00
Ishurdi | 236 | 08:00 | 225 | 13:00
Jhenaidah | 228 | 09:00 | 215 | 00:00
Kaliakoir | 230 | 07:00 | 221 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 08:00 | 127 | 15:00 | Madartek | 134 | 08:00 | 126 | 12:00
Agargaon | 132 | 08:00 | 124 | 15:00 | Madunaghat | 136 | 07:00 | 129 | 13:00
Agrabad | 137 | 06:00 | 128 | 01:00 | Magura | 132 | 08:00 | 122 | 00:00
AKS | 132 | 08:00 | 127 | 11:00 | Mahasthangarh | 132 | 01:00 | 129 | 13:00
Aminbazar | 131 | 18:00 | 125 | 12:00 | Manikganj | 135 | 09:00 | 120 | 00:00
Amnura | 137 | 19:30 | 123 | 00:00 | Maniknagar | 131 | 08:00 | 120 | 12:00
Ashuganj | 136 | 08:00 | 133 | 11:00 | Matarbari | 120 | 09:00 | 112 | 03:00
Bagerhat | 131 | 08:00 | 118 | 03:00 | Matuail | 130 | 18:00 | 125.4 | 12:00
Bajitpur | 131 | 09:00 | 125 | 19:30 | Millgate | 134 | 08:00 | 126 | 16:00
Bakulia | 137 | 06:00 | 130 | 05:00 | Mirpur | 130 | 18:00 | 123 | 12:00
Banani | 134 | 07:00 | 126 | 12:00 | Mirzapur | 133 | 09:00 | 126 | 12:00
Bangabhaban | 131 | 08:00 | 120 | 12:00 | Mithapukur | 130 | 01:00 | 124 | 13:00
Barapukuria | 134 | 01:00 | 130 | 13:00 | MI_Cement | 131 | 18:00 | 125 | 12:00
Barguna | 136 | 03:00 | 128 | 19:00 | Modern | 0 | 0:00 | 0 | 0:00
Barishal | 132 | 05:00 | 124 | 23:00 | Mogbazar | 135 | 08:00 | 127 | 12:00
Barishal-230 | 132 | 08:00 | 124 | 22:00 | Mongla | 131 | 08:00 | 121 | 00:00
Baroaulia | 139 | 09:00 | 129 | 14:00 | Motijheel | 131 | 08:00 | 120 | 12:00
Baroirhat | 126 | 06:00 | 117 | 12:00 | Muktagacha | 134 | 19:00 | 121 | 02:00
Bashundhara | 134 | 06:00 | 124 | 15:00 | Munshiganj | 130 | 18:00 | 124 | 12:00
BashundharaCement | 130 | 07:00 | 124 | 12:00 | Muradnagar | 127 | 08:00 | 120 | 12:00
Beanibazar | 130 | 08:00 | 122 | 23:00 | Mymensingh | 136 | 23:00 | 112 | 17:00
Benapole | 129 | 08:00 | 118 | 00:00 | Naogaon | 131 | 08:00 | 126 | 00:00
Bhaluka | 130 | 08:00 | 121 | 17:00 | Narail | 131 | 07:00 | 120 | 00:00
Bhandaria | 127 | 17:00 | 114 | 22:00 | Narinda | 131 | 08:00 | 120 | 12:00
Bhangura | 131 | 08:00 | 128 | 01:00 | Narshingdi | 128 | 07:00 | 117 | 00:00
Bheramara | 139 | 08:00 | 132 | 00:00 | Natore | 134 | 08:00 | 47 | 19:00
Bheramara(GK) | 138 | 08:00 | 131 | 01:00 | Nawabganj | 134 | 07:00 | 126 | 12:00
Bhulta | 125 | 09:00 | 120 | 00:00 | Netrakona | 120 | 10:00 | 110 | 15:00
Bog-Sherpur | 134 | 08:00 | 130 | 13:00 | New | 135 | 08:00 | 127 | 16:00
Bogura | 136 | 03:00 | 133 | 17:00 | Niamatpur | 132 | 08:00 | 128 | 00:00
Bogura-230 | 137 | 08:00 | 132 | 13:00 | Noapara | 132 | 07:00 | 122 | 13:00
Brahmanbaria | 130 | 08:00 | 121 | 16:00 | Pabna | 134 | 08:00 | 129 | 02:00
Cantonment | 132 | 08:00 | 125 | 12:00 | Palashbari | 127 | 10:00 | 121 | 13:00
Chandina | 128 | 07:00 | 121 | 12:00 | Panchagarh | 135 | 22:00 | 123 | 04:00
Chandpur | 129 | 09:00 | 118 | 13:00 | Patuakhali | 138 | 02:00 | 130 | 15:00
Chandraghona | 136 | 05:00 | 129 | 12:00 | Payra | 135 | 01:00 | 133 | 05:00
Chapai | 128 | 08:00 | 124 | 22:00 | PHP | 125 | 08:00 | 114 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 131 | 18:00 | 125 | 12:00 | Postogola | 132 | 08:00 | 127 | 12:00
Chauddagram | 125 | 08:00 | 12 | 18:00 | Purbachal | 134 | 05:00 | 126 | 12:00
Chhatak | 131 | 07:00 | 121 | 19:00 | Purbasadipur | 130 | 22:00 | 120 | 11:00
Chowmuhani | 122 | 08:00 | 110 | 13:00 | Rahanpur | 133 | 08:00 | 130 | 00:00
Chuadanga | 130 | 07:00 | 118 | 00:00 | Rahanpur-400 | 133 | 08:00 | 130 | 00:00
Coxsbazar | 120 | 11:00 | 111 | 09:00 | Rahim | 130 | 09:00 | 126 | 02:00
Cumilla(N) | 129 | 06:00 | 122 | 12:00 | Rajbari | 134 | 08:00 | 127 | 00:00
Cumilla(S) | 132 | 04:00 | 119 | 12:00 | Rajendrapur | 131 | 08:00 | 123 | 11:00
Daudkandi | 125 | 07:00 | 118 | 12:00 | Rajshahi | 134 | 08:00 | 128 | 13:00
Dhaka | 135 | 08:00 | 127 | 12:00 | Rajshahi-230 | 135 | 09:00 | 115 | 22:00
Dhamrai | 133 | 06:00 | 128 | 12:00 | Ramganj | 123 | 08:00 | 111 | 13:00
Dhanmondi | 135 | 08:00 | 127 | 12:00 | Rampur | 137 | 06:00 | 129 | 02:00
Dohazari | 135 | 08:00 | 123 | 09:00 | Rampura | 135 | 08:00 | 127 | 15:00
Faridpur | 135 | 08:00 | 129 | 23:00 | Rangamati | 134 | 06:00 | 127 | 15:00
Fatullah | 131 | 18:00 | 125 | 12:00 | Rangpur | 128 | 02:00 | 121 | 13:00
Fenchuganj | 134 | 08:00 | 130 | 16:00 | Ruppur | 138 | 08:00 | 132 | 13:00
Feni | 125 | 08:00 | 115 | 13:00 | Saidpur | 130 | 03:00 | 123 | 12:00
Ghatail | 131 | 19:00 | 122 | 06:00 | Satkhira | 131 | 08:00 | 117 | 00:00
Ghorashal | 134 | 01:00 | 130 | 13:00 | Satmasjid | 132 | 08:00 | 125 | 12:00
Goalpara | 136 | 08:00 | 124 | 02:00 | Savar | 131 | 18:00 | 123 | 15:00
Gollamari | 135 | 08:00 | 126 | 03:00 | SevenRings | 136 | 08:00 | 130 | 12:00
Gopalganj | 134 | 08:00 | 126 | 02:00 | ShahCement | 131 | 18:00 | 125 | 12:00
Gopalganj-400 | 136 | 08:00 | 130 | 02:00 | Shahjadpur | 135 | 05:00 | 132 | 00:00
Gulshan | 135 | 08:00 | 127 | 12:00 | Shahjibazar | 131 | 08:00 | 123 | 18:30
Halishahar | 135 | 23:00 | 128 | 03:00 | Shahmirpur | 136 | 21:00 | 129 | 04:00
Haripur | 130 | 08:00 | 126 | 11:00 | Shariatpur | 134 | 08:00 | 125 | 23:00
HaripurSBU | 130 | 08:00 | 126 | 11:00 | Sherpur | 136 | 18:00 | 120 | 02:00
Hasnabad | 132 | 07:00 | 127 | 12:00 | Shikalbaha | 125 | 21:00 | 118 | 09:00
Hathazari | 137 | 06:00 | 130 | 12:00 | Shikalbaha-230 | 137 | 19:30 | 131 | 01:00
Ishurdi | 139 | 08:00 | 133 | 03:00 | Shitalakhya | 131 | 18:00 | 125 | 12:00
Jaldhaka | 126 | 00:00 | 120 | 12:00 | Sholosohor | 136 | 06:00 | 128 | 12:00
Jamalpur | 141 | 19:00 | 124 | 02:00 | Shyampur | 131 | 18:30 | 125 | 00:00
Jashore | 130 | 08:00 | 120 | 00:00 | Shyampur-230 | 131 | 18:00 | 125 | 12:00
Jhenaidah | 133 | 08:00 | 124 | 00:00 | Siddhirganj | 130 | 08:00 | 126 | 12:00
Jhenaidah-230 | 134 | 09:00 | 124 | 02:00 | Sirajganj | 133 | 09:00 | 128 | 22:00
Joydebpur | 135 | 07:00 | 127 | 15:00 | Sonargaon | 128 | 02:00 | 122 | 12:00
Joypurhat | 128 | 09:00 | 120 | 23:00 | Sreemongol | 131 | 08:00 | 123 | 18:30
Juldah | 137 | 21:00 | 131 | 09:00 | Sreepur | 131 | 06:00 | 128 | 00:00
Kabirpur | 136 | 07:00 | 124 | 16:00 | Srinagar | 134 | 08:00 | 127 | 12:00
Kachua | 127 | 07:00 | 117 | 15:00 | SSM | 140 | 08:00 | 132 | 10:00
Kaliakoir | 138 | 08:00 | 131 | 16:00 | Sunamganj | 127 | 07:00 | 118 | 19:00
Kallyanpur | 129 | 09:00 | 125 | 12:00 | Sylhet | 131 | 08:00 | 124 | 19:00
Kalurghat | 136 | 06:00 | 129 | 14:00 | Sylhet-132 | 130 | 03:00 | 126 | 18:30
Kamrangirchar | 134 | 08:00 | 127 | 12:00 | Tangail | 129 | 18:00 | 122 | 05:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 137 | 22:00 | 124 | 04:00
Kasba | 127 | 08:00 | 119 | 12:00 | TK | 161 | 12:00 | 128 | 15:00
Kazla | 130 | 07:00 | 120 | 13:00 | Tongi | 134 | 08:00 | 130 | 12:00
Keranigonj | 134 | 08:00 | 128 | 12:00 | Ullahpara | 133 | 09:00 | 129 | 03:00
Khagrachori | 135 | 06:00 | 126 | 15:00 | Ullon | 134 | 08:00 | 127 | 12:00
Khulna | 133 | 09:00 | 124 | 00:00 | Uttara | 132 | 21:00 | 123 | 12:00
Khulna(S) | 135 | 08:00 | 126 | 02:00 | UttaraNew | 130 | 13:00 | 123 | 12:00
Khulshi | 136 | 05:00 | 127 | 12:00 | Zigatola | 135 | 08:00 | 128 | 15:00
Kishoreganj | 131 | 08:00 | 118 | 23:00
Kodda | 136 | 08:00 | 123 | 12:00
KSRM | 135 | 07:00 | 127 | 15:00
Kulaura | 133 | 08:00 | 128 | 16:00
Kurigram | 128 | 03:00 | 120 | 19:00
Kushtia | 135 | 08:00 | 128 | 00:00
Lalbag | 134 | 08:00 | 126 | 15:00
Lalmonirhat | 126 | 04:00 | 120 | 19:30
Madanganj | 130 | 07:00 | 124 | 12:00
Madaripur | 134 | 09:00 | 128 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division