## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 11-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-05-2025 | during | 11-05-2025 | during | 11-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 0 | 130 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 250 | 274 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 317 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 17 | 97 | 16 | 102 | 16 | 102
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 61 | 143 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 12 | 10 | 30 | 30 | 30 | 30
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 20 | 22 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 32 | 34 | 52.19 | 52.19 | 52.19 | 52.19 | -
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 287 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 92 | 130 | 135 | 135 | 135 | 135 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 70 | 105 | 105 | 105 | 105
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 32 | 50 | 104 | 104 | 104 | 104
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 63 | 90 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 30 | 0 | 33 | 0 | 33 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 420 | 584 | 584 | 450 | 450 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 250 | 400 | 583 | 583 | 450 | 450 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2382 | 3287 | 5233.9 | 5286.9 | 3929.81 | 3982.81
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 26 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 140 | 146 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 87 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 48 | 53 | 72 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 64 | 102 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 74 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 9 | 2 | 15 | 2 | 15 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 56 | 57 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.13 | 0 | 4.13 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 50 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 17 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 110 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 110 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 108 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 950 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 0 | 4 | 3 | 4 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 371 | 554 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2097 | 2983 | 3411.85 | 3405.72 | 3411.85 | 3405.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 199 | 216 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 0 | 0 | 353.35 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 280 | 345 | 345 | 345 | 345 | 345
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 31 | 33 | 46.94 | 46.94 | 38 | 38 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 42 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 178 | 180 | 195 | 195 | 195 | 195
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 90 | 125 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 26 | 37 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 40 | 70 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 183 | 21 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 44 | 48 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 53 | 53 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 16 | 17.75 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 37 | 113 | 113 | 113 | 113
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 50 | 90 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1475 | 1486 | 2467.24 | 2405.99 | 2018.2 | 1950.2
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 10-05-2025 | during | 11-05-2025 | during | 11-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 19 | 22 | 157.5 | 157.5 | 22 | 22 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 107 | 143 | 200 | 200 | 200 | 200 | -
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 64 | 92 | 115 | 115 | 115 | 115 | -
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 47 | 0 | 49.9 | 0 | 49.9 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 22 | 22 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 16 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 267 | 286 | 601 | 549 | 465.5 | 413.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 37 | 36 | 38 | 38 | 38 | 38 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 120 | 130 | 163 | 163 | 153 | 153 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 20 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 80 | 83 | 83 | 83 | 83
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 170 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 359 | 335 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | Under maintenance
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1171 | 1145 | 1290 | 1290 | 1203 | 1203
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 926 | 780 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 29 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 35 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 248 | 285 | 410 | 410 | 300 | 300 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 88 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 460 | 752 | 1234.2 | 1234.2 | 618 | 618 | Partial Shutdown due to maintenance
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1817 | 1898 | 3610.2 | 3512.2 | 2884 | 2786
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 451 | 453 | 620 | 620 | 620 | 620 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 80 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 105 | 125 | 125 | 113 | 113 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 947 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 100 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 2053 | 2520 | 2787.12 | 2786.12 | 2775.12 | 2774.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 6 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 200 | 203 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 195 | 198 | 220 | 220 | 220 | 220
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 366 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 8 | 15 | 15 | 15 | 15 | -
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 41 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 91 | 93 | 93 | 93 | 93 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 63 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1355 | 1344 | 1347.54 | 1347.54 | 1347.54 | 1347.54 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 103 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 2392 | 2568 | 3086.73 | 2920.53 | 2824.94 | 2658.74
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 50 | 50 | 50 | 55 | 55 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 166 | 160 | 160 | 160 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 51 | 105 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 70 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 32 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 178 | 0 | 181.81 | 0 | 181.81 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 556 | 430 | 690.41 | 472 | 685.41 | 467
System Total |  |  |  |  | 27566.2 | 28624.082 | 14210 | 16603 | 23178.45 | 22628.46 | 20197.83 | 19641.09
Forecast Scenario (11-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 16180 |  | 0 |  | 16180
|  |  |  | 1:00 | 15820 |  | 0 |  | 15820
|  |  |  | 2:00 | 15380 |  | 0 |  | 15380
|  |  |  | 3:00 | 15000 |  | 0 |  | 15000
|  |  |  | 4:00 | 14440 |  | 0 |  | 14440
|  |  |  | 5:00 | 14230 |  | 0 |  | 14230
|  |  |  | 6:00 | 13710 |  | 0 |  | 13710
|  |  |  | 7:00 | 13550 |  | 0 |  | 13550
|  |  |  | 8:00 | 13480 |  | 0 |  | 13480
|  |  |  | 9:00 | 13410 |  | 0 |  | 13410
|  |  |  | 10:00 | 13700 |  | 0 |  | 13700
|  |  |  | 11:00 | 14260 |  | 0 |  | 14260
|  |  |  | 12:00 | 14460 |  | 0 |  | 14460
|  |  |  | 13:00 | 14650 |  | 0 |  | 14650
|  |  |  | 14:00 | 14750 |  | 0 |  | 14750
|  |  |  | 15:00 | 15000 |  | 0 |  | 15000
|  |  |  | 16:00 | 14900 |  | 0 |  | 14900
|  |  |  | 17:00 | 14300 |  | 0 |  | 14300
|  |  |  | 18:00 | 14260 |  | 0 |  | 14260
|  |  |  | 18:30 | 14900 |  | 0 |  | 14900
|  |  |  | 19:00 | 15540 |  | 0 |  | 15540
|  |  |  | 19:30 | 16010 |  | 0 |  | 16010
|  |  |  | 20:00 | 16130 |  | 0 |  | 16130
|  |  |  | 21:00 | 16600 |  | 0 |  | 16600
|  |  |  | 22:00 | 16500 |  | 0 |  | 16500
|  |  |  | 23:00 | 16200 |  | 0 |  | 16200
Probable Maximum Temperature: |  |  | 35.90°C
Probable Maximum Demand at Day Peak: |  |  | 14460.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 16600.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 16600.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 356.45 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:14 hrs on 11-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 10-05-2025 | [28 empty] | Date: | 10-05-2025 | [28 empty] | Date: | 10-05-2025 | [28 empty] | Date: | 10-05-2025 | [28 empty] | Date: | 10-05-2025 | [16 empty] | Date: | 10-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 32 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 130 | 110 | 293 | 55 | 35 | 162 | 0 | 16 | 300 | 250 | 250 | 0 | 35 | 0 | 320 | 0 | 0 | 0 | 160 | 24 | 21 | 0 | 300 | 109 | 32 | 0 | 0 | 0 | 85 | 72 | 54 | 87 | 100 | 0 | 40 | 102 | 38 | 399 | 160 | 0 | 50 | 25 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 180 | 0 | 0 | 350 | 50 | 189 | 34 | 93 | 90 | 180 | 14 | 20 | 114 | 52 | 53 | 0 | 31 | 320 | 0 | 293 | 36 | 30 | 0 | 15 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 36 | 83 | 90 | 21 | 0 | 0 | 9 | 8682 | 831 | 213 | 0 | 31 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 86 | 1355 | 0 | 42 | 0 | 113 | 22 | 93 | 113 | 35 | 34 | 0 | 15 | 0 | 195 | 0 | 190 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 169 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 115 | 220 | 0 | 452 | 1244 | 100 | 7264 | 15946 | 78.42
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 28 | 17 | 130 | 94 | 293 | 55 | 35 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 35 | 0 | 295 | 0 | 0 | 0 | 160 | 24 | 21 | 0 | 300 | 110 | 95 | 1 | 0 | 0 | 85 | 73 | 35 | 87 | 100 | 0 | 40 | 108 | 36 | 400 | 54 | 0 | 34 | 26 | 87 | 145 | 0 | 0 | 0 | 1227 | 0 | 51 | 125 | 180 | 0 | 0 | 330 | 51 | 183 | 34 | 93 | 80 | 162 | 8 | 20 | 114 | 48 | 53 | 0 | 24 | 305 | 0 | 290 | 36 | 30 | 0 | 17 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 20 | 46 | 91 | 22 | 0 | 0 | 12 | 8263 | 929 | 212 | 0 | 31 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 87 | 1359 | 0 | 42 | 0 | 113 | 13 | 93 | 113 | 34 | 43 | 0 | 15 | 0 | 190 | 0 | 185 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 167 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 52 | 307 | 11 | 100 | 180 | 0 | 452 | 1244 | 100 | 7318 | 15581 | 78.41
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 130 | 64 | 245 | 55 | 17 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 35 | 0 | 256 | 0 | 0 | 0 | 160 | 25 | 21 | 0 | 300 | 90 | 196 | 23 | 0 | 0 | 85 | 48 | 0 | 87 | 100 | 0 | 40 | 110 | 36 | 402 | 17 | 0 | 26 | 26 | 87 | 145 | 0 | 0 | 0 | 1228 | 0 | 51 | 125 | 180 | 0 | 0 | 325 | 50 | 188 | 31 | 78 | 70 | 163 | 9 | 20 | 114 | 46 | 53 | 0 | 24 | 300 | 0 | 288 | 36 | 30 | 0 | 48 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 17 | 46 | 92 | 22 | 0 | 0 | 12 | 8114 | 928 | 221 | 0 | 20 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 88 | 1372 | 0 | 42 | 0 | 113 | 0 | 0 | 35 | 34 | 0 | 0 | 15 | 0 | 166 | 0 | 188 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 167 | 51 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 10 | 93 | 180 | 0 | 453 | 1244 | 81 | 7053 | 15167 | 78.4
03:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 90 | 63 | 195 | 55 | 0 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 35 | 0 | 287 | 0 | 0 | 0 | 160 | 25 | 21 | 0 | 300 | 53 | 15 | 48 | 0 | 0 | 68 | 48 | 0 | 87 | 100 | 0 | 40 | 110 | 36 | 402 | 0 | 0 | 26 | 26 | 87 | 148 | 0 | 0 | 0 | 1229 | 0 | 51 | 125 | 182 | 0 | 0 | 345 | 50 | 192 | 31 | 88 | 70 | 164 | 9 | 20 | 114 | 44 | 53 | 0 | 24 | 305 | 0 | 296 | 36 | 30 | 0 | 72 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 17 | 47 | 92 | 22 | 0 | 0 | 12 | 7888 | 929 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 53 | 1364 | 0 | 43 | 0 | 113 | 0 | 0 | 0 | 34 | 0 | 0 | 15 | 0 | 196 | 0 | 191 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 168 | 49 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 100 | 220 | 0 | 453 | 1244 | 63 | 6944 | 14832 | 78.39
04:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 74 | 63 | 45 | 55 | 0 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 35 | 0 | 257 | 0 | 0 | 0 | 125 | 25 | 21 | 0 | 300 | 17 | 0 | 50 | 0 | 0 | 51 | 48 | 0 | 87 | 88 | 0 | 40 | 110 | 36 | 401 | 0 | 0 | 0 | 8 | 87 | 148 | 0 | 0 | 0 | 1226 | 0 | 51 | 127 | 182 | 0 | 0 | 345 | 50 | 185 | 31 | 93 | 70 | 166 | 9 | 20 | 114 | 44 | 34 | 0 | 24 | 310 | 0 | 287 | 36 | 30 | 0 | 131 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 17 | 47 | 91 | 22 | 0 | 0 | 12 | 7567 | 928 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 17 | 1364 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 197 | 0 | 191 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 167 | 49 | 70 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 453 | 1244 | 63 | 6705 | 14272 | 78.38
05:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 17 | 78 | 63 | 45 | 55 | 0 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 35 | 0 | 278 | 0 | 0 | 0 | 125 | 25 | 21 | 0 | 300 | 17 | 0 | 51 | 0 | 0 | 51 | 48 | 0 | 87 | 88 | 0 | 40 | 110 | 36 | 401 | 0 | 0 | 0 | 8 | 87 | 148 | 0 | 0 | 0 | 1150 | 0 | 51 | 127 | 182 | 0 | 0 | 300 | 51 | 196 | 31 | 94 | 70 | 170 | 9 | 20 | 114 | 42 | 34 | 0 | 24 | 315 | 0 | 297 | 36 | 30 | 0 | 125 | 8 | 0 | 80 | 28 | 0 | 16 | 172 | 17 | 46 | 91 | 22 | 0 | 0 | 12 | 7464 | 928 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618 | 17 | 1361 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 197 | 0 | 191 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 169 | 48 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 112 | 220 | 0 | 453 | 1150 | 63 | 6622 | 14086 | 78.37
06:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 17 | 17 | 78 | 63 | 45 | 55 | 0 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 35 | 0 | 280 | 0 | 0 | 2 | 125 | 25 | 21 | 0 | 300 | 17 | 0 | 50 | 0 | 0 | 51 | 48 | 0 | 74 | 88 | 0 | 40 | 110 | 38 | 404 | 0 | 0 | 0 | 8 | 87 | 149 | 0 | 0 | 0 | 1005 | 1 | 51 | 128 | 182 | 0 | 0 | 300 | 52 | 191 | 34 | 80 | 70 | 150 | 9 | 20 | 114 | 40 | 34 | 4 | 17 | 300 | 0 | 303 | 36 | 30 | 0 | 122 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 17 | 46 | 103 | 22 | 0 | 3 | 12 | 7206 | 929 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 531 | 38 | 1357 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 3 | 197 | 0 | 191 | 0 | 0 | 0 | 330 | 0 | 1 | 0 | 164 | 49 | 35 | 1 | 49 | 0 | 0 | 1 | 10 | 1 | 0 | 250 | 10 | 111 | 180 | 0 | 453 | 1022 | 63 | 6278 | 13484 | 78.36
07:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 78 | 64 | 45 | 55 | 17 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 0 | 0 | 321 | 0 | 0 | 7 | 125 | 24 | 21 | 0 | 300 | 17 | 0 | 50 | 0 | 0 | 51 | 48 | 0 | 74 | 88 | 1 | 40 | 110 | 38 | 402 | 0 | 0 | 0 | 8 | 87 | 148 | 0 | 0 | 0 | 1000 | 5 | 51 | 125 | 182 | 0 | 0 | 300 | 52 | 193 | 34 | 58 | 75 | 155 | 8 | 20 | 114 | 38 | 34 | 16 | 17 | 315 | 0 | 292 | 36 | 30 | 0 | 117 | 8 | 0 | 80 | 30 | 0 | 16 | 172 | 17 | 66 | 118 | 22 | 0 | 12 | 12 | 6976 | 928 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 512 | 88 | 1372 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 198 | 0 | 192 | 0 | 0 | 0 | 331 | 0 | 1 | 0 | 163 | 49 | 35 | 6 | 49 | 0 | 0 | 2 | 41 | 1 | 0 | 250 | 9 | 113 | 180 | 0 | 455 | 1000 | 63 | 6390 | 13366 | 78.35
08:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 84 | 64 | 45 | 55 | 17 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 0 | 0 | 316 | 0 | 0 | 14 | 125 | 23 | 21 | 0 | 300 | 17 | 0 | 50 | 0 | 0 | 51 | 48 | 0 | 74 | 100 | 2 | 40 | 110 | 10 | 401 | 0 | 0 | 0 | 8 | 87 | 147 | 0 | 0 | 0 | 956 | 9 | 51 | 115 | 182 | 0 | 0 | 300 | 53 | 198 | 32 | 50 | 75 | 148 | 9 | 20 | 114 | 34 | 34 | 32 | 24 | 305 | 0 | 292 | 36 | 30 | 0 | 117 | 8 | 0 | 80 | 30 | 0 | 16 | 173 | 17 | 65 | 119 | 21 | 1 | 24 | 12 | 6928 | 879 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 486 | 89 | 1364 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 24 | 197 | 0 | 200 | 0 | 0 | 0 | 342 | 0 | 2 | 0 | 160 | 51 | 35 | 14 | 49 | 0 | 0 | 4 | 87 | 1 | 0 | 250 | 8 | 115 | 180 | 0 | 454 | 950 | 63 | 6405 | 13333 | 78.34
09:00 | 8 | 34 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 96 | 63 | 45 | 55 | 35 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 0 | 0 | 315 | 0 | 0 | 21 | 90 | 22 | 21 | 0 | 300 | 17 | 0 | 53 | 0 | 0 | 68 | 48 | 0 | 74 | 100 | 0 | 40 | 85 | 2 | 372 | 0 | 0 | 0 | 0 | 68 | 145 | 0 | 0 | 0 | 953 | 14 | 51 | 118 | 182 | 0 | 0 | 300 | 51 | 184 | 32 | 51 | 75 | 151 | 9 | 20 | 70 | 38 | 34 | 47 | 24 | 300 | 0 | 305 | 36 | 30 | 0 | 117 | 8 | 0 | 80 | 30 | 0 | 16 | 173 | 17 | 65 | 118 | 19 | 2 | 35 | 12 | 6859 | 878 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 466 | 90 | 1361 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 38 | 199 | 0 | 201 | 0 | 0 | 0 | 320 | 0 | 4 | 0 | 166 | 51 | 35 | 21 | 49 | 0 | 0 | 5 | 126 | 1 | 0 | 250 | 7 | 90 | 180 | 0 | 452 | 951 | 35 | 6415 | 13274 | 78.33
10:00 | 8 | 34 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 95 | 63 | 76 | 55 | 35 | 54 | 0 | 16 | 300 | 250 | 250 | 0 | 0 | 0 | 305 | 0 | 0 | 27 | 90 | 22 | 20 | 0 | 300 | 0 | 0 | 56 | 0 | 0 | 66 | 55 | 0 | 74 | 100 | 4 | 40 | 51 | 2 | 370 | 0 | 0 | 0 | 0 | 51 | 143 | 0 | 0 | 0 | 950 | 7 | 51 | 112 | 180 | 0 | 0 | 340 | 46 | 208 | 33 | 51 | 75 | 156 | 9 | 17 | 70 | 40 | 34 | 58 | 23 | 310 | 0 | 335 | 37 | 30 | 0 | 118 | 8 | 0 | 80 | 30 | 0 | 16 | 173 | 17 | 65 | 118 | 17 | 2 | 44 | 12 | 6942 | 927 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 460 | 88 | 1353 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 48 | 201 | 0 | 200 | 0 | 0 | 0 | 372 | 0 | 4 | 0 | 167 | 51 | 35 | 27 | 49 | 0 | 0 | 7 | 157 | 1 | 0 | 250 | 6 | 100 | 220 | 0 | 453 | 945 | 0 | 6593 | 13535 | 78.32
11:00 | 17 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 95 | 61 | 244 | 55 | 35 | 54 | 0 | 36 | 300 | 250 | 250 | 0 | 0 | 0 | 303 | 0 | 0 | 30 | 160 | 15 | 20 | 0 | 300 | 0 | 0 | 52 | 0 | 4 | 67 | 63 | 0 | 67 | 100 | 4 | 40 | 51 | 2 | 371 | 108 | 0 | 0 | 1 | 51 | 143 | 0 | 0 | 0 | 950 | 17 | 51 | 108 | 180 | 0 | 0 | 295 | 40 | 203 | 31 | 51 | 75 | 185 | 8 | 17 | 97 | 40 | 43 | 65 | 23 | 320 | 0 | 331 | 37 | 30 | 0 | 120 | 0 | 0 | 79 | 30 | 0 | 16 | 173 | 17 | 65 | 117 | 17 | 2 | 48 | 12 | 7360 | 926 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 461 | 88 | 1366 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 53 | 182 | 0 | 197 | 0 | 0 | 0 | 359 | 0 | 5 | 0 | 166 | 51 | 35 | 35 | 49 | 0 | 0 | 8 | 173 | 1 | 0 | 250 | 8 | 115 | 220 | 0 | 453 | 945 | 0 | 6637 | 13997 | 78.31
12:00 | 17 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 92 | 61 | 287 | 55 | 35 | 63 | 0 | 32 | 300 | 250 | 250 | 0 | 0 | 0 | 300 | 0 | 0 | 30 | 160 | 12 | 20 | 0 | 300 | 0 | 0 | 56 | 0 | 11 | 64 | 48 | 0 | 74 | 100 | 4 | 40 | 51 | 3 | 371 | 108 | 0 | 0 | 8 | 51 | 140 | 0 | 0 | 0 | 950 | 18 | 51 | 90 | 178 | 0 | 0 | 280 | 42 | 199 | 31 | 50 | 40 | 183 | 9 | 17 | 114 | 44 | 53 | 68 | 26 | 320 | 0 | 359 | 37 | 30 | 0 | 120 | 8 | 0 | 78 | 30 | 0 | 16 | 173 | 16 | 64 | 107 | 19 | 2 | 47 | 12 | 7392 | 926 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 460 | 88 | 1355 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 57 | 200 | 0 | 195 | 0 | 0 | 0 | 414 | 0 | 5 | 0 | 166 | 51 | 70 | 32 | 51 | 0 | 0 | 8 | 178 | 1 | 0 | 307 | 7 | 120 | 220 | 0 | 451 | 947 | 0 | 6818 | 14210 | 78.3
13:00 | 17 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 89 | 60 | 293 | 55 | 35 | 72 | 0 | 48 | 300 | 250 | 250 | 0 | 30 | 0 | 297 | 0 | 0 | 30 | 160 | 11 | 20 | 0 | 300 | 0 | 0 | 50 | 0 | 13 | 64 | 0 | 0 | 74 | 100 | 4 | 40 | 51 | 12 | 371 | 108 | 0 | 0 | 8 | 51 | 141 | 0 | 0 | 0 | 950 | 17 | 51 | 60 | 174 | 0 | 0 | 280 | 38 | 206 | 29 | 51 | 50 | 53 | 8 | 17 | 114 | 50 | 53 | 64 | 35 | 315 | 0 | 320 | 35 | 30 | 0 | 121 | 8 | 0 | 77 | 30 | 0 | 16 | 172 | 17 | 64 | 104 | 19 | 2 | 46 | 12 | 7207 | 926 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 512 | 87 | 1369 | 0 | 0 | 0 | 112 | 0 | 0 | 20 | 0 | 0 | 98 | 0 | 54 | 197 | 0 | 193 | 0 | 0 | 0 | 391 | 0 | 5 | 0 | 166 | 51 | 115 | 32 | 110 | 0 | 0 | 7 | 179 | 1 | 0 | 307 | 7 | 105 | 220 | 0 | 452 | 978 | 0 | 7032 | 14239 | 78.29
14:00 | 17 | 17 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 85 | 60 | 290 | 55 | 35 | 90 | 0 | 50 | 300 | 282 | 250 | 0 | 35 | 0 | 296 | 0 | 0 | 25 | 160 | 12 | 21 | 0 | 300 | 0 | 0 | 50 | 0 | 9 | 97 | 4 | 0 | 74 | 100 | 4 | 40 | 51 | 6 | 370 | 108 | 0 | 8 | 8 | 51 | 140 | 0 | 0 | 0 | 950 | 16 | 51 | 40 | 164 | 0 | 0 | 280 | 38 | 198 | 28 | 50 | 50 | 17 | 8 | 17 | 114 | 52 | 53 | 56 | 27 | 320 | 0 | 360 | 35 | 30 | 0 | 120 | 8 | 0 | 76 | 30 | 0 | 16 | 172 | 16 | 62 | 102 | 20 | 0 | 40 | 12 | 7191 | 927 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 512 | 87 | 1363 | 0 | 0 | 0 | 113 | 0 | 0 | 100 | 0 | 8 | 86 | 0 | 47 | 197 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 5 | 0 | 166 | 50 | 106 | 26 | 108 | 0 | 0 | 7 | 161 | 1 | 0 | 307 | 10 | 115 | 220 | 0 | 454 | 1000 | 0 | 7116 | 14307 | 78.28
15:00 | 17 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 17 | 17 | 80 | 59 | 288 | 55 | 35 | 90 | 0 | 50 | 300 | 290 | 250 | 0 | 35 | 0 | 298 | 0 | 0 | 19 | 160 | 12 | 21 | 0 | 300 | 0 | 0 | 50 | 0 | 7 | 98 | 34 | 0 | 75 | 100 | 3 | 40 | 51 | 1 | 370 | 160 | 0 | 41 | 0 | 51 | 142 | 0 | 0 | 0 | 1100 | 12 | 51 | 63 | 153 | 0 | 0 | 330 | 30 | 204 | 1 | 51 | 70 | 17 | 8 | 17 | 114 | 52 | 53 | 43 | 28 | 320 | 0 | 328 | 35 | 20 | 0 | 120 | 0 | 0 | 73 | 30 | 0 | 16 | 170 | 0 | 62 | 94 | 20 | 2 | 30 | 12 | 7464 | 927 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 512 | 87 | 1362 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 39 | 67 | 0 | 37 | 196 | 0 | 192 | 0 | 0 | 0 | 378 | 0 | 4 | 0 | 163 | 51 | 96 | 22 | 107 | 0 | 0 | 6 | 121 | 1 | 0 | 307 | 10 | 115 | 220 | 0 | 453 | 1055 | 0 | 7074 | 14538 | 78.27
16:00 | 32 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 17 | 17 | 75 | 59 | 272 | 55 | 35 | 90 | 0 | 50 | 300 | 275 | 250 | 0 | 35 | 0 | 300 | 0 | 0 | 12 | 160 | 13 | 21 | 0 | 300 | 0 | 0 | 55 | 0 | 8 | 98 | 38 | 0 | 75 | 100 | 2 | 40 | 34 | 2 | 450 | 160 | 0 | 50 | 1 | 17 | 143 | 0 | 0 | 0 | 1100 | 7 | 51 | 87 | 177 | 0 | 0 | 345 | 3 | 215 | 31 | 54 | 70 | 17 | 24 | 17 | 114 | 48 | 53 | 28 | 32 | 310 | 0 | 301 | 35 | 20 | 0 | 121 | 8 | 0 | 74 | 30 | 0 | 16 | 171 | 0 | 62 | 93 | 21 | 1 | 19 | 12 | 7516 | 926 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 550 | 17 | 1361 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 30 | 43 | 0 | 23 | 197 | 0 | 192 | 0 | 0 | 0 | 336 | 0 | 3 | 0 | 159 | 51 | 98 | 14 | 100 | 0 | 0 | 3 | 82 | 1 | 0 | 307 | 10 | 105 | 220 | 0 | 453 | 1100 | 0 | 6915 | 14431 | 78.26
17:00 | 49 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 17 | 17 | 86 | 59 | 272 | 55 | 35 | 90 | 0 | 50 | 300 | 275 | 250 | 0 | 35 | 0 | 310 | 0 | 0 | 5 | 160 | 16 | 21 | 0 | 300 | 0 | 0 | 56 | 0 | 6 | 100 | 38 | 0 | 75 | 88 | 0 | 40 | 34 | 6 | 450 | 160 | 0 | 50 | 21 | 17 | 143 | 0 | 0 | 0 | 1110 | 3 | 51 | 107 | 178 | 0 | 0 | 345 | 24 | 214 | 32 | 69 | 70 | 17 | 26 | 0 | 114 | 46 | 53 | 13 | 26 | 300 | 0 | 302 | 35 | 20 | 0 | 134 | 8 | 0 | 78 | 20 | 0 | 16 | 170 | 0 | 62 | 93 | 21 | 0 | 9 | 12 | 7586 | 926 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 557 | 17 | 1352 | 0 | 0 | 0 | 113 | 4 | 85 | 113 | 12 | 30 | 20 | 0 | 10 | 199 | 0 | 160 | 0 | 0 | 0 | 324 | 0 | 1 | 0 | 162 | 48 | 103 | 6 | 108 | 0 | 0 | 2 | 40 | 1 | 0 | 250 | 10 | 90 | 180 | 0 | 452 | 1100 | 0 | 6717 | 14303 | 78.25
18:00 | 85 | 52 | 30 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 22 | 17 | 107 | 112 | 275 | 55 | 35 | 90 | 0 | 50 | 300 | 290 | 250 | 0 | 35 | 0 | 270 | 0 | 0 | 1 | 160 | 13 | 21 | 0 | 300 | 0 | 0 | 57 | 0 | 3 | 100 | 49 | 0 | 88 | 88 | 0 | 80 | 34 | 2 | 400 | 160 | 0 | 50 | 26 | 17 | 144 | 0 | 0 | 0 | 1050 | 0 | 51 | 125 | 178 | 0 | 0 | 340 | 41 | 212 | 31 | 71 | 70 | 17 | 34 | 16 | 114 | 38 | 53 | 2 | 29 | 300 | 0 | 350 | 35 | 40 | 0 | 129 | 8 | 0 | 78 | 20 | 0 | 16 | 170 | 2 | 84 | 112 | 21 | 0 | 2 | 12 | 7787 | 926 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 508 | 17 | 1357 | 0 | 48 | 0 | 113 | 5 | 89 | 113 | 27 | 31 | 4 | 0 | 2 | 150 | 0 | 160 | 0 | 0 | 0 | 347 | 0 | 1 | 0 | 119 | 47 | 113 | 1 | 113 | 0 | 0 | 0 | 8 | 0 | 0 | 250 | 9 | 100 | 180 | 0 | 454 | 960 | 0 | 6476 | 14263 | 78.24
19:00 | 93 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 54 | 17 | 127 | 138 | 260 | 55 | 35 | 90 | 0 | 50 | 450 | 265 | 400 | 0 | 35 | 0 | 316 | 0 | 0 | 0 | 160 | 12 | 21 | 0 | 400 | 6 | 15 | 56 | 0 | 1 | 102 | 54 | 0 | 100 | 88 | 0 | 40 | 40 | 4 | 553 | 160 | 0 | 50 | 26 | 32 | 145 | 0 | 0 | 0 | 1224 | 0 | 51 | 127 | 178 | 0 | 0 | 340 | 49 | 212 | 32 | 90 | 70 | 17 | 36 | 16 | 114 | 44 | 53 | 0 | 29 | 315 | 0 | 340 | 37 | 40 | 0 | 132 | 8 | 0 | 80 | 30 | 0 | 16 | 170 | 17 | 91 | 121 | 22 | 0 | 0 | 12 | 8668 | 876 | 287 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 547 | 17 | 1362 | 0 | 48 | 0 | 113 | 5 | 91 | 113 | 37 | 41 | 0 | 12 | 0 | 171 | 0 | 195 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 157 | 47 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 105 | 220 | 0 | 454 | 1020 | 6 | 6882 | 15550 | 78.23
19:30 | 97 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 54 | 17 | 127 | 140 | 260 | 55 | 35 | 90 | 0 | 50 | 450 | 258 | 450 | 0 | 35 | 0 | 315 | 0 | 0 | 0 | 160 | 12 | 22 | 0 | 450 | 53 | 30 | 56 | 0 | 1 | 102 | 53 | 0 | 100 | 100 | 0 | 40 | 54 | 7 | 552 | 160 | 0 | 50 | 26 | 87 | 147 | 0 | 0 | 0 | 1226 | 0 | 51 | 121 | 178 | 0 | 0 | 345 | 49 | 215 | 32 | 90 | 70 | 17 | 36 | 14 | 114 | 42 | 53 | 0 | 29 | 295 | 0 | 300 | 37 | 40 | 0 | 130 | 8 | 0 | 80 | 30 | 0 | 16 | 170 | 17 | 91 | 131 | 22 | 0 | 0 | 12 | 8889 | 876 | 282 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 577 | 17 | 1364 | 0 | 46 | 0 | 113 | 5 | 91 | 113 | 37 | 41 | 0 | 12 | 0 | 204 | 0 | 196 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 157 | 50 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 105 | 220 | 0 | 454 | 1240 | 17 | 7129 | 16018
20:00 | 97 | 55 | 16 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 54 | 17 | 129 | 142 | 294 | 55 | 35 | 90 | 0 | 50 | 450 | 264 | 400 | 0 | 35 | 0 | 316 | 0 | 0 | 0 | 160 | 10 | 22 | 0 | 420 | 69 | 50 | 57 | 0 | 0 | 102 | 53 | 5 | 100 | 100 | 0 | 40 | 102 | 2 | 552 | 160 | 0 | 50 | 26 | 87 | 147 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 178 | 0 | 0 | 345 | 49 | 215 | 29 | 90 | 70 | 17 | 36 | 18 | 114 | 48 | 53 | 0 | 29 | 290 | 0 | 380 | 36 | 40 | 0 | 129 | 8 | 0 | 80 | 28 | 0 | 16 | 170 | 17 | 92 | 143 | 21 | 0 | 0 | 12 | 9025 | 876 | 282 | 0 | 36 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 17 | 1361 | 0 | 48 | 0 | 113 | 5 | 91 | 113 | 37 | 41 | 0 | 15 | 0 | 205 | 0 | 199 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 158 | 47 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 11 | 105 | 180 | 0 | 452 | 1240 | 60 | 7176 | 16201 | 78.22
21:00 | 97 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 54 | 17 | 130 | 143 | 294 | 55 | 35 | 90 | 0 | 50 | 450 | 274 | 400 | 0 | 35 | 0 | 317 | 0 | 0 | 0 | 160 | 10 | 22 | 0 | 420 | 110 | 50 | 57 | 0 | 0 | 102 | 53 | 17 | 100 | 88 | 0 | 40 | 110 | 9 | 554 | 160 | 0 | 50 | 26 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 180 | 0 | 0 | 345 | 50 | 216 | 33 | 90 | 70 | 21 | 37 | 16 | 114 | 48 | 53 | 0 | 37 | 310 | 0 | 335 | 36 | 40 | 0 | 130 | 8 | 0 | 80 | 20 | 0 | 16 | 170 | 17 | 92 | 143 | 22 | 0 | 0 | 12 | 9187 | 780 | 285 | 0 | 29 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 17 | 1344 | 0 | 48 | 0 | 113 | 6 | 91 | 113 | 37 | 41 | 0 | 8 | 0 | 203 | 0 | 198 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 160 | 50 | 115 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 80 | 307 | 11 | 105 | 220 | 0 | 453 | 1244 | 100 | 7416 | 16603 | 78.21
22:00 | 50 | 72 | 34 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 36 | 17 | 130 | 143 | 294 | 55 | 17 | 90 | 0 | 50 | 300 | 295 | 280 | 0 | 35 | 0 | 318 | 0 | 0 | 0 | 160 | 9.5 | 22 | 0 | 300 | 53 | 16 | 57 | 0 | 0 | 102 | 53 | 17 | 100 | 88 | 0 | 40 | 51 | 15 | 554 | 160 | 0 | 50 | 26 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 178 | 0 | 0 | 345 | 51 | 213 | 36 | 89 | 70 | 54 | 36 | 20 | 114 | 48 | 53 | 0 | 37 | 305 | 0 | 335 | 36 | 40 | 0 | 131 | 8 | 0 | 80 | 20 | 0 | 16 | 170 | 17 | 92 | 137 | 22 | 0 | 0 | 12 | 8857.5 | 780 | 275 | 0 | 29 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 842 | 17 | 1345.79 | 0 | 46 | 0 | 113 | 15 | 91 | 113 | 37 | 41 | 0 | 8 | 0 | 205 | 0 | 200 | 0 | 0 | 0 | 406 | 0 | 0 | 0 | 166 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 11 | 115 | 220 | 0 | 453 | 1244 | 63 | 7511.79 | 16369.29 | 78.2
23:00 | 32 | 72 | 34 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 23 | 17 | 130 | 127 | 294 | 55 | 0 | 90 | 0 | 50 | 300 | 298 | 250 | 0 | 17 | 0 | 250 | 0 | 0 | 0 | 160 | 9.2 | 22 | 0 | 300 | 53 | 50 | 57 | 0 | 0 | 102 | 53 | 54.36 | 100 | 88 | 0 | 40 | 76 | 11 | 552 | 160 | 0 | 50 | 25.5 | 87 | 146 | 0 | 0 | 0 | 1224 | 0 | 51 | 135 | 178 | 0 | 0 | 345 | 52 | 213 | 36 | 66 | 70 | 59 | 37 | 20 | 114 | 48 | 52.2 | 0 | 37 | 325 | 0 | 318 | 36 | 30 | 0 | 133 | 8 | 0 | 80 | 20 | 0 | 16 | 170 | 17 | 91 | 137 | 22 | 0 | 0 | 12 | 8789.26 | 780 | 270 | 0 | 30 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 17 | 1354.81 | 0 | 46 | 0 | 113 | 15 | 91 | 113 | 36 | 41 | 0 | 8 | 0 | 200 | 0 | 200 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 166 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 11 | 115 | 220 | 0 | 452 | 1244 | 35 | 7585.81 | 16375.07 | 78.19
Total KWH | 717408 | 962880 | 509280 | 0 | 0 | 0 | 0 | 0 | 3942000 | 0 | 0 | 582840 | 428040 | 2441232 | 1989600 | 4978538 | 1331143 | 594594 | 1743840 | 0 | 785280 | 7838500 | 6446691 | 6595909 | 0 | 601945 | 0 | 7184994 | 0 | 0 | 219636 | 3528000 | 413400 | 494280 | 0 | 7876818.18 | 800400 | 501818 | 1214400 | 0 | 66240 | 1917311 | 1142640 | 224764 | 1991040 | 2295360 | 28305 | 936800 | 2015636 | 404160 | 10407272.73 | 2144436 | 0 | 593280 | 324619.2 | 1680255 | 3400741 | 0 | 0 | 0 | 26383634 | 129330 | 1166952 | 2753309 | 4282182 | 0 | 0 | 7844000 | 1065600 | 4945000 | 752832 | 1672320 | 1657930 | 2381280 | 424200 | 404580 | 2657340 | 1087680 | 1108368 | 496382 | 685128 | 7539500 | 0 | 8107000 | 857000 | 678480 | 0 | 2788855 | 171312 | 0 | 1887360 | 637920 | 0 | 377000 | 4038510 | 366480 | 1544400 | 2632800 | 477120 | 15100 | 352380 | 294480 | 188960070.11 | 21635636 | 6020640 | 0 | 181920 | 206848 | 0 | 0 | 0 | 0 | 0 | 0 | 727200 | 14589095 | 1306080 | 32674498 | 0 | 466000 | 0 | 2301600 | 84710 | 773152 | 1446240 | 309070 | 434573 | 773450 | 120310 | 396752 | 4733818 | 0 | 4801764 | 0 | 0 | 0 | 8594472 | 0 | 33300 | 0 | 4001000 | 1164218 | 2049943 | 232507 | 2141865 | 0 | 0 | 50734.56 | 1385280 | 4986 | 374304 | 6939000 | 234678 | 2587000 | 5110430 | 0 | 10887272 | 26871272.73 | 916800 | 167562418.29 | 356522488.4

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 10-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14210 | MW | 12:00 Hr. | Energy Generated |  |  | 356.5225 |  | MKWHr.
| Day Peak Demand |  |  | 14466.03 | MW | 12:00 Hr. | Energy Unserverd |  |  | 7.163 |  | MKWHr.
| Evening Peak Generation |  |  | 16603 | MW | 21:00 Hr. | Energy Demand |  |  | 363.6855 |  | MKWHr.
| Evening Peak Demand |  |  | 16999.06 | MW | 21:00 Hr. | Maximum Temperature |  |  | 38 |  | °C
| Minimum Generation of the Day |  |  | 13274 | MW | 09:00 Hr. | Total Gas Supplied |  |  | 971.34 |  | MMCFD
| Maximum Generation of the Day |  |  | 16603 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 7.7633 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.7926 | 0 | 21.1946 | 0 | 0 | 0.21964 | 0 | 0 | 62.2068 | Gas | 126.3594 | Gas | 455043597.2706
| Chattogram Zone |  |  | 3.8049 | 36.7909 | 16.846 | 0 | 0.9368 | 0.15763 | 0 | 0.06624 | 58.6024 | Coal | 101.2428 | Coal | 647766823.6065
| Cumilla Zone |  |  | 22.1191 | 0 | 11.6819 | 0 | 0 | 0.49638 | 1.0877 | 0 | 35.3851 | HFO | 67.6741 | HFO | 1275672557.184
| Mymensingh Zone |  |  | 0.47712 | 0 | 4.8382 | 0 | 0 | 0.36748 | 0 | 0 | 5.6828 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 27.0829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0829 | Hydro | 0.9368 | Hydro | 93680
| Khulna Zone |  |  | 6.0206 | 14.5891 | 1.6948 | 0 | 0 | 0.7272 | 21.6356 | 0 | 44.6674 | Solar | 4.8453 | Solar | 79021121.8116
| Barishal Zone |  |  | 7.9321 | 44.6975 | 1.2911 | 0 | 0 | 0.004986 | 0 | 0 | 53.9257 | Import | 55.3978 | Import | 309207308
| Rajshahi Zone |  |  | 18.1301 | 0 | 5.9357 | 0 | 0 | 1.2035 | 32.6745 | 0 | 57.9437 | Wind | 0.06624 | Wind | 969753.6
| Rangpur Zone |  |  | 0 | 5.1652 | 4.1918 | 0 | 0 | 1.6685 | 0 | 0 | 11.0255
| Total |  |  | 126.3594 | 101.2428 | 67.6741 | 0 | 0.9368 | 4.8453 | 55.3978 | 0.06624 | 356.5225
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 455043597.2706 |  | Hydro | 93680
|  |  |  | Coal | 647766823.6065 |  | Solar | 79021121.8116
|  |  |  | HFO | 1275672557.184 |  | Import | 309207308
|  |  |  | HSD | 0 |  | Wind | 969753.6
[5 empty] | Total: | 276,77,74,841 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6356 | Peak Hr Flow | 780.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 36308600 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.6745 | Peak Hr Flow | 1344.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 596 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0877 | Peak Hr Flow | 48.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 796 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 55.3978 | Peak Hr Flow | 2172.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 55 |  | 5878
|  |  |  | Chattogram |  | 0 |  | 1603
|  |  |  | Cumilla |  | 0 |  | 1402
|  |  |  | Mymensingh |  | 272 |  | 1432
|  |  |  | Sylhet |  | 0 |  | 661
|  |  |  | Khulna |  | 52 |  | 2018
|  |  |  | Barishal |  | 0 |  | 555
|  |  |  | Rajshahi |  | 0 |  | 1820
|  |  |  | Rangpur |  | 0 |  | 1044
|  |  |  | Total |  | 379 |  | 16413
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 735.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:13 | 17:28 | Bhaluka 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to T2 33kv bushing clamp change.
| 08:14 | 17:27 | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to T2 33kv bushing clamp change
| 08:19 | 17:25 | Sunamganj 132/33kV S/S Tr-1 LT Scheduled S/D Due to 132 KV Transformer-1 Shutdown Due to | [7 empty] | 12.0MW load
|  |  | BPDB, 33 KV Sunamganj and Derai Feeder Bay Extension work. | [7 empty] | interrup.
| 08:22 | 17:21 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to 132 KV Transformer-1 Shutdown due to | [7 empty] | 12.0MW load
|  |  | BPDB, 33 KV Sunamganj and Derai Feeder Bay-Extension. | [7 empty] | interrup.
| 08:25 | 17:35 | Bheramara(GK) 132/33kV S/S TR-3 LT Scheduled S/D Due to PBS 33kV feeder underground from | [7 empty] | 52.0MW load interrup.
Overhead Shifting.
| 08:26 | 17:33 | Bheramara(GK) 132/33kV S/S TR-3 HT Scheduled S/D Due to PBS 33kV feeder underground from | [7 empty] | 52.0MW load
|  |  | Overhead Shifting. | [7 empty] | interrup.
| 08:40 | 16:53 | Mirpur 132/33kV S/S RPC Main Scheduled S/D Due to RPC Bank Unit# 2 ractor reaplacement work.
| 08:52 |  | Narail 132/33kV S/S TR1 (403-T) HT Scheduled S/D Due to 33 kb Bay Extension | [7 empty] | 20.0MW load interrup.
| 08:55 | 10:36 | Chandraghona 132/33kV S/S TR-02(416T) HT Forced S/D Due to টি-০২ ২৫/৪১ এমভিএ (৪১৬টি) এর
৩৩ কেভি ব্লু- ফেইজ এর নীচের কানেক্টরে সংরক্ষণ ও মেরামত কাজ।
| 08:55 | 10:36 | Chandraghona 132/33kV S/S TR-02(416T) LT Forced S/D Due to টি-০২ ২৫/৪১ এমভিএ (৪১৬টি) এর
৩৩ কেভি ব্লু- ফেইজ এর নীচের কানেক্টরে সংরক্ষণ ও মেরামত কাজ।
| 09:49 | 12:37 | Bogura(New)-Naogaon 132 kV Ckt-2 Forced S/D from Naogaon 132/33kV end Due to As following
instruction of ALDC Bogura.
| 09:52 | 21:08 | Jhenaidah 132/33kV S/S Jhenaidah-Chuadanga, 132kV Circuit-2(L8) Tripped showing 67N GFP
GROUND SYS.1, Zone-2 21 DISTANCE A,B,C PHASE, FAULT DISTANCE 41.9km. relays Due to Trip
| 09:52 | 20:58 | Chuadanga 132/33kV S/S Jhenaidah-Chuadanga Ckt-2 Tripped showing SIPROTEC Main protection
Relay. relays Due to Line -2 LA Blust.
| 09:57 | 15:12 | Sherpur 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to blast wall painting work.
| 09:57 | 15:12 | Sherpur 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to blast wall painting work.
|  | 10:48 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 is restored.
| 10:51 |  | BSRM 230/33kV S/S 230/33 kV Transformer-2 (125/140 MVA) HT Scheduled S/D Due to BSRM Maintenance
|  | 11:04 | Khulna(S) 230/132kV S/S 132 KV Main Bus is restored.
|  | 11:04 | Khulna(S) 230/132kV S/S TR-1 HT is restored.
|  | 11:06 | Khulna(S) 230/132kV S/S TR-3 LT is restored.
|  | 11:06 | Khulna(S) 230/132kV S/S TR-3 HT is restored.
|  | 11:07 | Khulna (S)-Satkhira 132kV Ckt-1 is restored.
|  | 11:08 | Khulna(S) 230/132kV S/S TR-2 HT is restored.
|  | 11:10 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 11:11 | Gallamari- Khulna (S) 132kV Ckt-1 is restored.
|  | 11:12 | Khulna (S)-Satkhira 132kV Ckt-2 is restored.
|  | 11:12 | Gallamari- Khulna (S) 132kV Ckt-2 is restored.
| 11:44 | 13:38 | Ghorasal- Ishwardi 230 kV Ckt-2 Tripped from Ishurdi 230/132kV end showing Z1,SOTF,C
Phase Ground relays. and from Ghorashal 230kV end showing Siprotec (7SA611) relays Due to
PBS transformer blust at Dhamrai.
| 11:48 | 12:14 | BSRM-Cumilla(N) 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Distance
Relay Auto-reclose Relay relays.
| 12:00 |  | Day Peak Generation: 14203 MW.
| 12:04 | 13:48 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to Red Hot Maintanance | [7 empty] | 25.0MW load interrup.
|  | 12:17 | Chauddagram 132/33kV S/S 132 kv T-2 HT is restored.
|  | 12:17 | Chauddagram 132/33kV S/S 132 kv T-2 LT is restored.
|  | 12:17 | Chauddagram 132/33kV S/S 132 kv T-2 HT is restored.
| 12:25 | 13:47 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Red hot maintance | [7 empty] | 25.0MW load interrup.
| 12:30 | 15:48 | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to Shut
down taken by Shikalbaha.
|  | 12:37 | Bogura(New)-Naogaon 132 kV Ckt-2 is restored.
|  | 12:43 | Gopalganj 132/33kV S/S T1 HT is restored.
| 12:44 | 15:45 | Shahmirpur-Sikalbaha 132kV Ckt-1 Forced S/D from Shahmirpur 132/33kV end Due to Works at Sikalbaha end
|  | 12:44 | Gopalganj 132/33kV S/S T1 LT is restored.
| 12:51 | 15:31 | Patuakhali 132/33kV S/S 425T (T-3) LT Scheduled S/D Due to Red hot maintenance
| 12:51 | 15:30 | Patuakhali 132/33kV S/S 425T (T-3) HT Scheduled S/D Due to Red hot Maintenance
| 14:22 |  | Haripur EGCB 412 MW CCPP GT was sync.
| 14:22 |  | Haripur 412 MW CCPP Synchronized with remarks:- GT
| 14:44 | 15:13 | Ashuganj-Ghorasal 132kV Ckt-2 Tripped from Ashuganj 230/132/33kV end showing Distance-A relays.
| 15:01 |  | Cumilla(S)-Kachua 132 kV Ckt-1 Project Work S/D from Cumilla(S) 132/33kV end Due to Bus
extension of Kachua S/S and from Kachua 132/33kV end Due to ESPN project for bus loop connection
| 15:28 | 19:17 | Kachua 132/33kV S/S Main Bus-1 Project Work S/D Due to ESPN project bus loop conection
| 15:42 | 15:54 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing
Distance Protection - A phase relays.
| 15:59 | 18:24 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing
Distance Protection -B phase -AIDDED Trip relays.
|  | 17:42 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt is restored.
| 18:19 | 19:48 | Tongi 230/132/33kV S/S Tongi-Uttara 3rd Phase Ckt Tripped showing Distance relay,
R-Phase,. 10.2 Km relays.
| 20:05 |  | Haripur EGCB 412 MW CCPP ST was sync.
| 20:05 |  | Haripur 412 MW CCPP Synchronized with remarks:- ST
| 20:25 |  | Rampal 1320 MW (BIFPCL) unit-1 was sync.
| 20:25 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 21:00 |  | **Highest generation so far = 16,603 MW
| 21:07 | 21:21 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Ins O/C,Ins E/F relays Due to 33kv feeder fault | [7 empty] | 47.0MW load
| 01:48 |  | Rampal 1320 MW (BIFPCL) Tripped with remarks:- U1
| 05:52 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 06:15 | 07:26 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Tripped showing Distance Protection | [7 empty] | 1.0MW load
|  |  | Relay relays Due to Thundering | [7 empty] | interrup.
| 06:15 | 07:26 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Tripped showing Distance Protection | [7 empty] | 1.0MW load
|  |  | Relay relays Due to Thundering | [7 empty] | interrup.
| 06:16 | 07:02 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Tripped from Beanibazar 132/33kV end | [7 empty] | 4.0MW load interrup.
|  |  | showing REL 670 relays Due to Sulhet-Fenchugang line -2 trip and from Fenchuganj | [7 empty] | Beanibazar 132/33kV
|  |  | 230/132/33kV end showing REL670, REC650 relays Due to Bad Weather | [7 empty] | end and 24.0MW load interrup.
Fenchuganj 230/132/33kV end
| 06:20 |  | Munshiganj 132/33kV S/S Transformer-2 LT Forced S/D Due to Emergency maintenance on PBS | [7 empty] | 30.0MW load interrup.
|  |  | 33 KV Feeder Red Hot | [7 empty] | interrup.
| 06:21 |  | Kodda 132/33kV S/S Tr-2 (416T) LT Scheduled S/D Due to Redhot maintenance | [7 empty] | 55.0MW load interrup.
| 06:22 |  | Kodda 132/33kV S/S Tr-2 (416T) HT Scheduled S/D
| 06:22 | 07:03 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Forced S/D from Fenchuganj 230/132/33kV | [7 empty] | 24.0MW load interrup.
|  |  | end Due to After trip | [7 empty] | Fenchuganj 230/132/33kV end
| 06:44 |  | Madunaghat-Sikalbaha 132kV Ckt-2 Scheduled S/D from Madunaghat 132/33kV end Due to
Shikalbaha circuit-1 maintenance work shut down.
| 06:56 |  | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end.
| 07:06 |  | Kushtia 132/33kV S/S T2 LT Scheduled S/D Due to Red hot T-2A 33kv CT Clamp Connector | [7 empty] | 10.0MW load interrup.
| 07:07 |  | Kushtia 132/33kV S/S T2 HT Scheduled S/D Due to Red hot T-2A 33kv CT Clamp Connector | [7 empty] | 10.0MW load interrup.
| 07:15 |  | Ishurdi 132/33kV S/S 132/33 kV T-1 HT Scheduled S/D | [7 empty] | 30.0MW load interrup.
| 07:15 |  | Ishurdi 132/33kV S/S 132/33 kV T-1 LT Scheduled S/D | [7 empty] | 30.0MW load interrup.
| 07:25 |  | Ghorashal 230kV S/S TARFO-2 LT Project Work S/D Due to Shutdown requisition from | [7 empty] | 50.0MW load
|  |  | Project-1(EnergyPack) for repair oil leakage in X-former & 33kV CT, earthing and | [7 empty] | interrup.
replacing damage Nut-Bolt in switchyard.
| 07:28 |  | Ghorashal 230kV S/S TARFO-2 HT Project Work S/D Due to Shutdown requisition from | [7 empty] | 50.0MW load
|  |  | Project-1(EnergyPack) for repair oil leakage in X-former & 33kV CT, earthing and | [7 empty] | interrup.
replacing damage Nut-Bolt in switchyard.
| 07:51 |  | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Project Work S/D from BIPTC end Due to Shutdown is
taken by WGND project for energy meter replacement and from Jhenaidah 230/132kV end Due
to For Faulty Energy Meter Replacing work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 10-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 130 | 3942000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 7838500 | Allocation limit by Titas Gas
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 274 | 6446691 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 1331143 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 317 | 7184994 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 97 | 717408 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 582840 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 143 | 1989600 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 594594 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 601945 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 10 | 413400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 494280 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 509280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 4978538 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 130 | 2441232 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 962880 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 50 | 785280 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1743840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 219636 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 428040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 420 | 7876818.18 | Allocation limit by Titas Gas
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 6595909 | Allocation limit by Titas Gas
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 3528000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 3287 | 62206848.18
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 26 | 324619.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 129330 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 593280 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 936800 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 146 | 3400741 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 87 | 1680255 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 53 | 1142640 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 102 | 1917311 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1991040 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 9 | 404160 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 57 | 1214400 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 28305 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 50 | 501818 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 17 | 224764 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 2015636 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 2295360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 110 | 800400 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 2144436 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 26383634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 66240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 554 | 10407272.73 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2983 | 58602441.93
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 216 | 4945000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 0 | 0 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 7844000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 752832 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1065600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 180 | 4282182 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1166952 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 2753309 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 37 | 685128 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1657930 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 21 | 2381280 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 48 | 1087680 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 53 | 1108368 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 16 | 404580 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2657340 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 424200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1672320 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 496382 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1486 | 35385083
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 22 | 477120 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15100 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 143 | 2632800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 92 | 1544400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 352380 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294480 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 366480 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 286 | 5682760
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 36 | 857000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 678480 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 2788855 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 20 | 637920 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1887360 | 01 engine maintenance
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 170 | 4038510 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 377000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 171312 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7539500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 8107000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | FGMO OFF
Sylhet Area Total |  |  |  |  | 2368.568 | 1145 | 27082937
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 780 | 21635636 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 29 | 181920 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 35 | 206848 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 285 | 6020640 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 1306080 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 727200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 752 | 14589095 | Partial Shutdown due to maintenance
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1898 | 44667419
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 453 | 10887272 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 80 | 374304 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 234678 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 105 | 2587000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26871272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5110430 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 916800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6939000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4986 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2520 | 53925742.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 48 | 466000 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 6 | 84710 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 37 | 309070 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 203 | 4733818 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 198 | 4801764 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 366 | 8594472 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 8 | 120310 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 41 | 434573 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 773152 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 2301600 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1446240 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 33300 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1344 | 32674498 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 396752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 773450 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2568 | 57943709
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1164218 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 4001000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 105 | 2141865 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50734.56 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2049943 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 232507 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1385280 | -
Rangpur Area Total |  |  |  |  | 950 | 430 | 11025547.56
Eastern Grid Total |  |  |  |  | 16921.242 | 9187 | 188960070.11
Western Grid Total |  |  |  |  | 11702.84 | 7416 | 167562418.29
National Grid Total |  |  |  |  | 28624.082 | 16603 | 356522488.4
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 10-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10649.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 5384.4 | MW
i) Dhaka area |  |  | 5823.36 |  | MW | i) Khulna area |  |  |  | 1965.8 | MW
ii) Chattogram area |  |  | 1602.9 |  | MW | ii) Barishal area |  |  |  | 554.8 | MW
iii) Cumilla area |  |  | 1402.27 |  | MW | iii) Rajshahi area |  |  |  | 1819.8 | MW
iv) Mymensingh area |  |  | 1160 |  | MW | iv) Rangpur area |  |  |  | 1044 | MW
v) Sylhet area |  |  | 661 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 16033.93 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 95 | 19:30 | 133 | Patuakhali | 83 | 22:00
2 | AKSML | 101 | 11:00 | 68 | Jaldhaka | 81 | 00:00 | 134 | Payra | 38 | 00:00
3 | Aftabnagar | 46 | 23:00 | 69 | Jamalpur | 116 | 10:00 | 135 | Postogola | 64 | 16:00
4 | Agargaon | 145 | 23:00 | 70 | Jashore | 165 | 20:00 | 136 | Purbachal | 22 | 00:00
5 | Agrabad | 96 | 00:00 | 71 | Jhenaidah | 150 | 20:00 | 137 | Purbasadipur | 142 | 21:00
6 | Amnura | 49 | 21:00 | 72 | Joydebpur | 159 | 21:00 | 138 | Rahanpur | 33 | 22:00
7 | Ashuganj | 121 | 00:00 | 73 | Joypurhat | 87 | 23:00 | 139 | Rahim | 29 | 15:00
8 | BSRM | 181 | 05:00 | 74 | Juldah | 20 | 23:00 | 140 | Rajbari | 96 | 19:30
9 | Bagerhat | 89 | 00:00 | 75 | KSRM | 21 | 13:00 | 141 | Rajendrapur | 148 | 21:00
10 | Bajitpur | 62 | 19:00 | 76 | Kabirpur | 281 | 15:00 | 142 | Rajshahi | 142 | 23:00
11 | Bakulia | 114 | 20:00 | 77 | Kachua | 103 | 22:00 | 143 | Rajshahi-230 | 108 | 23:00
12 | Banani | 46 | 13:00 | 78 | Kallyanpur | 114 | 00:00 | 144 | Ramganj | 116 | 03:00
13 | Bangabhaban | 8 | 11:00 | 79 | Kalurghat | 44 | 11:00 | 145 | Rampur | 50 | 01:00
14 | Barapukuria | 72 | 21:00 | 80 | Kamrangirchar | 69 | 12:00 | 146 | Rangamati | 22 | 19:00
15 | Barguna | 32 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 162 | 21:00
16 | Barishal | 123 | 12:00 | 82 | Kasba | 40 | 00:00 | 148 | Ruppur | 6 | 11:00
17 | Barishal-230 | 130 | 21:00 | 83 | Kazla | 107 | 22:00 | 149 | SSM | 3 | 21:00
18 | Baroaulia | 75 | 15:00 | 84 | Keranigonj | 89 | 19:00 | 150 | Saidpur | 119 | 12:00
19 | Baroirhat | 87 | 23:00 | 85 | Khagrachori | 38 | 19:30 | 151 | Satkhira | 144 | 22:00
20 | Bashundhara | 226 | 15:00 | 86 | Khulna | 79 | 22:00 | 152 | Satmasjid | 122 | 17:00
21 | BashundharaCement | 12 | 10:00 | 87 | Khulshi | 216 | 17:00 | 153 | Savar | 228 | 10:00
22 | Beanibazar | 76 | 19:00 | 88 | Kishoreganj | 154 | 00:00 | 154 | SevenRings | 18 | 11:00
23 | Benapole | 74 | 19:00 | 89 | Kodda | 278 | 14:00 | 155 | ShahCement | 30 | 23:00
24 | Bhaluka | 173 | 20:00 | 90 | Kulaura | 57 | 19:00 | 156 | Shahjadpur | 103 | 22:00
25 | Bhandaria | 60 | 21:00 | 91 | Kurigram | 66 | 00:00 | 157 | Shahjibazar | 119 | 01:00
26 | Bhangura | 54 | 19:00 | 92 | Kushtia | 171 | 19:30 | 158 | Shahmirpur | 55 | 00:00
27 | Bheramara(GK) | 80 | 19:30 | 93 | Lalbag | 74 | 13:00 | 159 | Shariatpur | 99 | 23:00
28 | Bhulta | 240 | 08:00 | 94 | Lalmonirhat | 66 | 00:00 | 160 | Sherpur | 140 | 23:00
29 | Bog-Sherpur | 80 | 19:30 | 95 | MI_Cement | 18 | 00:00 | 161 | Shikalbaha | 34 | 20:00
30 | Bogura | 211 | 22:00 | 96 | Madanganj | 56 | 21:00 | 162 | Shitalakhya | 101 | 16:00
31 | Borhanuddin | 101 | 22:00 | 97 | Madaripur | 134 | 22:00 | 163 | Sholosohor | 53 | 19:00
32 | Brahmanbaria | 133 | 05:00 | 98 | Madartek | 106 | 23:00 | 164 | Shyampur | 188 | 12:00
33 | Cantonment | 154 | 13:00 | 99 | Madunaghat | 60 | 16:00 | 165 | Siddhirganj | 122 | 19:00
34 | Chandina | 20 | 17:00 | 100 | Magura | 75 | 19:30 | 166 | Sirajganj | 130 | 22:00
35 | Chandpur | 78 | 22:00 | 101 | Mahasthangarh | 100 | 20:00 | 167 | Sonargaon | 120 | 18:30
36 | Chandraghona | 40 | 19:30 | 102 | Manikganj | 151 | 21:00 | 168 | Sreemongol | 96 | 19:00
37 | Chapai | 81 | 22:00 | 103 | Maniknagar | 72 | 16:00 | 169 | Sreepur | 114 | 19:00
38 | Charsaidpur | 45 | 23:00 | 104 | Matarbari | 55 | 23:00 | 170 | Srinagar | 55 | 21:00
39 | Chauddagram | 78 | 21:00 | 105 | Matuail | 72 | 15:00 | 171 | Sunamganj | 62 | 00:00
40 | Chhatak | 39 | 21:00 | 106 | Millgate | 135 | 16:00 | 172 | Sylhet | 53 | 19:30
41 | Chowmuhani | 216 | 03:00 | 107 | Mirpur | 157 | 16:00 | 173 | Sylhet-132 | 144 | 19:00
42 | Chuadanga | 132 | 23:00 | 108 | Mirsorai | 11 | 19:30 | 174 | TK | 26 | 20:00
43 | Coxsbazar | 146 | 18:30 | 109 | Mirzapur | 41 | 06:00 | 175 | Tangail | 188 | 12:00
44 | Cumilla(N) | 167 | 00:00 | 110 | Mithapukur | 78 | 19:00 | 176 | Thakurgaon | 110 | 20:00
45 | Cumilla(S) | 180 | 21:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 121 | 21:00
46 | Daudkandi | 147 | 19:30 | 112 | Mogbazar | 161 | 15:00 | 178 | Ullahpara | 50 | 00:00
47 | Dhaka | 58 | 13:00 | 113 | Mongla | 48 | 21:00 | 179 | Ullon | 65 | 00:00
48 | Dhamrai | 138 | 18:30 | 114 | Motijheel | 45 | 16:00 | 180 | Uttara | 108 | 17:00
49 | Dhanmondi | 169 | 13:00 | 115 | Muktagacha | 37 | 06:00 | 181 | UttaraNew | 60 | 23:00
50 | Dohazari | 113 | 21:00 | 116 | Munshiganj | 128 | 19:00 | 182 | Zigatola | 84 | 16:00
51 | Faridpur | 181 | 23:00 | 117 | Muradnagar | 31 | 00:00
52 | Fatullah | 111 | 15:00 | 118 | Mymensingh | 218 | 01:00
53 | Fenchuganj | 48 | 00:00 | 119 | Naogaon | 167 | 21:00
54 | Feni | 129 | 19:00 | 120 | Narail | 68 | 19:30
55 | GPH | 98 | 06:00 | 121 | Narinda | 72 | 18:30
56 | Ghatail | 68 | 22:00 | 122 | Narshingdi | 177 | 00:00
57 | Ghorashal | 18 | 10:00 | 123 | Natore | 184 | 19:30
58 | Ghorashal-230 | 99 | 20:00 | 124 | Nawabganj | 64 | 00:00
59 | Goalpara | 46 | 23:00 | 125 | Netrakona | 127 | 07:00
60 | Gollamari | 106 | 19:00 | 126 | New | 96 | 15:00
61 | Gopalganj | 121 | 23:00 | 127 | Niamatpur | 100 | 22:00
62 | Gulshan | 128 | 15:00 | 128 | Noapara | 51 | 19:30
63 | Halishahar | 91 | 16:00 | 129 | PHP | 7 | 09:00
64 | HaripurSBU | 176 | 22:00 | 130 | Pabna | 137 | 22:00
65 | Hasnabad | 92 | 19:30 | 131 | Palashbari | 134 | 23:00
66 | Hathazari | 94 | 23:00 | 132 | Panchagarh | 61 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 10-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15946 | 225 |  | 16181.13
1:00 | 15581 | 231 |  | 15822.4
2:00 | 15167 | 208 |  | 15384.36
3:00 | 14832 | 165 |  | 15004.43
4:00 | 14272 | 162 |  | 14441.29
5:00 | 14086 | 139 |  | 14231.26
6:00 | 13484 | 224 |  | 13718.08
7:00 | 13366 | 182 |  | 13556.19
8:00 | 13333 | 147 |  | 13486.62
9:00 | 13274 | 135 |  | 13415.08
10:00 | 13535 | 163 |  | 13705.34
11:00 | 13997 | 257 |  | 14265.57
12:00 | 14210 | 245 |  | 14466.03
13:00 | 14239 | 399 |  | 14655.96
14:00 | 14307 | 430 |  | 14756.35
15:00 | 14538 | 447 |  | 15005.12
16:00 | 14431 | 454 |  | 14905.43
17:00 | 14303 | 379 |  | 14699.06
18:00 | 14263 | 370 |  | 14649.65
19:00 | 15550 | 525 |  | 16098.63
19:30 | 16018 | 651 |  | 16698.3
20:00 | 16201 | 620 |  | 16848.9
21:00 | 16603 | 379 |  | 16999.06
22:00 | 16369.29 | 317 |  | 16700.56
23:00 | 16375.07 | 360 |  | 16751.07
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 10-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8682 | 7264 | 15946 | DAILY GENERATION CURVE
00:30 | 8472.5 | 7291 | 15763.5
01:00 | 8263 | 7318 | 15581 | 10-05-2025
01:30 | 8188.5 | 7185.5 | 15374
02:00 | 8114 | 7053 | 15167
02:30 | 8001 | 6998.5 | 14999.5
03:00 | 7888 | 6944 | 14832
03:30 | 7727.5 | 6824.5 | 14552
04:00 | 7567 | 6705 | 14272
04:30 | 7515.5 | 6663.5 | 14179
05:00 | 7464 | 6622 | 14086
05:30 | 7335 | 6450 | 13785
06:00 | 7206 | 6278 | 13484
06:30 | 7091 | 6334 | 13425
07:00 | 6976 | 6390 | 13366
07:30 | 6952 | 6397.5 | 13349.5
08:00 | 6928 | 6405 | 13333
08:30 | 6893.5 | 6410 | 13303.5
09:00 | 6859 | 6415 | 13274
09:30 | 6900.5 | 6504 | 13404.5
10:00 | 6942 | 6593 | 13535
10:30 | 7151 | 6615 | 13766
11:00 | 7360 | 6637 | 13997
11:30 | 7376 | 6727.5 | 14103.5
12:00 | 7392 | 6818 | 14210
12:30 | 7299.5 | 6925 | 14224.5
13:00 | 7207 | 7032 | 14239
13:30 | 7199 | 7074 | 14273
14:00 | 7191 | 7116 | 14307
14:30 | 7327.5 | 7095 | 14422.5
15:00 | 7464 | 7074 | 14538
15:30 | 7490 | 6994.5 | 14484.5
16:00 | 7516 | 6915 | 14431
16:30 | 7551 | 6816 | 14367
17:00 | 7586 | 6717 | 14303
17:30 | 7686.5 | 6596.5 | 14283
18:00 | 7787 | 6476 | 14263
18:30 | 8227.5 | 6679 | 14906.5
19:00 | 8668 | 6882 | 15550
19:30 | 8889 | 7129 | 16018
20:00 | 9025 | 7176 | 16201
20:30 | 9106 | 7296 | 16402 |  | Executive Engineer
21:00 | 9187 | 7416 | 16603 |  | Network Operation Division
21:30 | 9022.25 | 7463.895 | 16486.145
22:00 | 8857.5 | 7511.79 | 16369.29
22:30 | 8823.38 | 7548.8 | 16372.18
23:00 | 8789.26 | 7585.81 | 16375.07

## En-Curve
QF-LDC-12
Date | 10-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3169 | 2138 | 831 | 0 | 52 | 1355 | 40 | 4464 | 0 | 773 | 3124 | 0 | 0 | 0 | 225 | DAILY ENERGY CURVE
00:30 | 3116 | 2111 | 880 | 0 | 50 | 1357 | 40 | 4465 | 0 | 748.5 | 2996 | 0 | 0 | 0 | 228 | 10-05-2025
01:00 | 3063 | 2084 | 929 | 0 | 48 | 1359 | 40 | 4466 | 0 | 724 | 2868 | 0 | 0 | 0 | 231
01:30 | 3027.5 | 2096.5 | 928.5 | 0 | 47 | 1365.5 | 40 | 4468 | 0 | 638 | 2763 | 0 | 0 | 0 | 219.5 | Energy Generated | 356.5225 |  | MKWHr
02:00 | 2992 | 2109 | 928 | 0 | 46 | 1372 | 40 | 4470 | 0 | 552 | 2658 | 0 | 0 | 0 | 208 | Energy not Served | 7.163 |  | MKWHr
02:30 | 3050 | 2144.5 | 928.5 | 0 | 45 | 1368 | 40 | 4470 | 0 | 516 | 2437.5 | 0 | 0 | 0 | 186.5 | Total Energy Requirement | 363.6855 |  | MKWHr
03:00 | 3108 | 2180 | 929 | 0 | 44 | 1364 | 40 | 4470 | 0 | 480 | 2217 | 0 | 0 | 0 | 165
03:30 | 3076.5 | 2212.5 | 928.5 | 0 | 44 | 1364 | 40 | 4467.5 | 0 | 415.5 | 2003.5 | 0 | 0 | 0 | 163.5
04:00 | 3045 | 2245 | 928 | 0 | 44 | 1364 | 40 | 4465 | 0 | 351 | 1790 | 0 | 0 | 0 | 162
04:30 | 3087.5 | 2245 | 928 | 0 | 43 | 1362.5 | 40 | 4380.5 | 0 | 347 | 1745.5 | 0 | 0 | 0 | 150.5
05:00 | 3130 | 2245 | 928 | 0 | 42 | 1361 | 40 | 4296 | 0 | 343 | 1701 | 0 | 0 | 0 | 139
05:30 | 3064.5 | 2217 | 928.5 | 0 | 41 | 1359 | 40 | 4087 | 18 | 336 | 1694 | 0 | 0 | 0 | 181.5
06:00 | 2999 | 2189 | 929 | 0 | 40 | 1357 | 40 | 3878 | 36 | 329 | 1687 | 0 | 0 | 0 | 224
06:30 | 2875 | 2193 | 928.5 | 0 | 39 | 1364.5 | 40 | 3854.5 | 91 | 329.5 | 1710 | 0 | 0 | 0 | 203
07:00 | 2751 | 2197 | 928 | 0 | 38 | 1372 | 40 | 3831 | 146 | 330 | 1733 | 0 | 0 | 0 | 182
07:30 | 2764.5 | 2177.5 | 903.5 | 0 | 36 | 1368 | 40 | 3769.5 | 226.5 | 333.5 | 1730.5 | 0 | 0 | 0 | 164.5
08:00 | 2778 | 2158 | 879 | 0 | 34 | 1364 | 40 | 3708 | 307 | 337 | 1728 | 0 | 0 | 0 | 147
08:30 | 2750 | 2149.5 | 878.5 | 0 | 36 | 1362.5 | 40 | 3684.5 | 379 | 337.5 | 1686 | 0 | 0 | 0 | 141
09:00 | 2722 | 2141 | 878 | 0 | 38 | 1361 | 40 | 3661 | 451 | 338 | 1644 | 0 | 0 | 0 | 135
09:30 | 2793.5 | 2160.5 | 902.5 | 0 | 39 | 1357 | 40 | 3653.5 | 504.5 | 346.5 | 1607.5 | 0 | 0 | 0 | 149
10:00 | 2865 | 2180 | 927 | 0 | 40 | 1353 | 40 | 3646 | 558 | 355 | 1571 | 0 | 0 | 0 | 163
10:30 | 2825 | 2176 | 926.5 | 0 | 40 | 1359.5 | 40 | 3646.5 | 596 | 406.5 | 1748 | 0 | 0 | 2 | 210
11:00 | 2785 | 2172 | 926 | 0 | 40 | 1366 | 40 | 3647 | 634 | 458 | 1925 | 0 | 0 | 4 | 257
11:30 | 2808 | 2174 | 926 | 0 | 42 | 1360.5 | 40 | 3675 | 641 | 450.5 | 1979 | 0 | 0 | 7.5 | 251
12:00 | 2831 | 2176 | 926 | 0 | 44 | 1355 | 40 | 3703 | 648 | 443 | 2033 | 0 | 0 | 11 | 245
12:30 | 2794.5 | 2173.5 | 926 | 0 | 47 | 1362 | 40 | 3745 | 639 | 422 | 2063.5 | 0 | 0 | 12 | 322
13:00 | 2758 | 2171 | 926 | 0 | 50 | 1369 | 40 | 3787 | 630 | 401 | 2094 | 0 | 0 | 13 | 399
13:30 | 2791 | 2183 | 926.5 | 0 | 51 | 1366 | 40 | 3798 | 593.5 | 398 | 2115 | 0 | 0 | 11 | 414.5
14:00 | 2824 | 2195 | 927 | 0 | 52 | 1363 | 40 | 3809 | 557 | 395 | 2136 | 0 | 0 | 9 | 430
14:30 | 2830 | 2181.5 | 927 | 0 | 52 | 1362.5 | 40 | 3910 | 495 | 428 | 2188.5 | 0 | 0 | 8 | 438.5
15:00 | 2836 | 2168 | 927 | 0 | 52 | 1362 | 40 | 4011 | 433 | 461 | 2241 | 0 | 0 | 7 | 447
15:30 | 2826 | 2160 | 926.5 | 0 | 50 | 1361.5 | 40 | 4090.5 | 358.5 | 465 | 2199 | 0 | 0 | 7.5 | 450.5
16:00 | 2816 | 2152 | 926 | 0 | 48 | 1361 | 40 | 4170 | 284 | 469 | 2157 | 0 | 0 | 8 | 454
16:30 | 2773.5 | 2141.5 | 926 | 0 | 47 | 1356.5 | 40 | 4149.5 | 208 | 517.5 | 2200.5 | 0 | 0 | 7 | 416.5
17:00 | 2731 | 2131 | 926 | 0 | 46 | 1352 | 40 | 4129 | 132 | 566 | 2244 | 0 | 0 | 6 | 379
17:30 | 2747.5 | 2148.5 | 926 | 0 | 42 | 1354.5 | 60 | 3958.5 | 78.5 | 633.5 | 2329.5 | 0 | 0 | 4.5 | 374.5
18:00 | 2764 | 2166 | 926 | 0 | 38 | 1357 | 80 | 3788 | 25 | 701 | 2415 | 0 | 0 | 3 | 370
18:30 | 2862.5 | 2389 | 901 | 0 | 41 | 1359.5 | 60 | 4048.5 | 12.5 | 729 | 2501.5 | 0 | 0 | 2 | 447.5
19:00 | 2961 | 2612 | 876 | 0 | 44 | 1362 | 40 | 4309 | 0 | 757 | 2588 | 0 | 0 | 1 | 525
19:30 | 2918 | 2685 | 876 | 0 | 42 | 1364 | 40 | 4563 | 0 | 773 | 2756 | 0 | 0 | 1 | 651
20:00 | 2989 | 2562 | 876 | 0 | 48 | 1361 | 40 | 4560 | 0 | 796 | 2969 | 0 | 0 | 0 | 620
20:30 | 3021 | 2601.5 | 828 | 0 | 48 | 1352.5 | 40 | 4652 | 0 | 824.5 | 3034.5 | 0 | 0 | 0 | 499.5
21:00 | 3053 | 2641 | 780 | 0 | 48 | 1344 | 40 | 4744 | 0 | 853 | 3100 | 0 | 0 | 0 | 379
21:30 | 3190.5 | 2458.75 | 780 | 0 | 48 | 1344.895 | 40 | 4792 | 0 | 861.5 | 2970.5 | 0 | 0 | 0 | 348
22:00 | 3328 | 2276.5 | 780 | 0 | 48 | 1345.79 | 40 | 4840 | 0 | 870 | 2841 | 0 | 0 | 0 | 317
22:30 | 3297 | 2272.35 | 780 | 0 | 48 | 1350.3 | 40 | 4894.5 | 0 | 857.5 | 2832.53 | 0 | 0 | 0 | 338.5
23:00 | 3266 | 2268.2 | 780 | 0 | 48 | 1354.81 | 40 | 4949 | 0 | 845 | 2824.06 | 0 | 0 | 0 | 360
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 10-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 07:00 | 370 | 19:00 | Payra | 410 | 06:00 | 404 | 19:00
Ashuganj | 400 | 6:00 | 380 | 18:00 | Rahanpur | 401 | 18:30 | 392 | 21:00
Bhulta | 385 | 06:00 | 363 | 22:00 | Rampal | 395 | 06:00 | 375 | 19:30
Bibiana | 390 | 05:00 | 283 | 22:00
BIPTC | 399 | 09:00 | 385 | 01:00
Bogura | 385 | 14:00 | 375 | 21:00
Gopalganj | 391 | 06:00 | 377 | 19:00
Kaliakoir | 371 | 06:00 | 361 | 14:00
Madunaghat | 398 | 01:00 | 391 | 23:00
Meghnaghat | 387 | 06:00 | 376 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 06:00 | 213 | 12:00 | Keranigonj | 221 | 06:00 | 212 | 12:00
AKSML | 235 | 08:00 | 226 | 00:00 | Khulna(S) | 230 | 06:00 | 208 | 19:30
Aminbazar | 221 | 00:00 | 214 | 10:00 | Madunaghat | 237 | 00:00 | 232 | 13:00
Ashuganj | 229 | 06:00 | 219 | 22:00 | Madunaghat-400 | 237 | 00:00 | 233 | 15:00
Ashuganj-400 | 224 | 6:00 | 216 | 18:00 | Maniknagar | 220 | 04:00 | 210 | 12:00
Baghabari | 233 | 07:00 | 226 | 20:00 | Meghnaghat | 231 | 11:00 | 220 | 13:00
Barapukuria | 225 | 14:00 | 217 | 21:00 | Meghnaghat-400 | 224 | 06:00 | 216 | 10:00
Barapukuria-230 | 224 | 14:00 | 216 | 20:00 | Mirsorai | 237 | 12:00 | 224 | 03:00
Barishal | 233 | 06:00 | 225 | 19:00 | Rajshahi | 233 | 06:00 | 23 | 01:00
Bheramara | 233 | 08:00 | 223 | 16:00 | Rampal | 228 | 06:00 | 210 | 19:30
Bhulta | 221 | 06:00 | 209 | 18:30 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 06:00 | 216 | 22:00 | Rampura | 220 | 06:00 | 207 | 19:00
BIPTC | 236 | 06:00 | 223 | 16:00 | Shikalbaha | 237 | 00:00 | 231 | 17:00
Bogura | 233 | 14:00 | 227 | 21:00 | Shyampur | 222 | 06:00 | 213 | 11:00
Bogura-400 | 235 | 14:00 | 227 | 21:00 | Siddhirganj | 223 | 03:00 | 213 | 12:00
Borhanuddin | 239 | 07:00 | 231 | 01:00 | Sirajgonj | 238 | 04:00 | 233 | 22:00
BSRM | 234 | 12:00 | 226 | 03:00 | Sreepur | 228 | 15:00 | 218 | 22:00
Cumilla(N) | 222 | 04:00 | 215 | 22:00 | Tongi | 224 | 01:00 | 214 | 09:00
Faridpur | 229 | 06:00 | 218 | 19:00
Fenchuganj | 227 | 16:00 | 220 | 00:00
Ghorashal | 230 | 01:00 | 228 | 00:00
Ghorashal-230 | 222 | 01:00 | 212 | 12:00
Gopalganj | 231 | 07:00 | 222 | 19:00
GPH | 234 | 00:00 | 229 | 04:00
Haripur | 222 | 00:00 | 212 | 12:00
Hasnabad | 222 | 05:00 | 213 | 12:00
Hathazari | 236 | 07:00 | 232 | 22:00
Ishurdi | 235 | 06:00 | 226 | 13:00
Jhenaidah | 229 | 06:00 | 211 | 19:30
Kaliakoir | 233 | 21:00 | 220 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 133 | 04:00 | 123 | 12:00 | Madartek | 132 | 06:00 | 122 | 12:00
Agargaon | 131 | 06:00 | 122 | 12:00 | Madunaghat | 134 | 00:00 | 129 | 13:00
Agrabad | 134 | 00:00 | 131 | 18:30 | Magura | 132 | 06:00 | 118 | 19:30
AKS | 133 | 03:00 | 130 | 13:00 | Mahasthangarh | 135 | 18:00 | 128 | 21:00
Aminbazar | 130 | 02:00 | 122 | 10:00 | Manikganj | 132 | 13:00 | 118 | 11:00
Amnura | 136 | 00:00 | 121 | 22:00 | Maniknagar | 130 | 06:00 | 123 | 11:00
Ashuganj | 135 | 05:00 | 131 | 21:00 | Matarbari | 127 | 19:00 | 114 | 23:00
Bagerhat | 135 | 06:00 | 110 | 22:00 | Matuail | 129 | 05:00 | 123 | 14:00
Bajitpur | 130 | 16:00 | 121 | 22:00 | Millgate | 133 | 01:00 | 124 | 10:00
Bakulia | 138 | 19:00 | 134 | 10:00 | Mirpur | 127 | 00:00 | 120 | 12:00
Banani | 132 | 05:00 | 123 | 11:00 | Mirzapur | 133 | 13:00 | 127 | 10:00
Bangabhaban | 129 | 05:00 | 123 | 10:00 | Mithapukur | 133 | 18:30 | 122 | 21:00
Barapukuria | 137 | 14:00 | 129 | 21:00 | MI_Cement | 130 | 06:00 | 122 | 12:00
Barguna | 136 | 08:00 | 128 | 19:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 09:00 | 123 | 19:00 | Mogbazar | 134 | 05:00 | 123 | 19:00
Barishal-230 | 130 | 09:00 | 122 | 19:00 | Mongla | 130 | 08:00 | 112 | 19:00
Baroaulia | 135 | 00:00 | 130 | 04:00 | Motijheel | 129 | 03:00 | 123 | 10:00
Baroirhat | 125 | 10:00 | 119 | 19:00 | Muktagacha | 134 | 09:00 | 123 | 05:00
Bashundhara | 133 | 01:00 | 122 | 12:00 | Munshiganj | 129 | 06:00 | 122 | 10:00
BashundharaCement | 128 | 00:00 | 122 | 10:00 | Muradnagar | 125 | 07:00 | 119 | 12:00
Beanibazar | 130 | 07:00 | 122 | 22:00 | Mymensingh | 135 | 18:30 | 110 | 21:00
Benapole | 127 | 06:00 | 111 | 22:00 | Naogaon | 132 | 14:00 | 118 | 11:00
Bhaluka | 132 | 16:00 | 121 | 20:00 | Narail | 132 | 08:00 | 117 | 23:00
Bhandaria | 125 | 09:00 | 112 | 19:00 | Narinda | 130 | 6:00 | 123 | 11:00
Bhangura | 131 | 06:00 | 127 | 12:00 | Narshingdi | 131 | 16:00 | 115 | 21:00
Bheramara | 138 | 08:00 | 132 | 19:30 | Natore | 133 | 01:00 | 129 | 12:00
Bheramara(GK) | 138 | 08:00 | 132 | 19:30 | Nawabganj | 132 | 03:00 | 123 | 19:00
Bhulta | 121 | 06:00 | 115 | 11:00 | Netrakona | 124 | 16:00 | 110 | 20:00
Bog-Sherpur | 135 | 14:00 | 129 | 21:00 | New | 134 | 01:00 | 125 | 10:00
Bogura | 138 | 18:00 | 132 | 22:00 | Niamatpur | 131 | 04:00 | 127 | 21:00
Bogura-230 | 138 | 14:00 | 132 | 23:00 | Noapara | 134 | 06:00 | 116 | 19:30
Brahmanbaria | 132 | 16:00 | 118 | 21:00 | Pabna | 134 | 06:00 | 128 | 19:30
Cantonment | 131 | 06:00 | 122 | 12:00 | Palashbari | 131 | 14:00 | 121 | 21:00
Chandina | 128 | 16:00 | 121 | 22:00 | Panchagarh | 138 | 03:00 | 121 | 21:00
Chandpur | 128 | 10:00 | 115 | 18:30 | Patuakhali | 137 | 07:00 | 130 | 15:00
Chandraghona | 134 | 00:00 | 129 | 13:00 | Payra | 136 | 06:00 | 132 | 19:00
Chapai | 127 | 05:00 | 116 | 03:00 | PHP | 125 | 09:00 | 117 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 00:00 | 123 | 11:00 | Postogola | 131 | 05:00 | 124 | 12:00
Chauddagram | 125 | 08:00 | 117 | 22:00 | Purbachal | 132 | 05:00 | 122 | 13:00
Chhatak | 128 | 09:00 | 120 | 00:00 | Purbasadipur | 132 | 14:00 | 120 | 21:00
Chowmuhani | 120 | 09:00 | 110 | 22:00 | Rahanpur | 133 | 18:00 | 129 | 21:00
Chuadanga | 128 | 07:00 | 110 | 19:00 | Rahanpur-400 | 133 | 18:00 | 130 | 21:00
Coxsbazar | 122 | 22:00 | 113 | 18:30 | Rahim | 129 | 06:00 | 124 | 11:00
Cumilla(N) | 130 | 16:00 | 122 | 19:00 | Rajbari | 136 | 18:00 | 123 | 19:00
Cumilla(S) | 133 | 06:00 | 119 | 22:00 | Rajendrapur | 132 | 16:00 | 118 | 19:00
Daudkandi | 124 | 05:00 | 117 | 14:00 | Rajshahi | 133 | 02:00 | 128 | 14:00
Dhaka | 132 | 04:00 | 123 | 12:00 | Rajshahi-230 | 134 | 01:00 | 113 | 23:00
Dhamrai | 136 | 17:00 | 128 | 11:00 | Ramganj | 122 | 09:00 | 109 | 22:00
Dhanmondi | 133 | 04:00 | 124 | 14:00 | Rampur | 135 | 01:00 | 130 | 00:00
Dohazari | 135 | 19:00 | 129 | 23:00 | Rampura | 133 | 06:00 | 122 | 19:00
Faridpur | 133 | 06:00 | 126 | 18:30 | Rangamati | 133 | 06:00 | 128 | 18:30
Fatullah | 130 | 06:00 | 123 | 12:00 | Rangpur | 131 | 13:00 | 120 | 21:00
Fenchuganj | 134 | 05:00 | 129 | 20:00 | Ruppur | 137 | 06:00 | 132 | 18:00
Feni | 125 | 09:00 | 115 | 19:00 | Saidpur | 132 | 19:30 | 120 | 21:00
Ghatail | 132 | 09:00 | 121 | 05:00 | Satkhira | 124 | 04:00 | 110 | 19:30
Ghorashal | 133 | 00:00 | 129 | 10:00 | Satmasjid | 131 | 06:00 | 122 | 13:00
Goalpara | 134 | 06:00 | 120 | 19:30 | Savar | 128 | 00:00 | 120 | 10:00
Gollamari | 138 | 02:00 | 121 | 11:00 | SevenRings | 134 | 01:00 | 125 | 19:00
Gopalganj | 130 | 05:00 | 121 | 19:30 | ShahCement | 129 | 00:00 | 123 | 11:00
Gopalganj-400 | 134 | 07:00 | 127 | 19:30 | Shahjadpur | 135 | 02:00 | 132 | 23:00
Gulshan | 133 | 05:00 | 123 | 12:00 | Shahjibazar | 131 | 16:00 | 120 | 21:00
Halishahar | 139 | 21:00 | 131 | 10:00 | Shahmirpur | 138 | 19:00 | 130 | 02:00
Haripur | 129 | 00:00 | 123 | 11:00 | Shariatpur | 131 | 07:00 | 123 | 19:00
HaripurSBU | 130 | 04:00 | 123 | 11:00 | Sherpur | 136 | 18:30 | 121 | 01:00
Hasnabad | 131 | 04:00 | 124 | 11:00 | Shikalbaha | 128 | 10:00 | 123 | 04:00
Hathazari | 136 | 07:00 | 133 | 13:00 | Shikalbaha-230 | 139 | 08:00 | 135 | 17:00
Ishurdi | 138 | 06:00 | 132 | 18:30 | Shitalakhya | 130 | 06:00 | 122 | 12:00
Jaldhaka | 130 | 14:00 | 118 | 21:00 | Sholosohor | 135 | 18:00 | 128 | 18:30
Jamalpur | 138 | 19:30 | 124 | 01:00 | Shyampur | 128 | 00:00 | 123 | 12:00
Jashore | 131 | 06:00 | 113 | 22:00 | Shyampur-230 | 130 | 06:00 | 123 | 11:00
Jhenaidah | 133 | 05:00 | 120 | 19:30 | Siddhirganj | 130 | 05:00 | 123 | 10:00
Jhenaidah-230 | 134 | 06:00 | 121 | 19:30 | Sirajganj | 132 | 14:00 | 127 | 19:30
Joydebpur | 130 | 00:00 | 122 | 11:00 | Sonargaon | 127 | 17:00 | 121 | 12:00
Joypurhat | 127 | 14:00 | 114 | 12:00 | Sreemongol | 131 | 16:00 | 121 | 21:00
Juldah | 139 | 19:00 | 135 | 18:30 | Sreepur | 133 | 15:00 | 125 | 22:00
Kabirpur | 136 | 13:00 | 121 | 11:00 | Srinagar | 133 | 07:00 | 124 | 12:00
Kachua | 126 | 09:00 | 116 | 19:00 | SSM | 139 | 05:00 | 135 | 14:00
Kaliakoir | 137 | 06:00 | 131 | 10:00 | Sunamganj | 130 | 23:00 | 118 | 20:00
Kallyanpur | 129 | 02:00 | 121 | 12:00 | Sylhet | 130 | 06:00 | 124 | 21:00
Kalurghat | 133 | 03:00 | 129 | 14:00 | Sylhet-132 | 130 | 05:00 | 126 | 00:00
Kamrangirchar | 133 | 04:00 | 123 | 12:00 | Tangail | 131 | 13:00 | 122 | 23:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 139 | 03:00 | 123 | 21:00
Kasba | 125 | 08:00 | 119 | 17:00 | TK | 134 | 08:00 | 129 | 13:00
Kazla | 129 | 06:00 | 122 | 13:00 | Tongi | 135 | 01:00 | 127 | 21:00
Keranigonj | 133 | 06:00 | 124 | 19:00 | Ullahpara | 131 | 01:00 | 127 | 22:00
Khagrachori | 133 | 09:00 | 127 | 18:30 | Ullon | 133 | 04:00 | 123 | 12:00
Khulna | 134 | 07:00 | 117 | 19:30 | Uttara | 130 | 00:00 | 119 | 12:00
Khulna(S) | 136 | 06:00 | 120 | 19:30 | UttaraNew | 127 | 00:00 | 120 | 12:00
Khulshi | 134 | 00:00 | 131 | 10:00 | Zigatola | 133 | 06:00 | 124 | 13:00
Kishoreganj | 128 | 15:00 | 115 | 22:00
Kodda | 133 | 06:00 | 120 | 12:00
KSRM | 136 | 17:00 | 132 | 03:00
Kulaura | 133 | 08:00 | 128 | 00:00
Kurigram | 130 | 14:00 | 118 | 21:00
Kushtia | 135 | 05:00 | 126 | 19:30
Lalbag | 131 | 03:00 | 122 | 18:30
Lalmonirhat | 129 | 14:00 | 118 | 21:00
Madanganj | 128 | 00:00 | 122 | 10:00
Madaripur | 132 | 07:00 | 125 | 23:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division