## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 13-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-05-2025 | during | 13-05-2025 | during | 13-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 174.8 | 174.8 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 97.7 | 97.7 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 358 | 324 | 400.75 | 400.75 | 386 | 386 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 350 | 320 | 450 | 450 | 420 | 420 | Allocation limit by Titas Gas
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 150 | 150 | 150 | 150 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 335 | 332 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 57 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 12 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 148 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 19 | 18.8 | 30 | 30 | 23 | 23 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 20 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 33 | 33 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 32 | 17 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 95 | 294 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 95 | 113 | 135 | 135 | 135 | 135 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 88 | 88 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 47 | 104 | 104 | 50 | 50 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 90 | 162 | 162 | 90 | 90 | Liquid fuel shortage
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 300 | 584 | 584 | 500 | 500 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 150 | 250 | 583 | 583 | 250 | 250 | Allocation limit by Titas Gas
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 100 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2203 | 2828.8 | 5055.9 | 5055.9 | 3551.88 | 3587.88
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 15 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 145 | 148 | 145 | 150 | 145 | 150 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 68 | 105 | 105 | 87 | 87 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 16 | 77 | 64 | 76 | 64 | 76 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 101 | 98 | 98 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 3 | 3 | 22 | 3 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 70 | 70 | Engine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 4.09 | 0 | 4.09 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 15 | 74 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 53 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 54 | 144 | 144 | 144 | 144 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 531 | 612 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 5 | 8 | 5 | 8 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 530 | 551 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1443 | 2004 | 2778.95 | 2793.86 | 2722.95 | 2737.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 190 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 230 | 252 | 235 | 235 | 235 | 235 | ST Under Maintenance
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 345 | 345 | 345 | 345 | 345 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 37 | 37 | 46.94 | 46.94 | 46.94 | 46.94 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 52 | 52 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 26 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 38 | 130 | 150 | 150 | 140 | 140 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 30 | 24 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 80 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 127 | 155 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 20.83 | 24.5 | 20 | 20 | -
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 13 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 90 | 115 | 115 | 92 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 41 | 0 | 68 | 0 | 68 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1421 | 1687.2 | 2351.97 | 2287.64 | 2090.14 | 2051.14
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 12-05-2025 | during | 13-05-2025 | during | 13-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 22 | 22 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 55 | 168 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 103 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 15.78 | 0 | 31.9 | 0 | 31.9 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 108.78 | 318 | 583 | 549 | 315.5 | 353.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 36 | 38 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 142 | 154 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 78 | 83 | 83 | 78 | 78 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 275 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 363 | 336 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | -
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1168 | 1132 | 1291 | 1291 | 1197 | 1197
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 919 | 869 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 172 | 158 | 410 | 410 | 262 | 262 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 17 | 105 | 105 | 17 | 70 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 100.08 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 837 | 1208 | 617.1 | 617.1 | 1234.2 | 1234.2 | U#2 under shutdown
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2045.08 | 2252 | 2993.1 | 2895.1 | 3269.21 | 3224.21
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 413 | 402 | 300 | 300 | 300 | 300 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 105 | 125 | 125 | 125 | 125 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1102 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | -
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.66 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 2092.66 | 2289 | 2467.12 | 2466.12 | 2467.12 | 2466.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 23 | 47 | 47 | 47 | 47 | Engine Problem
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 5 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 27 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 186 | 178 | 214 | 214 | 206 | 206 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 165 | 189 | 220 | 220 | 202 | 202 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 22 | 22 | 22 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 92 | 92 | 92 | 92 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 18 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.65 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1221.28 | 1440.95 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 37.01 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 28 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 2053.94 | 2463.95 | 3192.07 | 3025.87 | 3124.28 | 2958.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 51 | 50 | 50 | 50 | 50 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 168 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 80 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 165 | 0 | 156.91 | 0 | 156.91 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 404 | 369 | 632.91 | 448 | 632.91 | 448
System Total |  |  |  |  | 27566.2 | 28624.082 | 12939.46 | 15343.95 | 21346.02 | 20812.49 | 19370.99 | 19023.79
Forecast Scenario (13-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14500 |  | 0 |  | 14500
|  |  |  | 1:00 | 13940 |  | 0 |  | 13940
|  |  |  | 2:00 | 13400 |  | 0 |  | 13400
|  |  |  | 3:00 | 12810 |  | 0 |  | 12810
|  |  |  | 4:00 | 12430 |  | 0 |  | 12430
|  |  |  | 5:00 | 12240 |  | 0 |  | 12240
|  |  |  | 6:00 | 11720 |  | 0 |  | 11720
|  |  |  | 7:00 | 11750 |  | 0 |  | 11750
|  |  |  | 8:00 | 11610 |  | 0 |  | 11610
|  |  |  | 9:00 | 12040 |  | 0 |  | 12040
|  |  |  | 10:00 | 12560 |  | 0 |  | 12560
|  |  |  | 11:00 | 13120 |  | 0 |  | 13120
|  |  |  | 12:00 | 13700 |  | 0 |  | 13700
|  |  |  | 13:00 | 14050 |  | 0 |  | 14050
|  |  |  | 14:00 | 14120 |  | 0 |  | 14120
|  |  |  | 15:00 | 14190 |  | 0 |  | 14190
|  |  |  | 16:00 | 14000 |  | 0 |  | 14000
|  |  |  | 17:00 | 13740 |  | 0 |  | 13740
|  |  |  | 18:00 | 13340 |  | 0 |  | 13340
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 14940 |  | 0 |  | 14940
|  |  |  | 19:30 | 15230 |  | 0 |  | 15230
|  |  |  | 20:00 | 15280 |  | 0 |  | 15280
|  |  |  | 21:00 | 15500 |  | 0 |  | 15500
|  |  |  | 22:00 | 15480 |  | 0 |  | 15480
|  |  |  | 23:00 | 15380 |  | 0 |  | 15380
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 13700.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 325.84 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:25 hrs on 13-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 12-05-2025 | [28 empty] | Date: | 12-05-2025 | [28 empty] | Date: | 12-05-2025 | [28 empty] | Date: | 12-05-2025 | [28 empty] | Date: | 12-05-2025 | [16 empty] | Date: | 12-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 17 | 113 | 147 | 175 | 0 | 35 | 90 | 0 | 67 | 300 | 150 | 250 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 90 | 17.5 | 21 | 0 | 300 | 33 | 15 | 12 | 0 | 0 | 94 | 76 | 14 | 100 | 100 | 0 | 40 | 38 | 22 | 554 | 90 | 0 | 19 | 17 | 69 | 147 | 0 | 0 | 0 | 1164 | 0 | 51 | 125 | 73 | 0 | 240 | 345 | 51 | 201 | 36 | 52 | 50 | 166 | 15 | 20 | 114 | 50 | 52.2 | 0 | 31 | 320 | 0 | 386 | 36 | 30 | 0 | 145 | 6 | 0 | 78 | 30 | 0 | 16 | 174 | 17 | 8 | 24 | 12 | 0 | 0 | 12 | 8059.7 | 926 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 17 | 1456 | 0 | 0 | 0 | 112 | 0 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 203 | 0 | 186 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 166 | 52 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 11 | 115 | 220 | 0 | 324 | 1102 | 150 | 6971 | 15030.7 | 77.94
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 113 | 97 | 195 | 10 | 0 | 54 | 0 | 50 | 300 | 150 | 250 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 34 | 17.5 | 21 | 0 | 300 | 58 | 15 | 12 | 0 | 0 | 101 | 70 | 17 | 100 | 100 | 0 | 40 | 103 | 22 | 556 | 90 | 0 | 40 | 17 | 85 | 147 | 0 | 0 | 0 | 1072 | 0 | 51 | 133 | 73 | 0 | 200 | 335 | 51 | 190 | 36 | 51 | 50 | 157 | 9 | 20 | 114 | 48 | 52.2 | 0 | 31 | 300 | 0 | 335 | 36 | 30 | 0 | 132 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 17 | 35 | 36 | 17 | 0 | 0 | 12 | 7818.7 | 926 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 17 | 1466 | 0 | 0 | 0 | 113 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 178 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 165 | 53 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 110 | 307 | 11 | 90 | 180 | 0 | 385 | 1090 | 124 | 6875 | 14693.7 | 77.93
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 113 | 97 | 195 | 55 | 0 | 54 | 0 | 50 | 300 | 150 | 250 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 17 | 17.5 | 21 | 0 | 300 | 0 | 0 | 12 | 0 | 0 | 101 | 70 | 0 | 100 | 100 | 0 | 40 | 34 | 22 | 552 | 53 | 0 | 50 | 17 | 34 | 147 | 0 | 0 | 0 | 972 | 0 | 51 | 118 | 8 | 0 | 200 | 300 | 51 | 193 | 35 | 55 | 50 | 154 | 9 | 20 | 114 | 44 | 52.2 | 0 | 31 | 305 | 0 | 339 | 36 | 30 | 0 | 134 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 17 | 46 | 83 | 17 | 0 | 0 | 12 | 7460.7 | 925 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 604 | 17 | 1458 | 0 | 0 | 0 | 113 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 177 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 164 | 51 | 50 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 180 | 0 | 416 | 1090 | 0 | 6483 | 13943.7 | 77.92
03:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 113 | 98 | 45 | 15 | 0 | 54 | 0 | 16 | 300 | 150 | 250 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 17 | 17.5 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 4 | 51 | 48 | 0 | 100 | 100 | 0 | 40 | 34 | 24 | 552 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 912 | 0 | 51 | 115 | 8 | 0 | 200 | 300 | 50 | 193 | 35 | 68 | 50 | 150 | 9 | 20 | 114 | 44 | 52.2 | 0 | 32 | 295 | 0 | 359 | 36 | 30 | 0 | 129 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 0 | 46 | 97 | 17 | 0 | 0 | 12 | 6944.7 | 925 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 606 | 17 | 1468 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 180 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 166 | 51 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 180 | 0 | 416 | 1092 | 0 | 6340 | 13284.7 | 77.91
04:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 113 | 98 | 0 | 15 | 0 | 54 | 0 | 16 | 420 | 150 | 0 | 0 | 35 | 0 | 335 | 0 | 0 | 0 | 0 | 17.5 | 21 | 0 | 500 | 0 | 0 | 0 | 0 | 8 | 51 | 48 | 0 | 100 | 60 | 0 | 40 | 0 | 24 | 553 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 30 | 8 | 0 | 250 | 345 | 51 | 182 | 35 | 69 | 50 | 147 | 9 | 20 | 114 | 42 | 16 | 0 | 32 | 300 | 0 | 347 | 36 | 30 | 0 | 145 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 0 | 46 | 96 | 17 | 0 | 0 | 12 | 6603.5 | 926 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 17 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 182 | 0 | 0 | 0 | 376 | 0 | 0 | 0 | 166 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 416 | 1110 | 0 | 6316 | 12919.5 | 77.9
05:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 17 | 113 | 98 | 0 | 15 | 0 | 17 | 0 | 16 | 420 | 151 | 0 | 0 | 35 | 0 | 335 | 0 | 0 | 0 | 0 | 17.5 | 21 | 0 | 450 | 0 | 0 | 0 | 0 | 8 | 51 | 16 | 0 | 48 | 24 | 0 | 40 | 0 | 27 | 553 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 0 | 51 | 10 | 8 | 0 | 248 | 345 | 51 | 189 | 35 | 69 | 50 | 120 | 9 | 20 | 64 | 40 | 16 | 0 | 32 | 300 | 0 | 354 | 36 | 30 | 0 | 130 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 0 | 49 | 96 | 17 | 0 | 0 | 12 | 6280.5 | 926 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 0 | 1454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 181 | 0 | 0 | 0 | 382 | 0 | 0 | 0 | 163 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 292 | 11 | 105 | 220 | 0 | 415 | 1220 | 0 | 6426 | 12706.5 | 77.89
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 114 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 420 | 150 | 65 | 0 | 0 | 0 | 335 | 0 | 0 | 1 | 0 | 17.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 14 | 37 | 16 | 0 | 48 | 24 | 0 | 40 | 0 | 33 | 553 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 612 | 1 | 51 | 0 | 8 | 0 | 250 | 345 | 51 | 198 | 35 | 57 | 50 | 105 | 9 | 20 | 52 | 36 | 16 | 5 | 32 | 305 | 0 | 351 | 36 | 30 | 0 | 132 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 0 | 48 | 45 | 17 | 0 | 1.88 | 12 | 6149.38 | 926 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 607 | 0 | 1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.14 | 206 | 0 | 181 | 0 | 0 | 0 | 400 | 0 | 0.06 | 0 | 165 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0.04 | 0 | 200 | 11 | 105 | 220 | 0 | 415 | 1020 | 0 | 6026.24 | 12175.62 | 77.88
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 112 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 150 | 65 | 0 | 0 | 0 | 335 | 0 | 0 | 4 | 0 | 17.5 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 1 | 17 | 16 | 0 | 48 | 24 | 0 | 40 | 0 | 34 | 551 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 600 | 3 | 51 | 0 | 8 | 0 | 249 | 345 | 51 | 198 | 35 | 51 | 50 | 111 | 9 | 20 | 52 | 34 | 16 | 2 | 32 | 315 | 0 | 365 | 36 | 30 | 0 | 137 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 0 | 24 | 24 | 11 | 0 | 3.62 | 12 | 6053.12 | 926 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 605 | 0 | 1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 10.72 | 206 | 0 | 182 | 0 | 0 | 0 | 402 | 0 | 0.59 | 0 | 163 | 52 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0.1 | 0 | 200 | 9 | 115 | 220 | 0 | 415 | 999 | 0 | 6060.41 | 12113.53 | 77.87
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 115 | 98 | 0 | 0 | 0 | 0 | 0 | 16 | 340 | 150 | 65 | 0 | 0 | 0 | 335 | 0 | 0 | 6 | 0 | 16 | 21 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 48 | 24 | 0 | 40 | 0 | 6 | 551 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 602 | 7 | 51 | 0 | 8 | 0 | 250 | 345 | 52 | 193 | 35 | 51 | 50 | 114 | 9 | 20 | 52 | 32 | 16 | 22 | 31 | 300 | 0 | 382 | 36 | 30 | 0 | 131 | 0 | 0 | 40 | 30 | 0 | 18 | 173 | 0 | 45 | 75 | 5 | 1 | 0 | 12 | 5916 | 877 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 601 | 0 | 1320.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 10.64 | 180 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0.78 | 0 | 162 | 52 | 0 | 15 | 0 | 0 | 0 | 2.1 | 14 | 0.33 | 0 | 200 | 8 | 90 | 220 | 0 | 417 | 1082 | 0 | 6134.16 | 12050.16 | 77.86
09:00 | 0 | 52 | 10 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 112 | 82 | 0 | 0 | 0 | 0 | 0 | 16 | 340 | 150 | 65 | 0 | 0 | 0 | 335 | 0 | 0 | 5 | 0 | 15 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 3 | 17 | 16 | 0 | 48 | 24 | 1 | 40 | 0 | 2 | 504 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 602 | 9 | 51 | 0 | 8 | 0 | 250 | 345 | 51 | 187 | 33 | 69 | 45 | 128 | 9 | 20 | 52 | 32 | 16 | 50 | 31 | 310 | 0 | 380 | 36 | 30 | 0 | 143 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 0 | 45 | 55 | 5 | 0 | 5.18 | 12 | 6041.18 | 876 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.89 | 596 | 0 | 1318.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 5.97 | 180 | 0 | 192 | 0 | 0 | 0 | 414 | 0 | 0.48 | 0 | 162 | 51 | 0 | 12 | 0 | 0 | 0 | 2.2 | 27 | 0.48 | 0 | 200 | 7 | 100 | 220 | 0 | 415 | 1094 | 0 | 6170.14 | 12211.32 | 77.85
10:00 | 0 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 17 | 114 | 82 | 0 | 0 | 11 | 10 | 0 | 16 | 400 | 150 | 65 | 0 | 0 | 0 | 335 | 0 | 0 | 17 | 0 | 0 | 21 | 0 | 350 | 0 | 0 | 0 | 0 | 13 | 17 | 16 | 0 | 48 | 24 | 4 | 40 | 0 | 2 | 560 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 0 | 612 | 16 | 51 | 0 | 8 | 0 | 245 | 345 | 52 | 191 | 33 | 69 | 40 | 127 | 9 | 12 | 52 | 32 | 8 | 42 | 30 | 310 | 0 | 356 | 36 | 30 | 0 | 155 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 0 | 45 | 55 | 5 | 2 | 12.55 | 12 | 6196.55 | 919 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.48 | 592 | 0 | 1317.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 48.01 | 180 | 0 | 193 | 0 | 0 | 0 | 414 | 0 | 3.75 | 0 | 162 | 50 | 0 | 14 | 0 | 0 | 0 | 4 | 175 | 0.29 | 0 | 250 | 7 | 100 | 220 | 0 | 415 | 1095 | 0 | 6508.94 | 12705.49 | 77.84
11:00 | 0 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 17 | 100 | 64 | 60 | 0 | 35 | 108 | 0 | 16 | 400 | 150 | 130 | 0 | 0 | 0 | 335 | 0 | 0 | 32 | 0 | 19 | 21 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 75 | 24 | 2 | 40 | 0 | 2 | 552 | 0 | 0 | 0 | 0 | 1 | 149 | 0 | 0 | 0 | 612 | 19 | 51 | 2 | 8 | 0 | 250 | 345 | 52 | 181 | 33 | 69 | 35 | 130 | 9 | 12 | 52 | 30 | 8 | 18 | 32 | 315 | 0 | 338 | 36 | 30 | 0 | 155 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 0 | 35 | 55 | 5 | 2 | 8.78 | 12 | 6450.78 | 918 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.89 | 596 | 0 | 1263.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 37.55 | 180 | 0 | 194 | 0 | 0 | 0 | 300 | 0 | 2.26 | 0 | 166 | 49 | 0 | 30 | 0 | 0 | 0 | 2.8 | 147 | 0.67 | 0 | 307 | 7 | 100 | 180 | 0 | 414 | 1118 | 0 | 6377.96 | 12828.74 | 77.83
12:00 | 0 | 52 | 32 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 12 | 17 | 95 | 48 | 95 | 0 | 35 | 108 | 0 | 16 | 350 | 150 | 150 | 0 | 0 | 0 | 335 | 0 | 0 | 31 | 0 | 19 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 88 | 24 | 3 | 40 | 15 | 2 | 530 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 531 | 15 | 51 | 38 | 8 | 0 | 230 | 345 | 52 | 190 | 37 | 69 | 30 | 127 | 13 | 17 | 105 | 30 | 8 | 41 | 30 | 300 | 0 | 363 | 36 | 30 | 0 | 142 | 0 | 0 | 75 | 30 | 0 | 18 | 174 | 0 | 24 | 55 | 0 | 2 | 15.78 | 12 | 6343.78 | 919 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.08 | 837 | 17 | 1221.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 37.01 | 186 | 0 | 165 | 0 | 0 | 0 | 414 | 0 | 2.65 | 0 | 169 | 50 | 0 | 15 | 0 | 0 | 0 | 5 | 165 | 0.66 | 0 | 250 | 7 | 100 | 220 | 0 | 413 | 1102 | 0 | 6595.68 | 12939.46 | 77.83
13:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 15 | 17 | 100 | 48 | 95 | 0 | 35 | 108 | 0 | 16 | 300 | 150 | 250 | 0 | 17 | 0 | 331 | 0 | 0 | 29 | 0 | 19 | 16 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 88 | 24 | 3 | 40 | 17 | 8 | 560 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 606 | 8 | 51 | 50 | 8 | 0 | 209 | 345 | 50 | 184 | 36 | 68 | 30 | 120 | 14 | 20 | 105 | 34 | 8 | 48 | 30 | 305 | 0 | 353 | 36 | 30 | 0 | 154 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 0 | 24 | 55 | 0 | 0 | 53.07 | 12 | 6572.07 | 918 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.83 | 1007 | 17 | 1260.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 18.44 | 192 | 0 | 187 | 0 | 0 | 0 | 414 | 0 | 1.53 | 0 | 168 | 50 | 0 | 21 | 0 | 0 | 0 | 2 | 60 | 0.64 | 0 | 291 | 8 | 105 | 220 | 0 | 366 | 1105 | 0 | 6760.41 | 13332.48 | 77.82
14:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 17 | 90 | 64 | 95 | 0 | 35 | 108 | 0 | 32 | 300 | 150 | 250 | 0 | 35 | 0 | 300 | 0 | 0 | 8 | 0 | 19 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 0 | 88 | 44 | 3 | 40 | 17 | 5 | 554 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 606 | 15 | 51 | 50 | 8 | 0 | 239 | 345 | 52 | 194 | 36 | 69 | 40 | 111 | 9 | 20 | 114 | 34 | 8 | 53 | 30 | 315 | 0 | 379 | 36 | 30 | 0 | 151 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 0 | 45 | 85 | 0 | 2 | 6.67 | 12 | 6633.67 | 919 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.47 | 1015 | 17 | 1264.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 0 | 43.59 | 187 | 0 | 188 | 0 | 0 | 0 | 350 | 0 | 4.66 | 0 | 160 | 50 | 0 | 7 | 0 | 0 | 0 | 1.7 | 72 | 0.58 | 0 | 307 | 8 | 115 | 220 | 0 | 366 | 1150 | 0 | 6763.44 | 13397.11 | 77.82
15:00 | 0 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 17 | 17 | 77 | 95 | 100 | 0 | 35 | 108 | 0 | 32 | 320 | 150 | 250 | 0 | 35 | 0 | 330 | 0 | 0 | 11 | 6 | 19 | 14 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 88 | 75 | 3 | 40 | 17 | 2 | 556 | 8 | 0 | 0 | 0 | 19 | 144 | 0 | 0 | 0 | 608 | 12 | 51 | 68 | 26 | 0 | 238 | 345 | 51 | 194 | 30 | 69 | 50 | 120 | 9 | 20 | 114 | 36 | 25 | 40 | 34 | 315 | 0 | 382 | 36 | 30 | 0 | 157 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 0 | 48 | 95 | 0 | 2 | 37.42 | 12 | 6902.42 | 918 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.15 | 1105 | 17 | 1311.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 34.23 | 187 | 0 | 188 | 0 | 0 | 0 | 414 | 0 | 2.59 | 0 | 162 | 50 | 0 | 9 | 0 | 0 | 0 | 0.9 | 72 | 0.46 | 0 | 307 | 8 | 105 | 220 | 0 | 366 | 1185 | 0 | 6932.03 | 13834.45 | 77.81
16:00 | 8 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 17 | 77 | 95 | 145 | 8 | 35 | 90 | 0 | 50 | 320 | 150 | 250 | 0 | 35 | 0 | 330 | 0 | 0 | 12 | 35 | 19 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 51 | 52 | 0 | 88 | 75 | 2 | 38 | 30 | 2 | 552 | 17 | 0 | 0 | 0 | 34 | 144 | 0 | 0 | 0 | 608 | 9 | 51 | 103 | 26 | 0 | 239 | 345 | 52 | 187 | 34 | 69 | 70 | 101 | 25 | 20 | 114 | 34 | 16 | 27 | 30 | 295 | 0 | 348 | 36 | 30 | 0 | 146 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 0 | 64 | 103 | 0 | 1 | 22.45 | 12 | 7027.45 | 918 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.52 | 1100 | 40 | 1218.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 21.14 | 186 | 0 | 188 | 0 | 0 | 0 | 350 | 0 | 2 | 0 | 167 | 50 | 0 | 7 | 0 | 0 | 0 | 0.5 | 74 | 0.06 | 0 | 307 | 8 | 115 | 220 | 0 | 300 | 1150 | 0 | 6678.61 | 13706.06 | 77.81
17:00 | 24 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 17 | 17 | 104 | 95 | 145 | 15 | 35 | 90 | 0 | 34 | 320 | 150 | 250 | 0 | 17 | 0 | 330 | 0 | 0 | 6 | 35 | 18.8 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 60 | 62 | 0 | 70 | 38 | 0 | 39 | 34 | 4 | 557 | 0 | 0 | 0 | 0 | 17 | 144 | 0 | 0 | 0 | 608 | 3 | 51 | 122 | 26 | 0 | 239 | 345 | 51 | 196 | 37 | 68 | 70 | 97 | 31 | 20 | 88 | 34 | 8 | 11 | 30 | 300 | 0 | 366 | 36 | 30 | 0 | 129 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 0 | 65 | 105 | 0 | 1 | 9.72 | 12 | 6923.52 | 918 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.42 | 1007 | 17 | 1212.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 9.31 | 184 | 0 | 188 | 0 | 0 | 0 | 350 | 0 | 0.86 | 0 | 168 | 50 | 0 | 2 | 0 | 0 | 0 | 0.1 | 26 | 0 | 0 | 307 | 5 | 105 | 220 | 0 | 320 | 1050 | 0 | 6327.21 | 13250.73 | 77.8
18:00 | 24 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 17 | 112 | 95 | 145 | 15 | 35 | 72 | 0 | 16 | 320 | 150 | 250 | 0 | 17 | 0 | 327 | 0 | 0 | 1 | 35 | 18.8 | 19 | 0 | 300 | 0 | 0 | 0 | 0 | 2 | 68 | 63 | 0 | 60 | 38 | 0 | 40 | 34 | 4 | 557 | 0 | 0 | 0 | 0 | 17 | 145 | 0 | 0 | 0 | 587 | 0 | 51 | 128 | 26 | 0 | 200 | 345 | 51 | 202 | 37 | 68 | 70 | 90 | 39 | 20 | 70 | 34 | 8 | 1 | 22 | 300 | 0 | 335 | 36 | 30 | 0 | 131 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 0 | 70 | 115 | 0 | 0 | 1.99 | 12 | 6843.79 | 919 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.64 | 1010 | 17 | 1211.06 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 2.02 | 182 | 0 | 160 | 0 | 0 | 0 | 300 | 0 | 0.18 | 0 | 168 | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 200 | 3 | 115 | 220 | 0 | 320 | 1011 | 0 | 6062.9 | 12906.69 | 77.8
19:00 | 42 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 54 | 17 | 113 | 142 | 245 | 18 | 35 | 90 | 0 | 32 | 320 | 150 | 250 | 0 | 35 | 0 | 325 | 0 | 0 | 0 | 76 | 18.8 | 20 | 0 | 300 | 5 | 15 | 0 | 0 | 4 | 101 | 75 | 0 | 100 | 95 | 0 | 40 | 37 | 2 | 553 | 34 | 0 | 0 | 0 | 24 | 145 | 0 | 0 | 0 | 612 | 0 | 51 | 130 | 26 | 0 | 240 | 345 | 52 | 203 | 37 | 74 | 80 | 108 | 39 | 20 | 114 | 40 | 43 | 0 | 22 | 320 | 0 | 398 | 38 | 30 | 0 | 156 | 0 | 0 | 78 | 30 | 0 | 18 | 174 | 8 | 103 | 127 | 0 | 0 | 0 | 12 | 7679.8 | 869 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1085 | 17 | 1378.47 | 0 | 0 | 0 | 1 | 5 | 97 | 0 | 12 | 0 | 0 | 22 | 0 | 173 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 51 | 41 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 122 | 220 | 0 | 320 | 1085 | 0 | 6785.47 | 14465.27 | 77.79
19:30 | 57 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 54 | 17 | 113 | 148 | 294 | 55 | 35 | 90 | 0 | 47 | 320 | 150 | 250 | 0 | 35 | 0 | 332 | 0 | 0 | 0 | 100 | 18.8 | 20 | 0 | 300 | 53 | 15 | 0 | 0 | 0 | 101 | 77 | 0 | 100 | 100 | 0 | 40 | 74 | 3 | 551 | 54 | 0 | 0 | 8 | 68 | 148 | 0 | 0 | 0 | 612 | 0 | 51 | 130 | 26 | 0 | 252 | 345 | 52 | 181 | 37 | 90 | 80 | 155 | 38 | 20 | 114 | 40 | 52.2 | 0 | 24 | 275 | 0 | 336 | 38 | 30 | 0 | 154 | 0 | 0 | 78 | 30 | 0 | 18 | 173 | 35 | 103 | 168 | 0 | 0 | 0 | 12 | 7970 | 869 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1208 | 17 | 1440.95 | 0 | 23 | 0 | 50 | 5 | 97 | 18 | 27 | 0 | 0 | 22 | 0 | 178 | 0 | 189 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 51 | 70 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 105 | 220 | 0 | 402 | 1244 | 0 | 7373.95 | 15343.95
20:00 | 8 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 54 | 17 | 113 | 148 | 95 | 15 | 35 | 90 | 0 | 32 | 320 | 150 | 250 | 0 | 35 | 0 | 330 | 0 | 0 | 0 | 108 | 18.8 | 20 | 0 | 300 | 43 | 0 | 0 | 0 | 0 | 101 | 77 | 0 | 100 | 48 | 0 | 40 | 80 | 4 | 553 | 0 | 0 | 0 | 8 | 84 | 146 | 0 | 0 | 0 | 612 | 0 | 51 | 130 | 26 | 0 | 246 | 345 | 52 | 180 | 37 | 90 | 80 | 155 | 38 | 20 | 114 | 38 | 25 | 0 | 30 | 290 | 0 | 368 | 38 | 30 | 0 | 151 | 5 | 0 | 81 | 30 | 0 | 18 | 173 | 17 | 104 | 169 | 0 | 0 | 0 | 12 | 7588.8 | 774 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1446.22 | 0 | 40 | 0 | 57 | 10 | 97 | 0 | 37 | 0 | 0 | 22 | 0 | 177 | 0 | 189 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 162 | 51 | 70 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 406 | 1230 | 0 | 7268.42 | 14857.22 | 77.79
21:00 | 8 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 17 | 113 | 148 | 95 | 15 | 35 | 90 | 0 | 30 | 350 | 150 | 250 | 0 | 35 | 0 | 330 | 0 | 0 | 0 | 70 | 18.8 | 20 | 0 | 300 | 17 | 0 | 0 | 0 | 4 | 101 | 77 | 0 | 100 | 48 | 0 | 40 | 110 | 2 | 550 | 0 | 0 | 0 | 8 | 87 | 145 | 0 | 0 | 0 | 612 | 0 | 51 | 135 | 26 | 0 | 243 | 345 | 52 | 197 | 37 | 90 | 90 | 155 | 39 | 20 | 114 | 40 | 25 | 0 | 31 | 320 | 0 | 350 | 38 | 30 | 0 | 156 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 104 | 169 | 0 | 0 | 0 | 12 | 7640.8 | 774 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1445.95 | 0 | 40 | 0 | 70 | 0 | 97 | 0 | 37 | 0 | 0 | 22 | 0 | 178 | 0 | 185 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 51 | 70 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 400 | 1244 | 0 | 7348.15 | 14988.95 | 77.78
22:00 | 8 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 54 | 17 | 113 | 148 | 95 | 15 | 35 | 90 | 0 | 20 | 350 | 150 | 250 | 0 | 35 | 0 | 325 | 0 | 0 | 0 | 70 | 18.8 | 20 | 0 | 300 | 18 | 15 | 0 | 0 | 2 | 84 | 77 | 0 | 100 | 70 | 0 | 40 | 110 | 7 | 553 | 0 | 0 | 0 | 8 | 87 | 146 | 0 | 0 | 0 | 612 | 0 | 51 | 138 | 26 | 0 | 241 | 345 | 52 | 207 | 37 | 90 | 90 | 136 | 39 | 20 | 114 | 40 | 25 | 0 | 31 | 310 | 0 | 350 | 36 | 30 | 0 | 156 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 104 | 172 | 0 | 0 | 0 | 12 | 7631.8 | 774 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 0 | 1440.09 | 0 | 40 | 0 | 75 | 0 | 97 | 0 | 37 | 0 | 0 | 22 | 0 | 177 | 0 | 179 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 165 | 51 | 98 | 0 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 115 | 220 | 0 | 450 | 1244 | 0 | 7099.09 | 14730.89 | 77.78
23:00 | 40 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 43 | 17 | 113 | 148 | 195 | 30 | 35 | 90 | 0 | 32 | 350 | 142 | 250 | 0 | 35 | 0 | 274 | 0 | 0 | 0 | 70 | 20 | 20 | 0 | 300 | 52 | 30 | 0 | 0 | 5 | 84 | 77 | 0 | 100 | 100 | 0 | 40 | 110 | 10 | 553 | 26 | 0 | 0 | 8 | 87 | 148 | 0 | 0 | 0 | 612 | 0 | 51 | 132 | 26 | 0 | 246 | 345 | 52 | 191 | 37 | 88 | 90 | 136 | 38 | 20 | 114 | 44 | 26 | 0 | 32 | 310 | 0 | 335 | 38 | 30 | 0 | 154 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 33 | 105 | 163 | 0 | 0 | 0 | 10 | 7826 | 822 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 589 | 48 | 1461.71 | 0 | 40 | 0 | 110 | 0 | 97 | 25 | 37 | 0 | 0 | 22 | 0 | 177 | 0 | 181 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 162 | 51 | 115 | 0 | 106 | 0 | 0 | 0 | 0 | 0 | 60 | 307 | 10 | 115 | 220 | 0 | 448 | 1244 | 6 | 6999.71 | 14825.71 | 77.77
Total KWH | 249984 | 788160 | 482400 | 0 | 0 | 0 | 0 | 0 | 8504000 | 0 | 0 | 393480 | 432720 | 2594592 | 2428800 | 2349011 | 378960 | 536203 | 1573920 | 0 | 639360 | 8377500 | 3541498 | 4372952 | 0 | 531138 | 0 | 7743685 | 0 | 0 | 156930 | 660000 | 426000 | 448560 | 0 | 8271363.64 | 345000 | 140509 | 35520 | 0 | 66720 | 1295482 | 999456 | 23547 | 1960320 | 1298880 | 21941 | 952200 | 955962 | 283680 | 13265454.55 | 312800 | 0 | 144480 | 102726 | 773636 | 3520007 | 0 | 0 | 0 | 15894544 | 109350 | 1329656 | 1843345 | 451636 | 0 | 5864500 | 8230000 | 1233120 | 4772000 | 850896 | 1663680 | 1386040 | 3056160 | 459480 | 459440 | 2266320 | 901440 | 557352 | 408773 | 720192 | 7438000 | 0 | 9096000 | 867000 | 684840 | 0 | 3456900 | 28104 | 0 | 1861440 | 718752 | 0 | 432000 | 3592420 | 147600 | 1407600 | 2275200 | 121920 | 10000 | 165340 | 291600 | 167432177.19 | 21557091 | 4241088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 694800 | 19752727 | 348000 | 31526546 | 0 | 180831 | 0 | 774432 | 14395 | 528972 | 289056 | 156019 | 2189 | 583710 | 118822 | 266248 | 4568636 | 0 | 4615536 | 0 | 0 | 0 | 9149818 | 0 | 22200 | 0 | 3998000 | 1184290 | 707917 | 124738 | 790281 | 0 | 0 | 22914.48 | 773280 | 4102 | 270720 | 6633000 | 223274 | 2591000 | 5255820 | 0 | 9446328 | 27671272.73 | 301200 | 159389253.21 | 326821430.4

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 12-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12939.46 | MW | 12:00 Hr. | Energy Generated |  |  | 326.8214 |  | MKWHr.
| Day Peak Demand |  |  | 12967.46 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.265 |  | MKWHr.
| Evening Peak Generation |  |  | 15343.95 | MW | 19:30 Hr. | Energy Demand |  |  | 327.0864 |  | MKWHr.
| Evening Peak Demand |  |  | 15343.95 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.3 |  | °C
| Minimum Generation of the Day |  |  | 12050.16 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 962.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 15343.95 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.8301 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.6856 | 0 | 14.0387 | 0 | 0 | 0.15693 | 0 | 0 | 55.8812 | Gas | 129.0091 | Gas | 459538455.5488
| Chattogram Zone |  |  | 3.8037 | 29.16 | 8.3883 | 0 | 0.9522 | 0.13129 | 0 | 0.06672 | 42.5022 | Coal | 97.8456 | Coal | 639834890.4465
| Cumilla Zone |  |  | 24.5773 | 0 | 10.5665 | 0 | 0 | 0.40877 | 0.90144 | 0 | 36.454 | HFO | 41.5984 | HFO | 779265809.85
| Mymensingh Zone |  |  | 0.12192 | 0 | 4.122 | 0 | 0 | 0.17534 | 0 | 0 | 4.4193 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.1755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1755 | Hydro | 0.9522 | Hydro | 95220
| Khulna Zone |  |  | 4.2411 | 19.7527 | 0.348 | 0 | 0 | 0.6948 | 21.5571 | 0 | 46.5937 | Solar | 3.3643 | Solar | 53723897.8428
| Barishal Zone |  |  | 8.0701 | 43.7506 | 0.57192 | 0 | 0 | 0.004102 | 0 | 0 | 52.3967 | Import | 53.9851 | Import | 298801357.27
| Rajshahi Zone |  |  | 18.334 | 0 | 2.0647 | 0 | 0 | 0.87216 | 31.5265 | 0 | 52.7974 | Wind | 0.06672 | Wind | 976780.8
| Rangpur Zone |  |  | 0 | 5.1823 | 1.4982 | 0 | 0 | 0.92093 | 0 | 0 | 7.6014
| Total |  |  | 129.0091 | 97.8456 | 41.5984 | 0 | 0.9522 | 3.3643 | 53.9851 | 0.06672 | 326.8214
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 459538455.5488 |  | Hydro | 95220
|  |  |  | Coal | 639834890.4465 |  | Solar | 53723897.8428
|  |  |  | HFO | 779265809.85 |  | Import | 298801357.27
|  |  |  | HSD | 0 |  | Wind | 976780.8
[5 empty] | Total: | 223,22,36,411 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.5571 | Peak Hr Flow | 869.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48160272.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.5265 | Peak Hr Flow | 1440.95 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 666 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.90144 | Peak Hr Flow | 40.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1120 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.9851 | Peak Hr Flow | 2349.95 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5609
|  |  |  | Chattogram |  | 0 |  | 1563
|  |  |  | Cumilla |  | 0 |  | 1397
|  |  |  | Mymensingh |  | 0 |  | 1080
|  |  |  | Sylhet |  | 0 |  | 472
|  |  |  | Khulna |  | 0 |  | 1810
|  |  |  | Barishal |  | 0 |  | 418
|  |  |  | Rajshahi |  | 0 |  | 1505
|  |  |  | Rangpur |  | 0 |  | 915
|  |  |  | Total |  | 0 |  | 14769
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Meghnaghat 104 MW PP (OPCL) |  |  | 104
|  | 3 | Meghnaghat CCPP(Summit) GT-1 |  |  | 110 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115 | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 410 |  |  |  | Total | 539.09
|  |  |  | Total Unavailable Capacity |  |  |  | 949.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:22 | Shahjibazar 132/33kV S/S TR-06 LT is restored.
|  | 08:22 | Shahjibazar 132/33kV S/S TR-04 LT is restored.
| 09:49 | 13:50 | Cumilla(N)-Kachua 132 kV Ckt-2 Project Work S/D from Kachua 132/33kV end Due to Project
work
| 09:49 | 13:49 | Cumilla(S)-Kachua 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end.
| 09:55 |  | Mirpur 132/33kV S/S RPC Main Scheduled S/D Due to Replacement work of unit-2
| 09:56 | 13:38 | Kachua 132/33kV S/S Main Bus-2 Project Work S/D Due to For project work
|  | 10:01 | Jhenaidah 132/33kV S/S Jhenaidah1-Jhenaidah2,132kV Circuit-2(L3) is restored.
|  | 10:02 | Jhenaidah 230/132kV S/S Jhenaidah (New)-Jhenaidah (Old) Ckt-2 is restored.
| 10:40 | 20:24 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT Scheduled S/D Due to CT raiser string repair
| 10:40 | 20:24 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Scheduled S/D Due to 33kv CT raiser string
repair
|  | 10:56 | Rampal 400/230kV S/S Generator Transformer-1 (GT-1) HT is restored.
| 10:56 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U1
| 11:07 |  | GPH 230/33kV S/S Transformer-01(D05) HT Tripped showing 86.1,86.2,87T1/T2 relays Due to | [7 empty] | 50.0MW load
|  |  | internal fault | [7 empty] | interrup.
| 12:00 |  | Day peak Generation is 12937 MW
| 12:12 | 12:25 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent relay P142 relays Due to Due
to Nikra Feeder fault.
| 12:42 | 14:09 | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 kV ashulia feeder Bus DS High | [7 empty] | 80.0MW load
|  |  | temperature maintenance. | [7 empty] | interrup.
| 13:10 | 17:55 | Sherpur 132/33kV S/S Transformer- 03 HT Scheduled S/D Due to Blast Wall Painting
| 13:10 | 17:56 | Sherpur 132/33kV S/S Transformer- 03 LT Scheduled S/D Due to Blast Wall Painting
| 13:42 | 13:48 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent relay P142 relays Due to Due
to 33kv Dohar & Nikra feeder fault.
| 16:43 | 16:59 | Gopalganj 132/33kV S/S T2 LT Tripped showing Inst over current relays Due to Reb- 8 | [7 empty] | 50.0MW load
|  |  | feeder fault. | [7 empty] | interrup.
| 19:30 |  | Evening peak generation 15342 MW
| 21:40 | 22:37 | Bhaluka 132/33kV S/S Transformer- 02 LT Scheduled S/D Due to Red Hot maintenance at 33 kV | [7 empty] | 35.0MW load
|  |  | feeder. | [7 empty] | interrup.
| 21:42 | 22:36 | Bhaluka 132/33kV S/S Transformer- 02 HT Scheduled S/D Due to Red Hot maintenance at 33 kV | [7 empty] | 35.0MW load
|  |  | feeder. | [7 empty] | interrup.
| 04:57 |  | Bhaluka-Mymensingh 132 kV Ckt-2 Scheduled S/D from Bhaluka 132/33kV end Due to Emergency
maintenance work.
| 04:57 |  | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Bhaluka 132/33kV end Due to Emergency
maintenance work.
| 05:26 |  | Bhaluka 132/33kV S/S Bus A Scheduled S/D Due to Maintenance work
| 05:28 |  | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) LT Scheduled S/D Due to Red Hot
Maintenance
| 05:29 |  | Agargaon 230/132kV S/S 230kV Transformer-2 ( 715T2) HT Scheduled S/D Due to Red Hot
Maintenance
| 05:37 | 07:40 | Thakurgaon 132/33kV S/S Panchagar CKT-2 Tripped showing SIPROTEC relays. | [7 empty] | 15.0MW load
interrup.
| 05:37 | 05:58 | Panchagar-Thakurgaon 132kV Ckt-1 Tripped from Thakurgaon 132/33kV end showing Micom P442 | [7 empty] | 15.0MW load
|  |  | relays. | [7 empty] | interrup.
Thakurgaon 132/33kV
end
| 06:00 |  | Minimum generation: 12251 MW
| 06:51 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 LT Forced S/D Due to T-2 33 kv bus Amtoli feeder | [7 empty] | 35.0MW load
|  |  | bus loop Red hot maintenance work. | [7 empty] | interrup.
| 06:52 |  | Mahasthangarh 132/33kV S/S 416T MTR 2 HT Forced S/D Due to T-2 33 kv bus Amtoli feeder | [7 empty] | 35.0MW load
|  |  | bus loop Red hot maintenance work.. | [7 empty] | interrup.
| 07:43 |  | Tongi 230/132/33kV S/S Tongi-Uttara Ckt Scheduled S/D Due to Shutdown taken by NLDC
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 12-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas Gas
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 324 | 8504000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 8377500 | Allocation limit by Titas Gas
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3541498 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 378960 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7743685 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 57 | 249984 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 393480 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 148 | 2428800 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 536203 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 531138 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18.8 | 426000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 20 | 448560 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 482400 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 294 | 2349011 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 2594592 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 788160 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 47 | 639360 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 90 | 1573920 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 156930 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 8271363.64 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 250 | 4372952 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 100 | 660000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2828.8 | 55881216.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Both units are under maintenance
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 102726 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 109350 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 144480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 952200 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 148 | 3520007 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 773636 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 77 | 999456 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 101 | 1295482 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1960320 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 3 | 283680 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 35520 | Liquid fuel shortage
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 21941 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 140509 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 23547 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 74 | 955962 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1298880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 53 | 345000 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 54 | 312800 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 15894544 | machine problem
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 66720 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 551 | 13265454.55 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2004 | 42502214.55
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4772000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 252 | 5864500 | ST Under Maintenance
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8230000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 37 | 850896 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 52 | 1233120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 26 | 451636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1329656 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 130 | 1843345 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 24 | 720192 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1386040 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 3056160 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 901440 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 557352 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 20 | 459440 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2266320 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 459480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1663680 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 408773 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1687.2 | 36454030
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 121920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 168 | 2275200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 1407600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 165340 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 291600 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 147600 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 318 | 4419260
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 38 | 867000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 684840 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 154 | 3456900 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 718752 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1861440 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 3592420 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 28104 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 275 | 7438000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 336 | 9096000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 0 | Under Maintenance
Sylhet Area Total |  |  |  |  | 2368.568 | 1132 | 28175456
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 869 | 21557091 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 158 | 4241088 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 348000 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 694800 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1208 | 19752727 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2252 | 46593706
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 402 | 9446328 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 270720 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 223274 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 105 | 2591000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27671272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5255820 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 301200 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6633000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4102 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2289 | 52396716.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 23 | 180831 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 5 | 14395 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 27 | 156019 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 178 | 4568636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 189 | 4615536 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9149818 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 22 | 118822 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 2189 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 528972 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 774432 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 18 | 289056 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22200 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1440.95 | 31526546 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 266248 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 583710 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2463.95 | 52797410
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 51 | 1184290 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 168 | 3998000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 80 | 790281 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 22914.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 707917 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 124738 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 773280 | -
Rangpur Area Total |  |  |  |  | 950 | 369 | 7601420.48
Eastern Grid Total |  |  |  |  | 16921.242 | 7970 | 167432177.19
Western Grid Total |  |  |  |  | 11702.84 | 7373.95 | 159389253.21
National Grid Total |  |  |  |  | 28624.082 | 15343.95 | 326821430.4
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 12-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10120.91 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4648.2 | MW
i) Dhaka area |  |  | 5608.78 |  | MW | i) Khulna area |  |  |  | 1810 | MW
ii) Chattogram area |  |  | 1563 |  | MW | ii) Barishal area |  |  |  | 418 | MW
iii) Cumilla area |  |  | 1397.13 |  | MW | iii) Rajshahi area |  |  |  | 1505.2 | MW
iv) Mymensingh area |  |  | 1080 |  | MW | iv) Rangpur area |  |  |  | 915 | MW
v) Sylhet area |  |  | 472 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14769.11 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 84 | 19:30 | 133 | Patuakhali | 88.2 | 00:00
2 | AKSML | 125 | 04:00 | 68 | Jaldhaka | 64 | 19:30 | 134 | Payra | 38 | 00:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jamalpur | 128 | 19:30 | 135 | Postogola | 58 | 00:00
4 | Agargaon | 133 | 13:00 | 70 | Jashore | 156 | 23:00 | 136 | Purbachal | 22 | 00:00
5 | Agrabad | 104 | 16:00 | 71 | Jhenaidah | 146 | 21:00 | 137 | Purbasadipur | 124 | 01:00
6 | Amnura | 43 | 22:00 | 72 | Joydebpur | 154 | 19:30 | 138 | Rahanpur | 32 | 01:00
7 | Ashuganj | 79 | 23:00 | 73 | Joypurhat | 76 | 00:00 | 139 | Rahim | 57 | 18:00
8 | BSRM | 198 | 07:00 | 74 | Juldah | 15 | 23:00 | 140 | Rajbari | 85 | 00:00
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 34 | 17:00 | 141 | Rajendrapur | 144 | 00:00
10 | Bajitpur | 39 | 19:00 | 76 | Kabirpur | 280 | 09:00 | 142 | Rajshahi | 146 | 22:00
11 | Bakulia | 101 | 00:00 | 77 | Kachua | 95 | 23:00 | 143 | Rajshahi-230 | 100 | 00:00
12 | Banani | 42 | 13:00 | 78 | Kallyanpur | 132 | 23:00 | 144 | Ramganj | 114 | 02:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 42 | 12:00 | 145 | Rampur | 45 | 00:00
14 | Barapukuria | 61 | 22:00 | 80 | Kamrangirchar | 71 | 19:00 | 146 | Rangamati | 16 | 19:00
15 | Barguna | 32 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 147 | 19:30
16 | Barishal | 122 | 23:00 | 82 | Kasba | 31 | 00:00 | 148 | Ruppur | 7.8 | 11:00
17 | Barishal-230 | 120 | 00:00 | 83 | Kazla | 98 | 16:00 | 149 | SSM | 12 | 07:00
18 | Baroaulia | 67 | 15:00 | 84 | Keranigonj | 81 | 19:30 | 150 | Saidpur | 104 | 12:00
19 | Baroirhat | 66 | 23:00 | 85 | Khagrachori | 28 | 19:00 | 151 | Satkhira | 150 | 19:30
20 | Bashundhara | 187 | 13:00 | 86 | Khulna | 86 | 19:30 | 152 | Satmasjid | 107 | 00:00
21 | BashundharaCement | 13 | 13:00 | 87 | Khulshi | 187 | 18:30 | 153 | Savar | 232 | 16:00
22 | Beanibazar | 60 | 00:00 | 88 | Kishoreganj | 110 | 00:00 | 154 | SevenRings | 18.56 | 13:00
23 | Benapole | 76 | 22:00 | 89 | Kodda | 304 | 18:00 | 155 | ShahCement | 37 | 23:00
24 | Bhaluka | 151 | 19:00 | 90 | Kulaura | 37 | 00:00 | 156 | Shahjadpur | 86 | 00:00
25 | Bhandaria | 64 | 00:00 | 91 | Kurigram | 56 | 19:00 | 157 | Shahjibazar | 108 | 01:00
26 | Bhangura | 46 | 00:00 | 92 | Kushtia | 170 | 00:00 | 158 | Shahmirpur | 63.5 | 00:00
27 | Bheramara(GK) | 70 | 00:00 | 93 | Lalbag | 69 | 13:00 | 159 | Shariatpur | 93 | 23:00
28 | Bhulta | 230 | 18:00 | 94 | Lalmonirhat | 54 | 19:30 | 160 | Sherpur | 124 | 21:00
29 | Bog-Sherpur | 70 | 01:00 | 95 | MI_Cement | 17.8 | 13:00 | 161 | Shikalbaha | 30 | 23:00
30 | Bogura | 172 | 02:00 | 96 | Madanganj | 48 | 00:00 | 162 | Shitalakhya | 85.1 | 12:00
31 | Borhanuddin | 102 | 22:00 | 97 | Madaripur | 122 | 00:00 | 163 | Sholosohor | 48 | 19:00
32 | Brahmanbaria | 117 | 00:00 | 98 | Madartek | 103.04 | 00:00 | 164 | Shyampur | 154 | 10:00
33 | Cantonment | 150 | 13:00 | 99 | Madunaghat | 58 | 00:00 | 165 | Siddhirganj | 118 | 19:00
34 | Chandina | 16.33 | 19:00 | 100 | Magura | 66 | 00:00 | 166 | Sirajganj | 114 | 20:00
35 | Chandpur | 75 | 23:00 | 101 | Mahasthangarh | 84 | 00:00 | 167 | Sonargaon | 128 | 19:00
36 | Chandraghona | 36 | 19:30 | 102 | Manikganj | 141 | 00:00 | 168 | Sreemongol | 64 | 00:00
37 | Chapai | 71 | 00:00 | 103 | Maniknagar | 74 | 13:00 | 169 | Sreepur | 114 | 19:00
38 | Charsaidpur | 47 | 17:00 | 104 | Matarbari | 54 | 23:00 | 170 | Srinagar | 48.42 | 22:00
39 | Chauddagram | 73 | 00:00 | 105 | Matuail | 68 | 12:00 | 171 | Sunamganj | 46 | 19:30
40 | Chhatak | 29 | 18:30 | 106 | Millgate | 115 | 16:00 | 172 | Sylhet | 41 | 00:00
41 | Chowmuhani | 233 | 21:00 | 107 | Mirpur | 133 | 23:00 | 173 | Sylhet-132 | 102 | 19:30
42 | Chuadanga | 128 | 22:00 | 108 | Mirsorai | 11 | 16:00 | 174 | TK | 33 | 22:00
43 | Coxsbazar | 144 | 20:00 | 109 | Mirzapur | 48 | 00:00 | 175 | Tangail | 196 | 00:00
44 | Cumilla(N) | 155 | 01:00 | 110 | Mithapukur | 54 | 19:30 | 176 | Thakurgaon | 98 | 19:30
45 | Cumilla(S) | 174 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 112 | 11:00
46 | Daudkandi | 148 | 19:30 | 112 | Mogbazar | 156 | 11:00 | 178 | Ullahpara | 46 | 00:00
47 | Dhaka | 64 | 13:00 | 113 | Mongla | 51 | 12:00 | 179 | Ullon | 56 | 00:00
48 | Dhamrai | 140 | 19:00 | 114 | Motijheel | 39 | 11:00 | 180 | Uttara | 90 | 13:00
49 | Dhanmondi | 162 | 13:00 | 115 | Muktagacha | 31 | 19:00 | 181 | UttaraNew | 51 | 00:00
50 | Dohazari | 106 | 00:00 | 116 | Munshiganj | 122 | 23:00 | 182 | Zigatola | 82 | 00:00
51 | Faridpur | 170 | 00:00 | 117 | Muradnagar | 27 | 00:00
52 | Fatullah | 103 | 11:00 | 118 | Mymensingh | 176 | 19:00
53 | Fenchuganj | 32 | 00:00 | 119 | Naogaon | 153 | 00:00
54 | Feni | 128 | 19:30 | 120 | Narail | 60.5 | 00:00
55 | GPH | 97 | 00:00 | 121 | Narinda | 74 | 13:00
56 | Ghatail | 74 | 19:00 | 122 | Narshingdi | 176 | 00:00
57 | Ghorashal | 15 | 01:00 | 123 | Natore | 170 | 00:00
58 | Ghorashal-230 | 97 | 19:30 | 124 | Nawabganj | 61 | 22:00
59 | Goalpara | 46 | 00:00 | 125 | Netrakona | 103 | 18:30
60 | Gollamari | 114 | 00:00 | 126 | New | 85.3 | 11:00
61 | Gopalganj | 108.4 | 00:00 | 127 | Niamatpur | 83 | 22:00
62 | Gulshan | 128 | 11:00 | 128 | Noapara | 51 | 21:00
63 | Halishahar | 82.5 | 15:00 | 129 | PHP | 9 | 10:00
64 | HaripurSBU | 176 | 10:00 | 130 | Pabna | 130 | 00:00
65 | Hasnabad | 88 | 00:00 | 131 | Palashbari | 110 | 19:30
66 | Hathazari | 87 | 23:00 | 132 | Panchagarh | 53 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 12-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15030.7 | 0 |  | 15030.7
1:00 | 14693.7 | 0 |  | 14693.7
2:00 | 13943.7 | 0 |  | 13943.7
3:00 | 13284.7 | 0 |  | 13284.7
4:00 | 12919.5 | 0 |  | 12919.5
5:00 | 12706.5 | 0 |  | 12706.5
6:00 | 12175.62 | 0 |  | 12175.62
7:00 | 12113.53 | 18 |  | 12132.53
8:00 | 12050.16 | 21 |  | 12072.16
9:00 | 12211.32 | 31 |  | 12243.32
10:00 | 12705.49 | 16 |  | 12722.49
11:00 | 12828.74 | 25 |  | 12854.74
12:00 | 12939.46 | 27 |  | 12967.46
13:00 | 13332.48 | 30 |  | 13363.48
14:00 | 13397.11 | 26 |  | 13424.11
15:00 | 13834.45 | 18 |  | 13853.45
16:00 | 13706.06 | 0 |  | 13706.06
17:00 | 13250.73 | 0 |  | 13250.73
18:00 | 12906.69 | 0 |  | 12906.69
19:00 | 14465.27 | 0 |  | 14465.27
19:30 | 15343.95 | 0 |  | 15343.95
20:00 | 14857.22 | 0 |  | 14857.22
21:00 | 14988.95 | 0 |  | 14988.95
22:00 | 14730.89 | 0 |  | 14730.89
23:00 | 14825.71 | 53 |  | 14880.71
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 12-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8059.7 | 6971 | 15030.7 | DAILY GENERATION CURVE
00:30 | 7939.2 | 6923 | 14862.2
01:00 | 7818.7 | 6875 | 14693.7 | 12-05-2025
01:30 | 7639.7 | 6679 | 14318.7
02:00 | 7460.7 | 6483 | 13943.7
02:30 | 7202.7 | 6411.5 | 13614.2
03:00 | 6944.7 | 6340 | 13284.7
03:30 | 6774.1 | 6328 | 13102.1
04:00 | 6603.5 | 6316 | 12919.5
04:30 | 6442 | 6371 | 12813
05:00 | 6280.5 | 6426 | 12706.5
05:30 | 6214.94 | 6226.12 | 12441.06
06:00 | 6149.38 | 6026.24 | 12175.62
06:30 | 6101.25 | 6043.325 | 12144.575
07:00 | 6053.12 | 6060.41 | 12113.53
07:30 | 5984.56 | 6097.285 | 12081.845
08:00 | 5916 | 6134.16 | 12050.16
08:30 | 5978.59 | 6152.15 | 12130.74
09:00 | 6041.18 | 6170.14 | 12211.32
09:30 | 6118.865 | 6339.54 | 12458.405
10:00 | 6196.55 | 6508.94 | 12705.49
10:30 | 6323.665 | 6443.45 | 12767.115
11:00 | 6450.78 | 6377.96 | 12828.74
11:30 | 6397.28 | 6486.82 | 12884.1
12:00 | 6343.78 | 6595.68 | 12939.46
12:30 | 6457.925 | 6678.045 | 13135.97
13:00 | 6572.07 | 6760.41 | 13332.48
13:30 | 6602.87 | 6761.925 | 13364.795
14:00 | 6633.67 | 6763.44 | 13397.11
14:30 | 6768.045 | 6847.735 | 13615.78
15:00 | 6902.42 | 6932.03 | 13834.45
15:30 | 6964.935 | 6805.32 | 13770.255
16:00 | 7027.45 | 6678.61 | 13706.06
16:30 | 6975.485 | 6502.91 | 13478.395
17:00 | 6923.52 | 6327.21 | 13250.73
17:30 | 6883.655 | 6195.055 | 13078.71
18:00 | 6843.79 | 6062.9 | 12906.69
18:30 | 7261.795 | 6424.185 | 13685.98
19:00 | 7679.8 | 6785.47 | 14465.27
19:30 | 7970 | 7373.95 | 15343.95
20:00 | 7588.8 | 7268.42 | 14857.22
20:30 | 7614.8 | 7308.285 | 14923.085 |  | Executive Engineer
21:00 | 7640.8 | 7348.15 | 14988.95 |  | Network Operation Division
21:30 | 7636.3 | 7223.62 | 14859.92
22:00 | 7631.8 | 7099.09 | 14730.89
22:30 | 7728.9 | 7049.4 | 14778.3
23:00 | 7826 | 6999.71 | 14825.71

## En-Curve
QF-LDC-12
Date | 12-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3452 | 2035.5 | 926 | 0 | 50 | 1456 | 40 | 4269 | 0 | 488 | 2314.2 | 0 | 0 | 0 | 0 | DAILY ENERGY CURVE
00:30 | 3338.5 | 1996 | 926 | 0 | 49 | 1461 | 40 | 4251.5 | 0 | 423 | 2377.2 | 0 | 0 | 0 | 0 | 12-05-2025
01:00 | 3225 | 1956.5 | 926 | 0 | 48 | 1466 | 40 | 4234 | 0 | 358 | 2440.2 | 0 | 0 | 0 | 0
01:30 | 3220 | 1927.5 | 925.5 | 0 | 46 | 1462 | 40 | 4195 | 0 | 349.5 | 2153.2 | 0 | 0 | 0 | 0 | Energy Generated | 326.8214 |  | MKWHr
02:00 | 3215 | 1898.5 | 925 | 0 | 44 | 1458 | 40 | 4156 | 0 | 341 | 1866.2 | 0 | 0 | 0 | 0 | Energy not Served | 0.265 |  | MKWHr
02:30 | 3222.5 | 1891.5 | 925 | 0 | 44 | 1463 | 40 | 4129 | 0 | 306 | 1591.2 | 0 | 0 | 2 | 0 | Total Energy Requirement | 327.0864 |  | MKWHr
03:00 | 3230 | 1884.5 | 925 | 0 | 44 | 1468 | 40 | 4102 | 0 | 271 | 1316.2 | 0 | 0 | 4 | 0
03:30 | 3325.5 | 1950.5 | 925.5 | 0 | 43 | 1442 | 40 | 3962 | 0 | 262.5 | 1145.1 | 0 | 0 | 6 | 0
04:00 | 3421 | 2016.5 | 926 | 0 | 42 | 1416 | 40 | 3822 | 0 | 254 | 974 | 0 | 0 | 8 | 0
04:30 | 3414.5 | 1986 | 926 | 0 | 41 | 1435 | 40 | 3868.5 | 0 | 238 | 856 | 0 | 0 | 8 | 0
05:00 | 3408 | 1955.5 | 926 | 0 | 40 | 1454 | 40 | 3915 | 0 | 222 | 738 | 0 | 0 | 8 | 0
05:30 | 3428 | 1969 | 926 | 0 | 38 | 1384 | 40 | 3769.5 | 10.06 | 215 | 650.5 | 0 | 0 | 11 | 0
06:00 | 3448 | 1982.5 | 926 | 0 | 36 | 1314 | 40 | 3624 | 20.12 | 208 | 563 | 0 | 0 | 14 | 0
06:30 | 3464.5 | 1969.5 | 926 | 0 | 35 | 1318 | 40 | 3604.5 | 42.075 | 198 | 539.5 | 0 | 0 | 7.5 | 9
07:00 | 3481 | 1956.5 | 926 | 0 | 34 | 1322 | 40 | 3585 | 64.03 | 188 | 516 | 0 | 0 | 1 | 18
07:30 | 3457 | 1842.25 | 901.5 | 0 | 33 | 1321.155 | 40 | 3626 | 117.94 | 187.5 | 555 | 0 | 0 | 0.5 | 19.5
08:00 | 3433 | 1728 | 877 | 0 | 32 | 1320.31 | 40 | 3667 | 171.85 | 187 | 594 | 0 | 0 | 0 | 21
08:30 | 3440.5 | 1779.5 | 876.5 | 0 | 32 | 1319.215 | 40 | 3645.5 | 200.025 | 197.5 | 598.5 | 0 | 0 | 1.5 | 26
09:00 | 3448 | 1831 | 876 | 0 | 32 | 1318.12 | 40 | 3624 | 228.2 | 208 | 603 | 0 | 0 | 3 | 31
09:30 | 3431.5 | 1856 | 897.5 | 0 | 32 | 1317.765 | 40 | 3680 | 367.14 | 218.5 | 610 | 0 | 0 | 8 | 23.5
10:00 | 3415 | 1881 | 919 | 0 | 32 | 1317.41 | 40 | 3736 | 506.08 | 229 | 617 | 0 | 0 | 13 | 16
10:30 | 3344 | 1930.5 | 918.5 | 0 | 31 | 1290.6 | 40 | 3775 | 497.515 | 221 | 712.5 | 0 | 0 | 6.5 | 20.5
11:00 | 3273 | 1980 | 918 | 0 | 30 | 1263.79 | 40 | 3814 | 488.95 | 213 | 808 | 0 | 0 | 0 | 25
11:30 | 3315.5 | 1911.5 | 918.5 | 0 | 30 | 1242.535 | 40 | 3848 | 475.065 | 204 | 899 | 0 | 0 | 0 | 26
12:00 | 3358 | 1843 | 919 | 0 | 30 | 1221.28 | 40 | 3882 | 461.18 | 195 | 990 | 0 | 0 | 0 | 27
12:30 | 3351 | 1890 | 918.5 | 0 | 32 | 1241.125 | 40 | 4017.5 | 443.845 | 196 | 1006 | 0 | 0 | 0 | 28.5
13:00 | 3344 | 1937 | 918 | 0 | 34 | 1260.97 | 40 | 4153 | 426.51 | 197 | 1022 | 0 | 0 | 0 | 30
13:30 | 3332.5 | 1939 | 918.5 | 0 | 34 | 1262.705 | 40 | 4180.5 | 401.59 | 187.5 | 1068.5 | 0 | 0 | 0 | 28
14:00 | 3321 | 1941 | 919 | 0 | 34 | 1264.44 | 40 | 4208 | 376.67 | 178 | 1115 | 0 | 0 | 0 | 26
14:30 | 3375.5 | 1961 | 918.5 | 0 | 35 | 1288.07 | 40 | 4273.5 | 357.21 | 207 | 1160 | 0 | 0 | 0 | 22
15:00 | 3430 | 1981 | 918 | 0 | 36 | 1311.7 | 40 | 4339 | 337.75 | 236 | 1205 | 0 | 0 | 0 | 18
15:30 | 3385 | 1968.5 | 918 | 0 | 35 | 1265.045 | 39 | 4286.5 | 309.21 | 275 | 1289 | 0 | 0 | 0 | 9
16:00 | 3340 | 1956 | 918 | 0 | 34 | 1218.39 | 38 | 4234 | 280.67 | 314 | 1373 | 0 | 0 | 0 | 0
16:30 | 3336.5 | 1948.9 | 918 | 0 | 34 | 1215.455 | 38.5 | 4150.5 | 191.54 | 323.5 | 1321.5 | 0 | 0 | 0 | 0
17:00 | 3333 | 1941.8 | 918 | 0 | 34 | 1212.52 | 39 | 4067 | 102.41 | 333 | 1270 | 0 | 0 | 0 | 0
17:30 | 3278 | 1941.8 | 918.5 | 0 | 34 | 1211.79 | 39.5 | 3985 | 63.12 | 353 | 1253 | 0 | 0 | 1 | 0
18:00 | 3223 | 1941.8 | 919 | 0 | 34 | 1211.06 | 40 | 3903 | 23.83 | 373 | 1236 | 0 | 0 | 2 | 0
18:30 | 3356 | 1968.3 | 894 | 0 | 37 | 1294.765 | 40 | 4042 | 11.915 | 497 | 1542 | 0 | 0 | 3 | 0
19:00 | 3489 | 1994.8 | 869 | 0 | 40 | 1378.47 | 40 | 4181 | 0 | 621 | 1848 | 0 | 0 | 4 | 0
19:30 | 3368 | 1948.8 | 869 | 0 | 40 | 1440.95 | 40 | 4543 | 0 | 693 | 2401.2 | 0 | 0 | 0 | 0
20:00 | 3351 | 1969.8 | 774 | 0 | 38 | 1446.22 | 40 | 4555.2 | 0 | 739 | 1944 | 0 | 0 | 0 | 0
20:30 | 3396 | 2001.8 | 774 | 0 | 39 | 1446.085 | 40 | 4560.7 | 0 | 715.5 | 1948 | 0 | 0 | 2 | 0
21:00 | 3441 | 2033.8 | 774 | 0 | 40 | 1445.95 | 40 | 4566.2 | 0 | 692 | 1952 | 0 | 0 | 4 | 0
21:30 | 3435.5 | 2030.8 | 774 | 0 | 40 | 1443.02 | 40 | 4434.1 | 0 | 683.5 | 1976 | 0 | 0 | 3 | 0
22:00 | 3430 | 2027.8 | 774 | 0 | 40 | 1440.09 | 40 | 4302 | 0 | 675 | 2000 | 0 | 0 | 2 | 0
22:30 | 3380.5 | 2024.9 | 798 | 0 | 42 | 1450.9 | 40 | 4134 | 0 | 675.5 | 2229 | 0 | 0 | 3.5 | 26.5
23:00 | 3331 | 2022 | 822 | 0 | 44 | 1461.71 | 40 | 3966 | 0 | 676 | 2458 | 0 | 0 | 5 | 53
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 12-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 376 | 18:00 | 366 | 15:00 | Payra | 409 | 17:00 | 406 | 00:00
Ashuganj | 399 | 2:00 | 367 | 12:00 | Rahanpur | 402 | 06:00 | 396 | 15:00
Bhulta | 397 | 17:00 | 369 | 14:00 | Rampal | 395 | 18:00 | 378 | 00:00
Bibiana | 391 | 19:30 | 381 | 15:00
BIPTC | 401 | 08:00 | 387 | 00:00
Bogura | 387 | 06:00 | 378 | 19:30
Gopalganj | 389 | 18:00 | 378 | 15:00
Kaliakoir | 370 | 22:00 | 359 | 15:00
Madunaghat | 392 | 01:00 | 381 | 11:00
Meghnaghat | 382 | 23:00 | 372 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 220 | 23:00 | 212 | 10:00 | Keranigonj | 218 | 23:00 | 211 | 10:00
AKSML | 231 | 00:00 | 218 | 15:00 | Khulna(S) | 227 | 18:00 | 211 | 00:00
Aminbazar | 220 | 22:00 | 213 | 10:00 | Madunaghat | 234 | 01:00 | 224 | 10:00
Ashuganj | 233 | 03:00 | 220 | 13:00 | Madunaghat-400 | 234 | 01:00 | 225 | 11:00
Ashuganj-400 | 233 | 03:00 | 220 | 13:00 | Maniknagar | 216 | 03:00 | 209 | 14:00
Baghabari | 233 | 05:00 | 225 | 15:00 | Meghnaghat | 225 | 00:00 | 220 | 09:00
Barapukuria | 226 | 06:00 | 219 | 19:00 | Meghnaghat-400 | 220 | 02:00 | 214 | 10:00
Barapukuria-230 | 226 | 06:00 | 219 | 19:00 | Mirsorai | 230 | 01:00 | 218 | 07:00
Barishal | 235 | 18:00 | 227 | 00:00 | Rajshahi | 233 | 07:00 | 222 | 15:00
Bheramara | 233 | 06:00 | 222 | 15:00 | Rampal | 225 | 18:00 | 211 | 00:00
Bhulta | 228 | 02:00 | 213 | 14:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 02:00 | 219 | 14:00 | Rampura | 227 | 06:00 | 211 | 15:00
BIPTC | 236 | 07:00 | 223 | 15:00 | Shikalbaha | 233 | 01:00 | 221 | 10:00
Bogura | 234 | 01:00 | 229 | 15:00 | Shyampur | 218 | 23:00 | 211 | 10:00
Bogura-400 | 236 | 06:00 | 230 | 13:00 | Siddhirganj | 218 | 22:00 | 213 | 10:00
Borhanuddin | 239 | 07:00 | 233 | 02:00 | Sirajgonj | 238 | 01:00 | 234 | 15:00
BSRM | 228 | 01:00 | 217 | 10:00 | Sreepur | 229 | 01:00 | 220 | 10:00
Cumilla(N) | 219 | 01:00 | 213 | 10:00 | Tongi | 225 | 23:00 | 214 | 13:00
Faridpur | 228 | 17:00 | 220 | 00:00
Fenchuganj | 227 | 09:00 | 219 | 01:00
Ghorashal | 230 | 00:00 | 222 | 13:00
Ghorashal-230 | 227 | 02:00 | 214 | 13:00
Gopalganj | 231 | 18:00 | 224 | 00:00
GPH | 230 | 01:00 | 219 | 10:00
Haripur | 217 | 02:00 | 211 | 10:00
Hasnabad | 218 | 03:00 | 211 | 15:00
Hathazari | 234 | 01:00 | 222 | 15:00
Ishurdi | 235 | 06:00 | 225 | 15:00
Jhenaidah | 227 | 18:00 | 214 | 01:00
Kaliakoir | 229 | 23:00 | 220 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 23:00 | 124 | 14:00 | Madartek | 136 | 03:00 | 125 | 13:00
Agargaon | 129 | 23:00 | 123 | 10:00 | Madunaghat | 134 | 23:00 | 125 | 14:00
Agrabad | 132 | 23:00 | 124 | 14:00 | Magura | 131 | 18:00 | 120 | 14:00
AKS | 130 | 01:00 | 124 | 11:00 | Mahasthangarh | 137 | 01:00 | 129 | 19:00
Aminbazar | 127 | 03:00 | 121 | 10:00 | Manikganj | 130 | 23:00 | 122 | 03:00
Amnura | 138 | 22:00 | 123 | 00:00 | Maniknagar | 127 | 02:00 | 121 | 15:00
Ashuganj | 138 | 06:00 | 133 | 15:00 | Matarbari | 120 | 19:00 | 110 | 07:00
Bagerhat | 134 | 18:00 | 112 | 00:00 | Matuail | 126 | 01:00 | 122 | 15:00
Bajitpur | 132 | 04:00 | 127 | 13:00 | Millgate | 134 | 01:00 | 125 | 14:00
Bakulia | 134 | 23:00 | 126 | 15:00 | Mirpur | 125 | 06:00 | 120 | 14:00
Banani | 137 | 23:00 | 124 | 15:00 | Mirzapur | 132 | 11:00 | 128 | 12:00
Bangabhaban | 127 | 03:00 | 121 | 15:00 | Mithapukur | 138 | 01:00 | 126 | 19:00
Barapukuria | 138 | 22:00 | 131 | 19:00 | MI_Cement | 127.1 | 19:30 | 121.3 | 10:00
Barguna | 135 | 00:00 | 128 | 02:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 18:00 | 123 | 15:00 | Mogbazar | 137 | 06:00 | 124 | 14:00
Barishal-230 | 130 | 18:00 | 124 | 15:00 | Mongla | 134 | 17:00 | 113 | 00:00
Baroaulia | 132 | 00:00 | 125 | 15:00 | Motijheel | 127 | 03:00 | 121 | 15:00
Baroirhat | 122 | 12:00 | 117 | 05:00 | Muktagacha | 135 | 02:00 | 123 | 13:00
Bashundhara | 136 | 02:00 | 125 | 14:00 | Munshiganj | 126 | 19:30 | 120 | 10:00
BashundharaCement | 126 | 20:00 | 120 | 10:00 | Muradnagar | 124 | 11:00 | 120 | 00:00
Beanibazar | 133 | 09:00 | 126 | 00:00 | Mymensingh | 136 | 10:00 | 117 | 14:00
Benapole | 129 | 18:00 | 112 | 00:00 | Naogaon | 132 | 06:00 | 127 | 13:00
Bhaluka | 132 | 01:00 | 122 | 14:00 | Narail | 132 | 06:00 | 121 | 00:00
Bhandaria | 128 | 17:00 | 114 | 02:00 | Narinda | 127 | 02:00 | 121 | 15:00
Bhangura | 132 | 01:00 | 129 | 00:00 | Narshingdi | 132 | 03:00 | 116 | 00:00
Bheramara | 137 | 08:00 | 131 | 14:00 | Natore | 134 | 06:00 | 129 | 00:00
Bheramara(GK) | 137 | 09:00 | 131 | 13:00 | Nawabganj | 129 | 05:00 | 124 | 15:00
Bhulta | 120 | 03:00 | 115 | 10:00 | Netrakona | 129 | 02:00 | 116 | 18:30
Bog-Sherpur | 136 | 23:00 | 131 | 19:00 | New | 136 | 02:00 | 126 | 14:00
Bogura | 139 | 01:00 | 134 | 13:00 | Niamatpur | 133 | 06:00 | 129 | 19:00
Bogura-230 | 139 | 01:00 | 134 | 14:00 | Noapara | 131 | 18:00 | 117 | 00:00
Brahmanbaria | 134 | 05:00 | 124 | 00:00 | Pabna | 133 | 07:00 | 129 | 01:00
Cantonment | 129 | 23:00 | 122 | 15:00 | Palashbari | 136 | 01:00 | 124 | 19:00
Chandina | 125 | 03:00 | 122 | 15:00 | Panchagarh | 139 | 22:00 | 120 | 11:00
Chandpur | 124 | 10:00 | 119 | 03:00 | Patuakhali | 134 | 02:00 | 130 | 21:00
Chandraghona | 133 | 01:00 | 127 | 10:00 | Payra | 136 | 00:00 | 132 | 05:00
Chapai | 130 | 18:00 | 124 | 00:00 | PHP | 120 | 01:00 | 116 | 06:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 23:00 | 121 | 15:00 | Postogola | 129 | 23:00 | 124 | 10:00
Chauddagram | 121 | 12:00 | 117 | 05:00 | Purbachal | 136 | 02:00 | 124 | 15:00
Chhatak | 131 | 07:00 | 125 | 19:30 | Purbasadipur | 135 | 22:00 | 121 | 10:00
Chowmuhani | 116 | 09:00 | 110 | 18:30 | Rahanpur | 134 | 06:00 | 131 | 00:00
Chuadanga | 130 | 18:00 | 115 | 00:00 | Rahanpur-400 | 135 | 17:00 | 131 | 15:00
Coxsbazar | 118 | 09:00 | 111 | 04:00 | Rahim | 126 | 02:00 | 123 | 11:00
Cumilla(N) | 125 | 03:00 | 122 | 00:00 | Rajbari | 132 | 18:00 | 125 | 00:00
Cumilla(S) | 133 | 04:00 | 119 | 18:30 | Rajendrapur | 133 | 01:00 | 122 | 16:00
Daudkandi | 122 | 11:00 | 118 | 21:00 | Rajshahi | 134 | 06:00 | 128 | 00:00
Dhaka | 137 | 06:00 | 126 | 13:00 | Rajshahi-230 | 134 | 06:00 | 117 | 00:00
Dhamrai | 134 | 23:00 | 127 | 10:00 | Ramganj | 118 | 12:00 | 110 | 05:00
Dhanmondi | 137 | 06:00 | 125 | 15:00 | Rampur | 133 | 00:00 | 125 | 11:00
Dohazari | 130 | 23:00 | 121 | 13:00 | Rampura | 136 | 02:00 | 125 | 15:00
Faridpur | 134 | 18:00 | 128 | 00:00 | Rangamati | 132 | 01:00 | 125 | 15:00
Fatullah | 127 | 03:00 | 123 | 10:00 | Rangpur | 135 | 06:00 | 123 | 19:00
Fenchuganj | 136 | 06:00 | 132 | 00:00 | Ruppur | 137 | 07:00 | 132 | 14:00
Feni | 121 | 12:00 | 114 | 00:00 | Saidpur | 136 | 01:00 | 123 | 19:00
Ghatail | 135 | 06:00 | 126 | 18:30 | Satkhira | 129 | 18:00 | 111 | 00:00
Ghorashal | 136 | 07:00 | 130 | 10:00 | Satmasjid | 129 | 23:00 | 122 | 13:00
Goalpara | 136 | 18:00 | 120 | 00:00 | Savar | 127 | 23:00 | 118 | 10:00
Gollamari | 135 | 18:00 | 122 | 00:00 | SevenRings | 136 | 02:00 | 128 | 13:00
Gopalganj | 133 | 17:00 | 123 | 00:00 | ShahCement | 127 | 23:00 | 121 | 15:00
Gopalganj-400 | 134 | 18:00 | 129 | 00:00 | Shahjadpur | 135 | 04:00 | 132 | 14:00
Gulshan | 136 | 00:00 | 125 | 15:00 | Shahjibazar | 136 | 03:00 | 126 | 00:00
Halishahar | 135 | 01:00 | 127 | 18:00 | Shahmirpur | 135 | 23:00 | 127 | 10:00
Haripur | 127 | 02:00 | 123 | 10:00 | Shariatpur | 132 | 18:00 | 125 | 00:00
HaripurSBU | 127 | 02:00 | 123 | 10:00 | Sherpur | 141 | 06:00 | 130 | 12:00
Hasnabad | 128 | 01:00 | 123 | 12:00 | Shikalbaha | 123 | 01:00 | 116 | 10:00
Hathazari | 136 | 01:00 | 129 | 18:00 | Shikalbaha-230 | 136 | 01:00 | 127 | 10:00
Ishurdi | 138 | 06:00 | 133 | 15:00 | Shitalakhya | 127.1 | 19:30 | 121.3 | 10:00
Jaldhaka | 133 | 06:00 | 123 | 12:00 | Sholosohor | 134 | 01:00 | 125 | 10:00
Jamalpur | 141 | 06:00 | 127 | 13:00 | Shyampur | 128 | 00:00 | 122 | 12:00
Jashore | 130 | 18:00 | 113 | 00:00 | Shyampur-230 | 127 | 02:00 | 120 | 15:00
Jhenaidah | 133 | 18:00 | 122 | 00:00 | Siddhirganj | 127 | 02:00 | 123 | 10:00
Jhenaidah-230 | 133 | 18:00 | 124 | 00:00 | Sirajganj | 132 | 23:00 | 129 | 07:00
Joydebpur | 133 | 23:00 | 124 | 16:00 | Sonargaon | 126 | 02:00 | 121 | 10:00
Joypurhat | 130 | 05:00 | 124 | 00:00 | Sreemongol | 135 | 02:00 | 126 | 00:00
Juldah | 135 | 23:00 | 128 | 12:00 | Sreepur | 134 | 01:00 | 127 | 10:00
Kabirpur | 134 | 13:00 | 124 | 14:00 | Srinagar | 129 | 02:00 | 124 | 15:00
Kachua | 122 | 09:00 | 118 | 00:00 | SSM | 136 | 00:00 | 131 | 05:00
Kaliakoir | 136 | 02:00 | 130 | 14:00 | Sunamganj | 130 | 05:00 | 124 | 00:00
Kallyanpur | 127 | 22:00 | 122 | 09:00 | Sylhet | 132 | 03:00 | 128 | 00:00
Kalurghat | 132 | 01:00 | 125 | 15:00 | Sylhet-132 | 131 | 04:00 | 128 | 00:00
Kamrangirchar | 129 | 04:00 | 124 | 12:00 | Tangail | 132 | 11:00 | 126 | 12:00
Kaptai | 136 | 0:00 | 129 | 14:00 | Thakurgaon | 140 | 22:00 | 122 | 11:00
Kasba | 123 | 03:00 | 119 | 00:00 | TK | 130 | 03:00 | 126 | 13:00
Kazla | 127 | 03:00 | 121 | 11:00 | Tongi | 137 | 21:00 | 128 | 15:00
Keranigonj | 130 | 06:00 | 125 | 15:00 | Ullahpara | 133 | 03:00 | 129 | 15:00
Khagrachori | 131 | 00:00 | 124 | 15:00 | Ullon | 136 | 06:00 | 125 | 14:00
Khulna | 134 | 18:00 | 118 | 00:00 | Uttara | 125 | 03:00 | 120 | 07:00
Khulna(S) | 136 | 18:00 | 122 | 00:00 | UttaraNew | 126 | 22:00 | 120 | 10:00
Khulshi | 132 | 23:00 | 125 | 05:00 | Zigatola | 131 | 13:00 | 125 | 10:00
Kishoreganj | 135 | 01:00 | 123 | 14:00
Kodda | 133 | 23:00 | 121 | 16:00
KSRM | 134 | 00:00 | 125 | 15:00
Kulaura | 135 | 03:00 | 131 | 00:00
Kurigram | 133 | 04:00 | 120 | 19:00
Kushtia | 134 | 18:00 | 127 | 00:00
Lalbag | 129 | 03:00 | 124 | 15:00
Lalmonirhat | 132 | 00:00 | 123 | 12:00
Madanganj | 126 | 19:30 | 120 | 10:00
Madaripur | 133 | 18:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division