## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 16-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-05-2025 | during | 16-05-2025 | during | 16-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 351 | 376 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 350 | 450 | 450 | 400 | 400 | Allocation limit by Titas Gas
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 155 | 143 | 150 | 150 | 134 | 134 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 290 | 335 | 335 | 301.5 | 301.5 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 16 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 17 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 82 | 127 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 16 | 30 | 30 | 19 | 19 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 16 | 16 | 22 | 22 | 20 | 20 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 17 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 160 | 195 | 300 | 300 | 281 | 281 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 93 | 126 | 149 | 149 | 113 | 113 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 34 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 48 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 4 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 300 | 584 | 584 | 340 | 340 | Allocation limit by Titas, instructed by DS(Gen)
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 300 | 300 | 583 | 583 | 340 | 340 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 142 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2471 | 2852 | 5086.9 | 5086.9 | 3134.91 | 3188.91
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 115 | 120 | 100 | 100 | 100 | 100 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 14 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 30 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 101 | 101 | 100 | 100 | 100 | 100 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 46 | 105 | 105 | 87 | 87 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 30 | 70 | 48 | 72 | 64 | 76 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 68 | 68 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 88 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 12 | 4 | 20 | 4 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 30 | 35 | 108 | 108 | 70 | 70 | Engine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 2.08 | 0 | 2.08 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 34 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 88 | 48 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 17 | 17 | 159.86 | 159.86 | 144 | 144 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 600 | 612 | 612 | 612 | 612 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 10 | 13 | 4 | 9 | 4 | 9 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 550 | 537 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1833 | 1837.5 | 2800.8 | 2824.72 | 2774.94 | 2786.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 202 | 201 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 300 | 351 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 320 | 325 | 320 | 320 | 320 | 320 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 30 | 35 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 53 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 92 | 125 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 37 | 39 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 75 | 80 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 102 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 54 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 17.75 | 17.75 | Schedule Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 92 | 115 | 115 | 51 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 31 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1600.2 | 1820.2 | 2439.24 | 2374.24 | 2142.3 | 2145.3
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 15-05-2025 | during | 16-05-2025 | during | 16-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 66 | 179 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 86 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 29.65 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 6 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 35 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 153.65 | 306 | 601.1 | 549 | 292.1 | 312
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 35 | 35 | 32 | 32 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 134 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 25 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 85 | 85 | 85 | 81 | 81 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 174 | 170 | 170 | 174 | 174 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 6 | 25 | 25 | 25 | 25 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 349 | 375 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1465 | 1530 | 1609 | 1609 | 1531 | 1531
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 914 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 101 | 154 | 410 | 410 | 150 | 150 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89.65 | 0 | 98 | 0 | 98 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 554 | 592 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1657.65 | 1677 | 3612.2 | 3514.2 | 3159.01 | 3061.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 249 | 305 | 450 | 450 | 450 | 450 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 5 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 115 | 50 | 125 | 125 | 113 | 113 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1130 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 180 | 216 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1989 | 2127 | 2617.12 | 2616.12 | 2565.12 | 2564.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 130 | 214 | 214 | 179 | 179 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 132 | 138 | 220 | 220 | 179 | 179 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 230 | 414 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 11 | 11 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 42 | 42 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 98 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 45 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.85 | 0 | 5 | 0 | 5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1450.37 | 1444.67 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 50.49 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 94 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 2089.71 | 2369.67 | 3197.87 | 3036.87 | 2891.68 | 2730.68
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 52 | 45 | 45 | 0 | 0 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 168 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 37 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.6 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 72 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 150 | 0 | 98.51 | 0 | 98.51 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 321.6 | 329 | 591.11 | 457 | 556.11 | 422
System Total |  |  |  |  | 27566.2 | 28624.082 | 13580.81 | 14848.37 | 22555.34 | 22068.05 | 19047.17 | 18741.88
Forecast Scenario (16-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14480 |  | 0 |  | 14480
|  |  |  | 1:00 | 14020 |  | 0 |  | 14020
|  |  |  | 2:00 | 13370 |  | 0 |  | 13370
|  |  |  | 3:00 | 12950 |  | 0 |  | 12950
|  |  |  | 4:00 | 12620 |  | 0 |  | 12620
|  |  |  | 5:00 | 12170 |  | 0 |  | 12170
|  |  |  | 6:00 | 10670 |  | 0 |  | 10670
|  |  |  | 7:00 | 10700 |  | 0 |  | 10700
|  |  |  | 8:00 | 10813 |  | 0 |  | 10813
|  |  |  | 9:00 | 10823 |  | 0 |  | 10823
|  |  |  | 10:00 | 11284 |  | 0 |  | 11284
|  |  |  | 11:00 | 11636 |  | 0 |  | 11636
|  |  |  | 12:00 | 12160 |  | 0 |  | 12160
|  |  |  | 13:00 | 12602 |  | 0 |  | 12602
|  |  |  | 14:00 | 12332 |  | 0 |  | 12332
|  |  |  | 15:00 | 12703 |  | 0 |  | 12703
|  |  |  | 16:00 | 12302 |  | 0 |  | 12302
|  |  |  | 17:00 | 12083 |  | 0 |  | 12083
|  |  |  | 18:00 | 11652 |  | 0 |  | 11652
|  |  |  | 18:30 | 12600 |  | 0 |  | 12600
|  |  |  | 19:00 | 13650 |  | 0 |  | 13650
|  |  |  | 19:30 | 14400 |  | 0 |  | 14400
|  |  |  | 20:00 | 14520 |  | 0 |  | 14520
|  |  |  | 21:00 | 14800 |  | 0 |  | 14800
|  |  |  | 22:00 | 14830 |  | 0 |  | 14830
|  |  |  | 23:00 | 14930 |  | 0 |  | 14930
Probable Maximum Temperature: |  |  | 34.30°C
Probable Maximum Demand at Day Peak: |  |  | 12160.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 14800.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14800.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 304.10 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:30 hrs on 16-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 15-05-2025 | [28 empty] | Date: | 15-05-2025 | [28 empty] | Date: | 15-05-2025 | [28 empty] | Date: | 15-05-2025 | [28 empty] | Date: | 15-05-2025 | [16 empty] | Date: | 15-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 8 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 17 | 110 | 146 | 95 | 15 | 35 | 162 | 0 | 84 | 350 | 150 | 300 | 0 | 17 | 0 | 265 | 0 | 0 | 0 | 125 | 16 | 17 | 0 | 300 | 90 | 65 | 39 | 100 | 0 | 0 | 69 | 17 | 100 | 70 | 0 | 40 | 110 | 28 | 545 | 17 | 0 | 33 | 25.5 | 87 | 101 | 0 | 0 | 0 | 606 | 0 | 51 | 123 | 16 | 0 | 355 | 320 | 53 | 187 | 36 | 92 | 75 | 170 | 16 | 15 | 88 | 54 | 16 | 0 | 40 | 295 | 320 | 360 | 34 | 30 | 0 | 153 | 8 | 0 | 81 | 20 | 0 | 18 | 174 | 17 | 85 | 149 | 0 | 0 | 0 | 12 | 8268.5 | 922 | 93 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 17 | 1455.63 | 0 | 48 | 0 | 113 | 21 | 88 | 50 | 35 | 8 | 0 | 30 | 0 | 162 | 0 | 128 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 165 | 0 | 115 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 11 | 115 | 220 | 0 | 398 | 1180 | 126 | 6947.63 | 15216.13 | 77.5
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 22 | 17 | 110 | 82 | 95 | 15 | 17 | 90 | 0 | 84 | 350 | 133 | 300 | 0 | 17 | 0 | 272 | 0 | 0 | 0 | 125 | 17 | 17 | 0 | 300 | 90 | 65 | 39 | 100 | 0 | 0 | 69 | 17 | 100 | 70 | 0 | 40 | 110 | 30 | 542 | 17 | 0 | 33 | 25.5 | 87 | 101 | 0 | 0 | 0 | 612 | 0 | 51 | 118 | 16 | 0 | 359 | 320 | 53 | 184 | 36 | 76 | 80 | 170 | 15 | 15 | 88 | 54 | 16 | 0 | 40 | 300 | 320 | 350 | 32 | 30 | 0 | 149 | 8 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 46 | 95 | 0 | 0 | 0 | 12 | 7918.5 | 922 | 95 | 0 | 31 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 17 | 1460.83 | 0 | 48 | 0 | 113 | 19 | 88 | 50 | 36 | 8 | 0 | 30 | 0 | 162 | 0 | 133 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 165 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 11 | 105 | 220 | 0 | 400 | 1180 | 82 | 6893.83 | 14812.33 | 77.49
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 17 | 99 | 82 | 45 | 0 | 0 | 54 | 0 | 84 | 350 | 133 | 300 | 0 | 17 | 0 | 265 | 0 | 0 | 0 | 125 | 14 | 17 | 0 | 300 | 72 | 30 | 38 | 100 | 2 | 0 | 61 | 0 | 100 | 70 | 0 | 39 | 110 | 30 | 544 | 0 | 0 | 12 | 8 | 87 | 101 | 0 | 0 | 0 | 612 | 0 | 51 | 108 | 16 | 0 | 358 | 320 | 52 | 181 | 36 | 73 | 80 | 170 | 9 | 15 | 105 | 54 | 16 | 0 | 40 | 300 | 320 | 350 | 32 | 30 | 0 | 148 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 48 | 95 | 0 | 0 | 0 | 12 | 7621 | 922 | 94 | 0 | 31 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 609 | 17 | 1447.14 | 0 | 48 | 0 | 113 | 0 | 0 | 0 | 36 | 0 | 0 | 30 | 0 | 162 | 0 | 135 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 162 | 0 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 48 | 307 | 11 | 105 | 220 | 0 | 350 | 1180 | 82 | 6731.14 | 14352.14 | 77.48
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 17 | 83 | 82 | 15 | 0 | 0 | 54 | 0 | 84 | 350 | 141 | 300 | 0 | 17 | 0 | 273 | 0 | 0 | 0 | 70 | 14 | 17 | 0 | 300 | 53 | 0 | 25 | 100 | 0 | 0 | 38 | 0 | 100 | 70 | 0 | 38 | 110 | 31 | 546 | 0 | 0 | 0 | 8 | 87 | 101 | 0 | 0 | 0 | 585 | 0 | 51 | 80 | 16 | 0 | 359 | 320 | 51 | 195 | 33 | 73 | 85 | 118 | 9 | 15 | 114 | 52 | 34 | 0 | 39 | 295 | 320 | 360 | 32 | 30 | 0 | 143 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 47 | 95 | 0 | 0 | 0 | 12 | 7371 | 922 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 17 | 1364.35 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 135 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 44 | 35 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 11 | 115 | 220 | 0 | 259 | 1120 | 82 | 6147.35 | 13518.35 | 77.47
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 17 | 17 | 83 | 82 | 15 | 0 | 0 | 54 | 0 | 51 | 350 | 139 | 300 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 17 | 14 | 17 | 0 | 300 | 53 | 0 | 0 | 100 | 0 | 0 | 38 | 0 | 100 | 70 | 0 | 38 | 110 | 31 | 545 | 0 | 0 | 0 | 8 | 87 | 101 | 0 | 0 | 0 | 555 | 0 | 51 | 80 | 16 | 0 | 358 | 320 | 51 | 193 | 36 | 74 | 85 | 102 | 9 | 14 | 114 | 52 | 52.2 | 0 | 39 | 310 | 320 | 362 | 32 | 30 | 0 | 146 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 47 | 95 | 0 | 0 | 0 | 12 | 7272.2 | 923 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 17 | 1359.18 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 135 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 115 | 220 | 0 | 247 | 1105 | 0 | 5943.18 | 13215.38 | 77.46
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 83 | 82 | 15 | 0 | 0 | 54 | 0 | 16 | 350 | 134 | 300 | 0 | 17 | 0 | 270 | 0 | 0 | 0 | 0 | 14 | 17 | 0 | 300 | 17 | 0 | 0 | 100 | 6 | 0 | 38 | 0 | 100 | 30 | 0 | 38 | 110 | 31 | 547 | 0 | 0 | 0 | 0 | 87 | 101 | 0 | 0 | 0 | 555 | 0 | 51 | 50 | 16 | 0 | 359 | 320 | 50 | 187 | 36 | 73 | 85 | 103 | 9 | 14 | 114 | 46 | 52.2 | 0 | 39 | 305 | 320 | 348 | 32 | 30 | 0 | 149 | 0 | 0 | 81 | 30 | 0 | 18 | 173 | 0 | 24 | 65 | 0 | 0 | 0 | 12 | 6992.2 | 923 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 17 | 1365.38 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 135 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 105 | 220 | 0 | 247 | 1105 | 0 | 5859.38 | 12851.58 | 77.45
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 17 | 17 | 83 | 82 | 0 | 0 | 1 | 17 | 0 | 0 | 350 | 140 | 300 | 0 | 17 | 0 | 266 | 0 | 0 | 1 | 0 | 13.5 | 17 | 0 | 300 | 17 | 0 | 0 | 100 | 4 | 0 | 15 | 0 | 100 | 12 | 0 | 39 | 68 | 32 | 547 | 0 | 0 | 0 | 0 | 87 | 101 | 0 | 0 | 0 | 550 | 1 | 51 | 30 | 16 | 0 | 325 | 320 | 51 | 182 | 36 | 72 | 85 | 102 | 9 | 14 | 105 | 52 | 52.2 | 5 | 39 | 300 | 320 | 354 | 32 | 30 | 0 | 148 | 0 | 0 | 81 | 30 | 0 | 18 | 173 | 0 | 24 | 65 | 0 | 0 | 0 | 12 | 6783.7 | 923 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 553 | 17 | 1360.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 162 | 0 | 135 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 105 | 220 | 0 | 247 | 1050 | 0 | 5713.05 | 12496.75 | 77.44
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 17 | 17 | 83 | 82 | 0 | 0 | 22 | 17 | 0 | 0 | 350 | 138 | 300 | 0 | 17 | 0 | 265 | 0 | 0 | 3 | 0 | 0 | 17 | 0 | 300 | 17 | 0 | 0 | 100 | 3 | 0 | 15 | 0 | 100 | 12 | 0 | 40 | 68 | 32 | 545 | 0 | 0 | 0 | 3 | 87 | 101 | 0 | 0 | 0 | 550 | 5 | 51 | 30 | 16 | 0 | 300 | 320 | 51 | 180 | 33 | 72 | 85 | 102 | 9 | 14 | 88 | 50 | 34 | 20 | 39 | 300 | 320 | 350 | 32 | 30 | 0 | 131 | 0 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 35 | 75 | 0 | 0 | 1.09 | 12 | 6757.09 | 923 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.84 | 554 | 17 | 1371.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 1.9 | 162 | 0 | 135 | 0 | 0 | 0 | 300 | 0 | 0.22 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0 | 0 | 307 | 9 | 105 | 180 | 0 | 248 | 1050 | 0 | 5664.92 | 12422.01 | 77.43
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 17 | 17 | 107 | 82 | 0 | 0 | 35 | 17 | 0 | 0 | 300 | 140 | 300 | 0 | 17 | 0 | 284 | 0 | 0 | 1 | 0 | 16.5 | 16 | 0 | 300 | 17 | 0 | 0 | 100 | 6 | 0 | 15 | 0 | 100 | 12 | 0 | 40 | 68 | 4 | 500 | 0 | 0 | 0 | 8 | 87 | 101 | 0 | 0 | 0 | 550 | 9 | 51 | 30 | 16 | 0 | 300 | 320 | 51 | 197 | 36 | 73 | 85 | 102 | 9 | 14 | 88 | 50 | 34 | 39 | 39 | 300 | 320 | 377 | 32 | 30 | 0 | 129 | 0 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 45 | 105 | 0 | 0 | 4.35 | 12 | 6808.85 | 866 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.79 | 555 | 0 | 1365.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 7.65 | 164 | 0 | 135 | 0 | 0 | 0 | 300 | 0 | 0.55 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 16 | 0 | 0 | 307 | 8 | 100 | 180 | 0 | 250 | 1050 | 0 | 5624.2 | 12433.05 | 77.42
09:00 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 17 | 17 | 128 | 82 | 0 | 0 | 35 | 17 | 0 | 0 | 300 | 146 | 300 | 0 | 17 | 0 | 302 | 0 | 0 | 7 | 0 | 16 | 17 | 0 | 300 | 17 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 100 | 36 | 3 | 40 | 68 | 2 | 505 | 0 | 0 | 0 | 8 | 87 | 101 | 0 | 0 | 0 | 555 | 14 | 43 | 30 | 8 | 0 | 353 | 320 | 48 | 205 | 23 | 71 | 85 | 103 | 9 | 14 | 88 | 50 | 34 | 48 | 38 | 310 | 320 | 392 | 32 | 30 | 0 | 141 | 0 | 0 | 81 | 30 | 0 | 18 | 173 | 0 | 8 | 75 | 0 | 0 | 1.67 | 12 | 6971.67 | 866 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.48 | 554 | 0 | 1377.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0.27 | 166 | 0 | 133 | 0 | 0 | 0 | 350 | 0 | 0.08 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 48 | 0 | 0 | 307 | 7 | 119 | 220 | 0 | 248 | 1083 | 0 | 5846.32 | 12817.99 | 77.42
10:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 17 | 116 | 82 | 15 | 0 | 40 | 108 | 0 | 0 | 300 | 140 | 300 | 0 | 17 | 0 | 285 | 0 | 0 | 25 | 0 | 13 | 17 | 0 | 300 | 17 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 88 | 70 | 4 | 40 | 34 | 2 | 550 | 0 | 0 | 0 | 8 | 51 | 101 | 0 | 0 | 0 | 612 | 17 | 43 | 40 | 8 | 0 | 355 | 320 | 49 | 202 | 24 | 69 | 80 | 102 | 9 | 14 | 88 | 52 | 34 | 67 | 38 | 305 | 320 | 366 | 32 | 30 | 0 | 137 | 0 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 8 | 65 | 0 | 1 | 9.68 | 12 | 7120.68 | 913 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.52 | 555 | 0 | 1381.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 25.36 | 167 | 0 | 129 | 0 | 0 | 0 | 414 | 0 | 1.69 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 36 | 0 | 0 | 307 | 7 | 115 | 220 | 0 | 250 | 1120 | 0 | 5998.47 | 13119.15 | 77.41
11:00 | 8 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 17 | 17 | 93 | 82 | 95 | 4 | 51 | 162 | 0 | 0 | 300 | 144 | 300 | 0 | 17 | 0 | 265 | 0 | 0 | 2 | 0 | 0 | 16 | 0 | 300 | 17 | 0 | 1 | 100 | 0 | 0 | 15 | 0 | 88 | 88 | 2 | 40 | 34 | 2 | 557 | 0 | 0 | 3 | 12 | 51 | 101 | 0 | 0 | 0 | 612 | 18 | 43 | 61 | 8 | 0 | 355 | 320 | 50 | 180 | 27 | 68 | 75 | 103 | 9 | 14 | 97 | 50 | 43 | 74 | 37 | 305 | 320 | 350 | 32 | 30 | 0 | 133 | 0 | 0 | 81 | 30 | 0 | 18 | 173 | 0 | 45 | 65 | 0 | 1 | 6.74 | 12 | 7257.74 | 914 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.85 | 553 | 0 | 1438.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 53.92 | 160 | 0 | 125 | 0 | 0 | 0 | 250 | 0 | 4.74 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 194 | 0 | 0 | 307 | 7 | 115 | 220 | 0 | 250 | 1120 | 0 | 6084.02 | 13341.76 | 77.41
12:00 | 8 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 17 | 93 | 82 | 160 | 15 | 55 | 162 | 0 | 0 | 300 | 155 | 300 | 0 | 17 | 0 | 300 | 0 | 0 | 4 | 17 | 16 | 16 | 0 | 300 | 17 | 0 | 30 | 115 | 10 | 0 | 30 | 0 | 88 | 88 | 4 | 40 | 34 | 2 | 550 | 17 | 0 | 30 | 17 | 34 | 101 | 0 | 0 | 0 | 612 | 14 | 43 | 92 | 8 | 0 | 300 | 320 | 48 | 202 | 30 | 69 | 75 | 102 | 9 | 14 | 114 | 54 | 52.2 | 31 | 37 | 295 | 320 | 349 | 35 | 30 | 0 | 134 | 0 | 0 | 81 | 30 | 0 | 18 | 173 | 0 | 45 | 66 | 0 | 1 | 29.65 | 12 | 7522.85 | 913 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.65 | 554 | 0 | 1450.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 50.49 | 130 | 0 | 132 | 0 | 0 | 0 | 230 | 0 | 2.85 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 150 | 0 | 0 | 307 | 8 | 115 | 180 | 0 | 249 | 1130 | 0 | 6057.96 | 13580.81 | 77.4
13:00 | 8 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 25 | 17 | 96 | 82 | 180 | 15 | 55 | 162 | 0 | 0 | 300 | 146 | 350 | 0 | 17 | 0 | 275 | 0 | 0 | 1 | 35 | 13.5 | 16 | 0 | 300 | 0 | 0 | 36 | 120 | 20 | 0 | 30 | 0 | 88 | 88 | 5 | 40 | 34 | 2 | 557 | 17 | 0 | 0 | 25.5 | 34 | 101 | 0 | 0 | 0 | 612 | 18 | 43 | 105 | 8 | 0 | 351 | 320 | 49 | 185 | 30 | 70 | 75 | 102 | 8 | 6 | 114 | 30 | 52.2 | 22 | 39 | 300 | 320 | 338 | 35 | 30 | 0 | 158 | 0 | 0 | 81 | 30 | 0 | 18 | 173 | 0 | 45 | 95 | 0 | 1 | 33.09 | 12 | 7643.29 | 913 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.15 | 587 | 0 | 1452.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 33 | 130 | 0 | 138 | 0 | 0 | 0 | 230 | 0 | 2.28 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 110 | 0.64 | 0 | 307 | 9 | 107 | 220 | 0 | 249 | 1215 | 0 | 6135.28 | 13778.57 | 77.4
14:00 | 8 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 54 | 17 | 120 | 82 | 195 | 15 | 35 | 162 | 0 | 8 | 300 | 149 | 350 | 0 | 17 | 0 | 297 | 0 | 0 | 1 | 35 | 13 | 16 | 0 | 300 | 0 | 0 | 36 | 120 | 29 | 0 | 38 | 0 | 88 | 100 | 2 | 40 | 30 | 2 | 556 | 17 | 0 | 0 | 25.5 | 17 | 101 | 0 | 0 | 0 | 612 | 16 | 51 | 112 | 8 | 0 | 346 | 320 | 51 | 202 | 35 | 89 | 75 | 102 | 9 | 14 | 114 | 38 | 52.2 | 50 | 39 | 305 | 320 | 386 | 35 | 30 | 0 | 147 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 47 | 106 | 0 | 1 | 36.12 | 12 | 7853.82 | 913 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.14 | 610 | 0 | 1459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 0 | 26.13 | 130 | 0 | 141 | 0 | 0 | 0 | 230 | 0 | 2.34 | 0 | 160 | 14 | 0 | 14 | 10 | 0 | 0 | 3.6 | 123 | 0.26 | 0 | 307 | 9 | 100 | 220 | 0 | 248 | 1244 | 0 | 6227.47 | 14081.29 | 77.39
15:00 | 8 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 35 | 17 | 126 | 81 | 216 | 30 | 35 | 108 | 0 | 22 | 300 | 139 | 350 | 0 | 0 | 0 | 282 | 0 | 0 | 3 | 70 | 13 | 16 | 0 | 300 | 0 | 0 | 39 | 120 | 29 | 0 | 43 | 0 | 100 | 88 | 3 | 39 | 30 | 2 | 555 | 53 | 0 | 0 | 25.5 | 25 | 101 | 0 | 0 | 0 | 612 | 12 | 51 | 105 | 8 | 0 | 353 | 320 | 51 | 182 | 30 | 91 | 75 | 102 | 9 | 14 | 114 | 36 | 52.2 | 45 | 24 | 305 | 320 | 337 | 35 | 30 | 0 | 155 | 6 | 0 | 81 | 30 | 0 | 18 | 174 | 0 | 63 | 122 | 0 | 1 | 32.53 | 12 | 7840.23 | 913 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.92 | 610 | 17 | 1460 | 0 | 0 | 0 | 25 | 0 | 0 | 35 | 0 | 0 | 59 | 0 | 34.32 | 130 | 0 | 143 | 0 | 0 | 0 | 230 | 0 | 3.06 | 0 | 163 | 47 | 70 | 8 | 70 | 0 | 0 | 2.9 | 60 | 0.44 | 0 | 307 | 10 | 115 | 220 | 0 | 249 | 1244 | 0 | 6398.64 | 14238.87 | 77.39
16:00 | 8 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 17 | 126 | 81 | 245 | 55 | 35 | 108 | 0 | 47 | 300 | 140 | 300 | 0 | 0 | 0 | 268 | 0 | 0 | 11 | 70 | 13 | 16 | 0 | 300 | 0 | 0 | 47 | 120 | 12 | 0 | 51 | 0 | 100 | 100 | 1 | 36 | 30 | 2 | 500 | 53 | 0 | 23 | 25.5 | 47 | 101 | 0 | 0 | 0 | 606 | 8 | 51 | 107 | 8 | 0 | 320 | 320 | 48 | 185 | 29 | 92 | 75 | 122 | 23 | 14 | 114 | 36 | 25 | 26 | 24 | 300 | 320 | 311 | 35 | 30 | 0 | 129 | 6 | 0 | 79 | 30 | 0 | 18 | 174 | 2 | 65 | 122 | 0 | 1 | 17.6 | 12 | 7715.1 | 913 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.47 | 608 | 17 | 1458 | 0 | 0 | 0 | 70 | 5 | 0 | 35 | 12 | 0 | 15 | 0 | 22.27 | 130 | 0 | 140 | 0 | 0 | 0 | 230 | 0 | 0.86 | 0 | 162 | 49 | 70 | 10 | 70 | 0 | 0 | 0.5 | 49 | 0.18 | 0 | 250 | 9 | 90 | 200 | 0 | 247 | 1100 | 0 | 6155.28 | 13870.38 | 77.38
17:00 | 16 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 54 | 17 | 126 | 81 | 195 | 55 | 35 | 108 | 0 | 48 | 300 | 142 | 300 | 0 | 35 | 0 | 283 | 0 | 0 | 6 | 70 | 16 | 16 | 0 | 300 | 0 | 0 | 58 | 120 | 11 | 0 | 53 | 0 | 100 | 72 | 1 | 35 | 30 | 2 | 500 | 17 | 0 | 50 | 25.5 | 45 | 101 | 0 | 0 | 0 | 533 | 3 | 51 | 107 | 8 | 0 | 320 | 280 | 44 | 194 | 32 | 92 | 75 | 162 | 36 | 14 | 114 | 36 | 8 | 12 | 24 | 310 | 320 | 315 | 35 | 30 | 0 | 133 | 6 | 0 | 80 | 30 | 0 | 18 | 174 | 17 | 66 | 131 | 0 | 0 | 9.95 | 12 | 7657.45 | 914 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.98 | 507 | 17 | 1310 | 0 | 13 | 0 | 35 | 5 | 20 | 35 | 33 | 0 | 1 | 30 | 10.07 | 130 | 0 | 140 | 0 | 0 | 0 | 230 | 0 | 0.95 | 0 | 162 | 50 | 35 | 4 | 37 | 0 | 0 | 0.5 | 40 | 0.02 | 0 | 250 | 6 | 90 | 214 | 0 | 247 | 1010 | 0 | 5747.52 | 13404.97 | 77.38
18:00 | 16 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 54 | 17 | 126 | 81 | 195 | 15 | 55 | 122 | 0 | 48 | 300 | 151 | 300 | 0 | 35 | 0 | 284 | 0 | 0 | 1 | 108 | 16 | 16 | 0 | 300 | 2 | 5 | 66 | 120 | 14 | 0 | 65 | 0 | 70 | 48 | 0 | 37 | 30 | 2 | 450 | 17 | 0 | 50 | 8 | 44 | 101 | 0 | 0 | 0 | 485 | 1 | 51 | 108 | 8 | 0 | 270 | 260 | 49 | 193 | 36 | 92 | 75 | 170 | 37 | 14 | 114 | 32 | 8 | 1 | 24 | 300 | 320 | 330 | 35 | 30 | 0 | 129 | 6 | 0 | 82 | 20 | 0 | 18 | 174 | 18 | 85 | 170 | 0 | 0 | 0.91 | 12 | 7563.91 | 914 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.54 | 501 | 17 | 1261 | 0 | 42 | 0 | 35 | 6 | 42 | 35 | 33 | 0 | 0 | 30 | 0.23 | 130 | 0 | 140 | 0 | 0 | 0 | 230 | 0 | 0.02 | 0 | 160 | 50 | 35 | 1 | 40 | 0 | 0 | 0.1 | 8 | 0.2 | 0 | 200 | 6 | 0 | 215 | 0 | 296 | 900 | 4 | 5467.09 | 13031 | 77.37
19:00 | 32 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 126 | 118 | 275 | 20 | 55 | 162 | 0 | 48 | 300 | 135 | 300 | 0 | 35 | 0 | 270 | 0 | 0 | 0 | 120 | 16 | 16 | 0 | 300 | 18 | 15 | 51 | 120 | 6 | 0 | 68 | 0 | 88 | 100 | 0 | 38 | 35 | 2 | 457 | 122 | 0 | 50 | 12 | 52 | 101 | 0 | 0 | 0 | 560 | 0 | 51 | 118 | 8 | 0 | 352 | 325 | 50 | 189 | 36 | 92 | 75 | 165 | 38 | 14 | 114 | 36 | 10 | 0 | 25 | 315 | 320 | 387 | 35 | 30 | 0 | 152 | 6 | 0 | 85 | 28 | 0 | 18 | 174 | 35 | 94 | 179 | 0 | 0 | 0 | 12 | 8271 | 879 | 145 | 0 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 462 | 17 | 1368 | 0 | 50 | 0 | 50 | 10 | 45 | 35 | 32 | 8 | 0 | 30 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 51 | 105 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 28 | 307 | 10 | 0 | 215 | 0 | 350 | 975 | 17 | 6151 | 14422 | 77.37
19:30 | 74 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 54 | 17 | 126 | 128 | 291 | 55 | 55 | 162 | 0 | 48 | 300 | 142 | 300 | 0 | 35 | 0 | 266 | 0 | 0 | 0 | 142 | 16 | 16 | 0 | 300 | 17 | 15 | 57 | 120 | 4 | 0 | 70 | 17 | 88 | 100 | 0 | 39 | 34 | 4 | 461 | 90 | 0 | 50 | 25.5 | 44 | 101 | 0 | 0 | 0 | 570 | 0 | 51 | 122 | 8 | 0 | 356 | 325 | 53 | 182 | 35 | 92 | 75 | 200 | 38 | 14 | 114 | 40 | 43 | 0 | 16 | 300 | 320 | 336 | 35 | 30 | 0 | 143 | 6 | 0 | 85 | 28 | 0 | 18 | 174 | 35 | 94 | 179 | 0 | 0 | 0 | 12 | 8390.5 | 866 | 147 | 0 | 20 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 494 | 17 | 1436 | 0 | 50 | 0 | 70 | 10 | 91 | 35 | 37 | 8 | 0 | 30 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 161 | 51 | 90 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 32 | 307 | 9 | 0 | 215 | 0 | 315 | 1120 | 17 | 6389 | 14779.5
20:00 | 16 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 126 | 143 | 195 | 15 | 55 | 162 | 0 | 48 | 300 | 150 | 300 | 0 | 35 | 0 | 275 | 0 | 0 | 0 | 142 | 16 | 16 | 0 | 300 | 17 | 15 | 56 | 120 | 2 | 0 | 70 | 0 | 88 | 100 | 0 | 40 | 34 | 9 | 537 | 17 | 0 | 50 | 25.5 | 34 | 101 | 0 | 0 | 0 | 600 | 0 | 51 | 117 | 8 | 0 | 354 | 325 | 53 | 185 | 35 | 92 | 80 | 198 | 37 | 14 | 114 | 40 | 52.2 | 0 | 24 | 300 | 320 | 365 | 35 | 30 | 0 | 129 | 6 | 0 | 85 | 28 | 0 | 18 | 174 | 35 | 86 | 178 | 0 | 0 | 0 | 12 | 8262.7 | 868 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 17 | 1448 | 0 | 50 | 0 | 35 | 10 | 98 | 35 | 37 | 8 | 0 | 30 | 0 | 130 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 163 | 52 | 52 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 0 | 216 | 0 | 305 | 1170 | 0 | 6288 | 14550.7 | 77.36
21:00 | 16 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 54 | 17 | 126 | 127 | 195 | 15 | 55 | 162 | 0 | 48 | 350 | 143 | 300 | 0 | 35 | 0 | 290 | 0 | 0 | 0 | 142 | 16 | 16 | 0 | 300 | 17 | 15 | 35 | 120 | 13 | 0 | 70 | 0 | 88 | 48 | 0 | 40 | 34 | 12 | 537 | 17 | 0 | 19 | 25.5 | 46 | 101 | 0 | 0 | 0 | 600 | 0 | 51 | 125 | 8 | 0 | 351 | 325 | 53 | 201 | 35 | 92 | 80 | 200 | 38 | 14 | 114 | 42 | 52.2 | 0 | 39 | 310 | 320 | 375 | 35 | 30 | 0 | 152 | 6 | 0 | 85 | 25 | 0 | 18 | 174 | 35 | 86 | 179 | 0 | 0 | 0 | 6 | 8345.7 | 914 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 17 | 1444.67 | 0 | 0 | 0 | 45 | 0 | 98 | 70 | 0 | 0 | 0 | 30 | 0 | 130 | 0 | 138 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 52 | 72 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 5 | 50 | 216 | 0 | 305 | 1244 | 0 | 6502.67 | 14848.37 | 77.36
22:00 | 16 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 39 | 17 | 128 | 128 | 95 | 15 | 35 | 162 | 0 | 48 | 320 | 142 | 280 | 0 | 35 | 0 | 266 | 0 | 0 | 0 | 125 | 16 | 16 | 0 | 300 | 17 | 15 | 29 | 120 | 1 | 0 | 70 | 0 | 100 | 48 | 0 | 40 | 34 | 17 | 537 | 17 | 0 | 19 | 25.5 | 44 | 101 | 0 | 0 | 0 | 600 | 0 | 51 | 128 | 8 | 0 | 320 | 325 | 54 | 182 | 36 | 92 | 80 | 200 | 38 | 14 | 114 | 42 | 52.2 | 0 | 39 | 305 | 320 | 300 | 35 | 30 | 0 | 136 | 6 | 0 | 85 | 25 | 0 | 18 | 174 | 35 | 86 | 169 | 0 | 0 | 0 | 0 | 7923.7 | 914 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 592 | 17 | 1446.46 | 0 | 0 | 0 | 70 | 0 | 98 | 35 | 0 | 0 | 0 | 30 | 0 | 130 | 0 | 137 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 165 | 53 | 72 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 100 | 220 | 0 | 305 | 1190 | 0 | 6528.46 | 14452.16 | 77.35
23:00 | 8 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 35 | 17 | 128 | 128 | 95 | 15 | 35 | 54 | 0 | 48 | 320 | 152 | 280 | 0 | 35 | 0 | 305 | 0 | 0 | 0 | 125 | 16 | 16 | 0 | 340 | 17 | 15 | 0 | 120 | 0 | 0 | 69 | 0 | 100 | 48 | 0 | 40 | 34 | 25 | 537 | 17 | 0 | 19 | 25.5 | 48 | 101 | 0 | 0 | 0 | 600 | 0 | 51 | 130 | 8 | 0 | 350 | 325 | 54 | 210 | 36 | 92 | 80 | 200 | 39 | 14 | 114 | 42 | 52.2 | 0 | 39 | 310 | 320 | 367 | 36 | 30 | 0 | 146 | 6 | 0 | 85 | 28 | 0 | 18 | 174 | 35 | 86 | 169 | 0 | 0 | 0 | 0 | 8032.7 | 914 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 590 | 17 | 1458.8 | 0 | 0 | 0 | 70 | 0 | 98 | 35 | 0 | 0 | 0 | 30 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 55 | 72 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 305 | 1170 | 0 | 6532.8 | 14565.5 | 77.35
Total KWH | 206496 | 759360 | 480480 | 0 | 0 | 0 | 0 | 0 | 8528400 | 0 | 0 | 780120 | 432360 | 2672352 | 2222880 | 2752975 | 371540 | 798990 | 2364480 | 0 | 782400 | 7959500 | 3407680 | 7366818 | 0 | 530567 | 0 | 6844594 | 0 | 0 | 57767 | 1572000 | 342000 | 384120 | 0 | 7872272.73 | 614727 | 265964 | 592320 | 2700000 | 170400 | 0 | 1155604 | 35106 | 2017920 | 1516800 | 23937 | 103680 | 1480357 | 330240 | 12676363.64 | 384727 | 0 | 419040 | 398779.2 | 1518836 | 2357294 | 0 | 0 | 0 | 13936363 | 1127305 | 1160648 | 2259854 | 301090 | 0 | 8428700 | 7716000 | 1217280 | 4722000 | 807408 | 1949760 | 1907180 | 3298080 | 451920 | 329580 | 2570700 | 1081920 | 937728 | 446618 | 825088 | 7377000 | 7649400 | 8931000 | 798000 | 678120 | 0 | 3417381.8 | 96408 | 0 | 1959360 | 687072 | 0 | 433000 | 3596000 | 240480 | 1316400 | 2738400 | 0 | 9500 | 206410 | 255600 | 184117000.37 | 21999272 | 2989728 | 0 | 87840 | 72064 | 0 | 0 | 0 | 0 | 0 | 0 | 635040 | 14174545 | 298080 | 33883637 | 0 | 222483 | 0 | 1068000 | 56327 | 662246 | 474336 | 180973 | 29006 | 454350 | 278300 | 252000 | 3588000 | 0 | 3475418 | 0 | 0 | 0 | 8040800 | 0 | 20520 | 0 | 4015000 | 511854 | 912019 | 30650 | 906460 | 0 | 0 | 18846.12 | 819360 | 1767 | 217536 | 7200000 | 226141 | 2190000 | 5201390 | 0 | 6690909 | 27492363.64 | 339600 | 149716860.76 | 333833861.13

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 15-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13580.81 | MW | 12:00 Hr. | Energy Generated |  |  | 333.8339 |  | MKWHr.
| Day Peak Demand |  |  | 13648.74 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.585 |  | MKWHr.
| Evening Peak Generation |  |  | 14848.37 | MW | 21:00 Hr. | Energy Demand |  |  | 335.4189 |  | MKWHr.
| Evening Peak Demand |  |  | 14921.37 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.9 |  | °C
| Minimum Generation of the Day |  |  | 12422.01 | MW | 07:00 Hr. | Total Gas Supplied |  |  | 1011.1 |  | MMCFD
| Maximum Generation of the Day |  |  | 15216.13 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.1322 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.7054 | 0 | 16.727 | 0 | 0 | 0.057767 | 0 | 0 | 59.4902 | Gas | 136.017 | Gas | 487906650.5021
| Chattogram Zone |  |  | 5.3875 | 26.6127 | 10.4002 | 0 | 0.10368 | 1.1512 | 0 | 0.1704 | 43.8258 | Coal | 86.6974 | Coal | 574551299.142
| Cumilla Zone |  |  | 26.5899 | 0 | 12.2931 | 0 | 0 | 0.44662 | 1.0819 | 0 | 40.4116 | HFO | 49.7765 | HFO | 930606290.194
| Mymensingh Zone |  |  | 0 | 0 | 4.5509 | 0 | 0 | 0.21591 | 0 | 0 | 4.7668 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.6227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6227 | Hydro | 0.10368 | Hydro | 10368
| Khulna Zone |  |  | 2.9897 | 14.1745 | 0.45798 | 0 | 0 | 0.63504 | 21.9993 | 0 | 40.2566 | Solar | 4.1041 | Solar | 66394976.3232
| Barishal Zone |  |  | 7.6175 | 41.3833 | 0.55714 | 0 | 0 | 0.001767 | 0 | 0 | 49.5597 | Import | 56.9648 | Import | 319020509.74
| Rajshahi Zone |  |  | 15.1042 | 0 | 2.9717 | 0 | 0 | 0.72687 | 33.8836 | 0 | 52.6864 | Wind | 0.1704 | Wind | 2494656
| Rangpur Zone |  |  | 0 | 4.5269 | 1.8185 | 0 | 0 | 0.86886 | 0 | 0 | 7.2142
| Total |  |  | 136.017 | 86.6974 | 49.7765 | 0 | 0.10368 | 4.1041 | 56.9648 | 0.1704 | 333.8339
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 487906650.5021 |  | Hydro | 10368
|  |  |  | Coal | 574551299.142 |  | Solar | 66394976.3232
|  |  |  | HFO | 930606290.194 |  | Import | 319020509.74
|  |  |  | HSD | 0 |  | Wind | 2494656
[5 empty] | Total: | 238,09,84,749 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9993 | Peak Hr Flow | 914.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 11926345.54 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 33.8836 | Peak Hr Flow | 1444.67 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 428 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0819 | Peak Hr Flow | 42.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 904 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 56.9648 | Peak Hr Flow | 2400.67 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 35 |  | 5537
|  |  |  | Chattogram |  | 0 |  | 1578
|  |  |  | Cumilla |  | 10 |  | 1488
|  |  |  | Mymensingh |  | 25 |  | 1150
|  |  |  | Sylhet |  | 0 |  | 533
|  |  |  | Khulna |  | 0 |  | 1261
|  |  |  | Barishal |  | 0 |  | 493
|  |  |  | Rajshahi |  | 0 |  | 1497
|  |  |  | Rangpur |  | 0 |  | 884
|  |  |  | Total |  | 70 |  | 14421
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Meghnaghat CCPP(Summit) GT-2 |  |  | 110 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
|  | 4 | Siddhirgonj 210 MW TPP |  |  | 115
[5 empty] | Total | 410 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 845.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:26 |  | Ashuganj-Ghorasal 132kV Ckt-1 Project Work S/D from Ashuganj 230/132/33kV end Due to
conductor change
|  | 08:33 | Srinagar 132/33kV S/S Tr-02 HT is restored.
|  | 09:31 | Srinagar 132/33kV S/S Tr-01 HT is restored.
| 09:55 | 14:06 | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to Temperature correction | [7 empty] | 15.0MW load
interrup.
| 09:56 | 14:05 | Bhaluka 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to Temperature correction | [7 empty] | 15.0MW load
interrup.
| 10:21 | 11:12 | BIPTC S/S 10CF16 Forced S/D Due to Due to unbalance 60/61 instant L3
| 10:46 | 12:55 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to SPMD
multifunction meter installation
| 11:15 | 14:42 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Forced S/D Due to For maintenance
work
| 11:20 | 14:42 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Forced S/D Due to For maintenance
work
|  | 11:20 | Hathazari 230/132/33kV S/S T-01 LT is restored.
| 12:00 |  | Day Peak Generation: 13577 MW.
|  | 13:17 | Hasnabad 230/132kV S/S AUTO TR-3 HT is restored.
|  | 13:18 | Hasnabad 230/132kV S/S AUTO TR-3 LT is restored.
| 13:50 | 16:48 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 HT Forced S/D Due to PRD capping due to
rain
| 14:49 | 16:52 | Beanibazar 132/33kV S/S 132KV Transformer TR-02 LT Forced S/D Due to PRD capping due to
rain
| 15:28 | 16:10 | Daudkandi-Sonargaon 132 kV Ckt-1 Tripped from Daudkandi 132/33kV end showing Distance
Relay relays Due to over current Earth Fault and from Sonargaon 132/33kV end showing line
Distant Relay 21L DIR O/C & EF relay 67/67N relays Due to Perhaps bad weather , NB:
no sound during trip
| 16:48 |  | Madanganj 132/33kV S/S Madanganj -Summit 102 MW 132 kv Ckt Scheduled S/D Due to PDB
Letter & NLDC Order For Complete Disconnect
|  | 17:10 | Dhamrai 132/33kV S/S Main Bus-2 is restored.
| 21:00 |  | Evening Peak Gen. 14848 MW
| 21:10 | 22:16 | Tangail 132/33kV S/S Tr-2 LT Forced S/D Due to high temperature | [7 empty] | 90.0MW load
interrup.
| 21:11 | 22:15 | Tangail 132/33kV S/S Tr-2 HT Forced S/D Due to high temperature | [7 empty] | 90.0MW load
interrup.
| 23:18 |  | Rampal 1320 MW (BIFPCL) Synchronized with remarks:- U2
| 23:24 | 00:51 | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to Red hot maintenance. | [7 empty] | 50.0MW load
interrup.
| 23:25 | 02:23 | Ramganj 132/33kV S/S Transformer-01 LT Scheduled S/D Due to Red hot maintenance | [7 empty] | 50.0MW load
interrup.
| 00:03 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT .then ST sd-00:02
| 00:12 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 00:33 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 06:08 |  | Borhanuddin 230/33KV Transformer S/D. | [7 empty] | 48MW load interrup.
| 06:27 |  | Munshiganj 132/33kV S/S Transformer-1 LT Forced S/D Due to Emergency Maintenance on | [7 empty] | 20.0MW load
|  |  | Isolator loop point of 33KV Incoming-1 due to Red Hot | [7 empty] | interrup.
| 06:39 |  | Hasnabad 132/33kV S/S 33kv Reserve Bus Tripped showing E/F relays Due to 33kv feeders not | [7 empty] | 25.0MW load
|  |  | operate. | [7 empty] | interrup.
| 06:39 |  | Hasnabad 132/33kV S/S 33kv Reserve Bus Tripped showing E/F relays Due to 33kv feeders not | [7 empty] | 25.0MW load
|  |  | operate. | [7 empty] | interrup.
| 06:39 |  | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Tripped showing Master trip relays Due to PBS | [7 empty] | 25.0MW load
|  |  | faulty feeder not operate. | [7 empty] | interrup.
| 07:03 |  | Bakulia 132/33kV S/S T-1 (402T) HT Scheduled S/D Due to ট্রান্সফরমার -০১(৪০২টি)
সেকেন্ডারি Y-phase এর ক্যাবল সংযোগ কাজ।
| 07:14 |  | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to TR-7 installation work | [7 empty] | 5.5MW load
interrup.
| 07:14 |  | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to TR-7 installation Work | [7 empty] | 5.5MW load
interrup.
| 07:15 |  | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to TR-7 installation work | [7 empty] | 5.5MW load
interrup.
| 07:15 |  | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to TR-7 installation work | [7 empty] | 5.5MW load
interrup.
| 07:23 |  | Bheramara 230/132kV S/S Transformer-2 LT Scheduled S/D Due to underground cable
maintenance
| 07:24 |  | Bheramara 230/132kV S/S Transformer-2 HT Scheduled S/D Due to Underground cable
maintenance
| 07:25 |  | Jhenaidah 132/33kV S/S Transformer T-2 HT Scheduled S/D Due to 33 kv Bus isolator-1 loop | [7 empty] | 35.0MW load
|  |  | wire change | [7 empty] | interrup.
| 07:25 |  | Jhenaidah 132/33kV S/S Transformer T-2 LT Scheduled S/D Due to 33 kv Bus isolator-1 loop | [7 empty] | 35.0MW load
|  |  | wire change | [7 empty] | interrup.
| 07:26 |  | Magura 132/33kV S/S T-1 (405T) LT Scheduled S/D Due to WZPDCL -Magura feeder red hot | [7 empty] | 12.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 07:28 |  | Magura 132/33kV S/S T-1 (405T) HT Scheduled S/D Due to WZPDCL -Magura feeder red hot | [7 empty] | 12.0MW load
|  |  | maintenance. | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 15-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 376 | 8528400 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 7959500 | Allocation limit by Titas Gas
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 143 | 3407680 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 371540 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 290 | 6844594 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 206496 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 780120 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 127 | 2222880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 798990 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 530567 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 342000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 16 | 384120 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 480480 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 2752975 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 126 | 2672352 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 759360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 48 | 782400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2364480 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 57767 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432360 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 300 | 7872272.73 | Allocation limit by Titas, instructed by DS(Gen)
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 300 | 7366818 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1572000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2852 | 59490151.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 120 | 2700000 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 25.5 | 398779.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 1127305 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 419040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 103680 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 101 | 2357294 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 46 | 1518836 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 70 | 1155604 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 88 | 2017920 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 12 | 330240 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 35 | 592320 | Engine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 23937 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 265964 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 35106 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 1480357 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 1516800 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 614727 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 384727 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 600 | 13936363 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 13 | 170400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 537 | 12676363.64 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1837.5 | 43825762.84
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 201 | 4722000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 351 | 8428700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 325 | 7716000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 807408 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 53 | 1217280 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 301090 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1160648 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 125 | 2259854 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 825088 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1907180 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3298080 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 42 | 1081920 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 937728 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 329580 | -
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2570700 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 451920 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1949760 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 446618 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1820.2 | 40411554
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9500 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 179 | 2738400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 86 | 1316400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 206410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 255600 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 240480 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 306 | 4766790
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 35 | 798000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 678120 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3417381.8 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 25 | 687072 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1959360 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 174 | 3596000 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 433000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 96408 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7377000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 375 | 8931000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7649400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1530 | 35622741.8
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 914 | 21999272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 87840 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 72064 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 154 | 2989728 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 298080 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 635040 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 592 | 14174545 | U#2 under shutdown
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1677 | 40256569
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 305 | 6690909 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 217536 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 5 | 226141 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 50 | 2190000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27492363.64 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 216 | 5201390 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 339600 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 7200000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 1767 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2127 | 49559706.64
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 222483 | Engine Problem
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 56327 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 180973 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 130 | 3588000 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 138 | 3475418 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8040800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 30 | 278300 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 29006 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 662246 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 45 | 1068000 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 474336 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20520 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1444.67 | 33883637 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 252000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 454350 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2369.67 | 52686396
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 52 | 511854 | Partial Shutdown due to maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 168 | 4015000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 37 | 906460 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 18846.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 72 | 912019 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 30650 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 819360 | -
Rangpur Area Total |  |  |  |  | 950 | 329 | 7214189.12
Eastern Grid Total |  |  |  |  | 16921.242 | 8345.7 | 184117000.37
Western Grid Total |  |  |  |  | 11702.84 | 6502.67 | 149716860.76
National Grid Total |  |  |  |  | 28624.082 | 14848.37 | 333833861.13
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 15-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10215.99 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4134.8 | MW
i) Dhaka area |  |  | 5502.29 |  | MW | i) Khulna area |  |  |  | 1261 | MW
ii) Chattogram area |  |  | 1577.6 |  | MW | ii) Barishal area |  |  |  | 493 | MW
iii) Cumilla area |  |  | 1478.1 |  | MW | iii) Rajshahi area |  |  |  | 1496.8 | MW
iv) Mymensingh area |  |  | 1125 |  | MW | iv) Rangpur area |  |  |  | 884 | MW
v) Sylhet area |  |  | 533 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14350.79 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 81 | 00:00 | 133 | Patuakhali | 91 | 23:00
2 | AKSML | 120 | 13:00 | 68 | Jaldhaka | 68 | 19:00 | 134 | Payra | 38 | 23:00
3 | Aftabnagar | 40 | 19:00 | 69 | Jamalpur | 116 | 19:30 | 135 | Postogola | 61 | 13:00
4 | Agargaon | 132 | 11:00 | 70 | Jashore | 148 | 00:00 | 136 | Purbachal | 22 | 22:00
5 | Agrabad | 110 | 15:00 | 71 | Jhenaidah | 135 | 03:00 | 137 | Purbasadipur | 128 | 00:00
6 | Amnura | 46 | 00:00 | 72 | Joydebpur | 159 | 16:00 | 138 | Rahanpur | 32 | 00:00
7 | Ashuganj | 93 | 00:00 | 73 | Joypurhat | 76 | 00:00 | 139 | Rahim | 55 | 08:00
8 | BSRM | 198 | 18:30 | 74 | Juldah | 14 | 00:00 | 140 | Rajbari | 88 | 00:00
9 | Bagerhat | 83 | 19:00 | 75 | KSRM | 27 | 17:00 | 141 | Rajendrapur | 128 | 22:00
10 | Bajitpur | 50 | 22:00 | 76 | Kabirpur | 288 | 15:00 | 142 | Rajshahi | 156 | 00:00
11 | Bakulia | 110 | 19:00 | 77 | Kachua | 96 | 23:00 | 143 | Rajshahi-230 | 91 | 00:00
12 | Banani | 42 | 11:00 | 78 | Kallyanpur | 102 | 00:00 | 144 | Ramganj | 116 | 00:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 44 | 15:00 | 145 | Rampur | 50 | 00:00
14 | Barapukuria | 64 | 01:00 | 80 | Kamrangirchar | 70 | 13:00 | 146 | Rangamati | 19 | 19:00
15 | Barguna | 32 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 144 | 19:00
16 | Barishal | 118 | 00:00 | 82 | Kasba | 38 | 22:00 | 148 | Ruppur | 9 | 16:00
17 | Barishal-230 | 102 | 00:00 | 83 | Kazla | 100 | 23:00 | 149 | SSM | 13 | 00:00
18 | Baroaulia | 78 | 15:00 | 84 | Keranigonj | 87 | 16:00 | 150 | Saidpur | 111 | 19:00
19 | Baroirhat | 75 | 19:00 | 85 | Khagrachori | 34 | 19:00 | 151 | Satkhira | 151 | 19:30
20 | Bashundhara | 194 | 19:00 | 86 | Khulna | 82 | 12:00 | 152 | Satmasjid | 110 | 14:00
21 | BashundharaCement | 15 | 14:00 | 87 | Khulshi | 211 | 16:00 | 153 | Savar | 233 | 11:00
22 | Beanibazar | 60 | 00:00 | 88 | Kishoreganj | 133 | 19:30 | 154 | SevenRings | 3 | 17:00
23 | Benapole | 74 | 00:00 | 89 | Kodda | 318 | 15:00 | 155 | ShahCement | 38 | 17:00
24 | Bhaluka | 160 | 19:00 | 90 | Kulaura | 41 | 19:30 | 156 | Shahjadpur | 85 | 06:00
25 | Bhandaria | 61 | 22:00 | 91 | Kurigram | 56 | 21:00 | 157 | Shahjibazar | 123 | 23:00
26 | Bhangura | 46 | 00:00 | 92 | Kushtia | 174 | 00:00 | 158 | Shahmirpur | 62 | 00:00
27 | Bheramara(GK) | 73 | 00:00 | 93 | Lalbag | 70 | 13:00 | 159 | Shariatpur | 82 | 21:00
28 | Bhulta | 232 | 10:00 | 94 | Lalmonirhat | 48 | 19:00 | 160 | Sherpur | 132 | 23:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | MI_Cement | 16 | 02:00 | 161 | Shikalbaha | 36 | 13:00
30 | Bogura | 185 | 00:00 | 96 | Madanganj | 50 | 19:00 | 162 | Shitalakhya | 89 | 11:00
31 | Borhanuddin | 103 | 22:00 | 97 | Madaripur | 111 | 00:00 | 163 | Sholosohor | 54 | 16:00
32 | Brahmanbaria | 133 | 22:00 | 98 | Madartek | 91 | 00:00 | 164 | Shyampur | 152 | 23:00
33 | Cantonment | 152 | 13:00 | 99 | Madunaghat | 70 | 18:00 | 165 | Siddhirganj | 115 | 10:00
34 | Chandina | 23 | 22:00 | 100 | Magura | 72 | 00:00 | 166 | Sirajganj | 114 | 00:00
35 | Chandpur | 76 | 19:00 | 101 | Mahasthangarh | 90 | 00:00 | 167 | Sonargaon | 114 | 15:00
36 | Chandraghona | 39 | 21:00 | 102 | Manikganj | 135 | 00:00 | 168 | Sreemongol | 70 | 23:00
37 | Chapai | 77 | 00:00 | 103 | Maniknagar | 86 | 12:00 | 169 | Sreepur | 111 | 19:00
38 | Charsaidpur | 41 | 23:00 | 104 | Matarbari | 52 | 19:30 | 170 | Srinagar | 46 | 10:00
39 | Chauddagram | 74 | 20:00 | 105 | Matuail | 66 | 09:00 | 171 | Sunamganj | 54 | 00:00
40 | Chhatak | 28 | 00:00 | 106 | Millgate | 124 | 11:00 | 172 | Sylhet | 40 | 23:00
41 | Chowmuhani | 229 | 19:30 | 107 | Mirpur | 132 | 19:00 | 173 | Sylhet-132 | 105 | 00:00
42 | Chuadanga | 118 | 02:00 | 108 | Mirsorai | 11 | 14:00 | 174 | TK | 37 | 00:00
43 | Coxsbazar | 154 | 12:00 | 109 | Mirzapur | 53 | 15:00 | 175 | Tangail | 181 | 19:30
44 | Cumilla(N) | 166 | 23:00 | 110 | Mithapukur | 52 | 20:00 | 176 | Thakurgaon | 97 | 19:30
45 | Cumilla(S) | 186 | 11:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 122 | 19:00
46 | Daudkandi | 155 | 20:00 | 112 | Mogbazar | 155 | 12:00 | 178 | Ullahpara | 44 | 00:00
47 | Dhaka | 66 | 11:00 | 113 | Mongla | 54 | 16:00 | 179 | Ullon | 42 | 21:00
48 | Dhamrai | 138 | 18:30 | 114 | Motijheel | 41 | 13:00 | 180 | Uttara | 80 | 19:00
49 | Dhanmondi | 155 | 12:00 | 115 | Muktagacha | 32 | 19:00 | 181 | UttaraNew | 59 | 00:00
50 | Dohazari | 116 | 19:30 | 116 | Munshiganj | 110 | 00:00 | 182 | Zigatola | 76 | 01:00
51 | Faridpur | 166 | 00:00 | 117 | Muradnagar | 30 | 19:30
52 | Fatullah | 105 | 11:00 | 118 | Mymensingh | 193 | 20:00
53 | Fenchuganj | 37 | 19:00 | 119 | Naogaon | 154 | 00:00
54 | Feni | 132 | 22:00 | 120 | Narail | 62 | 02:00
55 | GPH | 25 | 02:00 | 121 | Narinda | 72 | 12:00
56 | Ghatail | 72 | 19:30 | 122 | Narshingdi | 182 | 21:00
57 | Ghorashal | 16 | 19:00 | 123 | Natore | 173 | 01:00
58 | Ghorashal-230 | 101 | 23:00 | 124 | Nawabganj | 59 | 00:00
59 | Goalpara | 44 | 02:00 | 125 | Netrakona | 120 | 00:00
60 | Gollamari | 106 | 00:00 | 126 | New | 88 | 12:00
61 | Gopalganj | 112 | 00:00 | 127 | Niamatpur | 86 | 00:00
62 | Gulshan | 132 | 11:00 | 128 | Noapara | 52 | 19:30
63 | Halishahar | 88 | 15:00 | 129 | PHP | 9 | 16:00
64 | HaripurSBU | 184 | 11:00 | 130 | Pabna | 129 | 01:00
65 | Hasnabad | 86 | 19:00 | 131 | Palashbari | 110 | 00:00
66 | Hathazari | 90 | 19:00 | 132 | Panchagarh | 58 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 15-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15216.13 | 181 |  | 15405.13
1:00 | 14812.33 | 152 |  | 14971.33
2:00 | 14352.14 | 160 |  | 14519.14
3:00 | 13518.35 | 69 |  | 13590.46
4:00 | 13215.38 | 38 |  | 13255.38
5:00 | 12851.58 | 34 |  | 12887.11
6:00 | 12496.75 | 19 |  | 12516.75
7:00 | 12422.01 | 20 |  | 12443.01
8:00 | 12433.05 | 0 |  | 12433.05
9:00 | 12817.99 | 33 |  | 12851.99
10:00 | 13119.15 | 52 |  | 13173.15
11:00 | 13341.76 | 65 |  | 13409.69
12:00 | 13580.81 | 65 |  | 13648.74
13:00 | 13778.57 | 61 |  | 13842.57
14:00 | 14081.29 | 68 |  | 14152.29
15:00 | 14238.87 | 72 |  | 14313.87
16:00 | 13870.38 | 60 |  | 13933.38
17:00 | 13404.97 | 66 |  | 13473.94
18:00 | 13031 | 39 |  | 13072
19:00 | 14422 | 55 |  | 14479
19:30 | 14779.5 | 49 |  | 14830.71
20:00 | 14550.7 | 67 |  | 14620.7
21:00 | 14848.37 | 70 |  | 14921.37
22:00 | 14452.16 | 66 |  | 14521.16
23:00 | 14565.5 | 73 |  | 14641.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 15-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8268.5 | 6947.63 | 15216.13 | DAILY GENERATION CURVE
00:30 | 8093.5 | 6920.73 | 15014.23
01:00 | 7918.5 | 6893.83 | 14812.33 | 15-05-2025
01:30 | 7769.75 | 6812.485 | 14582.235
02:00 | 7621 | 6731.14 | 14352.14
02:30 | 7496 | 6439.245 | 13935.245
03:00 | 7371 | 6147.35 | 13518.35
03:30 | 7321.6 | 6045.265 | 13366.865
04:00 | 7272.2 | 5943.18 | 13215.38
04:30 | 7132.2 | 5901.28 | 13033.48
05:00 | 6992.2 | 5859.38 | 12851.58
05:30 | 6887.95 | 5786.215 | 12674.165
06:00 | 6783.7 | 5713.05 | 12496.75
06:30 | 6770.395 | 5688.985 | 12459.38
07:00 | 6757.09 | 5664.92 | 12422.01
07:30 | 6782.97 | 5644.56 | 12427.53
08:00 | 6808.85 | 5624.2 | 12433.05
08:30 | 6890.26 | 5735.26 | 12625.52
09:00 | 6971.67 | 5846.32 | 12817.99
09:30 | 7046.175 | 5922.395 | 12968.57
10:00 | 7120.68 | 5998.47 | 13119.15
10:30 | 7189.21 | 6041.245 | 13230.455
11:00 | 7257.74 | 6084.02 | 13341.76
11:30 | 7390.295 | 6070.99 | 13461.285
12:00 | 7522.85 | 6057.96 | 13580.81
12:30 | 7583.07 | 6096.62 | 13679.69
13:00 | 7643.29 | 6135.28 | 13778.57
13:30 | 7748.555 | 6181.375 | 13929.93
14:00 | 7853.82 | 6227.47 | 14081.29
14:30 | 7847.025 | 6313.055 | 14160.08
15:00 | 7840.23 | 6398.64 | 14238.87
15:30 | 7777.665 | 6276.96 | 14054.625
16:00 | 7715.1 | 6155.28 | 13870.38
16:30 | 7686.275 | 5951.4 | 13637.675
17:00 | 7657.45 | 5747.52 | 13404.97
17:30 | 7610.68 | 5607.305 | 13217.985
18:00 | 7563.91 | 5467.09 | 13031
18:30 | 7917.455 | 5809.045 | 13726.5
19:00 | 8271 | 6151 | 14422
19:30 | 8390.5 | 6389 | 14779.5
20:00 | 8262.7 | 6288 | 14550.7
20:30 | 8304.2 | 6395.335 | 14699.535 |  | Executive Engineer
21:00 | 8345.7 | 6502.67 | 14848.37 |  | Network Operation Division
21:30 | 8134.7 | 6515.565 | 14650.265
22:00 | 7923.7 | 6528.46 | 14452.16
22:30 | 7978.2 | 6530.63 | 14508.83
23:00 | 8032.7 | 6532.8 | 14565.5

## En-Curve
QF-LDC-12
Date | 15-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3598 | 2064 | 922 | 0 | 54 | 1455.63 | 40 | 3811 | 0 | 675 | 2596.5 | 0 | 0 | 0 | 181 | DAILY ENERGY CURVE
00:30 | 3569 | 2057.5 | 922 | 0 | 54 | 1458.23 | 40 | 3814 | 0 | 646 | 2453.5 | 0 | 0 | 0 | 166.5 | 15-05-2025
01:00 | 3540 | 2051 | 922 | 0 | 54 | 1460.83 | 40 | 3817 | 0 | 617 | 2310.5 | 0 | 0 | 0 | 152
01:30 | 3567 | 2047.5 | 922 | 0 | 54 | 1453.985 | 39.5 | 3790.5 | 0 | 559.5 | 2147.25 | 0 | 0 | 1 | 156 | Energy Generated | 333.8339 |  | MKWHr
02:00 | 3594 | 2044 | 922 | 0 | 54 | 1447.14 | 39 | 3764 | 0 | 502 | 1984 | 0 | 0 | 2 | 160 | Energy not Served | 1.585 |  | MKWHr
02:30 | 3639 | 2043 | 922 | 0 | 53 | 1405.745 | 38.5 | 3699 | 0 | 378 | 1756 | 0 | 0 | 1 | 114.5 | Total Energy Requirement | 335.4189 |  | MKWHr
03:00 | 3684 | 2042 | 922 | 0 | 52 | 1364.35 | 38 | 3634 | 0 | 254 | 1528 | 0 | 0 | 0 | 69
03:30 | 3697 | 2049.5 | 922.5 | 0 | 52 | 1361.765 | 38 | 3587 | 0 | 227.5 | 1431.6 | 0 | 0 | 0 | 53.5
04:00 | 3710 | 2057 | 923 | 0 | 52 | 1359.18 | 38 | 3540 | 0 | 201 | 1335.2 | 0 | 0 | 0 | 38
04:30 | 3651 | 2050 | 923 | 0 | 49 | 1362.28 | 38 | 3538.5 | 0 | 192.5 | 1226.2 | 0 | 0 | 3 | 36
05:00 | 3592 | 2043 | 923 | 0 | 46 | 1365.38 | 38 | 3537 | 0 | 184 | 1117.2 | 0 | 0 | 6 | 34
05:30 | 3573.5 | 2043.75 | 923 | 0 | 49 | 1362.815 | 38.5 | 3478 | 7.4 | 172.5 | 1020.7 | 0 | 0 | 5 | 26.5
06:00 | 3555 | 2044.5 | 923 | 0 | 52 | 1360.25 | 39 | 3419 | 14.8 | 161 | 924.2 | 0 | 0 | 4 | 19
06:30 | 3521 | 2007.25 | 923 | 0 | 51 | 1365.855 | 39.5 | 3416.5 | 41.675 | 161 | 929.1 | 0 | 0 | 3.5 | 19.5
07:00 | 3487 | 1970 | 923 | 0 | 50 | 1371.46 | 40 | 3414 | 68.55 | 161 | 934 | 0 | 0 | 3 | 20
07:30 | 3509.5 | 1938.25 | 894.5 | 0 | 50 | 1368.485 | 40 | 3393 | 101.295 | 161 | 967 | 0 | 0 | 4.5 | 10
08:00 | 3532 | 1906.5 | 866 | 0 | 50 | 1365.51 | 40 | 3372 | 134.04 | 161 | 1000 | 0 | 0 | 6 | 0
08:30 | 3623 | 1929.75 | 866 | 0 | 50 | 1371.55 | 40 | 3393 | 178.72 | 182 | 988.5 | 0 | 0 | 3 | 16.5
09:00 | 3714 | 1953 | 866 | 0 | 50 | 1377.59 | 40 | 3414 | 223.4 | 203 | 977 | 0 | 0 | 0 | 33
09:30 | 3711.5 | 1944.5 | 889.5 | 0 | 51 | 1379.395 | 40 | 3476.5 | 263.175 | 212 | 1001 | 0 | 0 | 0 | 42.5
10:00 | 3709 | 1936 | 913 | 0 | 52 | 1381.2 | 40 | 3539 | 302.95 | 221 | 1025 | 0 | 0 | 0 | 52
10:30 | 3583.5 | 1929.5 | 913.5 | 0 | 51 | 1410.005 | 40 | 3553 | 386.45 | 220.5 | 1143 | 0 | 0 | 0 | 58.5
11:00 | 3458 | 1923 | 914 | 0 | 50 | 1438.81 | 40 | 3567 | 469.95 | 220 | 1261 | 0 | 0 | 0 | 65
11:30 | 3457.5 | 1911.5 | 913.5 | 0 | 52 | 1444.59 | 40 | 3569 | 471.595 | 236 | 1360.6 | 0 | 0 | 5 | 65
12:00 | 3457 | 1900 | 913 | 0 | 54 | 1450.37 | 40 | 3571 | 473.24 | 252 | 1460.2 | 0 | 0 | 10 | 65
12:30 | 3466 | 1950.75 | 913 | 0 | 42 | 1451.29 | 40 | 3631 | 428.2 | 262 | 1480.45 | 0 | 0 | 15 | 63
13:00 | 3475 | 2001.5 | 913 | 0 | 30 | 1452.21 | 40 | 3691 | 383.16 | 272 | 1500.7 | 0 | 0 | 20 | 61
13:30 | 3521 | 2011.75 | 913 | 0 | 34 | 1455.605 | 40 | 3721 | 401.375 | 258.5 | 1549.2 | 0 | 0 | 24.5 | 64.5
14:00 | 3567 | 2022 | 913 | 0 | 38 | 1459 | 40 | 3751 | 419.59 | 245 | 1597.7 | 0 | 0 | 29 | 68
14:30 | 3553.5 | 2021.5 | 913 | 0 | 37 | 1459.5 | 39.5 | 3769 | 359.88 | 257 | 1721.2 | 0 | 0 | 29 | 70
15:00 | 3540 | 2021 | 913 | 0 | 36 | 1460 | 39 | 3787 | 300.17 | 269 | 1844.7 | 0 | 0 | 29 | 72
15:30 | 3473.5 | 1968 | 913 | 0 | 36 | 1459 | 37.5 | 3654.5 | 255.525 | 281.5 | 1955.6 | 0 | 0 | 20.5 | 66
16:00 | 3407 | 1915 | 913 | 0 | 36 | 1458 | 36 | 3522 | 210.88 | 294 | 2066.5 | 0 | 0 | 12 | 60
16:30 | 3408 | 1928.5 | 913.5 | 0 | 36 | 1384 | 35.5 | 3390.5 | 164.675 | 337 | 2028.5 | 0 | 0 | 11.5 | 63
17:00 | 3409 | 1942 | 914 | 0 | 36 | 1310 | 35 | 3259 | 118.47 | 380 | 1990.5 | 0 | 0 | 11 | 66
17:30 | 3328 | 1943.5 | 914 | 0 | 34 | 1285.5 | 36 | 3150.5 | 68.735 | 448.5 | 1996.75 | 0 | 0 | 12.5 | 52.5
18:00 | 3247 | 1945 | 914 | 0 | 32 | 1261 | 37 | 3042 | 19 | 517 | 2003 | 0 | 0 | 14 | 39
18:30 | 3438 | 1960 | 896.5 | 0 | 34 | 1314.5 | 37.5 | 3182.5 | 9.5 | 548 | 2296 | 0 | 0 | 10 | 47
19:00 | 3629 | 1975 | 879 | 0 | 36 | 1368 | 38 | 3323 | 0 | 579 | 2589 | 0 | 0 | 6 | 55
19:30 | 3512 | 1962 | 866 | 0 | 40 | 1436 | 39 | 3479 | 0 | 676 | 2765.5 | 0 | 0 | 4 | 49
20:00 | 3545 | 1964 | 868 | 0 | 40 | 1448 | 40 | 3708 | 0 | 673 | 2262.7 | 0 | 0 | 2 | 67
20:30 | 3643.5 | 2000.5 | 891 | 0 | 41 | 1446.335 | 40 | 3756.5 | 0 | 624 | 2249.2 | 0 | 0 | 7.5 | 68.5
21:00 | 3742 | 2037 | 914 | 0 | 42 | 1444.67 | 40 | 3805 | 0 | 575 | 2235.7 | 0 | 0 | 13 | 70
21:30 | 3673.5 | 2008 | 914 | 0 | 42 | 1445.565 | 40 | 3777 | 0 | 567 | 2176.2 | 0 | 0 | 7 | 68
22:00 | 3605 | 1979 | 914 | 0 | 42 | 1446.46 | 40 | 3749 | 0 | 559 | 2116.7 | 0 | 0 | 1 | 66
22:30 | 3710 | 2016.5 | 914 | 0 | 42 | 1452.63 | 40 | 3738 | 0 | 549.5 | 2045.7 | 0 | 0 | 0.5 | 69.5
23:00 | 3815 | 2054 | 914 | 0 | 42 | 1458.8 | 40 | 3727 | 0 | 540 | 1974.7 | 0 | 0 | 0 | 73
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 15-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 378 | 01:00 | 372 | 10:00 | Payra | 412 | 18:00 | 406 | 00:00
Ashuganj | 393 | 6:00 | 371 | 14:00 | Rahanpur | 404 | 17:00 | 393 | 13:00
Bhulta | 384 | 04:00 | 370 | 10:00 | Rampal | 393 | 17:00 | 377 | 00:00
Bibiana | 391 | 05:00 | 385 | 23:00
BIPTC | 399 | 19:00 | 386 | 00:00
Bogura | 388 | 18:00 | 377 | 13:00
Gopalganj | 392 | 18:00 | 379 | 00:00
Kaliakoir | 371 | 18:00 | 363 | 14:00
Madunaghat | 392 | 08:00 | 385 | 15:00
Meghnaghat | 384 | 06:00 | 377 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 221 | 07:00 | 214 | 10:00 | Keranigonj | 219 | 07:00 | 212 | 10:00
AKSML | 231 | 00:00 | 224 | 12:00 | Khulna(S) | 226 | 18:00 | 210 | 00:00
Aminbazar | 220 | 05:00 | 215 | 10:00 | Madunaghat | 233 | 19:00 | 227 | 14:00
Ashuganj | 229 | 07:00 | 221 | 15:00 | Madunaghat-400 | 232 | 00:00 | 228 | 14:00
Ashuganj-400 | 218 | 6:00 | 210 | 14:00 | Maniknagar | 218 | 05:00 | 210 | 12:00
Baghabari | 233 | 17:00 | 227 | 00:00 | Meghnaghat | 225 | 04:00 | 220 | 10:00
Barapukuria | 227 | 00:00 | 219 | 20:00 | Meghnaghat-400 | 221 | 06:00 | 216 | 10:00
Barapukuria-230 | 226 | 23:00 | 220 | 19:00 | Mirsorai | 229 | 19:30 | 220 | 10:00
Barishal | 236 | 17:00 | 227 | 00:00 | Rajshahi | 236 | 17:00 | 223 | 00:00
Bheramara | 235 | 17:00 | 223 | 00:00 | Rampal | 225 | 17:00 | 211 | 00:00
Bhulta | 222 | 04:00 | 212 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 04:00 | 220 | 12:00 | Rampura | 222 | 07:00 | 210 | 10:00
BIPTC | 236 | 17:00 | 223 | 02:00 | Shikalbaha | 231 | 00:00 | 224 | 13:00
Bogura | 235 | 17:00 | 228 | 14:00 | Shyampur | 219 | 06:00 | 213 | 10:00
Bogura-400 | 236 | 17:00 | 230 | 13:00 | Siddhirganj | 219 | 07:00 | 213 | 10:00
Borhanuddin | 240 | 17:00 | 233 | 01:00 | Sirajgonj | 238 | 17:00 | 235 | 00:00
BSRM | 228 | 19:00 | 219 | 10:00 | Sreepur | 225 | 02:00 | 220 | 15:00
Cumilla(N) | 220 | 05:00 | 210 | 18:30 | Tongi | 222 | 23:00 | 216 | 04:00
Faridpur | 232 | 17:00 | 221 | 00:00
Fenchuganj | 228 | 06:00 | 222 | 19:00
Ghorashal | 233 | 01:00 | 220 | 13:00
Ghorashal-230 | 222 | 07:00 | 214 | 15:00
Gopalganj | 233 | 18:00 | 224 | 00:00
GPH | 230 | 19:00 | 223 | 10:00
Haripur | 218 | 00:00 | 216 | 01:00
Hasnabad | 222 | 08:00 | 212 | 14:00
Hathazari | 232 | 19:00 | 227 | 10:00
Ishurdi | 236 | 17:00 | 226 | 00:00
Jhenaidah | 230 | 18:00 | 211 | 00:00
Kaliakoir | 226 | 07:00 | 221 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 06:00 | 127 | 10:00 | Madartek | 135 | 04:00 | 126 | 10:00
Agargaon | 160 | 18:30 | 127 | 10:00 | Madunaghat | 132 | 18:30 | 128 | 10:00
Agrabad | 131 | 00:00 | 127 | 12:00 | Magura | 137 | 18:00 | 120 | 00:00
AKS | 129 | 00:00 | 126 | 10:00 | Mahasthangarh | 136 | 01:00 | 131 | 14:00
Aminbazar | 129 | 00:00 | 124 | 09:00 | Manikganj | 129 | 22:00 | 122 | 01:00
Amnura | 138 | 17:00 | 124 | 00:00 | Maniknagar | 131 | 05:00 | 125 | 12:00
Ashuganj | 135 | 00:00 | 132 | 15:00 | Matarbari | 117 | 15:00 | 107 | 20:00
Bagerhat | 128 | 18:00 | 113 | 00:00 | Matuail | 127 | 05:00 | 123 | 10:00
Bajitpur | 129 | 09:00 | 124 | 14:00 | Millgate | 132 | 07:00 | 126 | 09:00
Bakulia | 133 | 19:00 | 129 | 10:00 | Mirpur | 128 | 07:00 | 123 | 10:00
Banani | 137 | 07:00 | 126 | 15:00 | Mirzapur | 134 | 10:00 | 127 | 23:00
Bangabhaban | 131 | 04:00 | 125 | 11:00 | Mithapukur | 136 | 00:00 | 126 | 21:00
Barapukuria | 138 | 00:00 | 131 | 20:00 | MI_Cement | 128 | 05:00 | 123 | 10:00
Barguna | 134 | 00:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 17:00 | 123 | 23:00 | Mogbazar | 137 | 03:00 | 127 | 10:00
Barishal-230 | 132 | 17:00 | 124 | 23:00 | Mongla | 129 | 17:00 | 115 | 00:00
Baroaulia | 135 | 04:00 | 128 | 13:00 | Motijheel | 131 | 04:00 | 125 | 11:00
Baroirhat | 124 | 07:00 | 119 | 10:00 | Muktagacha | 135 | 11:00 | 128 | 23:00
Bashundhara | 137 | 04:00 | 124 | 09:00 | Munshiganj | 127 | 06:00 | 121 | 10:00
BashundharaCement | 127 | 00:00 | 122 | 10:00 | Muradnagar | 124 | 03:00 | 120 | 10:00
Beanibazar | 136 | 05:00 | 132 | 22:00 | Mymensingh | 136 | 09:00 | 116 | 19:00
Benapole | 129 | 20:00 | 112 | 00:00 | Naogaon | 135 | 17:00 | 128 | 00:00
Bhaluka | 129 | 03:00 | 123 | 15:00 | Narail | 139 | 20:00 | 119 | 00:00
Bhandaria | 126 | 17:00 | 113 | 23:00 | Narinda | 131 | 5:00 | 125 | 12:00
Bhangura | 133 | 17:00 | 129 | 00:00 | Narshingdi | 126 | 18:00 | 116 | 10:00
Bheramara | 137 | 18:30 | 129 | 00:00 | Natore | 136 | 17:00 | 129 | 00:00
Bheramara(GK) | 137 | 18:30 | 129 | 00:00 | Nawabganj | 130 | 05:00 | 125 | 10:00
Bhulta | 119 | 05:00 | 115 | 10:00 | Netrakona | 126 | 04:00 | 113 | 14:00
Bog-Sherpur | 136 | 17:00 | 132 | 03:00 | New | 132 | 00:00 | 127 | 09:00
Bogura | 139 | 17:00 | 133 | 14:00 | Niamatpur | 138 | 14:00 | 129 | 21:00
Bogura-230 | 139 | 17:00 | 134 | 14:00 | Noapara | 132 | 11:00 | 117 | 00:00
Brahmanbaria | 128 | 06:00 | 122 | 00:00 | Pabna | 134 | 11:00 | 128 | 00:00
Cantonment | 132 | 04:00 | 127 | 10:00 | Palashbari | 133 | 01:00 | 125 | 21:00
Chandina | 127 | 06:00 | 122 | 10:00 | Panchagarh | 141 | 02:00 | 123 | 14:00
Chandpur | 126 | 06:00 | 120 | 14:00 | Patuakhali | 136 | 00:00 | 130 | 21:00
Chandraghona | 132 | 19:00 | 128 | 10:00 | Payra | 135 | 08:00 | 132 | 21:00
Chapai | 133 | 17:00 | 126 | 00:00 | PHP | 123 | 06:00 | 116 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 19:00 | 122 | 12:00 | Postogola | 131 | 05:00 | 125 | 10:00
Chauddagram | 124 | 06:00 | 117 | 14:00 | Purbachal | 136 | 02:00 | 126 | 10:00
Chhatak | 134 | 04:00 | 124 | 00:00 | Purbasadipur | 132 | 00:00 | 121 | 13:00
Chowmuhani | 116 | 06:00 | 111 | 14:00 | Rahanpur | 135 | 18:00 | 130 | 13:00
Chuadanga | 138 | 20:00 | 117 | 00:00 | Rahanpur-400 | 136 | 17:00 | 131 | 13:00
Coxsbazar | 116 | 05:00 | 108 | 19:30 | Rahim | 127 | 03:00 | 123 | 10:00
Cumilla(N) | 129 | 21:00 | 122 | 14:00 | Rajbari | 134 | 17:00 | 126 | 00:00
Cumilla(S) | 132 | 22:00 | 120 | 23:00 | Rajendrapur | 131 | 03:00 | 122 | 11:00
Daudkandi | 123 | 04:00 | 118 | 15:00 | Rajshahi | 138 | 17:00 | 128 | 00:00
Dhaka | 136 | 05:00 | 128 | 10:00 | Rajshahi-230 | 138 | 17:00 | 118 | 00:00
Dhamrai | 132 | 18:00 | 13 | 21:00 | Ramganj | 119 | 18:00 | 113 | 14:00
Dhanmondi | 137 | 07:00 | 127 | 11:00 | Rampur | 132 | 19:00 | 126 | 13:00
Dohazari | 125 | 04:00 | 121 | 20:00 | Rampura | 136 | 04:00 | 127 | 10:00
Faridpur | 136 | 17:00 | 128 | 00:00 | Rangamati | 130 | 01:00 | 127 | 10:00
Fatullah | 129 | 05:00 | 28 | 18:00 | Rangpur | 136 | 00:00 | 124 | 21:00
Fenchuganj | 136 | 05:00 | 132 | 19:00 | Ruppur | 138 | 18:00 | 132 | 00:00
Feni | 124 | 06:00 | 115 | 15:00 | Saidpur | 137 | 02:00 | 124 | 14:00
Ghatail | 136 | 10:00 | 126 | 23:00 | Satkhira | 128 | 18:00 | 112 | 00:00
Ghorashal | 135 | 07:00 | 129 | 13:00 | Satmasjid | 133 | 07:00 | 126 | 10:00
Goalpara | 134 | 18:00 | 121 | 00:00 | Savar | 128 | 18:00 | 122 | 09:00
Gollamari | 134 | 18:00 | 123 | 00:00 | SevenRings | 134 | 07:00 | 129 | 10:00
Gopalganj | 134 | 18:00 | 124 | 00:00 | ShahCement | 128 | 19:00 | 122 | 12:00
Gopalganj-400 | 135 | 17:00 | 129 | 00:00 | Shahjadpur | 135 | 07:00 | 132 | 00:00
Gulshan | 136 | 05:00 | 127 | 10:00 | Shahjibazar | 131 | 08:00 | 124 | 23:00
Halishahar | 134 | 19:00 | 127 | 10:00 | Shahmirpur | 133 | 01:00 | 129 | 13:00
Haripur | 127 | 01:00 | 124 | 10:00 | Shariatpur | 134 | 17:00 | 124 | 00:00
HaripurSBU | 127 | 00:00 | 124 | 11:00 | Sherpur | 140 | 08:00 | 134 | 03:00
Hasnabad | 130 | 01:00 | 124 | 09:00 | Shikalbaha | 122 | 01:00 | 118 | 10:00
Hathazari | 135 | 07:00 | 131 | 16:00 | Shikalbaha-230 | 133 | 02:00 | 126 | 09:00
Ishurdi | 138 | 17:00 | 132 | 00:00 | Shitalakhya | 128 | 05:00 | 123 | 10:00
Jaldhaka | 137 | 02:00 | 123 | 13:00 | Sholosohor | 132 | 01:00 | 127 | 10:00
Jamalpur | 141 | 08:00 | 129 | 01:00 | Shyampur | 129 | 07:00 | 123 | 10:00
Jashore | 129 | 20:00 | 114 | 00:00 | Shyampur-230 | 128 | 04:00 | 124 | 10:00
Jhenaidah | 139 | 20:00 | 120 | 15:00 | Siddhirganj | 127 | 01:00 | 123 | 10:00
Jhenaidah-230 | 138 | 18:00 | 122 | 00:00 | Sirajganj | 133 | 10:00 | 129 | 00:00
Joydebpur | 135 | 13:00 | 129 | 19:00 | Sonargaon | 126 | 00:00 | 120 | 10:00
Joypurhat | 132 | 17:00 | 126 | 00:00 | Sreemongol | 131 | 05:00 | 126 | 19:30
Juldah | 134 | 19:00 | 130 | 10:00 | Sreepur | 131 | 00:00 | 126 | 15:00
Kabirpur | 134 | 13:00 | 123 | 10:00 | Srinagar | 132 | 07:00 | 125 | 10:00
Kachua | 124 | 05:00 | 119 | 14:00 | SSM | 139 | 13:00 | 130 | 14:00
Kaliakoir | 136 | 18:00 | 132 | 12:00 | Sunamganj | 135 | 05:00 | 122 | 01:00
Kallyanpur | 129 | 00:00 | 124 | 09:00 | Sylhet | 135 | 05:00 | 128 | 00:00
Kalurghat | 131 | 19:00 | 128 | 10:00 | Sylhet-132 | 133 | 05:00 | 129 | 00:00
Kamrangirchar | 130 | 05:00 | 124 | 10:00 | Tangail | 134 | 10:00 | 125 | 01:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 143 | 02:00 | 124 | 14:00
Kasba | 124 | 05:00 | 119 | 15:00 | TK | 131 | 02:00 | 127 | 14:00
Kazla | 131 | 05:00 | 125 | 11:00 | Tongi | 133 | 00:00 | 128 | 15:00
Keranigonj | 131 | 07:00 | 126 | 10:00 | Ullahpara | 134 | 11:00 | 130 | 00:00
Khagrachori | 130 | 00:00 | 126 | 10:00 | Ullon | 136 | 05:00 | 127 | 10:00
Khulna | 132 | 18:00 | 119 | 00:00 | Uttara | 128 | 07:00 | 122 | 10:00
Khulna(S) | 134 | 18:00 | 122 | 00:00 | UttaraNew | 128 | 07:00 | 123 | 09:00
Khulshi | 131 | 19:00 | 126 | 13:00 | Zigatola | 131 | 08:00 | 125 | 11:00
Kishoreganj | 127 | 04:00 | 120 | 15:00
Kodda | 134 | 22:00 | 121 | 10:00
KSRM | 135 | 19:00 | 128 | 14:00
Kulaura | 135 | 05:00 | 131 | 00:00
Kurigram | 138 | 02:00 | 118 | 21:00
Kushtia | 136 | 18:30 | 124 | 00:00
Lalbag | 131 | 07:00 | 125 | 10:00
Lalmonirhat | 135 | 01:00 | 120 | 21:00
Madanganj | 127 | 07:00 | 122 | 10:00
Madaripur | 135 | 18:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division