## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 17-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-05-2025 | during | 17-05-2025 | during | 17-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 348 | 330 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 420 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 140 | 143 | 335 | 335 | 133.25 | 133.25 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 282 | 267 | 335 | 335 | 301.5 | 301.5 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 6 | 17 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 68 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 2 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 18 | 30 | 30 | 19 | 19 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 19 | 18 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 16 | 16 | 52.19 | 52.19 | 25 | 25 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 60 | 300 | 300 | 281 | 281 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 85 | 70 | 149 | 149 | 113 | 113 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 34 | 105 | 105 | 34 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 35 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 126 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 27 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 470 | 550 | 584 | 584 | 584 | 584 | Allocation limit by Titas, instructed by DS(Gen)
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 130 | 61 | 0 | 0 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 17 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2218.5 | 2267 | 4688.9 | 4750.9 | 3090.15 | 3206.15
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 120 | 120 | 120 | 120 | 120 | 120 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 16 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 35 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 6 | 0 | 105 | 105 | 87 | 87 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 8 | 31 | 48 | 72 | 64 | 76 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 0 | 68 | 68 | 98 | 98 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 48 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 27 | 32 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 43 | 108 | 108 | 70 | 70 | Engine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 4 | 0 | 4.48 | 0 | 4.48 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 3 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 72 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 607 | 612 | 612 | 1224 | 612 | 612 | Unit-1 Under Start-Up
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 11 | 15 | 10 | 14 | 10 | 14 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 555 | 549 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1493 | 1636 | 2730.2 | 3353.72 | 2704.34 | 2703.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 191 | 182 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 340 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 335 | 320 | 320 | 320 | 320 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 33 | 46.94 | 46.94 | 37 | 37 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 45 | 49 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 55 | 26 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 5 | 0 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 18 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 120 | 136 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 9 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 17.75 | 17.75 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 105 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 35 | 113 | 113 | 9 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 92 | 115 | 115 | 51 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 48 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1541 | 1611.2 | 2424.24 | 2374.24 | 2127.3 | 2145.3
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 16-05-2025 | during | 17-05-2025 | during | 17-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 0 | 0 | 0 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 122 | 168 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 66 | 45 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.23 | 0 | 26 | 0 | 26 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 251.23 | 242 | 575 | 549 | 266 | 312
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 35 | 33 | 32 | 32 | 32 | 32 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 142 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 80 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 170 | 170 | 170 | 174 | 174 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 16 | 20 | 20 | 20 | 20 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 8 | 25 | 25 | 10 | 10 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 382 | 335 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1521 | 1449 | 1611 | 1611 | 1522 | 1522
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 913 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 190 | 192 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 89.43 | 0 | 96 | 0 | 96 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 910 | 1000 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2102.43 | 2085 | 3610.2 | 3514.2 | 3207.01 | 3111.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 295 | 461 | 450 | 450 | 450 | 450 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 7 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 115 | 90 | 125 | 125 | 113 | 113 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1046 | 1235 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1987.8 | 2320 | 2616.12 | 2616.12 | 2564.12 | 2564.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 130 | 176 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 127 | 187 | 220 | 220 | 180 | 180 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 367 | 319 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 42 | 42 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 49 | 98 | 98 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.11 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1209.23 | 1452.31 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.22 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 50 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 1936.56 | 2183.31 | 3195.17 | 3028.87 | 2846.19 | 2679.89
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 54 | 54 | 55 | 55 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 161 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.2 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 29 | 0 | 29 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 34 | 0 | 98.52 | 0 | 98.52 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 267.2 | 284 | 581.12 | 447 | 581.12 | 447
System Total |  |  |  |  | 27566.2 | 28624.082 | 13318.72 | 14077.51 | 22031.95 | 22245.05 | 18908.23 | 18691.33
Forecast Scenario (17-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13077 |  | 0 |  | 13077
|  |  |  | 1:00 | 12500 |  | 0 |  | 12500
|  |  |  | 2:00 | 12450 |  | 0 |  | 12450
|  |  |  | 3:00 | 12441 |  | 0 |  | 12441
|  |  |  | 4:00 | 12279 |  | 0 |  | 12279
|  |  |  | 5:00 | 12321 |  | 0 |  | 12321
|  |  |  | 6:00 | 12789 |  | 0 |  | 12789
|  |  |  | 7:00 | 13067 |  | 0 |  | 13067
|  |  |  | 8:00 | 13118 |  | 0 |  | 13118
|  |  |  | 9:00 | 13389 |  | 0 |  | 13389
|  |  |  | 10:00 | 13864 |  | 0 |  | 13864
|  |  |  | 11:00 | 14182 |  | 0 |  | 14182
|  |  |  | 12:00 | 14338 |  | 0 |  | 14338
|  |  |  | 13:00 | 14435 |  | 0 |  | 14435
|  |  |  | 14:00 | 14594 |  | 0 |  | 14594
|  |  |  | 15:00 | 14887 |  | 0 |  | 14887
|  |  |  | 16:00 | 14645 |  | 0 |  | 14645
|  |  |  | 17:00 | 14403 |  | 0 |  | 14403
|  |  |  | 18:00 | 14387 |  | 0 |  | 14387
|  |  |  | 18:30 | 14977 |  | 0 |  | 14977
|  |  |  | 19:00 | 15709 |  | 0 |  | 15709
|  |  |  | 19:30 | 15821 |  | 0 |  | 15821
|  |  |  | 20:00 | 15400 |  | 0 |  | 15400
|  |  |  | 21:00 | 15551 |  | 0 |  | 15551
|  |  |  | 22:00 | 15482 |  | 0 |  | 15482
|  |  |  | 23:00 | 15200 |  | 0 |  | 15200
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 14338.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15821.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15821.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 333.73532 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:04 hrs on 17-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 16-05-2025 | [28 empty] | Date: | 16-05-2025 | [28 empty] | Date: | 16-05-2025 | [28 empty] | Date: | 16-05-2025 | [28 empty] | Date: | 16-05-2025 | [16 empty] | Date: | 16-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [16 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 8 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35 | 17 | 133 | 112 | 95 | 15 | 35 | 54 | 0 | 48 | 320 | 138 | 200 | 0 | 35 | 0 | 270 | 0 | 0 | 0 | 125 | 16 | 16 | 0 | 370 | 27 | 30 | 0 | 120 | 11 | 0 | 69 | 0 | 100 | 48 | 0 | 40 | 58 | 28 | 540 | 17 | 0 | 19 | 25.5 | 48 | 101 | 0 | 0 | 0 | 600 | 0 | 51 | 130 | 8 | 0 | 358 | 325 | 54 | 183 | 32 | 92 | 80 | 170 | 15 | 14 | 114 | 42 | 52.2 | 0 | 38 | 305 | 320 | 350 | 36 | 30 | 0 | 151 | 6 | 0 | 85 | 25 | 0 | 18 | 174 | 20 | 48 | 95 | 0 | 0 | 0 | 4 | 7746.7 | 914 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 755 | 17 | 1440.3 | 0 | 0 | 0 | 101 | 0 | 98 | 35 | 0 | 0 | 0 | 30 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 163 | 55 | 72 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 305 | 1210 | 0 | 6686.3 | 14433 | 77.34
01:00 | 4 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 35 | 17 | 112 | 82 | 60 | 15 | 55 | 54 | 0 | 48 | 380 | 147 | 0 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 125 | 16 | 16 | 0 | 480 | 0 | 0 | 0 | 120 | 0 | 0 | 61 | 0 | 100 | 48 | 0 | 40 | 66 | 30 | 556 | 0 | 0 | 19 | 25.5 | 46 | 101 | 0 | 0 | 0 | 550 | 0 | 51 | 70 | 8 | 0 | 354 | 325 | 55 | 199 | 32 | 72 | 80 | 170 | 9 | 14 | 114 | 38 | 52.2 | 0 | 38 | 310 | 320 | 356 | 34 | 30 | 0 | 152 | 6 | 0 | 85 | 28 | 0 | 18 | 174 | 17 | 48 | 95 | 0 | 0 | 0 | 12 | 7463.7 | 914 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 922 | 17 | 1451.09 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 164 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 115 | 220 | 0 | 306 | 1150 | 0 | 6478.09 | 13941.79 | 77.34
02:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 35 | 17 | 102 | 82 | 15 | 0 | 17 | 17 | 0 | 47 | 340 | 144 | 0 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 90 | 16.5 | 16 | 0 | 480 | 0 | 0 | 0 | 120 | 5 | 0 | 61 | 0 | 100 | 36 | 0 | 39 | 17 | 30 | 557 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 540 | 0 | 51 | 50 | 8 | 0 | 353 | 320 | 54 | 191 | 32 | 72 | 80 | 170 | 9 | 14 | 114 | 38 | 52.2 | 0 | 38 | 305 | 320 | 360 | 34 | 30 | 0 | 148 | 6 | 0 | 85 | 28 | 0 | 18 | 174 | 17 | 48 | 95 | 0 | 0 | 0 | 12 | 7015.7 | 914 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1017 | 0 | 1463.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 163 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 115 | 220 | 0 | 306 | 1150 | 0 | 6492.96 | 13508.66 | 77.33
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 17 | 86 | 64 | 0 | 0 | 0 | 0 | 0 | 16 | 340 | 141 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 90 | 16.5 | 16 | 0 | 480 | 0 | 0 | 0 | 120 | 11 | 0 | 61 | 0 | 100 | 36 | 0 | 38 | 0 | 30 | 558 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 540 | 0 | 51 | 30 | 8 | 0 | 354 | 325 | 54 | 182 | 32 | 72 | 85 | 170 | 9 | 14 | 114 | 38 | 52.2 | 0 | 38 | 310 | 320 | 368 | 34 | 30 | 0 | 151 | 6 | 0 | 85 | 28 | 0 | 18 | 174 | 0 | 48 | 95 | 0 | 0 | 0 | 12 | 6856.7 | 913 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 1455.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 164 | 55 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 115 | 220 | 0 | 294 | 1150 | 0 | 6469.45 | 13326.15 | 77.33
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 35 | 17 | 86 | 64 | 0 | 0 | 0 | 0 | 0 | 16 | 340 | 144 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 70 | 16.5 | 16 | 0 | 480 | 0 | 0 | 0 | 120 | 8 | 0 | 61 | 0 | 100 | 36 | 0 | 38 | 0 | 30 | 557 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 540 | 0 | 51 | 15 | 8 | 0 | 354 | 325 | 54 | 194 | 32 | 72 | 85 | 170 | 9 | 14 | 114 | 38 | 52.2 | 0 | 38 | 300 | 320 | 365 | 34 | 30 | 0 | 149 | 6 | 0 | 85 | 30 | 0 | 18 | 174 | 0 | 48 | 95 | 0 | 0 | 0 | 12 | 6812.7 | 914 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 985 | 0 | 1412.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 165 | 57 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 115 | 220 | 0 | 249 | 1150 | 0 | 6328.41 | 13141.11 | 77.32
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 26 | 17 | 80 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 143 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 70 | 17 | 16 | 0 | 480 | 0 | 0 | 0 | 120 | 9 | 0 | 61 | 0 | 100 | 36 | 0 | 37 | 0 | 30 | 504 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 540 | 0 | 51 | 0 | 8 | 0 | 354 | 325 | 54 | 187 | 32 | 72 | 85 | 170 | 9 | 14 | 114 | 36 | 52.2 | 0 | 38 | 310 | 320 | 350 | 35 | 30 | 0 | 152 | 6 | 0 | 85 | 30 | 0 | 18 | 174 | 0 | 47 | 95 | 0 | 0 | 0 | 12 | 6706.2 | 914 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 962 | 0 | 1358.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 136 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 167 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 105 | 220 | 0 | 248 | 1100 | 0 | 6161.04 | 12867.24 | 77.32
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 17 | 76 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 142 | 0 | 0 | 0 | 0 | 277 | 0 | 0 | 1 | 35 | 17 | 16 | 0 | 450 | 0 | 0 | 0 | 120 | 17 | 0 | 16 | 0 | 70 | 12 | 0 | 38 | 0 | 30 | 500 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 500 | 1 | 51 | 0 | 8 | 0 | 320 | 300 | 55 | 186 | 36 | 72 | 85 | 136 | 9 | 14 | 114 | 34 | 52.2 | 2 | 0 | 295 | 320 | 350 | 34 | 30 | 0 | 133 | 6 | 0 | 85 | 30 | 0 | 18 | 174 | 0 | 48 | 99 | 0 | 0 | 3.67 | 12 | 6246.87 | 914 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7 | 962 | 0 | 1312.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3.12 | 130 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0.3 | 0 | 162 | 55 | 0 | 2 | 0 | 0 | 0 | 0.2 | 8 | 0 | 0 | 200 | 11 | 115 | 220 | 0 | 250 | 1050 | 0 | 6015.21 | 12262.08 | 77.31
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 87 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 148 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 7 | 35 | 17 | 19 | 0 | 400 | 0 | 0 | 0 | 120 | 5 | 0 | 0 | 0 | 70 | 12 | 1 | 39 | 0 | 32 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 503 | 5 | 51 | 0 | 8 | 0 | 320 | 300 | 55 | 200 | 36 | 72 | 85 | 136 | 9 | 14 | 114 | 32 | 52.2 | 16 | 0 | 305 | 320 | 385 | 35 | 30 | 0 | 132 | 6 | 0 | 85 | 30 | 0 | 18 | 174 | 0 | 68 | 122 | 0 | 1 | 11.93 | 5 | 6226.13 | 914 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.8 | 912 | 0 | 1215.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 10.78 | 130 | 0 | 142 | 0 | 0 | 0 | 300 | 0 | 0.97 | 0 | 164 | 54 | 0 | 3 | 0 | 0 | 0 | 2 | 30 | 0.09 | 0 | 200 | 7 | 115 | 220 | 0 | 248 | 1000 | 0 | 5891.41 | 12117.54 | 77.31
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 84 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 143 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 12 | 35 | 17 | 19 | 0 | 450 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 48 | 12 | 2 | 40 | 0 | 30 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 455 | 10 | 51 | 0 | 8 | 0 | 353 | 305 | 55 | 190 | 35 | 72 | 85 | 136 | 9 | 14 | 114 | 34 | 43 | 36 | 0 | 300 | 320 | 357 | 35 | 30 | 0 | 132 | 6 | 0 | 85 | 30 | 0 | 18 | 174 | 0 | 68 | 122 | 0 | 1 | 22.4 | 12 | 6171.4 | 865 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.83 | 910 | 0 | 1217.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 24.83 | 130 | 0 | 142 | 0 | 0 | 0 | 300 | 0 | 1.93 | 0 | 162 | 54 | 0 | 7 | 0 | 0 | 0 | 0 | 23 | 0.17 | 0 | 200 | 9 | 115 | 220 | 0 | 248 | 1000 | 0 | 5877.18 | 12048.58 | 77.3
09:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 17 | 86 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 146 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 22 | 70 | 17 | 19 | 0 | 450 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 24 | 12 | 4 | 40 | 0 | 24 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 7 | 51 | 0 | 8 | 0 | 344 | 300 | 55 | 201 | 29 | 72 | 80 | 136 | 9 | 14 | 114 | 32 | 8 | 44 | 0 | 300 | 320 | 386 | 35 | 20 | 0 | 139 | 6 | 0 | 85 | 30 | 0 | 18 | 173 | 0 | 66 | 120 | 0 | 1 | 32.34 | 12 | 6222.34 | 865 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.78 | 908 | 0 | 1215.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 37.51 | 130 | 0 | 142 | 0 | 0 | 0 | 352 | 0 | 3.3 | 0 | 165 | 54 | 0 | 2 | 0 | 0 | 0 | 1.8 | 48 | 0.23 | 0 | 200 | 9 | 115 | 220 | 0 | 222 | 1000 | 0 | 5987.11 | 12209.45 | 77.3
10:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 17 | 85 | 64 | 0 | 0 | 0 | 0 | 0 | 10 | 420 | 146 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 26 | 70 | 17.5 | 19 | 0 | 520 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 24 | 12 | 2 | 40 | 0 | 22 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 16 | 51 | 0 | 26 | 0 | 344 | 325 | 52 | 207 | 30 | 72 | 80 | 120 | 9 | 14 | 105 | 32 | 8 | 39 | 0 | 290 | 320 | 388 | 35 | 20 | 0 | 147 | 6 | 0 | 85 | 30 | 0 | 18 | 171 | 0 | 67 | 111 | 0 | 2 | 31.18 | 12 | 6439.68 | 912 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.04 | 907 | 0 | 1160.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 37.26 | 130 | 0 | 143 | 0 | 0 | 0 | 358 | 0 | 3.87 | 0 | 166 | 54 | 0 | 19 | 0 | 0 | 0 | 6.7 | 22 | 0.4 | 0 | 230 | 10 | 115 | 219 | 0 | 144 | 1010 | 0 | 5934.76 | 12374.44 | 77.29
11:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 17 | 85 | 64 | 0 | 0 | 0 | 0 | 0 | 16 | 380 | 148 | 57 | 0 | 0 | 0 | 287 | 0 | 0 | 27 | 70 | 17.5 | 19 | 0 | 540 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 24 | 12 | 4 | 40 | 0 | 26 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 0 | 51 | 0 | 26 | 0 | 340 | 330 | 50 | 203 | 32 | 72 | 80 | 120 | 8 | 14 | 105 | 34 | 8 | 63 | 0 | 275 | 320 | 385 | 35 | 20 | 0 | 153 | 6 | 0 | 85 | 30 | 0 | 18 | 171 | 0 | 66 | 120 | 0 | 1 | 48.86 | 12 | 6529.36 | 912 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.22 | 909 | 0 | 1162.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 51.43 | 130 | 0 | 135 | 0 | 0 | 0 | 357 | 0 | 4.87 | 0 | 115 | 55 | 0 | 10 | 0 | 0 | 0 | 7.4 | 10 | 0.62 | 0 | 250 | 10 | 115 | 220 | 0 | 244 | 1033 | 0 | 6037.67 | 12567.03 | 77.28
12:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 6 | 17 | 85 | 68 | 0 | 0 | 2 | 54 | 0 | 16 | 380 | 140 | 130 | 0 | 17 | 0 | 282 | 0 | 0 | 27 | 90 | 17.5 | 19 | 0 | 470 | 0 | 0 | 0 | 120 | 11 | 0 | 8 | 0 | 48 | 48 | 4 | 40 | 3 | 27 | 555 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 607 | 16 | 51 | 5 | 55 | 0 | 340 | 330 | 45 | 191 | 32 | 72 | 80 | 120 | 8 | 14 | 105 | 36 | 9 | 48 | 0 | 290 | 320 | 382 | 35 | 30 | 0 | 152 | 6 | 0 | 85 | 30 | 0 | 18 | 173 | 0 | 66 | 122 | 0 | 1 | 50.23 | 12 | 7024.73 | 913 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.43 | 910 | 0 | 1209.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 48.22 | 130 | 0 | 127 | 0 | 0 | 0 | 367 | 0 | 5.11 | 0 | 160 | 54 | 0 | 13 | 0 | 0 | 0 | 6.2 | 34 | 0.8 | 0 | 307 | 4 | 115 | 220 | 0 | 295 | 1046 | 0 | 6293.99 | 13318.72 | 77.27
13:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 17 | 85 | 51 | 0 | 0 | 27 | 54 | 0 | 16 | 380 | 139 | 140 | 0 | 17 | 0 | 280 | 0 | 0 | 27 | 108 | 18 | 13 | 0 | 430 | 0 | 0 | 0 | 120 | 36 | 0 | 25 | 0 | 88 | 72 | 3 | 40 | 20 | 30 | 562 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 612 | 18 | 51 | 26 | 102 | 0 | 335 | 330 | 42 | 195 | 31 | 69 | 80 | 140 | 9 | 14 | 114 | 38 | 30 | 5 | 0 | 310 | 320 | 323 | 35 | 30 | 0 | 152 | 6 | 0 | 82 | 28 | 0 | 18 | 171 | 0 | 65 | 120 | 0 | 1 | 48.96 | 12 | 7221.96 | 912 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.53 | 1017 | 0 | 1313.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 46.07 | 130 | 0 | 136 | 0 | 0 | 0 | 378 | 0 | 4.75 | 0 | 169 | 53 | 0 | 31 | 0 | 0 | 0 | 5.1 | 30 | 0.64 | 0 | 307 | 11 | 105 | 220 | 0 | 295 | 1093 | 0 | 6554.5 | 13776.46 | 77.26
14:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 17 | 85 | 60 | 0 | 0 | 35 | 54 | 0 | 16 | 320 | 143 | 150 | 0 | 17 | 0 | 286 | 0 | 0 | 25 | 108 | 20 | 13 | 0 | 430 | 0 | 0 | 0 | 120 | 32 | 0 | 31 | 0 | 88 | 72 | 2 | 40 | 34 | 30 | 450 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 552 | 15 | 51 | 40 | 100 | 0 | 300 | 300 | 47 | 203 | 31 | 69 | 80 | 170 | 9 | 14 | 114 | 36 | 43 | 28 | 20 | 285 | 320 | 349 | 34 | 30 | 0 | 132 | 6 | 0 | 82 | 30 | 0 | 18 | 171 | 17 | 65 | 111 | 0 | 1 | 30.78 | 12 | 7035.78 | 913 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.63 | 1017 | 0 | 1308.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 40.38 | 130 | 0 | 141 | 0 | 0 | 0 | 354 | 0 | 4.19 | 0 | 168 | 53 | 0 | 12 | 0 | 0 | 0 | 6.4 | 33 | 0.57 | 0 | 200 | 4 | 100 | 220 | 0 | 295 | 1150 | 0 | 6468.56 | 13504.34 | 77.25
15:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 376 | 0 | 0 | 17 | 17 | 85 | 60 | 0 | 0 | 35 | 54 | 0 | 16 | 380 | 141 | 100 | 0 | 17 | 0 | 295 | 0 | 0 | 20 | 108 | 18 | 13 | 0 | 430 | 0 | 0 | 0 | 120 | 32 | 0 | 31 | 0 | 88 | 72 | 3 | 38 | 34 | 30 | 560 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 612 | 14 | 51 | 40 | 55 | 0 | 330 | 335 | 46 | 198 | 31 | 69 | 80 | 170 | 8 | 14 | 114 | 36 | 43 | 51 | 20 | 295 | 320 | 332 | 33 | 30 | 0 | 150 | 8 | 0 | 80 | 25 | 0 | 16 | 169 | 17 | 65 | 113 | 0 | 1 | 32.64 | 12 | 7289.64 | 912 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.82 | 1017 | 0 | 1314.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 19.34 | 130 | 0 | 141 | 0 | 0 | 0 | 390 | 0 | 2.09 | 0 | 165 | 54 | 0 | 7 | 0 | 0 | 0 | 3.6 | 28 | 0.2 | 0 | 250 | 7 | 115 | 215 | 0 | 339 | 1150 | 0 | 6583.41 | 13873.05 | 77.24
16:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 17 | 17 | 84 | 78 | 0 | 0 | 35 | 54 | 0 | 16 | 420 | 139 | 65 | 0 | 17 | 0 | 267 | 0 | 0 | 13 | 17 | 18 | 13 | 0 | 550 | 0 | 0 | 0 | 120 | 33 | 0 | 31 | 0 | 100 | 36 | 1 | 36 | 30 | 27 | 566 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 612 | 7 | 51 | 20 | 55 | 0 | 344 | 335 | 42 | 182 | 30 | 68 | 80 | 170 | 28 | 14 | 114 | 36 | 37 | 28 | 20 | 290 | 320 | 315 | 33 | 30 | 0 | 148 | 8 | 0 | 81 | 30 | 0 | 16 | 169 | 27 | 65 | 113 | 0 | 0 | 1.03 | 12 | 7120.03 | 912 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.4 | 935 | 0 | 1320.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 19.89 | 130 | 0 | 141 | 0 | 0 | 0 | 319 | 0 | 1.5 | 0 | 162 | 54 | 0 | 11 | 0 | 0 | 0 | 2.1 | 43 | 0.33 | 0 | 200 | 7 | 105 | 215 | 0 | 409 | 1120 | 0 | 6377.28 | 13497.31 | 77.23
17:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 17 | 103 | 78 | 0 | 0 | 35 | 35 | 0 | 16 | 420 | 138 | 61 | 0 | 17 | 0 | 271 | 0 | 0 | 6 | 17 | 18 | 13 | 0 | 548 | 0 | 0 | 0 | 120 | 20 | 0 | 31 | 0 | 60 | 12 | 1 | 33 | 0 | 27 | 564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 3 | 51 | 10 | 55 | 0 | 339 | 335 | 40 | 184 | 30 | 82 | 80 | 136 | 36 | 14 | 114 | 34 | 43 | 15 | 20 | 300 | 320 | 325 | 33 | 30 | 0 | 149 | 8 | 0 | 81 | 30 | 0 | 16 | 169 | 16 | 45 | 113 | 0 | 0 | 3.5 | 12 | 6940.5 | 913 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.48 | 781 | 0 | 1224.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 1.91 | 130 | 0 | 141 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 162 | 54 | 0 | 4 | 0 | 0 | 0 | 1.2 | 12 | 0.16 | 0 | 200 | 9 | 105 | 215 | 0 | 462 | 1050 | 0 | 6018.37 | 12958.87 | 77.22
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 103 | 78 | 0 | 0 | 35 | 35 | 0 | 16 | 350 | 144 | 61 | 0 | 17 | 0 | 266 | 0 | 0 | 1 | 17 | 18 | 13 | 0 | 350 | 0 | 0 | 0 | 120 | 13 | 0 | 31 | 0 | 60 | 12 | 0 | 33 | 0 | 27 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552 | 1 | 51 | 10 | 8 | 0 | 300 | 305 | 44 | 181 | 27 | 92 | 80 | 136 | 36 | 14 | 114 | 32 | 25 | 3 | 21 | 295 | 320 | 325 | 33 | 30 | 0 | 130 | 8 | 0 | 21 | 30 | 0 | 16 | 169 | 17 | 45 | 113 | 0 | 0 | 3.12 | 12 | 6248.12 | 912 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.62 | 761 | 0 | 1221.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 9.1 | 130 | 0 | 147 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 163 | 54 | 0 | 1 | 0 | 0 | 0 | 0.2 | 6 | 0.01 | 0 | 200 | 9 | 105 | 180 | 0 | 461 | 1050 | 0 | 5929.2 | 12177.32 | 77.21
19:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17 | 17 | 103 | 78 | 15 | 0 | 55 | 108 | 0 | 17 | 420 | 123 | 90 | 0 | 17 | 0 | 290 | 0 | 0 | 0 | 17 | 18 | 18 | 0 | 550 | 0 | 0 | 32 | 120 | 9 | 0 | 31 | 0 | 100 | 50 | 0 | 35 | 0 | 27 | 566 | 0 | 0 | 11 | 2 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 51 | 10 | 26 | 0 | 350 | 305 | 51 | 199 | 33 | 92 | 80 | 136 | 35 | 14 | 114 | 40 | 26 | 0 | 22 | 300 | 320 | 350 | 34 | 30 | 0 | 139 | 8 | 0 | 80 | 30 | 0 | 16 | 170 | 17 | 45 | 114 | 0 | 0 | 0 | 12 | 7209 | 876 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 798 | 14 | 1409.67 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 178 | 0 | 0 | 0 | 403 | 0 | 0 | 0 | 164 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 10 | 115 | 220 | 0 | 461 | 1180 | 0 | 6559.67 | 13768.67 | 77.2
19:30 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 70 | 16 | 60 | 0 | 35 | 126 | 0 | 35 | 420 | 143 | 61 | 0 | 17 | 0 | 267 | 0 | 0 | 0 | 17 | 18 | 18 | 0 | 550 | 0 | 0 | 43 | 120 | 15 | 0 | 31 | 0 | 100 | 72 | 0 | 35 | 0 | 32 | 549 | 0 | 0 | 19 | 8 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 0 | 26 | 0 | 354 | 335 | 49 | 182 | 33 | 92 | 80 | 136 | 35 | 14 | 114 | 40 | 52.2 | 0 | 18 | 285 | 320 | 335 | 33 | 30 | 0 | 142 | 8 | 0 | 80 | 30 | 0 | 16 | 170 | 17 | 45 | 168 | 0 | 0 | 0 | 12 | 7205.2 | 876 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 17 | 1452.31 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 187 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 161 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 7 | 90 | 220 | 0 | 461 | 1235 | 0 | 6872.31 | 14077.51
20:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 0 | 62 | 0 | 0 | 0 | 17 | 72 | 0 | 30 | 380 | 140 | 109 | 0 | 17 | 0 | 266 | 0 | 0 | 0 | 17 | 19 | 0 | 0 | 500 | 0 | 0 | 35 | 120 | 12 | 0 | 31 | 0 | 100 | 60 | 0 | 36 | 0 | 31 | 549 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 51 | 0 | 45 | 0 | 360 | 335 | 48 | 180 | 35 | 92 | 80 | 136 | 37 | 14 | 114 | 40 | 25 | 0 | 30 | 275 | 320 | 338 | 33 | 30 | 0 | 130 | 8 | 0 | 80 | 30 | 0 | 18 | 169 | 17 | 8 | 169 | 0 | 0 | 0 | 12 | 6855 | 876 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 17 | 1411.66 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 190 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 160 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 4 | 100 | 220 | 0 | 461 | 1235 | 0 | 6806.66 | 13661.66 | 77.19
21:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 24 | 0 | 49 | 0 | 0 | 0 | 0 | 17 | 0 | 32 | 380 | 123 | 109 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 120 | 6 | 0 | 31 | 0 | 100 | 60 | 0 | 37 | 0 | 20 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 0 | 51 | 0 | 45 | 0 | 360 | 335 | 46 | 180 | 35 | 92 | 90 | 120 | 37 | 14 | 114 | 42 | 25 | 0 | 30 | 290 | 320 | 338 | 33 | 30 | 0 | 129 | 8 | 0 | 83 | 30 | 0 | 18 | 170 | 17 | 8 | 169 | 0 | 0 | 0 | 12 | 6566 | 923 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 876 | 17 | 1250.87 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 160 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 159 | 54 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 11 | 105 | 220 | 0 | 461 | 1080 | 0 | 6348.87 | 12914.87 | 77.18
22:00 | 0 | 29 | 16 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 29 | 0 | 69 | 48 | 0 | 0 | 0 | 0 | 0 | 32 | 350 | 135 | 109 | 0 | 0 | 0 | 251 | 0 | 0 | 0 | 42 | 0 | 6 | 0 | 500 | 0 | 0 | 0 | 120 | 0 | 0 | 32 | 0 | 100 | 60 | 0 | 38 | 0 | 30 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505 | 0 | 51 | 0 | 8 | 0 | 300 | 300 | 50 | 189 | 35 | 92 | 90 | 120 | 37 | 14 | 114 | 44 | 43 | 0 | 30 | 310 | 320 | 343 | 33 | 30 | 0 | 136 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 17 | 19 | 170 | 0 | 0 | 0 | 12 | 6528 | 922 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 761 | 17 | 1167.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 160 | 54 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 105 | 180 | 0 | 461 | 950 | 0 | 5820.67 | 12348.67 | 77.17
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 85 | 48 | 0 | 0 | 0 | 0 | 0 | 32 | 400 | 149 | 109 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 52 | 0 | 12 | 0 | 500 | 0 | 0 | 0 | 120 | 3 | 0 | 32 | 0 | 100 | 60 | 0 | 40 | 0 | 30 | 460 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 51 | 0 | 8 | 0 | 346 | 335 | 54 | 207 | 35 | 92 | 90 | 122 | 37 | 14 | 114 | 44 | 52.2 | 0 | 32 | 300 | 320 | 375 | 33 | 30 | 0 | 135 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 17 | 75 | 123 | 0 | 0 | 0 | 12 | 6807.2 | 922 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 17 | 1179.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 163 | 33 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 222 | 10 | 115 | 200 | 0 | 420 | 941 | 0 | 5849.27 | 12656.47 | 77.16
Total KWH | 17280 | 541440 | 317280 | 0 | 0 | 0 | 0 | 0 | 8532000 | 0 | 0 | 429120 | 357840 | 2097072 | 1439520 | 215280 | 28123 | 431625 | 665280 | 0 | 426240 | 8835500 | 3405673 | 1352055 | 0 | 239093 | 0 | 6828076 | 0 | 0 | 197120 | 1494000 | 358800 | 353880 | 0 | 11554545.45 | 31364 | 25091 | 68160 | 3000000 | 275520 | 0 | 695136 | 0 | 1903680 | 938880 | 27723 | 904140 | 264289 | 732960 | 11600000 | 0 | 0 | 62400 | 72909 | 269309 | 638193 | 0 | 0 | 0 | 13019998 | 98955 | 1168136 | 486764 | 652363 | 0 | 8416400 | 7752000 | 1199520 | 4728000 | 781560 | 1876800 | 1982580 | 3552000 | 437640 | 318530 | 2734860 | 879360 | 947933 | 354618 | 463760 | 7254000 | 7677700 | 8909000 | 802000 | 638400 | 0 | 3421145 | 169488 | 0 | 1904640 | 695040 | 0 | 424000 | 4554410 | 240840 | 1290000 | 2805600 | 0 | 9600 | 310970 | 279840 | 164865046.45 | 21953454 | 4411008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 663840 | 21803630 | 133920 | 30869274 | 0 | 0 | 0 | 106848 | 0 | 158096 | 7200 | 0 | 0 | 510502 | 20305 | 326256 | 3364273 | 0 | 3705800 | 0 | 0 | 0 | 8355272 | 0 | 29100 | 0 | 3930000 | 1244509 | 235078 | 114103 | 332592 | 0 | 0 | 44525.88 | 415000 | 4018.5 | 0 | 5804000 | 212726 | 2644000 | 5227990 | 0 | 7898182 | 26478545.45 | 0 | 151004047.83 | 315869094.28

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 16-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13318.72 | MW | 12:00 Hr. | Energy Generated |  |  | 315.8691 |  | MKWHr.
| Day Peak Demand |  |  | 13318.72 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.585 |  | MKWHr.
| Evening Peak Generation |  |  | 14077.51 | MW | 19:30 Hr. | Energy Demand |  |  | 317.4541 |  | MKWHr.
| Evening Peak Demand |  |  | 14077.51 | MW | 19:30 Hr. | Maximum Temperature |  |  | 36.3 |  | °C
| Minimum Generation of the Day |  |  | 12048.58 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 995.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 14433 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.3348 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.2205 | 0 | 8.6992 | 0 | 0 | 0.19712 | 0 | 0 | 50.1168 | Gas | 136.9617 | Gas | 494023689.1465
| Chattogram Zone |  |  | 4.3712 | 24.62 | 4.3312 | 0 | 0.90414 | 0.12668 | 0 | 0.27552 | 34.6287 | Coal | 91.7789 | Coal | 610581760.9225
| Cumilla Zone |  |  | 26.9991 | 0 | 10.4998 | 0 | 0 | 0.35462 | 0.87936 | 0 | 38.7328 | HFO | 29.1405 | HFO | 547767030.77
| Mymensingh Zone |  |  | 0 | 0 | 4.6163 | 0 | 0 | 0.32057 | 0 | 0 | 4.9368 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.4498 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.4498 | Hydro | 0.90414 | Hydro | 90414
| Khulna Zone |  |  | 4.411 | 21.8036 | 0.13392 | 0 | 0 | 0.66384 | 21.9535 | 0 | 48.9659 | Solar | 3.1063 | Solar | 49610820.6318
| Barishal Zone |  |  | 8.0847 | 40.1807 | 0 | 0 | 0 | 0.0040185 | 0 | 0 | 48.2695 | Import | 53.7021 | Import | 294849733.38
| Rajshahi Zone |  |  | 15.4253 | 0 | 0.29245 | 0 | 0 | 0.86586 | 30.8693 | 0 | 47.4529 | Wind | 0.27552 | Wind | 4033612.8
| Rangpur Zone |  |  | 0 | 5.1745 | 0.56767 | 0 | 0 | 0.57363 | 0 | 0 | 6.3158
| Total |  |  | 136.9617 | 91.7789 | 29.1405 | 0 | 0.90414 | 3.1063 | 53.7021 | 0.27552 | 315.8691
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 494023689.1465 |  | Hydro | 90414
|  |  |  | Coal | 610581760.9225 |  | Solar | 49610820.6318
|  |  |  | HFO | 547767030.77 |  | Import | 294849733.38
|  |  |  | HSD | 0 |  | Wind | 4033612.8
[5 empty] | Total: | 200,09,57,061 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.9535 | Peak Hr Flow | 876.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47495672.82 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 30.8693 | Peak Hr Flow | 1452.31 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 462 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.87936 | Peak Hr Flow | 40.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 924 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 53.7021 | Peak Hr Flow | 2368.31 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4746
|  |  |  | Chattogram |  | 0 |  | 1513
|  |  |  | Cumilla |  | 0 |  | 1384
|  |  |  | Mymensingh |  | 0 |  | 798
|  |  |  | Sylhet |  | 0 |  | 462
|  |  |  | Khulna |  | 0 |  | 1810
|  |  |  | Barishal |  | 0 |  | 484
|  |  |  | Rajshahi |  | 0 |  | 1504
|  |  |  | Rangpur |  | 0 |  | 877
|  |  |  | Total |  | 0 |  | 13578
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 735.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:11 | 09:29 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to ৩৩ কেভি ইনকামার-০১ এর বাস-এ ক্লাম্প | [7 empty] | 15.0MW load
|  |  | প্রতিস্থাপনের জন্য | [7 empty] | interrup.
| 08:27 | 17:51 | Jamalpur-Mymensingh 132kV Ckt-1 Project Work S/D from Jamalpur 132/33kV end Due to G2G
project work (guktagacha grid)
| 08:30 | 18:06 | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Under Ground Cable
Maintenance.
|  | 08:35 | Hasnabad 132/33kV S/S 33kv Reserve Bus is restored.
|  | 08:35 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT is restored.
| 08:37 | 10:31 | Barguna 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Emergency Shotdown for Betagi | [7 empty] | 5.0MW load
|  |  | 33kv Feeder Maintenance | [7 empty] | interrup.
| 08:38 | 10:31 | Barguna 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Emergency Shotdown for Betagi | [7 empty] | 5.0MW load
|  |  | 33kv Feeder Maintenance | [7 empty] | interrup.
| 08:54 | 18:05 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Under Ground Cable
Maintenance.
| 08:56 | 09:17 | Rajbari 132/33kV S/S Transformer-3 LT Tripped showing 50 DMT & 51 DMT O/C, 86.1&86.2 | [7 empty] | 10.0MW load
|  |  | Operate. relays Due to Tr-3 incoming trip due to fault of 33 kv sajankanda feeder. | [7 empty] | interrup.
|  | 09:05 | Munshiganj 132/33kV S/S Transformer-1 LT is restored.
|  | 09:06 | Magura 132/33kV S/S T-1 (405T) HT is restored.
|  | 09:07 | Bakulia 132/33kV S/S T-1 (402T) HT is restored.
|  | 09:10 | Magura 132/33kV S/S T-1 (405T) LT is restored.
| 09:25 |  | Shahjadpur-Ullahpara 132kV Ckt-1 Project Work S/D from Ullahpara 132/33kV end Due to
Project Work. and from Shahjadpur 132/33kV end Due to Bagabari ckt-02 Reconducting work.
| 09:27 |  | Baghabari-Shahjadpur 132 kV Ckt-2 Project Work S/D from Shahjadpur 132/33kV end Due to
Bagabari Ckt -2 Reconducting work.
| 10:14 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 10:17 | 12:07 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Project Work S/D Due to Red hot Maintenance | [7 empty] | 30.0MW load
|  |  | at 33kV side. | [7 empty] | interrup.
| 10:18 | 12:06 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to Red hot Maintenance at | [7 empty] | 30.0MW load
|  |  | 33kV side. | [7 empty] | interrup.
|  | 10:47 | Goalpara 132/33kV S/S T-5 HT is restored.
|  | 10:47 | Goalpara 132/33kV S/S T-6 HT is restored.
|  | 10:48 | Goalpara 132/33kV S/S T-5 LT is restored.
|  | 10:48 | Goalpara 132/33kV S/S T-6 LT is restored.
|  | 10:58 | Jhenaidah 132/33kV S/S Transformer T-2 LT is restored.
|  | 10:58 | Jhenaidah 132/33kV S/S Transformer T-2 HT is restored.
| 11:33 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 12:00 |  | Day peak generation 13316 MW
| 12:40 | 12:54 | Narshingdi 132/33kV S/S T-4 LT Tripped showing Lockout relay relays Due to df/dt fault | [7 empty] | 21.0MW load
interrup.
|  | 14:06 | Bheramara 230/132kV S/S Transformer-2 HT is restored.
|  | 14:10 | Bheramara 230/132kV S/S Transformer-2 LT is restored.
| 14:42 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- ST
| 14:50 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- STG ( False Entry)
| 19:04 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 19:14 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- ST
| 19:30 |  | Evening Peak Generation: 14077 MW.
| 19:33 |  | Ghorasal-Joydeb-B 132kV Ckt-1 Tripped from Joydebpur 132/33kV end showing
1.MVTR 2.SOTF 3.Main protection Trip relays Due to STROM
| 19:38 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 19:44 | 20:21 | Bashundhara-Tongi 132 kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance
relay Phase- C relays Due to Stormy weather
| 19:55 | 20:30 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Tripped showing MiCOM P441: PH B, Z2 relays.
| 20:17 |  | BIPTC S/S 20DF12 Tripped showing 87.1 Differential Relay relays Due to Tripped by C1
unbalance 60/61 instant L1-Trip.
| 21:05 | 22:31 | Maniknagar 230/132kV S/S Auto Transformer-01(705T) HT Tripped showing N/A relays.
| 21:05 | 22:31 | Maniknagar-Siddhirganj 230kV Ckt-1 Tripped from Maniknagar 230/132kV end showing REL670
relays.
| 21:35 | 22:22 | Hasnabad-Sitalakhya 132kV Ckt-1 Tripped from Hasnabad 132/33kV end showing Main | [7 empty] | 70.0MW load
|  |  | protection trip Relay and lock out Relay and Back up protection Relay relays. | [7 empty] | interrup. Hasnabad
132/33kV end
| 21:37 | 22:48 | Haripur-Meghnaghat 230kV Ckt-1 Tripped from Haripur 230/132kV end showing Micromho: B,
N, Z1. Optimho: DEF Start. relays. and from Meghnaghat 230/132kV end showing Distance
Relay relays.
| 21:38 | 23:50 | Meghnaghat-Shyampur 230kV Ckt-1 Tripped from Shyampur 230/132kV end showing SOTF,
Distance 21 relays Due to Distance Protection Operated,
| 21:38 | 21:43 | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Optimho: DEF,
Aided. relays Due to Thunderstorm.
| 00:07 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- ST
| 00:09 |  | Madanganj-Munsiganj 132 kV Ckt-2 Tripped from Madanganj 132/33kV end showing Directional
O/C & E/F relay relays Due to Due to heavy rain & storm
| 00:11 |  | Meghnaghat CCPP(Summit)-2 Shutdown with remarks:- GT
| 01:12 | 02:33 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage relays Due to Due to
Rain
|  | 01:19 | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) is restored.
| 01:52 | 02:47 | Ghorashal 230kV S/S TARFO-2 LT Tripped showing Over current Earth fault relays Due to | [7 empty] | 70.0MW load
|  |  | Outgonig-1 CT jumper out | [7 empty] | interrup.
| 02:30 | 02:53 | Amnura-Rajshahi 132kV Ckt-1 Tripped from Amnura 132/33kV end showing K35 relays Due to
N/A
| 05:28 | 06:42 | Ghorasal-Tongi 230kV Ckt-1 Tripped from Tongi 230/132/33kV end showing Distance relay
relays.
| 06:00 |  | Min. Gen. 10304 MW
| 06:25 |  | Haripur-Narsingdi 132kV Ckt-1 Project Work S/D from Narshingdi 132/33kV end Due to Line
LILO work
| 06:29 |  | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
| 07:01 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Scheduled S/D Due to Due to 33kv faulty D/S | [7 empty] | 25.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:02 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Scheduled S/D Due to Due to 33kv faulty D/S | [7 empty] | 25.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:02 |  | Gollamari 132/33kV S/S Tr-2 LT Scheduled S/D Due to Hot Spot Maintenance
| 07:03 |  | Gollamari 132/33kV S/S Tr-2 HT Scheduled S/D Due to Hot Spot Maintenance
| 07:32 |  | Meghnaghat CCPP(Summit) GT-2 Synchronized with remarks:- GT-2 synchronized
| 07:35 |  | Bogura 132/33kV S/S Transformer-4 HT Scheduled S/D Due to Red hot. | [7 empty] | 10.0MW load
interrup.
| 07:35 |  | Bogura 132/33kV S/S Transformer-4 LT Scheduled S/D Due to Red hot | [7 empty] | 10.0MW load
interrup.
| 07:57 |  | Chowmuhani 132/33kV S/S TR2 Forced S/D Due to Tr-2 bus maintenance | [7 empty] | 50.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 16-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas Gas
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas Gas
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 330 | 8532000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8835500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 143 | 3405673 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 28123 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 267 | 6828076 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 17280 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 429120 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 1439520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 431625 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 239093 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 18 | 358800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 353880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 317280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 60 | 215280 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 70 | 2097072 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 541440 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 35 | 426240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 665280 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 197120 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 357840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 550 | 11554545.45 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 61 | 1352055 | Allocation limit by Titas, instructed by DS(Gen)
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 17 | 1494000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2267 | 50116842.45
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 120 | 3000000 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 72909 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 98955 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 62400 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 904140 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 638193 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 269309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 31 | 695136 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1903680 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 32 | 732960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 43 | 68160 | Engine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 27723 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 25091 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 264289 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 72 | 938880 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 31364 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 13019998 | Partial Shutdown due to maintenance
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 15 | 275520 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 549 | 11600000 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 1636 | 34628707
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4728000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8416400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 7752000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 33 | 781560 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1199520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 26 | 652363 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1168136 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 486764 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 18 | 463760 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1982580 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 3552000 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 879360 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 947933 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 318530 | Schedule Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2734860 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 35 | 437640 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1876800 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 354618 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1611.2 | 38732824
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 168 | 2805600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 45 | 1290000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 310970 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 279840 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 240840 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 242 | 4936850
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 33 | 802000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 638400 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3421145 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 695040 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1904640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 170 | 4554410 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 424000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 169488 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7254000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 335 | 8909000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7677700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1449 | 36449823
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 21953454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 192 | 4411008 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 133920 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 663840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1000 | 21803630 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2085 | 48965852
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 461 | 7898182 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 7 | 212726 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 90 | 2644000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1235 | 26478545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5227990 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5804000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4018.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2320 | 48269461.95
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 176 | 3364273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 187 | 3705800 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 319 | 8355272 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 20305 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 49 | 158096 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 106848 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 7200 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29100 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1452.31 | 30869274 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 326256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 510502 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2183.31 | 47452926
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 54 | 1244509 | Under Maintenance
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 3930000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 332592 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 44525.88 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 235078 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 114103 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 415000 | -
Rangpur Area Total |  |  |  |  | 950 | 284 | 6315807.88
Eastern Grid Total |  |  |  |  | 16921.242 | 7205.2 | 164865046.45
Western Grid Total |  |  |  |  | 11702.84 | 6872.31 | 151004047.83
National Grid Total |  |  |  |  | 28624.082 | 14077.51 | 315869094.28
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 16-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8902.43 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4676 | MW
i) Dhaka area |  |  | 4745.89 |  | MW | i) Khulna area |  |  |  | 1810.5 | MW
ii) Chattogram area |  |  | 1513 |  | MW | ii) Barishal area |  |  |  | 484.5 | MW
iii) Cumilla area |  |  | 1383.54 |  | MW | iii) Rajshahi area |  |  |  | 1504 | MW
iv) Mymensingh area |  |  | 798 |  | MW | iv) Rangpur area |  |  |  | 877 | MW
v) Sylhet area |  |  | 462 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13578.43 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 85 | 21:00 | 133 | Patuakhali | 88 | 00:00
2 | AKSML | 113 | 03:00 | 68 | Jaldhaka | 66 | 19:30 | 134 | Payra | 38 | 00:00
3 | Aftabnagar | 42 | 19:00 | 69 | Jamalpur | 116 | 19:30 | 135 | Postogola | 54 | 00:00
4 | Agargaon | 128 | 19:00 | 70 | Jashore | 142 | 22:00 | 136 | Purbachal | 22 | 12:00
5 | Agrabad | 92 | 22:00 | 71 | Jhenaidah | 142 | 23:00 | 137 | Purbasadipur | 129 | 00:00
6 | Amnura | 44 | 19:30 | 72 | Joydebpur | 137 | 00:00 | 138 | Rahanpur | 28 | 19:30
7 | Ashuganj | 102 | 02:00 | 73 | Joypurhat | 65 | 00:00 | 139 | Rahim | 39 | 01:00
8 | BSRM | 198 | 00:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 86 | 21:00
9 | Bagerhat | 83 | 22:00 | 75 | KSRM | 30 | 23:00 | 141 | Rajendrapur | 125 | 00:00
10 | Bajitpur | 50 | 20:00 | 76 | Kabirpur | 258 | 01:00 | 142 | Rajshahi | 144 | 21:00
11 | Bakulia | 100 | 23:00 | 77 | Kachua | 105 | 22:00 | 143 | Rajshahi-230 | 82 | 21:00
12 | Banani | 36 | 19:00 | 78 | Kallyanpur | 108 | 19:00 | 144 | Ramganj | 118 | 05:00
13 | Bangabhaban | 5 | 17:00 | 79 | Kalurghat | 34 | 01:00 | 145 | Rampur | 50 | 00:00
14 | Barapukuria | 57 | 00:00 | 80 | Kamrangirchar | 62.3 | 00:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 24 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 133 | 19:30
16 | Barishal | 116 | 00:00 | 82 | Kasba | 37 | 22:00 | 148 | Ruppur | 7 | 11:00
17 | Barishal-230 | 112 | 22:00 | 83 | Kazla | 97 | 00:00 | 149 | SSM | 5 | 03:00
18 | Baroaulia | 66 | 09:00 | 84 | Keranigonj | 81 | 13:00 | 150 | Saidpur | 93 | 00:00
19 | Baroirhat | 72 | 22:00 | 85 | Khagrachori | 32 | 19:30 | 151 | Satkhira | 153 | 21:00
20 | Bashundhara | 197 | 19:00 | 86 | Khulna | 88 | 13:00 | 152 | Satmasjid | 109 | 19:00
21 | BashundharaCement | 8 | 00:00 | 87 | Khulshi | 183 | 19:30 | 153 | Savar | 200 | 12:00
22 | Beanibazar | 78 | 23:00 | 88 | Kishoreganj | 128 | 00:00 | 154 | SevenRings | 8.66 | 21:00
23 | Benapole | 73 | 21:00 | 89 | Kodda | 287 | 10:00 | 155 | ShahCement | 38 | 07:00
24 | Bhaluka | 149 | 00:00 | 90 | Kulaura | 50 | 19:00 | 156 | Shahjadpur | 81 | 19:00
25 | Bhandaria | 63 | 23:00 | 91 | Kurigram | 50 | 19:30 | 157 | Shahjibazar | 123 | 00:00
26 | Bhangura | 43 | 19:30 | 92 | Kushtia | 152 | 21:00 | 158 | Shahmirpur | 51 | 02:00
27 | Bheramara(GK) | 71 | 22:00 | 93 | Lalbag | 61 | 01:00 | 159 | Shariatpur | 98 | 22:00
28 | Bhulta | 237 | 19:30 | 94 | Lalmonirhat | 49 | 20:00 | 160 | Sherpur | 130 | 19:30
29 | Bog-Sherpur | 68 | 00:00 | 95 | MI_Cement | 12.5 | 05:00 | 161 | Shikalbaha | 29 | 00:00
30 | Bogura | 161 | 00:00 | 96 | Madanganj | 44 | 00:00 | 162 | Shitalakhya | 65.6 | 00:00
31 | Borhanuddin | 103 | 00:00 | 97 | Madaripur | 110 | 23:00 | 163 | Sholosohor | 47 | 00:00
32 | Brahmanbaria | 128 | 23:00 | 98 | Madartek | 90.18 | 19:00 | 164 | Shyampur | 202 | 11:00
33 | Cantonment | 144 | 19:00 | 99 | Madunaghat | 71 | 19:30 | 165 | Siddhirganj | 102 | 12:00
34 | Chandina | 26.1 | 21:00 | 100 | Magura | 70 | 22:00 | 166 | Sirajganj | 100 | 00:00
35 | Chandpur | 80 | 22:00 | 101 | Mahasthangarh | 78 | 00:00 | 167 | Sonargaon | 117 | 20:00
36 | Chandraghona | 38 | 19:00 | 102 | Manikganj | 136 | 19:00 | 168 | Sreemongol | 74 | 22:00
37 | Chapai | 74 | 21:00 | 103 | Maniknagar | 84 | 13:00 | 169 | Sreepur | 103 | 00:00
38 | Charsaidpur | 46 | 19:30 | 104 | Matarbari | 50 | 19:00 | 170 | Srinagar | 52 | 20:00
39 | Chauddagram | 80 | 22:00 | 105 | Matuail | 64 | 00:00 | 171 | Sunamganj | 60 | 20:00
40 | Chhatak | 38 | 22:00 | 106 | Millgate | 99 | 16:00 | 172 | Sylhet | 45 | 19:00
41 | Chowmuhani | 222 | 00:00 | 107 | Mirpur | 132 | 19:00 | 173 | Sylhet-132 | 113 | 21:00
42 | Chuadanga | 122 | 23:00 | 108 | Mirsorai | 10 | 00:00 | 174 | TK | 37 | 00:00
43 | Coxsbazar | 135 | 01:00 | 109 | Mirzapur | 44 | 11:00 | 175 | Tangail | 170 | 13:00
44 | Cumilla(N) | 164 | 00:00 | 110 | Mithapukur | 52 | 19:30 | 176 | Thakurgaon | 97 | 19:30
45 | Cumilla(S) | 175 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 110 | 00:00
46 | Daudkandi | 153 | 20:00 | 112 | Mogbazar | 129 | 15:00 | 178 | Ullahpara | 39 | 19:00
47 | Dhaka | 46 | 19:00 | 113 | Mongla | 50 | 00:00 | 179 | Ullon | 57 | 19:00
48 | Dhamrai | 136 | 00:00 | 114 | Motijheel | 36 | 13:00 | 180 | Uttara | 85 | 19:00
49 | Dhanmondi | 134 | 19:00 | 115 | Muktagacha | 32 | 20:00 | 181 | UttaraNew | 60 | 19:00
50 | Dohazari | 106 | 00:00 | 116 | Munshiganj | 113 | 20:00 | 182 | Zigatola | 74 | 12:00
51 | Faridpur | 159 | 19:00 | 117 | Muradnagar | 32 | 19:30
52 | Fatullah | 88 | 00:00 | 118 | Mymensingh | 196 | 13:00
53 | Fenchuganj | 41 | 19:00 | 119 | Naogaon | 138 | 00:00
54 | Feni | 134 | 22:00 | 120 | Narail | 62.5 | 19:30
55 | GPH | 92 | 18:00 | 121 | Narinda | 56 | 13:00
56 | Ghatail | 68 | 13:00 | 122 | Narshingdi | 180 | 00:00
57 | Ghorashal | 16 | 00:00 | 123 | Natore | 167 | 20:00
58 | Ghorashal-230 | 97 | 00:00 | 124 | Nawabganj | 62.8 | 20:00
59 | Goalpara | 40 | 00:00 | 125 | Netrakona | 110 | 00:00
60 | Gollamari | 94 | 23:00 | 126 | New | 72.5 | 12:00
61 | Gopalganj | 116 | 23:00 | 127 | Niamatpur | 79 | 19:30
62 | Gulshan | 106 | 15:00 | 128 | Noapara | 54 | 23:00
63 | Halishahar | 56 | 15:00 | 129 | PHP | 9 | 02:00
64 | HaripurSBU | 174 | 00:00 | 130 | Pabna | 129 | 22:00
65 | Hasnabad | 82 | 00:00 | 131 | Palashbari | 106 | 19:30
66 | Hathazari | 85 | 00:00 | 132 | Panchagarh | 55 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 16-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14433 | 160 |  | 14600
1:00 | 13941.79 | 200 |  | 14150.79
2:00 | 13508.66 | 184 |  | 13700.66
3:00 | 13326.15 | 177 |  | 13511.15
4:00 | 13141.11 | 172 |  | 13321.11
5:00 | 12867.24 | 165 |  | 13039.24
6:00 | 12262.08 | 154 |  | 12423.08
7:00 | 12117.54 | 102 |  | 12224.54
8:00 | 12048.58 | 72 |  | 12123.58
9:00 | 12209.45 | 42 |  | 12253.45
10:00 | 12374.44 | 0 |  | 12374.44
11:00 | 12567.03 | 0 |  | 12567.03
12:00 | 13318.72 | 0 |  | 13318.72
13:00 | 13776.46 | 0 |  | 13776.46
14:00 | 13504.34 | 0 |  | 13504.34
15:00 | 13873.05 | 38 |  | 13913.05
16:00 | 13497.31 | 29 |  | 13527.31
17:00 | 12958.87 | 0 |  | 12958.87
18:00 | 12177.32 | 0 |  | 12177.32
19:00 | 13768.67 | 40 |  | 13810.67
19:30 | 14077.51 | 0 |  | 14077.51
20:00 | 13661.66 | 0 |  | 13661.66
21:00 | 12914.87 | 0 |  | 12914.87
22:00 | 12348.67 | 50 |  | 12400.67
23:00 | 12656.47 | 0 |  | 12656.47
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 16-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7746.7 | 6686.3 | 14433 | DAILY GENERATION CURVE
00:30 | 7605.2 | 6582.195 | 14187.395
01:00 | 7463.7 | 6478.09 | 13941.79 | 16-05-2025
01:30 | 7239.7 | 6485.525 | 13725.225
02:00 | 7015.7 | 6492.96 | 13508.66
02:30 | 6936.2 | 6481.205 | 13417.405
03:00 | 6856.7 | 6469.45 | 13326.15
03:30 | 6834.7 | 6398.93 | 13233.63
04:00 | 6812.7 | 6328.41 | 13141.11
04:30 | 6759.45 | 6244.725 | 13004.175
05:00 | 6706.2 | 6161.04 | 12867.24
05:30 | 6476.535 | 6088.125 | 12564.66
06:00 | 6246.87 | 6015.21 | 12262.08
06:30 | 6236.5 | 5953.31 | 12189.81
07:00 | 6226.13 | 5891.41 | 12117.54
07:30 | 6198.765 | 5884.295 | 12083.06
08:00 | 6171.4 | 5877.18 | 12048.58
08:30 | 6196.87 | 5932.145 | 12129.015
09:00 | 6222.34 | 5987.11 | 12209.45
09:30 | 6331.01 | 5960.935 | 12291.945
10:00 | 6439.68 | 5934.76 | 12374.44
10:30 | 6484.52 | 5986.215 | 12470.735
11:00 | 6529.36 | 6037.67 | 12567.03
11:30 | 6777.045 | 6165.83 | 12942.875
12:00 | 7024.73 | 6293.99 | 13318.72
12:30 | 7123.345 | 6424.245 | 13547.59
13:00 | 7221.96 | 6554.5 | 13776.46
13:30 | 7128.87 | 6511.53 | 13640.4
14:00 | 7035.78 | 6468.56 | 13504.34
14:30 | 7162.71 | 6525.985 | 13688.695
15:00 | 7289.64 | 6583.41 | 13873.05
15:30 | 7204.835 | 6480.345 | 13685.18
16:00 | 7120.03 | 6377.28 | 13497.31
16:30 | 7030.265 | 6197.825 | 13228.09
17:00 | 6940.5 | 6018.37 | 12958.87
17:30 | 6594.31 | 5973.785 | 12568.095
18:00 | 6248.12 | 5929.2 | 12177.32
18:30 | 6728.56 | 6244.435 | 12972.995
19:00 | 7209 | 6559.67 | 13768.67
19:30 | 7205.2 | 6872.31 | 14077.51
20:00 | 6855 | 6806.66 | 13661.66
20:30 | 6710.5 | 6577.765 | 13288.265 |  | Executive Engineer
21:00 | 6566 | 6348.87 | 12914.87 |  | Network Operation Division
21:30 | 6547 | 6084.77 | 12631.77
22:00 | 6528 | 5820.67 | 12348.67
22:30 | 6667.6 | 5834.97 | 12502.57
23:00 | 6807.2 | 5849.27 | 12656.47

## En-Curve
QF-LDC-12
Date | 16-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3661 | 1993 | 914 | 0 | 42 | 1440.3 | 40 | 3935 | 0 | 514 | 1882.7 | 0 | 0 | 11 | 160 | DAILY ENERGY CURVE
00:30 | 3687.5 | 1987 | 914 | 0 | 40 | 1445.695 | 40 | 3944 | 0 | 422.5 | 1701.2 | 0 | 0 | 5.5 | 180 | 16-05-2025
01:00 | 3714 | 1981 | 914 | 0 | 38 | 1451.09 | 40 | 3953 | 0 | 331 | 1519.7 | 0 | 0 | 0 | 200
01:30 | 3682.5 | 1954.25 | 914 | 0 | 38 | 1457.525 | 39.5 | 3995.5 | 0 | 313.5 | 1327.95 | 0 | 0 | 2.5 | 192 | Energy Generated | 315.8691 |  | MKWHr
02:00 | 3651 | 1927.5 | 914 | 0 | 38 | 1463.96 | 39 | 4038 | 0 | 296 | 1136.2 | 0 | 0 | 5 | 184 | Energy not Served | 1.585 |  | MKWHr
02:30 | 3664.5 | 1930 | 913.5 | 0 | 38 | 1459.705 | 38.5 | 4029.5 | 0 | 287 | 1048.7 | 0 | 0 | 8 | 180.5 | Total Energy Requirement | 317.4541 |  | MKWHr
03:00 | 3678 | 1932.5 | 913 | 0 | 38 | 1455.45 | 38 | 4021 | 0 | 278 | 961.2 | 0 | 0 | 11 | 177
03:30 | 3681.5 | 1928 | 913.5 | 0 | 38 | 1433.93 | 38 | 3987 | 0 | 268 | 936.2 | 0 | 0 | 9.5 | 174.5
04:00 | 3685 | 1923.5 | 914 | 0 | 38 | 1412.41 | 38 | 3953 | 0 | 258 | 911.2 | 0 | 0 | 8 | 172
04:30 | 3674 | 1929.75 | 914 | 0 | 37 | 1385.225 | 37.5 | 3889.5 | 0 | 258 | 870.7 | 0 | 0 | 8.5 | 168.5
05:00 | 3663 | 1936 | 914 | 0 | 36 | 1358.04 | 37 | 3826 | 0 | 258 | 830.2 | 0 | 0 | 9 | 165
05:30 | 3577 | 1904.5 | 914 | 0 | 35 | 1335.465 | 37.5 | 3752.5 | 14.495 | 199 | 782.2 | 0 | 0 | 13 | 159.5
06:00 | 3491 | 1873 | 914 | 0 | 34 | 1312.89 | 38 | 3679 | 28.99 | 140 | 734.2 | 0 | 0 | 17 | 154
06:30 | 3524 | 1836 | 914 | 0 | 33 | 1264.33 | 38.5 | 3605 | 82.78 | 132 | 749.2 | 0 | 0 | 11 | 128
07:00 | 3557 | 1799 | 914 | 0 | 32 | 1215.77 | 39 | 3531 | 136.57 | 124 | 764.2 | 0 | 0 | 5 | 102
07:30 | 3548.5 | 1844 | 889.5 | 0 | 33 | 1216.595 | 39.5 | 3460 | 174.865 | 124 | 750.6 | 0 | 0 | 2.5 | 87
08:00 | 3540 | 1889 | 865 | 0 | 34 | 1217.42 | 40 | 3389 | 213.16 | 124 | 737 | 0 | 0 | 0 | 72
08:30 | 3586 | 1891 | 865 | 0 | 33 | 1216.455 | 40 | 3369 | 268.06 | 154 | 706.5 | 0 | 0 | 0 | 57
09:00 | 3632 | 1893 | 865 | 0 | 32 | 1215.49 | 40 | 3349 | 322.96 | 184 | 676 | 0 | 0 | 0 | 42
09:30 | 3650 | 1968.75 | 888.5 | 0 | 32 | 1187.99 | 40 | 3355 | 321.705 | 184 | 664 | 0 | 0 | 0 | 21
10:00 | 3668 | 2044.5 | 912 | 0 | 32 | 1160.49 | 40 | 3361 | 320.45 | 184 | 652 | 0 | 0 | 0 | 0
10:30 | 3653.5 | 2061 | 912 | 0 | 33 | 1161.31 | 40 | 3426 | 341.425 | 184 | 658.5 | 0 | 0 | 0 | 0
11:00 | 3639 | 2077.5 | 912 | 0 | 34 | 1162.13 | 40 | 3491 | 362.4 | 184 | 665 | 0 | 0 | 0 | 0
11:30 | 3639.5 | 2091.5 | 912.5 | 0 | 35 | 1185.68 | 40 | 3712.5 | 377.695 | 200 | 743 | 0 | 0 | 5.5 | 0
12:00 | 3640 | 2105.5 | 913 | 0 | 36 | 1209.23 | 40 | 3934 | 392.99 | 216 | 821 | 0 | 0 | 11 | 0
12:30 | 3620.5 | 2122.75 | 912.5 | 0 | 37 | 1261.32 | 40 | 4021 | 362.02 | 225 | 922 | 0 | 0 | 23.5 | 0
13:00 | 3601 | 2140 | 912 | 0 | 38 | 1313.41 | 40 | 4108 | 331.05 | 234 | 1023 | 0 | 0 | 36 | 0
13:30 | 3553 | 2093.5 | 912.5 | 0 | 37 | 1310.9 | 40 | 3996.5 | 340.5 | 243 | 1079.5 | 0 | 0 | 34 | 0
14:00 | 3505 | 2047 | 913 | 0 | 36 | 1308.39 | 40 | 3885 | 349.95 | 252 | 1136 | 0 | 0 | 32 | 0
14:30 | 3578 | 2040 | 912.5 | 0 | 36 | 1311.375 | 39 | 4016 | 335.32 | 252 | 1136.5 | 0 | 0 | 32 | 19
15:00 | 3651 | 2033 | 912 | 0 | 36 | 1314.36 | 38 | 4147 | 320.69 | 252 | 1137 | 0 | 0 | 32 | 38
15:30 | 3570.5 | 2088 | 912 | 0 | 36 | 1317.21 | 37 | 4102.5 | 266.97 | 215.5 | 1107 | 0 | 0 | 32.5 | 33.5
16:00 | 3490 | 2143 | 912 | 0 | 36 | 1320.06 | 36 | 4058 | 213.25 | 179 | 1077 | 0 | 0 | 33 | 29
16:30 | 3502.5 | 2145 | 912.5 | 0 | 35 | 1272.34 | 34.5 | 3971.5 | 151.25 | 179 | 998 | 0 | 0 | 26.5 | 14.5
17:00 | 3515 | 2147 | 913 | 0 | 34 | 1224.62 | 33 | 3885 | 89.25 | 179 | 919 | 0 | 0 | 20 | 0
17:30 | 3470 | 1935 | 912.5 | 0 | 33 | 1222.945 | 33 | 3789 | 61.15 | 179.5 | 915.5 | 0 | 0 | 16.5 | 0
18:00 | 3425 | 1723 | 912 | 0 | 32 | 1221.27 | 33 | 3693 | 33.05 | 180 | 912 | 0 | 0 | 13 | 0
18:30 | 3581.5 | 1934 | 894 | 0 | 36 | 1315.47 | 34 | 3901.5 | 16.525 | 213.5 | 1035.5 | 0 | 0 | 11 | 20
19:00 | 3738 | 2145 | 876 | 0 | 40 | 1409.67 | 35 | 4110 | 0 | 247 | 1159 | 0 | 0 | 9 | 40
19:30 | 3599 | 2124 | 876 | 0 | 40 | 1452.31 | 35 | 4379 | 0 | 181 | 1376.2 | 0 | 0 | 15 | 0
20:00 | 3586 | 2054 | 876 | 0 | 40 | 1411.66 | 36 | 4370 | 0 | 160 | 1116 | 0 | 0 | 12 | 0
20:30 | 3578.5 | 2041.5 | 899.5 | 0 | 41 | 1331.265 | 36.5 | 4152 | 0 | 160 | 1039 | 0 | 0 | 9 | 0
21:00 | 3571 | 2029 | 923 | 0 | 42 | 1250.87 | 37 | 3934 | 0 | 160 | 962 | 0 | 0 | 6 | 0
21:30 | 3527.5 | 2004.5 | 922.5 | 0 | 43 | 1209.27 | 37.5 | 3742.5 | 0 | 178.5 | 963.5 | 0 | 0 | 3 | 25
22:00 | 3484 | 1980 | 922 | 0 | 44 | 1167.67 | 38 | 3551 | 0 | 197 | 965 | 0 | 0 | 0 | 50
22:30 | 3594 | 2021.5 | 922 | 0 | 44 | 1173.47 | 39 | 3524 | 0 | 205.5 | 977.6 | 0 | 0 | 1.5 | 25
23:00 | 3704 | 2063 | 922 | 0 | 44 | 1179.27 | 40 | 3497 | 0 | 214 | 990.2 | 0 | 0 | 3 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 16-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 21:00 | 365 | 12:00 | Payra | 411 | 08:00 | 406 | 13:00
Ashuganj | 401 | 21:00 | 370 | 12:00 | Rahanpur | 406 | 23:00 | 391 | 19:00
Bhulta | 394 | 21:00 | 370 | 12:00 | Rampal | 396 | 18:00 | 383 | 13:00
Bibiana | 393 | 21:00 | 385 | 02:00
BIPTC | 403 | 08:00 | 391 | 15:00
Bogura | 388 | 18:00 | 374 | 19:00
Gopalganj | 389 | 08:00 | 379 | 13:00
Kaliakoir | 374 | 07:00 | 365 | 02:00
Madunaghat | 388 | 00:00 | 381 | 13:00
Meghnaghat | 386 | 21:00 | 373 | 13:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 21:00 | 213 | 12:00 | Keranigonj | 224 | 21:00 | 211 | 12:00
AKSML | 229 | 00:00 | 221 | 12:00 | Khulna(S) | 227 | 18:00 | 215 | 19:30
Aminbazar | 227 | 21:00 | 212 | 12:00 | Madunaghat | 230 | 00:00 | 224 | 11:00
Ashuganj | 231 | 19:00 | 220 | 13:00 | Madunaghat-400 | 230 | 00:00 | 225 | 12:00
Ashuganj-400 | 231 | 19:00 | 220 | 13:00 | Maniknagar | 221 | 21:00 | 211 | 12:00
Baghabari | 234 | 16:00 | 226 | 12:00 | Meghnaghat | 225 | 21:00 | 220 | 10:00
Barapukuria | 225 | 23:00 | 216 | 19:00 | Meghnaghat-400 | 225 | 22:00 | 215 | 12:00
Barapukuria-230 | 225 | 23:00 | 216 | 19:00 | Mirsorai | 224 | 18:00 | 219 | 10:00
Barishal | 233 | 07:00 | 227 | 19:30 | Rajshahi | 235 | 18:00 | 222 | 19:30
Bheramara | 235 | 18:00 | 224 | 19:00 | Rampal | 226 | 08:00 | 215 | 19:30
Bhulta | 229 | 21:00 | 212 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 18:00 | 219 | 12:00 | Rampura | 229 | 21:00 | 211 | 12:00
BIPTC | 236 | 17:00 | 224 | 19:00 | Shikalbaha | 229 | 00:00 | 222 | 11:00
Bogura | 236 | 23:00 | 226 | 19:00 | Shyampur | 223 | 21:00 | 212 | 12:00
Bogura-400 | 236 | 18:00 | 227 | 19:00 | Siddhirganj | 218 | 04:00 | 215 | 09:00
Borhanuddin | 239 | 09:00 | 233 | 00:00 | Sirajgonj | 240 | 18:00 | 234 | 01:00
BSRM | 225 | 22:00 | 218 | 12:00 | Sreepur | 228 | 18:00 | 221 | 02:00
Cumilla(N) | 221 | 22:00 | 211 | 12:00 | Tongi | 225 | 20:00 | 214 | 11:00
Faridpur | 230 | 18:00 | 222 | 13:00
Fenchuganj | 226 | 16:00 | 220 | 01:00
Ghorashal | 235 | 20:00 | 220 | 14:00
Ghorashal-230 | 229 | 21:00 | 218 | 11:00
Gopalganj | 231 | 08:00 | 224 | 13:00
GPH | 226 | 01:00 | 223 | 12:00
Haripur | 223 | 22:00 | 213 | 12:00
Hasnabad | 224 | 21:00 | 210 | 12:00
Hathazari | 229 | 14:00 | 224 | 12:00
Ishurdi | 237 | 18:00 | 227 | 13:00
Jhenaidah | 230 | 18:00 | 215 | 23:00
Kaliakoir | 229 | 20:00 | 218 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 21:00 | 128 | 12:00 | Madartek | 141 | 21:00 | 128 | 12:00
Agargaon | 136 | 21:00 | 126 | 13:00 | Madunaghat | 131 | 00:00 | 126 | 12:00
Agrabad | 130 | 01:00 | 125 | 11:00 | Magura | 136 | 06:00 | 123 | 19:00
AKS | 128 | 03:00 | 124 | 12:00 | Mahasthangarh | 137 | 23:00 | 128 | 19:00
Aminbazar | 135 | 21:00 | 122 | 12:00 | Manikganj | 134 | 21:00 | 123 | 12:00
Amnura | 136 | 00:00 | 124 | 19:30 | Maniknagar | 132 | 21:00 | 127 | 12:00
Ashuganj | 136 | 18:00 | 132 | 12:00 | Matarbari | 118 | 15:00 | 107 | 21:00
Bagerhat | 130 | 07:00 | 116 | 22:00 | Matuail | 132.2 | 22:00 | 124 | 12:00
Bajitpur | 133 | 18:00 | 123 | 12:00 | Millgate | 138 | 21:00 | 126 | 12:00
Bakulia | 132 | 01:00 | 126 | 12:00 | Mirpur | 134 | 21:00 | 122 | 12:00
Banani | 138 | 20:00 | 127 | 12:00 | Mirzapur | 135 | 18:00 | 127 | 13:00
Bangabhaban | 134 | 21:00 | 126 | 13:00 | Mithapukur | 134 | 23:00 | 124 | 19:00
Barapukuria | 136 | 23:00 | 128 | 19:00 | MI_Cement | 131.7 | 22:00 | 123.6 | 12:00
Barguna | 133 | 10:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 18:00 | 124 | 00:00 | Mogbazar | 141 | 21:00 | 129 | 12:00
Barishal-230 | 130 | 07:00 | 124 | 19:30 | Mongla | 130 | 07:00 | 117 | 23:00
Baroaulia | 131 | 04:00 | 127 | 11:00 | Motijheel | 134 | 21:00 | 126 | 13:00
Baroirhat | 125 | 18:00 | 118 | 03:00 | Muktagacha | 137 | 00:00 | 127 | 01:00
Bashundhara | 140 | 21:00 | 125 | 12:00 | Munshiganj | 132 | 21:00 | 122 | 12:00
BashundharaCement | 130 | 21:00 | 123 | 10:00 | Muradnagar | 127 | 22:00 | 119 | 13:00
Beanibazar | 130 | 06:00 | 126 | 15:00 | Mymensingh | 137 | 18:00 | 114 | 13:00
Benapole | 129 | 06:00 | 114 | 23:00 | Naogaon | 137 | 22:00 | 125 | 19:00
Bhaluka | 131 | 16:00 | 123 | 12:00 | Narail | 136 | 05:00 | 123 | 13:00
Bhandaria | 125 | 18:00 | 114 | 00:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 134 | 18:00 | 129 | 20:00 | Narshingdi | 126 | 18:30 | 117 | 00:00
Bheramara | 138 | 09:00 | 130 | 13:00 | Natore | 135 | 18:00 | 127 | 19:00
Bheramara(GK) | 137 | 08:00 | 131 | 19:30 | Nawabganj | 135 | 21:00 | 124 | 13:00
Bhulta | 126 | 21:00 | 118 | 01:00 | Netrakona | 128 | 16:00 | 112 | 13:00
Bog-Sherpur | 139 | 23:00 | 129 | 19:00 | New | 139 | 21:00 | 127 | 11:00
Bogura | 140 | 23:00 | 131 | 19:00 | Niamatpur | 134 | 18:00 | 128 | 19:30
Bogura-230 | 140 | 23:00 | 132 | 19:00 | Noapara | 132 | 18:00 | 119 | 23:00
Brahmanbaria | 128 | 18:30 | 122 | 00:00 | Pabna | 135 | 17:00 | 129 | 13:00
Cantonment | 136 | 21:00 | 126 | 12:00 | Palashbari | 133 | 23:00 | 123 | 19:00
Chandina | 126 | 18:00 | 121 | 12:00 | Panchagarh | 136 | 23:00 | 121 | 13:00
Chandpur | 127 | 18:00 | 119 | 12:00 | Patuakhali | 133 | 09:00 | 129 | 22:00
Chandraghona | 130 | 00:00 | 127 | 10:00 | Payra | 135 | 07:00 | 132 | 13:00
Chapai | 130 | 08:00 | 124 | 19:00 | PHP | 123 | 18:00 | 117 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 132 | 22:00 | 123 | 13:00 | Postogola | 134 | 21:00 | 126 | 12:00
Chauddagram | 123 | 18:00 | 117 | 12:00 | Purbachal | 140 | 21:00 | 128 | 12:00
Chhatak | 129 | 06:00 | 123 | 22:00 | Purbasadipur | 130 | 23:00 | 118 | 19:00
Chowmuhani | 120 | 10:00 | 111 | 04:00 | Rahanpur | 135 | 18:00 | 129 | 19:30
Chuadanga | 135 | 05:00 | 120 | 19:00 | Rahanpur-400 | 136 | 22:00 | 130 | 01:00
Coxsbazar | 117 | 15:00 | 106 | 23:00 | Rahim | 130 | 00:00 | 124 | 12:00
Cumilla(N) | 128 | 18:00 | 121 | 12:00 | Rajbari | 133 | 06:00 | 126 | 19:00
Cumilla(S) | 134 | 04:00 | 119 | 11:00 | Rajendrapur | 139 | 19:00 | 121 | 13:00
Daudkandi | 128 | 22:00 | 118 | 12:00 | Rajshahi | 135 | 18:00 | 128 | 19:00
Dhaka | 140 | 21:00 | 129 | 13:00 | Rajshahi-230 | 135 | 18:00 | 118 | 19:00
Dhamrai | 143 | 21:00 | 126 | 12:00 | Ramganj | 122 | 18:30 | 112 | 03:00
Dhanmondi | 141 | 21:00 | 129 | 12:00 | Rampur | 130 | 01:00 | 125 | 11:00
Dohazari | 126 | 15:00 | 121 | 11:00 | Rampura | 141 | 21:00 | 128 | 12:00
Faridpur | 134 | 04:00 | 130 | 13:00 | Rangamati | 129 | 00:00 | 125 | 12:00
Fatullah | 133 | 22:00 | 124 | 12:00 | Rangpur | 130 | 09:00 | 124 | 19:00
Fenchuganj | 135 | 16:00 | 131 | 01:00 | Ruppur | 138 | 16:00 | 131 | 19:00
Feni | 123 | 18:00 | 115 | 12:00 | Saidpur | 131 | 09:00 | 120 | 19:00
Ghatail | 137 | 18:00 | 125 | 00:00 | Satkhira | 131 | 18:00 | 114 | 23:00
Ghorashal | 140 | 21:00 | 130 | 14:00 | Satmasjid | 135 | 21:00 | 125 | 11:00
Goalpara | 133 | 07:00 | 123 | 22:00 | Savar | 135 | 21:00 | 121 | 08:00
Gollamari | 135 | 18:00 | 125 | 23:00 | SevenRings | 140 | 21:00 | 129 | 12:00
Gopalganj | 132 | 06:00 | 125 | 19:30 | ShahCement | 132 | 22:00 | 123 | 13:00
Gopalganj-400 | 135 | 18:00 | 128 | 10:00 | Shahjadpur | 136 | 03:00 | 133 | 19:00
Gulshan | 141 | 21:00 | 128 | 12:00 | Shahjibazar | 131 | 19:00 | 124 | 00:00
Halishahar | 132 | 00:00 | 126 | 11:00 | Shahmirpur | 132 | 14:00 | 127 | 11:00
Haripur | 132 | 22:00 | 124 | 12:00 | Shariatpur | 135 | 19:00 | 125 | 19:30
HaripurSBU | 131 | 21:00 | 124 | 13:00 | Sherpur | 140 | 15:00 | 125 | 00:00
Hasnabad | 131 | 18:00 | 126 | 12:00 | Shikalbaha | 121 | 03:00 | 115 | 11:00
Hathazari | 133 | 02:00 | 128 | 11:00 | Shikalbaha-230 | 132 | 14:00 | 128 | 11:00
Ishurdi | 139 | 18:00 | 132 | 19:00 | Shitalakhya | 131.7 | 22:00 | 123.6 | 12:00
Jaldhaka | 130 | 23:00 | 117 | 19:00 | Sholosohor | 129 | 00:00 | 125 | 12:00
Jamalpur | 140 | 15:00 | 129 | 00:00 | Shyampur | 130 | 22:00 | 125 | 00:00
Jashore | 129 | 05:00 | 116 | 23:00 | Shyampur-230 | 132 | 21:00 | 124 | 10:00
Jhenaidah | 137 | 08:00 | 119 | 13:00 | Siddhirganj | 132 | 21:00 | 124 | 09:00
Jhenaidah-230 | 137 | 08:00 | 126 | 19:30 | Sirajganj | 136 | 23:00 | 128 | 19:00
Joydebpur | 140 | 19:30 | 124 | 15:00 | Sonargaon | 133 | 22:00 | 120 | 20:00
Joypurhat | 133 | 22:00 | 122 | 19:30 | Sreemongol | 131 | 19:00 | 126 | 00:00
Juldah | 132 | 00:00 | 128 | 08:00 | Sreepur | 134 | 20:00 | 128 | 01:00
Kabirpur | 138 | 21:00 | 123 | 12:00 | Srinagar | 136 | 21:00 | 124 | 12:00
Kachua | 125 | 18:00 | 118 | 11:00 | SSM | 134 | 00:00 | 132 | 07:00
Kaliakoir | 138 | 20:00 | 131 | 11:00 | Sunamganj | 128 | 07:00 | 122 | 22:00
Kallyanpur | 135 | 21:00 | 124 | 10:00 | Sylhet | 131 | 07:00 | 128 | 01:00
Kalurghat | 129 | 00:00 | 126 | 11:00 | Sylhet-132 | 131 | 07:00 | 129 | 00:00
Kamrangirchar | 135 | 21:00 | 125 | 11:00 | Tangail | 135 | 18:00 | 125 | 00:00
Kaptai | 133 | 1:00 | 130 | 12:00 | Thakurgaon | 136 | 23:00 | 121 | 19:00
Kasba | 126 | 22:00 | 119 | 12:00 | TK | 130 | 02:00 | 126 | 12:00
Kazla | 133 | 22:00 | 126 | 13:00 | Tongi | 140 | 21:00 | 128 | 11:00
Keranigonj | 135 | 21:00 | 125 | 13:00 | Ullahpara | 135 | 10:00 | 129 | 19:30
Khagrachori | 129 | 01:00 | 125 | 11:00 | Ullon | 140 | 21:00 | 129 | 12:00
Khulna | 133 | 07:00 | 122 | 23:00 | Uttara | 131 | 21:00 | 120 | 20:00
Khulna(S) | 135 | 18:00 | 124 | 23:00 | UttaraNew | 134 | 21:00 | 122 | 10:00
Khulshi | 129 | 00:00 | 123 | 07:00 | Zigatola | 136 | 21:00 | 124 | 12:00
Kishoreganj | 131 | 16:00 | 120 | 12:00
Kodda | 139 | 19:30 | 122 | 15:00
KSRM | 132 | 00:00 | 127 | 12:00
Kulaura | 133 | 08:00 | 131 | 00:00
Kurigram | 132 | 23:00 | 119 | 19:00
Kushtia | 135 | 17:00 | 124 | 13:00
Lalbag | 135 | 21:00 | 125 | 13:00
Lalmonirhat | 128 | 11:00 | 119 | 19:00
Madanganj | 131 | 22:00 | 123 | 10:00
Madaripur | 133 | 08:00 | 128 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division