## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 18-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-05-2025 | during | 18-05-2025 | during | 18-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 352 | 333 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 300 | 253 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 286 | 264 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 30 | 54 | 53.97 | 53.97 | 17 | 53 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 64 | 131 | 133 | 133 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 53 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 17.5 | 17 | 30 | 30 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 18 | 22 | 22 | 19 | 19 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 16 | 52.19 | 52.19 | 34 | 34 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 15 | 0 | 300 | 300 | 281 | 281 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 117 | 98 | 149 | 149 | 113 | 113 | Engine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 52 | 105 | 105 | 34 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 21 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 450 | 400 | 584 | 584 | 350 | 350 | Allocation limit by Titas, instructed by DS(Gen)
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 118 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2315.5 | 2408 | 4672.54 | 4672.54 | 3080.8 | 3134.8
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 120 | 120 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 1 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 22 | 10 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 30 | 0 | 105 | 105 | 87 | 87 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 78 | 48 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 21 | 0 | 0 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 75 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 8 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 26 | 6 | 108 | 108 | 70 | 70 | Engine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 3.95 | 0 | 3.95 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 6 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 144 | 144 | Engine Problem
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 612 | 925 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 1 | 25 | 11 | 6 | 11 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 569 | 559 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1633 | 2023 | 3304.67 | 3315.72 | 3226.81 | 3213.86
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 201 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 330 | 335 | 335 | 335 | 335 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 32 | 36 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 56 | 51 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 45 | 195 | 195 | 102 | 102 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 25 | 0 | 150 | 150 | 135 | 135 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 85 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 136 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 36 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 25 | 34 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 12 | 17.75 | 17.75 | 17.75 | 17.75 | Schedule Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 108 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 71 | 92 | 115 | 115 | 51 | 90 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 67 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1640 | 1628 | 2439.24 | 2389.24 | 2092.3 | 2081.3
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 17-05-2025 | during | 18-05-2025 | during | 18-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 0 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 169 | 200 | 200 | 125 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 94 | 115 | 115 | 68 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 1.47 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 6 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 35 | 35 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 133.47 | 269 | 599.1 | 549 | 290.1 | 312
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 35 | 35 | 35 | 35 | 35 | 35 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 0 | 0 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 150 | 163 | 163 | 163 | 163 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 83 | 85 | 85 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 173 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 16 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 6 | 7 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 270 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 387 | 303 | 380 | 380 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1544 | 1415 | 1567 | 1567 | 1523 | 1523
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 876 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 212 | 175 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78.82 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 852 | 1010 | 1234.2 | 1234.2 | 1234 | 1234 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2066.82 | 2078 | 3604.2 | 3514.2 | 3201.01 | 3111.01
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 295 | 295 | 620 | 620 | 450 | 450 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 0 | 10 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 0 | 125 | 125 | 125 | 125 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 930 | 1170 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 218 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.5 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1850.5 | 2002 | 2787.12 | 2786.12 | 2577.12 | 2576.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 160 | 168 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 197 | 220 | 220 | 190 | 190 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 370 | 350 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 2.91 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 925 | 1416.08 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 36.98 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 73 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 1707.89 | 2131.08 | 3201.17 | 3039.87 | 2864.39 | 2703.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 55 | 55 | -
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 160 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.5 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 6 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 132 | 0 | 62.69 | 0 | 62.69 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 313.5 | 265 | 509.29 | 412 | 564.29 | 467
System Total |  |  |  |  | 27566.2 | 28624.082 | 13204.68 | 14219.08 | 22684.33 | 22245.69 | 19419.82 | 19122.18
Forecast Scenario (18-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13350 |  | 0 |  | 13350
|  |  |  | 1:00 | 13100 |  | 0 |  | 13100
|  |  |  | 2:00 | 13020 |  | 0 |  | 13020
|  |  |  | 3:00 | 12740 |  | 0 |  | 12740
|  |  |  | 4:00 | 12510 |  | 0 |  | 12510
|  |  |  | 5:00 | 12440 |  | 0 |  | 12440
|  |  |  | 6:00 | 11710 |  | 0 |  | 11710
|  |  |  | 7:00 | 11580 |  | 0 |  | 11580
|  |  |  | 8:00 | 11600 |  | 0 |  | 11600
|  |  |  | 9:00 | 11930 |  | 0 |  | 11930
|  |  |  | 10:00 | 12220 |  | 0 |  | 12220
|  |  |  | 11:00 | 12840 |  | 0 |  | 12840
|  |  |  | 12:00 | 13400 |  | 0 |  | 13400
|  |  |  | 13:00 | 13880 |  | 0 |  | 13880
|  |  |  | 14:00 | 14370 |  | 0 |  | 14370
|  |  |  | 15:00 | 14300 |  | 0 |  | 14300
|  |  |  | 16:00 | 13680 |  | 0 |  | 13680
|  |  |  | 17:00 | 12680 |  | 0 |  | 12680
|  |  |  | 18:00 | 11510 |  | 0 |  | 11510
|  |  |  | 18:30 | 12200 |  | 0 |  | 12200
|  |  |  | 19:00 | 12790 |  | 0 |  | 12790
|  |  |  | 19:30 | 13840 |  | 0 |  | 13840
|  |  |  | 20:00 | 13850 |  | 0 |  | 13850
|  |  |  | 21:00 | 14000 |  | 0 |  | 14000
|  |  |  | 22:00 | 14080 |  | 0 |  | 14080
|  |  |  | 23:00 | 14220 |  | 0 |  | 14220
Probable Maximum Temperature: |  |  | 32.00°C
Probable Maximum Demand at Day Peak: |  |  | 13400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14000.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 311.80 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:34 hrs on 18-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 17-05-2025 | [28 empty] | Date: | 17-05-2025 | [28 empty] | Date: | 17-05-2025 | [28 empty] | Date: | 17-05-2025 | [28 empty] | Date: | 17-05-2025 | [16 empty] | Date: | 17-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 105 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 148 | 109 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 400 | 0 | 0 | 0 | 120 | 11 | 0 | 31 | 0 | 100 | 30 | 0 | 40 | 0 | 30 | 505 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 8 | 0 | 350 | 335 | 54 | 206 | 35 | 91 | 90 | 136 | 15 | 14 | 114 | 52 | 52.2 | 0 | 24 | 315 | 320 | 384 | 33 | 30 | 0 | 139 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 17 | 45 | 55 | 0 | 0 | 0 | 9 | 6696.2 | 923 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 17 | 1008.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 115 | 220 | 0 | 300 | 1045 | 0 | 5837.89 | 12534.09 | 77.15
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 104 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 146 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 35 | 20 | 19 | 0 | 400 | 0 | 0 | 0 | 120 | 16 | 0 | 31 | 0 | 88 | 30 | 0 | 40 | 0 | 30 | 507 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 51 | 0 | 8 | 0 | 354 | 335 | 54 | 192 | 35 | 91 | 90 | 136 | 9 | 14 | 114 | 48 | 52.2 | 0 | 24 | 295 | 320 | 349 | 33 | 30 | 0 | 139 | 8 | 0 | 83 | 30 | 0 | 18 | 169 | 0 | 45 | 45 | 0 | 0 | 0 | 12 | 6427.2 | 922 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 17 | 1018.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 105 | 220 | 0 | 298 | 1087 | 0 | 5902.72 | 12329.92 | 77.14
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 104 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 140 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 20 | 19 | 0 | 350 | 0 | 0 | 0 | 120 | 17 | 0 | 31 | 0 | 50 | 30 | 0 | 40 | 0 | 30 | 502 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 51 | 0 | 8 | 0 | 320 | 335 | 54 | 193 | 35 | 89 | 90 | 136 | 9 | 14 | 114 | 46 | 52.2 | 0 | 24 | 300 | 320 | 300 | 33 | 30 | 0 | 140 | 8 | 0 | 83 | 20 | 0 | 18 | 169 | 0 | 45 | 45 | 0 | 0 | 0 | 12 | 6071.2 | 922 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1009 | 17 | 831.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 100 | 180 | 0 | 298 | 1000 | 0 | 5463.38 | 11534.58 | 77.13
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 0 | 103 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 141 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 20 | 19 | 0 | 350 | 0 | 0 | 0 | 120 | 13 | 0 | 31 | 0 | 50 | 30 | 0 | 40 | 0 | 30 | 506 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 51 | 0 | 8 | 0 | 320 | 335 | 54 | 197 | 35 | 72 | 90 | 136 | 9 | 14 | 114 | 44 | 52.2 | 0 | 24 | 305 | 320 | 313 | 33 | 30 | 0 | 152 | 0 | 0 | 83 | 20 | 0 | 18 | 169 | 0 | 45 | 45 | 0 | 0 | 0 | 12 | 6091.2 | 923 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 17 | 831.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 100 | 205 | 0 | 295 | 900 | 0 | 5269.68 | 11360.88 | 77.12
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 0 | 104 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 140 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 17 | 19 | 0 | 400 | 0 | 0 | 0 | 120 | 9 | 0 | 31 | 0 | 36 | 0 | 0 | 40 | 0 | 42 | 400 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 51 | 0 | 8 | 0 | 354 | 335 | 55 | 189 | 35 | 72 | 90 | 136 | 9 | 14 | 114 | 42 | 52.2 | 0 | 24 | 300 | 320 | 325 | 33 | 30 | 0 | 154 | 0 | 0 | 83 | 20 | 0 | 18 | 171 | 0 | 24 | 45 | 0 | 0 | 0 | 12 | 6110.2 | 922 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 17 | 824.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 100 | 220 | 0 | 298 | 800 | 0 | 5109.77 | 11219.97 | 77.11
05:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 141 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 400 | 0 | 0 | 0 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 42 | 401 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 51 | 0 | 8 | 0 | 354 | 335 | 54 | 196 | 35 | 72 | 90 | 136 | 9 | 14 | 114 | 42 | 52.2 | 0 | 0 | 295 | 320 | 295 | 33 | 30 | 0 | 152 | 0 | 0 | 83 | 20 | 0 | 18 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5836.2 | 923 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 7 | 821.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 150 | 10 | 90 | 220 | 0 | 297 | 722 | 0 | 4966.91 | 10803.11 | 77.1
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 140 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 1 | 0 | 20 | 19 | 0 | 300 | 0 | 0 | 0 | 120 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 42 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 2 | 51 | 0 | 8 | 0 | 354 | 335 | 53 | 194 | 35 | 69 | 90 | 136 | 9 | 6 | 114 | 40 | 52.2 | 4 | 0 | 285 | 320 | 318 | 33 | 30 | 0 | 143 | 0 | 0 | 83 | 20 | 0 | 18 | 171 | 0 | 0 | 0 | 0 | 0 | 1.34 | 0 | 5479.54 | 924 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.59 | 754 | 0 | 825.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 2.2 | 140 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0.05 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 10 | 100 | 220 | 0 | 298 | 606 | 0 | 4826.33 | 10305.87 | 77.09
07:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 68 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 136 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 7 | 0 | 19 | 19 | 0 | 300 | 0 | 0 | 0 | 120 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 37 | 0 | 32 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 6 | 51 | 0 | 8 | 0 | 344 | 335 | 55 | 181 | 34 | 69 | 90 | 100 | 9 | 6 | 114 | 36 | 52.2 | 10 | 0 | 295 | 320 | 292 | 33 | 30 | 0 | 129 | 0 | 0 | 83 | 20 | 0 | 18 | 172 | 0 | 18 | 45 | 0 | 1 | 7.25 | 2 | 5476.45 | 923 | 227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.64 | 758 | 0 | 825.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 9.92 | 140 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0.27 | 0 | 136 | 0 | 0 | 1 | 0 | 0 | 0 | 0.5 | 17 | 0.04 | 0 | 150 | 8 | 90 | 220 | 0 | 297 | 600 | 0 | 4856.29 | 10332.74 | 77.08
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 79 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 158 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 15 | 0 | 18 | 19 | 0 | 350 | 0 | 0 | 0 | 120 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 9 | 10 | 0 | 8 | 0 | 320 | 300 | 55 | 215 | 0 | 69 | 90 | 100 | 9 | 12 | 114 | 36 | 25 | 18 | 0 | 305 | 320 | 348 | 33 | 30 | 0 | 144 | 0 | 0 | 83 | 20 | 0 | 18 | 172 | 0 | 45 | 45 | 0 | 0 | 24.51 | 12 | 5758.51 | 876 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.3 | 768 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 25.79 | 140 | 0 | 140 | 0 | 0 | 0 | 350 | 0 | 0.74 | 0 | 148 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 19 | 0.19 | 0 | 150 | 9 | 100 | 180 | 0 | 298 | 605 | 0 | 4958.02 | 10716.53 | 77.07
09:00 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 | 105 | 56 | 0 | 0 | 2 | 17 | 0 | 0 | 400 | 175 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 21 | 0 | 15 | 0 | 0 | 450 | 0 | 0 | 0 | 120 | 12 | 0 | 0 | 0 | 75 | 5 | 3 | 35 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 10 | 0 | 8 | 0 | 355 | 335 | 56 | 186 | 30 | 69 | 90 | 100 | 9 | 12 | 114 | 34 | 25 | 20 | 0 | 315 | 320 | 370 | 35 | 30 | 0 | 156 | 5 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 45 | 75 | 0 | 2 | 39.44 | 12 | 6360.44 | 876 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.78 | 755 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 40.63 | 140 | 0 | 140 | 0 | 0 | 0 | 370 | 0 | 3.38 | 0 | 148 | 0 | 0 | 12 | 0 | 0 | 0 | 1.6 | 105 | 0.34 | 0 | 150 | 7 | 100 | 220 | 0 | 296 | 630 | 0 | 5184.73 | 11545.17 | 77.06
10:00 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 109 | 64 | 0 | 0 | 26 | 17 | 0 | 0 | 400 | 315 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 24 | 35 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 120 | 8 | 0 | 0 | 0 | 75 | 88 | 3 | 35 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 9 | 10 | 0 | 8 | 0 | 350 | 335 | 56 | 218 | 33 | 69 | 90 | 100 | 9 | 12 | 114 | 36 | 25 | 31 | 0 | 310 | 320 | 390 | 35 | 30 | 0 | 159 | 5 | 0 | 80 | 28 | 0 | 18 | 172 | 0 | 45 | 75 | 0 | 2 | 49.64 | 12 | 6795.64 | 923 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60.94 | 754 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 50.36 | 140 | 0 | 140 | 0 | 0 | 0 | 340 | 0 | 4.21 | 0 | 154 | 0 | 0 | 1 | 0 | 0 | 0 | 1.8 | 75 | 0.43 | 0 | 173 | 6 | 100 | 220 | 0 | 297 | 650 | 0 | 5203.74 | 11999.38 | 77.05
11:00 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 3 | 0 | 120 | 64 | 0 | 0 | 35 | 45 | 0 | 0 | 400 | 286 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 30 | 35 | 17.5 | 0 | 0 | 500 | 0 | 0 | 0 | 120 | 1 | 0 | 0 | 0 | 75 | 100 | 5 | 35 | 0 | 2 | 560 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 35 | 0 | 45 | 0 | 350 | 340 | 56 | 186 | 33 | 69 | 90 | 100 | 9 | 14 | 114 | 36 | 25 | 70 | 0 | 320 | 320 | 390 | 35 | 30 | 0 | 155 | 6 | 0 | 80 | 28 | 0 | 18 | 172 | 0 | 45 | 75 | 0 | 0 | 28.62 | 12 | 6997.12 | 924 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.44 | 804 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 33.52 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 1.91 | 0 | 167 | 0 | 0 | 5 | 0 | 0 | 0 | 2.7 | 9 | 0.72 | 0 | 280 | 7 | 100 | 218 | 0 | 296 | 740 | 0 | 5475.29 | 12472.41 | 77.04
12:00 | 0 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 30 | 0 | 117 | 64 | 15 | 0 | 53 | 54 | 0 | 0 | 400 | 300 | 0 | 0 | 35 | 0 | 286 | 0 | 0 | 21 | 52 | 17.5 | 0 | 0 | 450 | 0 | 0 | 26 | 150 | 1 | 0 | 0 | 0 | 75 | 100 | 5 | 35 | 6 | 2 | 569 | 0 | 0 | 22 | 0 | 30 | 0 | 0 | 0 | 0 | 612 | 0 | 51 | 25 | 63 | 0 | 344 | 340 | 56 | 201 | 32 | 71 | 90 | 100 | 9 | 14 | 114 | 38 | 25 | 67 | 0 | 310 | 320 | 387 | 35 | 30 | 0 | 152 | 6 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 45 | 75 | 0 | 0 | 1.47 | 12 | 7265.97 | 924 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.82 | 852 | 0 | 925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 36.98 | 160 | 0 | 140 | 0 | 0 | 0 | 370 | 0 | 2.91 | 0 | 169 | 0 | 0 | 6 | 0 | 0 | 0 | 6.5 | 132 | 0.5 | 0 | 307 | 0 | 100 | 218 | 0 | 295 | 930 | 0 | 5938.71 | 13204.68 | 77.03
13:00 | 0 | 35 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 35 | 0 | 113 | 64 | 15 | 0 | 55 | 126 | 0 | 0 | 400 | 265 | 0 | 0 | 35 | 0 | 266 | 0 | 0 | 28 | 52 | 17 | 0 | 0 | 400 | 0 | 0 | 76 | 150 | 16 | 0 | 17 | 0 | 88 | 100 | 0 | 35 | 18 | 5 | 569 | 0 | 0 | 25 | 0 | 51 | 0 | 0 | 0 | 0 | 612 | 13 | 51 | 60 | 63 | 0 | 356 | 335 | 56 | 183 | 32 | 90 | 90 | 100 | 9 | 14 | 114 | 40 | 25 | 29 | 0 | 310 | 320 | 349 | 35 | 6 | 0 | 151 | 6 | 0 | 82 | 25 | 0 | 18 | 173 | 0 | 45 | 85 | 0 | 0 | 1.92 | 12 | 7327.92 | 924 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.6 | 1004 | 0 | 1086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 56.02 | 179 | 0 | 200 | 0 | 0 | 0 | 340 | 0 | 5.12 | 0 | 170 | 0 | 0 | 34 | 0 | 0 | 0 | 4.4 | 0 | 0.63 | 0 | 307 | 9 | 100 | 217 | 0 | 295 | 1050 | 0 | 6325.77 | 13653.69 | 77.02
14:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 35 | 0 | 120 | 64 | 15 | 0 | 55 | 126 | 0 | 0 | 350 | 300 | 0 | 0 | 35 | 0 | 292 | 0 | 0 | 25 | 52 | 0 | 0 | 0 | 370 | 0 | 0 | 81 | 150 | 50 | 0 | 45 | 0 | 88 | 100 | 2 | 40 | 51 | 5 | 520 | 0 | 0 | 40 | 0 | 51 | 0 | 0 | 0 | 0 | 580 | 8 | 51 | 60 | 63 | 0 | 320 | 335 | 56 | 203 | 34 | 90 | 85 | 100 | 9 | 14 | 114 | 40 | 25 | 51 | 0 | 300 | 320 | 384 | 35 | 6 | 0 | 149 | 7 | 0 | 82 | 30 | 0 | 16 | 173 | 0 | 45 | 85 | 0 | 0 | 43.69 | 12 | 7372.69 | 924 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.08 | 1014 | 0 | 1056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 46.22 | 179 | 0 | 170 | 0 | 0 | 0 | 340 | 0 | 4.37 | 0 | 171 | 0 | 0 | 11 | 0 | 0 | 0 | 5.4 | 122 | 0.62 | 0 | 257 | 9 | 100 | 180 | 0 | 296 | 1020 | 0 | 6229.69 | 13602.38 | 77.01
15:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 35 | 0 | 117 | 32 | 0 | 0 | 41 | 126 | 0 | 0 | 400 | 283 | 0 | 0 | 35 | 0 | 282 | 0 | 0 | 20 | 35 | 17 | 0 | 0 | 370 | 0 | 0 | 78 | 150 | 63 | 0 | 45 | 0 | 88 | 100 | 3 | 40 | 51 | 2 | 575 | 0 | 0 | 50 | 0 | 51 | 0 | 0 | 0 | 0 | 580 | 0 | 51 | 60 | 63 | 0 | 354 | 335 | 53 | 196 | 34 | 89 | 85 | 100 | 9 | 14 | 114 | 40 | 25 | 41 | 0 | 315 | 320 | 355 | 35 | 30 | 0 | 152 | 7 | 0 | 0 | 25 | 0 | 16 | 173 | 0 | 48 | 85 | 0 | 2 | 29.14 | 2 | 7338.14 | 923 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.75 | 1014 | 0 | 1064.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 35.46 | 176 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 3.16 | 0 | 170 | 0 | 0 | 5 | 0 | 0 | 0 | 2.9 | 26 | 0.35 | 0 | 280 | 10 | 90 | 220 | 0 | 296 | 982 | 0 | 6155.08 | 13493.22 | 77
16:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 35 | 0 | 86 | 47 | 0 | 0 | 35 | 108 | 0 | 0 | 350 | 293 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 12 | 35 | 17 | 0 | 0 | 370 | 0 | 0 | 69 | 150 | 55 | 0 | 70 | 0 | 100 | 100 | 2 | 40 | 17 | 2 | 520 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 0 | 0 | 606 | 0 | 51 | 10 | 82 | 0 | 330 | 320 | 50 | 205 | 37 | 90 | 90 | 100 | 25 | 6 | 105 | 32 | 25 | 33 | 0 | 295 | 320 | 348 | 36 | 30 | 0 | 145 | 7 | 0 | 50 | 30 | 0 | 16 | 171 | 0 | 67 | 121 | 0 | 1 | 22 | 2 | 7137 | 924 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 1006 | 0 | 1013.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 16.11 | 173 | 0 | 199 | 0 | 0 | 0 | 330 | 0 | 1.69 | 0 | 167 | 0 | 0 | 3 | 0 | 0 | 0 | 1.6 | 25 | 0.25 | 0 | 250 | 6 | 100 | 220 | 0 | 297 | 950 | 0 | 5961.3 | 13098.3 | 76.99
17:00 | 0 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 35 | 0 | 68 | 86 | 0 | 0 | 48 | 108 | 0 | 0 | 350 | 277 | 0 | 0 | 0 | 0 | 283 | 0 | 0 | 1 | 44 | 17 | 0 | 0 | 370 | 0 | 0 | 54 | 150 | 51 | 0 | 75 | 0 | 100 | 100 | 0 | 40 | 0 | 4 | 520 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 4 | 51 | 10 | 45 | 0 | 330 | 300 | 52 | 197 | 36 | 90 | 90 | 100 | 36 | 0 | 105 | 22 | 8 | 13 | 0 | 320 | 320 | 319 | 36 | 30 | 0 | 142 | 7 | 0 | 51 | 30 | 0 | 16 | 171 | 0 | 67 | 123 | 0 | 0 | 7.53 | 2 | 7086.53 | 924 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 965 | 0 | 1027.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 10.07 | 172 | 0 | 200 | 0 | 0 | 0 | 330 | 0 | 0.88 | 0 | 165 | 0 | 0 | 1 | 0 | 0 | 0 | 0.4 | 15 | 0.16 | 0 | 250 | 10 | 94 | 220 | 0 | 297 | 944 | 0 | 5854.95 | 12941.48 | 76.96
18:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 35 | 17 | 68 | 112 | 0 | 0 | 55 | 90 | 0 | 0 | 300 | 282 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 1 | 52 | 16.5 | 6 | 0 | 370 | 0 | 0 | 53 | 150 | 34 | 0 | 78 | 0 | 76 | 80 | 0 | 40 | 0 | 5 | 520 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 833 | 1 | 51 | 0 | 45 | 0 | 330 | 300 | 50 | 198 | 30 | 68 | 90 | 68 | 37 | 6 | 70 | 12 | 8 | 3 | 0 | 305 | 320 | 333 | 36 | 30 | 0 | 133 | 7 | 0 | 51 | 30 | 0 | 16 | 171 | 0 | 70 | 128 | 0 | 0 | 1.46 | 2 | 7052.96 | 924 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 935 | 0 | 972.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.63 | 173 | 0 | 199 | 0 | 0 | 0 | 394 | 0 | 0.05 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 5 | 0.03 | 0 | 200 | 9 | 100 | 220 | 0 | 297 | 900 | 0 | 5677.31 | 12730.27 | 76.97
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 35 | 17 | 86 | 131 | 0 | 0 | 55 | 126 | 0 | 0 | 420 | 295 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 108 | 17 | 18 | 0 | 400 | 0 | 0 | 39 | 150 | 34 | 0 | 78 | 0 | 88 | 100 | 0 | 40 | 0 | 8 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 45 | 0 | 355 | 330 | 51 | 201 | 33 | 72 | 85 | 74 | 37 | 12 | 108 | 30 | 10 | 0 | 39 | 310 | 320 | 335 | 36 | 30 | 0 | 141 | 7 | 0 | 83 | 30 | 0 | 16 | 171 | 0 | 94 | 169 | 0 | 0 | 0 | 3 | 7713 | 923 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 931 | 17 | 1267.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 200 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 157 | 0 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 11 | 115 | 220 | 0 | 295 | 930 | 0 | 6201.42 | 13914.42 | 76.96
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 17 | 98 | 131 | 0 | 0 | 55 | 162 | 0 | 0 | 420 | 253 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 118 | 17 | 18 | 0 | 400 | 0 | 0 | 6 | 150 | 25 | 21 | 78 | 0 | 100 | 100 | 0 | 40 | 0 | 8 | 559 | 0 | 0 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 925 | 0 | 51 | 0 | 45 | 0 | 354 | 330 | 51 | 181 | 36 | 92 | 85 | 136 | 38 | 12 | 108 | 36 | 34 | 0 | 39 | 270 | 320 | 303 | 35 | 30 | 0 | 150 | 7 | 0 | 83 | 30 | 0 | 16 | 171 | 0 | 94 | 169 | 0 | 0 | 0 | 6 | 7743 | 876 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 17 | 1416.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 197 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 160 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 0 | 220 | 0 | 295 | 1170 | 0 | 6476.08 | 14219.08
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 43 | 17 | 114 | 131 | 0 | 0 | 35 | 108 | 0 | 0 | 350 | 269 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 125 | 17 | 18 | 0 | 400 | 0 | 0 | 0 | 150 | 29 | 34 | 78 | 0 | 100 | 100 | 0 | 40 | 0 | 2 | 501 | 0 | 0 | 33 | 2 | 0 | 0 | 0 | 0 | 0 | 914 | 0 | 51 | 0 | 45 | 0 | 355 | 330 | 52 | 182 | 36 | 82 | 85 | 133 | 39 | 14 | 108 | 36 | 34 | 0 | 0 | 300 | 320 | 311 | 35 | 30 | 0 | 148 | 7 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 94 | 169 | 0 | 0 | 0 | 5 | 7583 | 876 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 944 | 17 | 1291.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 197 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 180 | 0 | 295 | 1190 | 0 | 6239.37 | 13822.37 | 76.95
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 110 | 110 | 0 | 0 | 17 | 17 | 0 | 0 | 420 | 295 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 0 | 125 | 16.5 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 20 | 34 | 78 | 0 | 100 | 100 | 0 | 40 | 0 | 2 | 456 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 45 | 0 | 354 | 330 | 52 | 184 | 36 | 91 | 85 | 120 | 38 | 14 | 108 | 36 | 34 | 0 | 0 | 310 | 320 | 300 | 35 | 30 | 0 | 149 | 7 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 65 | 170 | 0 | 0 | 0 | 9 | 7456.5 | 924 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 17 | 1055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 105 | 220 | 0 | 297 | 1050 | 0 | 5959 | 13415.5 | 76.94
22:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 17 | 92 | 82 | 0 | 0 | 17 | 0 | 0 | 0 | 420 | 287 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 35 | 16.5 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 11 | 34 | 78 | 0 | 100 | 48 | 0 | 40 | 0 | 16 | 370 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 0 | 51 | 0 | 45 | 0 | 355 | 330 | 51 | 182 | 36 | 92 | 90 | 120 | 39 | 14 | 108 | 38 | 34 | 0 | 0 | 290 | 320 | 303 | 35 | 30 | 0 | 148 | 7 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 8 | 45 | 0 | 0 | 0 | 3 | 6878.5 | 924 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 17 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 197 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286 | 11 | 105 | 220 | 0 | 296 | 865 | 0 | 5470 | 12348.5 | 76.93
23:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 75 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 314 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 17 | 16.5 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 15 | 34 | 78 | 0 | 100 | 48 | 0 | 40 | 0 | 20 | 356 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 51 | 0 | 45 | 0 | 353 | 330 | 49 | 200 | 36 | 91 | 90 | 120 | 39 | 14 | 107 | 38 | 34 | 0 | 0 | 280 | 320 | 343 | 35 | 30 | 0 | 149 | 7 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 8 | 8 | 0 | 0 | 0 | 10 | 6712.5 | 924 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 767 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 150 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 115 | 220 | 0 | 209 | 700 | 0 | 4887 | 11599.5 | 76.92
Total KWH | 0 | 663360 | 407520 | 0 | 0 | 0 | 0 | 0 | 8571600 | 0 | 0 | 331920 | 127080 | 2343024 | 1406880 | 66742 | 0 | 548786 | 1054080 | 0 | 0 | 8925500 | 5600291 | 0 | 0 | 158004 | 0 | 6883694 | 0 | 0 | 191745 | 876000 | 340200 | 258120 | 0 | 9682272.73 | 0 | 0 | 484800 | 3300000 | 512160 | 146447 | 872736 | 0 | 1643520 | 1431360 | 25883 | 922640 | 185673 | 388320 | 11541818.18 | 0 | 0 | 513120 | 51769.8 | 263454 | 0 | 0 | 0 | 0 | 14885453 | 80730 | 1084336 | 324509 | 853091 | 0 | 8650400 | 8000000 | 1276320 | 4769000 | 818784 | 1941120 | 2138590 | 2793600 | 445200 | 271190 | 2635680 | 876480 | 800870 | 394764 | 152832 | 7366000 | 7685100 | 8455000 | 817000 | 623640 | 0 | 3545345 | 127560 | 0 | 1797120 | 634368 | 0 | 432000 | 3556270 | 11160 | 1134000 | 1840800 | 0 | 7050 | 260220 | 195360 | 162401461.71 | 22142545 | 4871520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 546480 | 20952730 | 158880 | 22666765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 557542 | 0 | 343496 | 3792909 | 0 | 4176145 | 0 | 0 | 0 | 8484072 | 0 | 28560 | 0 | 3800000 | 0 | 56016 | 93970 | 91776 | 0 | 0 | 32020.2 | 544000 | 4533 | 0 | 5542000 | 213844 | 2367000 | 5233930 | 0 | 7010208 | 22001454.55 | 0 | 135712395.75 | 298113857.46

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 17-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13204.68 | MW | 12:00 Hr. | Energy Generated |  |  | 298.1139 |  | MKWHr.
| Day Peak Demand |  |  | 13204.68 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 14219.08 | MW | 19:30 Hr. | Energy Demand |  |  | 298.1139 |  | MKWHr.
| Evening Peak Demand |  |  | 14219.08 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.6 |  | °C
| Minimum Generation of the Day |  |  | 10305.87 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1006.13 |  | MMCFD
| Maximum Generation of the Day |  |  | 14219.08 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.1882 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.2617 | 0 | 7.9834 | 0 | 0 | 0.19174 | 0 | 0 | 48.4368 | Gas | 135.9905 | Gas | 493003736.8941
| Chattogram Zone |  |  | 3.6883 | 26.4273 | 5.5929 | 0 | 0.92264 | 0.10661 | 0 | 0.51216 | 37.2499 | Coal | 85.7337 | Coal | 566298481.0875
| Cumilla Zone |  |  | 27.8617 | 0 | 9.0938 | 0 | 0 | 0.39476 | 0.87648 | 0 | 38.2268 | HFO | 26.1581 | HFO | 493593022.106
| Mymensingh Zone |  |  | 0 | 0 | 3.1813 | 0 | 0 | 0.26727 | 0 | 0 | 3.4486 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0394 | Hydro | 0.92264 | Hydro | 92264
| Khulna Zone |  |  | 4.8715 | 20.9527 | 0.15888 | 0 | 0 | 0.54648 | 22.1425 | 0 | 48.6722 | Solar | 3.111 | Solar | 49183079.712
| Barishal Zone |  |  | 7.8148 | 34.5537 | 0 | 0 | 0 | 0.004533 | 0 | 0 | 42.373 | Import | 45.6858 | Import | 235132233.35
| Rajshahi Zone |  |  | 16.4531 | 0 | 0 | 0 | 0 | 0.9296 | 22.6668 | 0 | 40.0495 | Wind | 0.51216 | Wind | 7498022.4
| Rangpur Zone |  |  | 0 | 3.8 | 0.14779 | 0 | 0 | 0.66999 | 0 | 0 | 4.6178
| Total |  |  | 135.9905 | 85.7337 | 26.1581 | 0 | 0.92264 | 3.111 | 45.6858 | 0.51216 | 298.1139
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 493003736.8941 |  | Hydro | 92264
|  |  |  | Coal | 566298481.0875 |  | Solar | 49183079.712
|  |  |  | HFO | 493593022.106 |  | Import | 235132233.35
|  |  |  | HSD | 0 |  | Wind | 7498022.4
[5 empty] | Total: | 184,48,00,839 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1425 | Peak Hr Flow | 876.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45787781.93 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.6668 | Peak Hr Flow | 1416.08 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 764 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.87648 | Peak Hr Flow | 36.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1098 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.6858 | Peak Hr Flow | 2328.08 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5298
|  |  |  | Chattogram |  | 0 |  | 1426
|  |  |  | Cumilla |  | 0 |  | 1294
|  |  |  | Mymensingh |  | 0 |  | 1067
|  |  |  | Sylhet |  | 0 |  | 583
|  |  |  | Khulna |  | 0 |  | 1545
|  |  |  | Barishal |  | 0 |  | 498
|  |  |  | Rajshahi |  | 0 |  | 1277
|  |  |  | Rangpur |  | 0 |  | 718
|  |  |  | Total |  | 0 |  | 13706
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 735.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:28 | 11:37 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to Shutdown Proposal Due to T1
Transformer 33 kV B phase CT P1 terminal connector red hot.
| 08:45 | 14:29 | AKSML-Baroaulia 132kV Ckt-1 Scheduled S/D from AKS 132/33kV end Due to Akspl to Baraulia
132kv(ckt-1) line shutdown due to maintenance for Tower No. 57 .
| 08:52 | 15:26 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end.
|  | 09:07 | Gollamari 132/33kV S/S Tr-2 HT is restored.
|  | 09:10 | Gollamari 132/33kV S/S Tr-2 LT is restored.
| 09:22 | 15:55 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Project Work
|  | 09:25 | Bogura 132/33kV S/S Transformer-4 HT is restored.
|  | 09:25 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT is restored.
|  | 09:25 | Bogura 132/33kV S/S Transformer-4 LT is restored.
|  | 09:26 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT is restored.
| 09:52 | 17:40 | Hasnabad 132/33kV S/S 33kv Reserve Bus Scheduled S/D Due to 33 kv pangaon, nawabgonj -2,
lalbagh -1 bus insulator work.
| 10:10 | 10:25 | Mahasthangarh 132/33kV S/S 406T MTR1 LT Tripped showing Micom-P139 relays Due to BPBS-2
33 kv Sukanpukor Feeder Earth fault
| 10:11 |  | Dhamrai 132/33kV S/S Main Bus-1 Project Work S/D Due to Bay Extention work
| 10:35 | 14:30 | Muktagacha 132/33kV S/S T-3(424T) HT Scheduled S/D
| 10:36 | 17:16 | Madanganj 132/33kV S/S BUS Coupler Scheduled S/D Due to Red hot maintenance.
| 10:45 | 19:21 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Scheduled S/D Due to CB and isolator change by
PDB
|  | 10:57 | Ghorasal-Joydeb-B 132kV Ckt-1 is restored.
| 10:58 | 11:52 | Muktagacha 132/33kV S/S T-1(404T) HT Scheduled S/D
|  | 11:07 | BSRM 230/33kV S/S 230/33 kV Transformer-2 (125/140 MVA) HT is restored.
| 11:42 | 12:29 | BIPTC S/S 20DF12 Scheduled S/D Due to Corrective maintenance work
|  | 11:48 | Madanganj-Munsiganj 132 kV Ckt-2 is restored.
| 12:00 |  | Day peak Generation is 13200 MW
| 13:05 |  | Hathazari 230/132/33kV S/S MT-03 HT Scheduled S/D Due to 230 KV Old CB removed and New CB
Installation
| 13:05 |  | Hathazari 230/132/33kV S/S MT-03 LT Scheduled S/D Due to 230 KV Old CB removed and New CB
Installation
|  | 13:16 | Gopalganj 400/132kV S/S 400kV Bus-01 is restored.
| 13:56 | 18:42 | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
| 14:36 | 15:09 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Tripped from Brahmanbaria 132/33kV end showing
Distance Relay relays. and from Shahjibazar 132/33kV end showing Distance Relay relays
Due to Heavy Rain and Stormy Weather
| 15:06 | 15:45 | Gulshan 132/33kV S/S MT-2 LT Forced S/D
| 15:07 | 15:43 | Gulshan 132/33kV S/S MT-2 HT Forced S/D
| 15:14 | 16:14 | Bogura 132/33kV S/S Transformer-3 LT Forced S/D Due to banani 33kv nesco work | [7 empty] | 23.0MW load
interrup.
| 15:15 | 16:14 | Bogura 132/33kV S/S Transformer-3 HT Forced S/D Due to banani 33kv nesco work
| 15:27 | 15:44 | Jamalpur 132/33kV S/S T-3 HT Tripped showing Micom p132 relays Due to Bird fall in 33 kv | [7 empty] | 15.0MW load
|  |  | R & B phase | [7 empty] | interrup.
| 15:27 | 15:44 | Jamalpur 132/33kV S/S T-3 LT Tripped showing Micom p132 relays Due to Bird fall in 33 kv | [7 empty] | 15.0MW load
|  |  | R& B phase | [7 empty] | interrup.
|  | 15:29 | Chowmuhani 132/33kV S/S TR2 is restored.
|  | 16:28 | Haripur-Narsingdi 132kV Ckt-1 is restored.
|  | 18:26 | Tongi 230/132/33kV S/S Tongi-Uttara Ckt is restored.
| 18:27 | 22:18 | Barishal(N)-Madaripur 132 kV Ckt-2 Forced S/D from Barishal 230/132kV end Due to Taken by
ALDC
| 19:10 | 21:26 | Kushtia 132/33kV S/S T-3 LT Tripped showing O/C DMT, E/F DMT relays Due to 33kv Gangni,
Bamundi, Khoksha Feeder Trip
| 19:30 |  | Evening peak generation 14219 MW
| 20:25 | 21:25 | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to Bus Section-3 auxillary transformer post | [7 empty] | 60.0MW load
|  |  | insulator crak | [7 empty] | interrup.
| 20:30 | 22:18 | Barishal(N)-Madaripur 132 kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to 132
kV Madaripur-Barishal(N) CKT-2 due to Line DS problem.
| 21:21 | 22:12 | Rajbari 132/33kV S/S Bheramara-2 Tripped showing Distance, 86.1&86.2 relays Due to 3
phase fault.
| 21:42 | 23:18 | Jamalpur 132/33kV S/S T-2 HT Tripped showing Micom 132 relays Due to 33kv Jamuna feeder | [7 empty] | 20.0MW load
|  |  | loop disconnected by flashing | [7 empty] | interrup.
| 21:42 | 23:17 | Jamalpur 132/33kV S/S T-1 LT Tripped showing Micom 132 relays Due to 33kv Jamuna feeder | [7 empty] | 20.0MW load
|  |  | loop disconnected by flashing | [7 empty] | interrup.
| 22:39 | 00:13 | Mongla 132/33kV S/S T-1 LT Tripped showing O/C relays Due to 33kv Seven Cercle Feeder | [7 empty] | 11.0MW load
|  |  | fault | [7 empty] | interrup.
| 22:39 | 00:13 | Mongla 132/33kV S/S T-1 LT Tripped showing O/C relays Due to 33kv Seven Cercle Feeder | [7 empty] | 11.0MW load
|  |  | fault | [7 empty] | interrup.
| 22:39 | 00:13 | Mongla 132/33kV S/S T-1 LT Tripped showing O/C relays Due to 33kv Seven Cercle Feeder | [7 empty] | 11.0MW load
|  |  | fault | [7 empty] | interrup.
| 23:02 | 00:20 | Fenchuganj 230/132/33kV S/S TR-02 LT Scheduled S/D Due to According to application of pbs | [7 empty] | 15.0MW load
|  |  | 33 kv rajnogor feeder authority for red hot of 33kv load side | [7 empty] | interrup.
| 23:07 | 00:17 | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to For pbs rajnogor 33 kv load | [7 empty] | 15.0MW load
|  |  | side red hot problem | [7 empty] | interrup.
|  | 00:14 | Rampal 400/230kV S/S Gopalganj Line-1 Reactor is restored.
| 03:03 | 05:07 | Chandina 132/33kV S/S TR-3 HT Tripped showing K86L1 lock out relay-1 K86L2 lock out | [7 empty] | 18.0MW load
|  |  | relay-2 F87T1, F87T2. relays Due to Due to cumilla pbs-01 feeder earth fault. | [7 empty] | interrup.
| 03:03 | 05:07 | Chandina 132/33kV S/S TR-3 LT Tripped showing K86L1 lock out realy optd. K86L2 lock out | [7 empty] | 18.0MW load
|  |  | relay optd. F51 TR-03 backup relay relays Due to Due to 33kv cumilla pbs-01 feeder earth | [7 empty] | interrup.
fault
| 05:40 | 06:25 | Naogaon 132/33kV S/S T-1 LT Tripped showing No relays Due to Nesco T-5 Bus DS side ( B
Phase) heavy flashing & cut off from 33 kv Bus.For that T-1 (33KV) CB off by hand. under
bus-1 & bus-2 the Badalgachi & chowmasia 33 KV feeder trip by over current.
| 05:40 | 07:12 | Naogaon 132/33kV S/S T-2 LT Tripped showing No relays Due to Nesco T-5 Bus DS side ( B
Phase) heavy flashing & cut off from 33 kv Bus.For that T-2 (33KV) CB off by hand. under
bus-1 & bus-2 the Badalgachi & chowmasia 33 KV feeder trip by over current.
| 05:40 | 06:40 | Naogaon 132/33kV S/S T-3 LT Tripped showing No relays Due to Nesco T-5 Bus DS side ( B
Phase) heavy flashing & cut off from 33 kv Bus.For that T-3 (33KV) CB off by hand.
| 06:00 |  | Minimum generation: 10232 MW
| 06:19 |  | Natore 132/33kV S/S Rajlanka Project Work S/D Due to Natore-Ishurdi ckt-2 reconducting
work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 17-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 333 | 8571600 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 8925500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 253 | 5600291 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 264 | 6883694 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 331920 | Liquid fuel shortage
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 131 | 1406880 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 548786 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 158004 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 340200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 258120 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 407520 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 66742 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 98 | 2343024 | Engine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 663360 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1054080 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 191745 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 127080 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9682272.73 | Allocation limit by Titas, instructed by DS(Gen)
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 118 | 876000 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2408 | 48436818.73
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3300000 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 1 | 51769.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 80730 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 10 | 513120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 922640 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 263454 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 78 | 872736 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 21 | 146447 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1643520 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 388320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 6 | 484800 | Engine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 25883 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 185673 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1431360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 925 | 14885453 | Unit-1 Under Start-Up
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 25 | 512160 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 559 | 11541818.18 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2023 | 37249883.98
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4769000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8650400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 8000000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 36 | 818784 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 1276320 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 45 | 853091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1084336 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 324509 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 39 | 152832 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2138590 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 2793600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 36 | 876480 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 34 | 800870 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 12 | 271190 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 108 | 2635680 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 445200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1941120 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 394764 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1628 | 38226766
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 169 | 1840800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 94 | 1134000 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 260220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 195360 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 11160 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 269 | 3448590
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 35 | 817000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 623640 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3545345 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 634368 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1797120 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 171 | 3556270 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 16 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 127560 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7366000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 303 | 8455000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7685100 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1415 | 35039403
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 876 | 22142545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 175 | 4871520 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 158880 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 546480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1010 | 20952730 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2078 | 48672155
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 295 | 7010208 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 10 | 213844 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 0 | 2367000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 22001454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5233930 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5542000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4533 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2002 | 42372969.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 168 | 3792909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4176145 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 8484072 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | Engine Problem
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 28560 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1416.08 | 22666765 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 343496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 557542 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2131.08 | 40049489
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3800000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 91776 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 32020.2 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 56016 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 93970 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 544000 | -
Rangpur Area Total |  |  |  |  | 950 | 265 | 4617782.2
Eastern Grid Total |  |  |  |  | 16921.242 | 7743 | 162401461.71
Western Grid Total |  |  |  |  | 11702.84 | 6476.08 | 135712395.75
National Grid Total |  |  |  |  | 28624.082 | 14219.08 | 298113857.46
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 17-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9668.48 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4037.8 | MW
i) Dhaka area |  |  | 5298.03 |  | MW | i) Khulna area |  |  |  | 1545 | MW
ii) Chattogram area |  |  | 1426 |  | MW | ii) Barishal area |  |  |  | 498 | MW
iii) Cumilla area |  |  | 1294.45 |  | MW | iii) Rajshahi area |  |  |  | 1276.8 | MW
iv) Mymensingh area |  |  | 1067 |  | MW | iv) Rangpur area |  |  |  | 718 | MW
v) Sylhet area |  |  | 583 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13706.28 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 81 | 19:00 | 133 | Patuakhali | 89.5 | 22:00
2 | AKSML | 139 | 16:00 | 68 | Jaldhaka | 50 | 18:00 | 134 | Payra | 38 | 00:00
3 | Aftabnagar | 62 | 15:00 | 69 | Jamalpur | 108 | 19:00 | 135 | Postogola | 60 | 13:00
4 | Agargaon | 140 | 13:00 | 70 | Jashore | 157 | 19:00 | 136 | Purbachal | 20 | 13:00
5 | Agrabad | 94 | 15:00 | 71 | Jhenaidah | 139 | 19:00 | 137 | Purbasadipur | 107 | 19:30
6 | Amnura | 31 | 19:00 | 72 | Joydebpur | 147 | 12:00 | 138 | Rahanpur | 21 | 23:00
7 | Ashuganj | 98 | 00:00 | 73 | Joypurhat | 55 | 00:00 | 139 | Rahim | 44 | 12:00
8 | BSRM | 205 | 10:00 | 74 | Juldah | 14 | 12:00 | 140 | Rajbari | 81 | 00:00
9 | Bagerhat | 92 | 22:00 | 75 | KSRM | 22 | 00:00 | 141 | Rajendrapur | 130 | 19:30
10 | Bajitpur | 50 | 21:00 | 76 | Kabirpur | 287 | 19:00 | 142 | Rajshahi | 108 | 15:00
11 | Bakulia | 117 | 16:00 | 77 | Kachua | 96 | 00:00 | 143 | Rajshahi-230 | 81 | 13:00
12 | Banani | 52 | 16:00 | 78 | Kallyanpur | 105 | 13:00 | 144 | Ramganj | 118 | 23:00
13 | Bangabhaban | 17 | 11:00 | 79 | Kalurghat | 36 | 09:00 | 145 | Rampur | 45 | 00:00
14 | Barapukuria | 54 | 19:00 | 80 | Kamrangirchar | 65 | 12:00 | 146 | Rangamati | 16 | 13:00
15 | Barguna | 24 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 127 | 19:00
16 | Barishal | 119 | 23:00 | 82 | Kasba | 35 | 21:00 | 148 | Ruppur | 5 | 12:00
17 | Barishal-230 | 100 | 19:00 | 83 | Kazla | 100 | 13:00 | 149 | SSM | 10 | 23:00
18 | Baroaulia | 72 | 16:00 | 84 | Keranigonj | 85 | 17:00 | 150 | Saidpur | 93 | 18:30
19 | Baroirhat | 68 | 22:00 | 85 | Khagrachori | 28 | 00:00 | 151 | Satkhira | 154 | 21:00
20 | Bashundhara | 197 | 13:00 | 86 | Khulna | 88 | 13:00 | 152 | Satmasjid | 116 | 13:00
21 | BashundharaCement | 8 | 11:00 | 87 | Khulshi | 201 | 16:00 | 153 | Savar | 234 | 16:00
22 | Beanibazar | 77 | 19:00 | 88 | Kishoreganj | 126 | 21:00 | 154 | SevenRings | 21.21 | 15:00
23 | Benapole | 74 | 20:00 | 89 | Kodda | 306 | 18:30 | 155 | ShahCement | 34 | 02:00
24 | Bhaluka | 156 | 19:30 | 90 | Kulaura | 48 | 00:00 | 156 | Shahjadpur | 81 | 19:30
25 | Bhandaria | 91 | 02:00 | 91 | Kurigram | 53 | 19:00 | 157 | Shahjibazar | 113 | 21:00
26 | Bhangura | 32 | 19:30 | 92 | Kushtia | 152 | 14:00 | 158 | Shahmirpur | 55 | 17:00
27 | Bheramara(GK) | 60 | 01:00 | 93 | Lalbag | 80 | 11:00 | 159 | Shariatpur | 98 | 02:00
28 | Bhulta | 233 | 21:00 | 94 | Lalmonirhat | 52 | 19:00 | 160 | Sherpur | 120 | 19:00
29 | Bog-Sherpur | 60 | 19:30 | 95 | MI_Cement | 12.3 | 02:00 | 161 | Shikalbaha | 32 | 17:00
30 | Bogura | 155 | 20:00 | 96 | Madanganj | 42 | 20:00 | 162 | Shitalakhya | 92 | 15:00
31 | Borhanuddin | 105 | 00:00 | 97 | Madaripur | 120 | 21:00 | 163 | Sholosohor | 51 | 15:00
32 | Brahmanbaria | 128 | 00:00 | 98 | Madartek | 84.02 | 13:00 | 164 | Shyampur | 186 | 12:00
33 | Cantonment | 156 | 13:00 | 99 | Madunaghat | 60 | 19:00 | 165 | Siddhirganj | 125 | 15:00
34 | Chandina | 22.16 | 01:00 | 100 | Magura | 69 | 19:30 | 166 | Sirajganj | 106 | 20:00
35 | Chandpur | 76 | 23:00 | 101 | Mahasthangarh | 66 | 00:00 | 167 | Sonargaon | 108 | 21:00
36 | Chandraghona | 36 | 19:00 | 102 | Manikganj | 132 | 19:30 | 168 | Sreemongol | 79 | 19:00
37 | Chapai | 68 | 00:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 109 | 12:00
38 | Charsaidpur | 46 | 06:00 | 104 | Matarbari | 52 | 19:30 | 170 | Srinagar | 49.56 | 22:00
39 | Chauddagram | 74 | 00:00 | 105 | Matuail | 72 | 15:00 | 171 | Sunamganj | 57 | 19:00
40 | Chhatak | 36 | 19:30 | 106 | Millgate | 120 | 12:00 | 172 | Sylhet | 48 | 23:00
41 | Chowmuhani | 235 | 19:00 | 107 | Mirpur | 131 | 15:00 | 173 | Sylhet-132 | 118 | 13:00
42 | Chuadanga | 121 | 00:00 | 108 | Mirsorai | 11 | 15:00 | 174 | TK | 34.5 | 00:00
43 | Coxsbazar | 139 | 19:30 | 109 | Mirzapur | 41 | 19:30 | 175 | Tangail | 159 | 20:00
44 | Cumilla(N) | 151 | 15:00 | 110 | Mithapukur | 48 | 19:30 | 176 | Thakurgaon | 73 | 19:30
45 | Cumilla(S) | 173 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 104 | 11:00
46 | Daudkandi | 142 | 19:30 | 112 | Mogbazar | 169.1 | 15:00 | 178 | Ullahpara | 45 | 20:00
47 | Dhaka | 88 | 12:00 | 113 | Mongla | 55 | 22:00 | 179 | Ullon | 48 | 00:00
48 | Dhamrai | 136 | 21:00 | 114 | Motijheel | 23 | 14:00 | 180 | Uttara | 91 | 13:00
49 | Dhanmondi | 168 | 13:00 | 115 | Muktagacha | 31 | 20:00 | 181 | UttaraNew | 60 | 13:00
50 | Dohazari | 109 | 23:00 | 116 | Munshiganj | 121 | 20:00 | 182 | Zigatola | 78 | 15:00
51 | Faridpur | 153 | 01:00 | 117 | Muradnagar | 33 | 20:00
52 | Fatullah | 103 | 16:00 | 118 | Mymensingh | 190 | 20:00
53 | Fenchuganj | 39 | 00:00 | 119 | Naogaon | 114 | 20:00
54 | Feni | 124 | 15:00 | 120 | Narail | 66 | 19:30
55 | GPH | 93 | 14:00 | 121 | Narinda | 74 | 13:00
56 | Ghatail | 68 | 19:00 | 122 | Narshingdi | 182 | 20:00
57 | Ghorashal | 17 | 13:00 | 123 | Natore | 139 | 19:30
58 | Ghorashal-230 | 75 | 10:00 | 124 | Nawabganj | 56 | 21:00
59 | Goalpara | 42 | 19:30 | 125 | Netrakona | 99 | 18:30
60 | Gollamari | 100 | 19:30 | 126 | New | 88 | 12:00
61 | Gopalganj | 114.2 | 21:00 | 127 | Niamatpur | 58 | 19:30
62 | Gulshan | 134 | 13:00 | 128 | Noapara | 55 | 07:00
63 | Halishahar | 87.5 | 11:00 | 129 | PHP | 8 | 01:00
64 | HaripurSBU | 181 | 09:00 | 130 | Pabna | 115 | 18:30
65 | Hasnabad | 84 | 16:00 | 131 | Palashbari | 100 | 19:00
66 | Hathazari | 85 | 14:00 | 132 | Panchagarh | 54 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 17-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12534.09 | 0 |  | 12534.09
1:00 | 12329.92 | 0 |  | 12329.92
2:00 | 11534.58 | 0 |  | 11534.58
3:00 | 11360.88 | 0 |  | 11360.88
4:00 | 11219.97 | 0 |  | 11219.97
5:00 | 10803.11 | 0 |  | 10803.11
6:00 | 10305.87 | 0 |  | 10305.87
7:00 | 10332.74 | 0 |  | 10332.74
8:00 | 10716.53 | 0 |  | 10716.53
9:00 | 11545.17 | 0 |  | 11545.17
10:00 | 11999.38 | 0 |  | 11999.38
11:00 | 12472.41 | 0 |  | 12472.41
12:00 | 13204.68 | 0 |  | 13204.68
13:00 | 13653.69 | 0 |  | 13653.69
14:00 | 13602.38 | 0 |  | 13602.38
15:00 | 13493.22 | 0 |  | 13493.22
16:00 | 13098.3 | 0 |  | 13098.3
17:00 | 12941.48 | 0 |  | 12941.48
18:00 | 12730.27 | 0 |  | 12730.27
19:00 | 13914.42 | 0 |  | 13914.42
19:30 | 14219.08 | 0 |  | 14219.08
20:00 | 13822.37 | 0 |  | 13822.37
21:00 | 13415.5 | 0 |  | 13415.5
22:00 | 12348.5 | 0 |  | 12348.5
23:00 | 11599.5 | 0 |  | 11599.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 17-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6696.2 | 5837.89 | 12534.09 | DAILY GENERATION CURVE
00:30 | 6561.7 | 5870.305 | 12432.005
01:00 | 6427.2 | 5902.72 | 12329.92 | 17-05-2025
01:30 | 6249.2 | 5683.05 | 11932.25
02:00 | 6071.2 | 5463.38 | 11534.58
02:30 | 6081.2 | 5366.53 | 11447.73
03:00 | 6091.2 | 5269.68 | 11360.88
03:30 | 6100.7 | 5189.725 | 11290.425
04:00 | 6110.2 | 5109.77 | 11219.97
04:30 | 5973.2 | 5038.34 | 11011.54
05:00 | 5836.2 | 4966.91 | 10803.11
05:30 | 5657.87 | 4896.62 | 10554.49
06:00 | 5479.54 | 4826.33 | 10305.87
06:30 | 5477.995 | 4841.31 | 10319.305
07:00 | 5476.45 | 4856.29 | 10332.74
07:30 | 5617.48 | 4907.155 | 10524.635
08:00 | 5758.51 | 4958.02 | 10716.53
08:30 | 6059.475 | 5071.375 | 11130.85
09:00 | 6360.44 | 5184.73 | 11545.17
09:30 | 6578.04 | 5194.235 | 11772.275
10:00 | 6795.64 | 5203.74 | 11999.38
10:30 | 6896.38 | 5339.515 | 12235.895
11:00 | 6997.12 | 5475.29 | 12472.41
11:30 | 7131.545 | 5707 | 12838.545
12:00 | 7265.97 | 5938.71 | 13204.68
12:30 | 7296.945 | 6132.24 | 13429.185
13:00 | 7327.92 | 6325.77 | 13653.69
13:30 | 7350.305 | 6277.73 | 13628.035
14:00 | 7372.69 | 6229.69 | 13602.38
14:30 | 7355.415 | 6192.385 | 13547.8
15:00 | 7338.14 | 6155.08 | 13493.22
15:30 | 7237.57 | 6058.19 | 13295.76
16:00 | 7137 | 5961.3 | 13098.3
16:30 | 7111.765 | 5908.125 | 13019.89
17:00 | 7086.53 | 5854.95 | 12941.48
17:30 | 7069.745 | 5766.13 | 12835.875
18:00 | 7052.96 | 5677.31 | 12730.27
18:30 | 7382.98 | 5939.365 | 13322.345
19:00 | 7713 | 6201.42 | 13914.42
19:30 | 7743 | 6476.08 | 14219.08
20:00 | 7583 | 6239.37 | 13822.37
20:30 | 7519.75 | 6099.185 | 13618.935 |  | Executive Engineer
21:00 | 7456.5 | 5959 | 13415.5 |  | Network Operation Division
21:30 | 7167.5 | 5714.5 | 12882
22:00 | 6878.5 | 5470 | 12348.5
22:30 | 6795.5 | 5178.5 | 11974
23:00 | 6712.5 | 4887 | 11599.5

## En-Curve
QF-LDC-12
Date | 17-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3749 | 2008 | 923 | 0 | 52 | 1008.89 | 40 | 3752 | 0 | 197 | 793.2 | 0 | 0 | 11 | 0 | DAILY ENERGY CURVE
00:30 | 3688 | 1952.5 | 922.5 | 0 | 50 | 1013.805 | 40 | 3807.5 | 0 | 172 | 772.2 | 0 | 0 | 13.5 | 0 | 17-05-2025
01:00 | 3627 | 1897 | 922 | 0 | 48 | 1018.72 | 40 | 3863 | 0 | 147 | 751.2 | 0 | 0 | 16 | 0
01:30 | 3550 | 1802 | 922 | 0 | 47 | 925.05 | 40 | 3769 | 0 | 129.5 | 731.2 | 0 | 0 | 16.5 | 0 | Energy Generated | 298.1139 |  | MKWHr
02:00 | 3473 | 1707 | 922 | 0 | 46 | 831.38 | 40 | 3675 | 0 | 112 | 711.2 | 0 | 0 | 17 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 3488.5 | 1724.5 | 922.5 | 0 | 45 | 831.53 | 40 | 3566.5 | 0 | 112 | 702.2 | 0 | 0 | 15 | 0 | Total Energy Requirement | 298.1139 |  | MKWHr
03:00 | 3504 | 1742 | 923 | 0 | 44 | 831.68 | 40 | 3458 | 0 | 112 | 693.2 | 0 | 0 | 13 | 0
03:30 | 3526.5 | 1827.5 | 922.5 | 0 | 43 | 828.225 | 40 | 3318.5 | 0 | 112 | 661.2 | 0 | 0 | 11 | 0
04:00 | 3549 | 1913 | 922 | 0 | 42 | 824.77 | 40 | 3179 | 0 | 112 | 629.2 | 0 | 0 | 9 | 0
04:30 | 3534.5 | 1901 | 922.5 | 0 | 42 | 823.325 | 38.5 | 3114 | 0.015 | 56 | 562.7 | 0 | 0 | 17 | 0
05:00 | 3520 | 1889 | 923 | 0 | 42 | 821.88 | 37 | 3049 | 0.03 | 0 | 496.2 | 0 | 0 | 25 | 0
05:30 | 3529.5 | 1784.5 | 923.5 | 0 | 41 | 823.685 | 37 | 2907.5 | 13.105 | 0 | 472.2 | 0 | 0 | 22.5 | 0
06:00 | 3539 | 1680 | 924 | 0 | 40 | 825.49 | 37 | 2766 | 26.18 | 0 | 448.2 | 0 | 0 | 20 | 0
06:30 | 3503.5 | 1670.5 | 923.5 | 0 | 38 | 825.705 | 37 | 2753.5 | 59.9 | 32.5 | 462.7 | 0 | 0 | 12.5 | 0
07:00 | 3468 | 1661 | 923 | 0 | 36 | 825.92 | 37 | 2741 | 93.62 | 65 | 477.2 | 0 | 0 | 5 | 0
07:30 | 3552.5 | 1706 | 899.5 | 0 | 36 | 825.96 | 36 | 2756 | 148.575 | 69 | 487.6 | 0 | 0 | 7.5 | 0
08:00 | 3637 | 1751 | 876 | 0 | 36 | 826 | 35 | 2771 | 203.53 | 73 | 498 | 0 | 0 | 10 | 0
08:30 | 3673.5 | 1832.5 | 876 | 0 | 35 | 826.5 | 35 | 2875 | 291.85 | 99 | 575.5 | 0 | 0 | 11 | 0
09:00 | 3710 | 1914 | 876 | 0 | 34 | 827 | 35 | 2979 | 380.17 | 125 | 653 | 0 | 0 | 12 | 0
09:30 | 3727.5 | 1998.5 | 899.5 | 0 | 35 | 826 | 35 | 3003.5 | 382.275 | 146.5 | 708.5 | 0 | 0 | 10 | 0
10:00 | 3745 | 2083 | 923 | 0 | 36 | 825 | 35 | 3028 | 384.38 | 168 | 764 | 0 | 0 | 8 | 0
10:30 | 3764 | 2112.25 | 923.5 | 0 | 36 | 823 | 35 | 3212.5 | 361.145 | 168 | 796 | 0 | 0 | 4.5 | 0
11:00 | 3783 | 2141.5 | 924 | 0 | 36 | 821 | 35 | 3397 | 337.91 | 168 | 828 | 0 | 0 | 1 | 0
11:30 | 3776.5 | 2132 | 924 | 0 | 37 | 873 | 35 | 3565.5 | 384.545 | 176.5 | 933.5 | 0 | 0 | 1 | 0
12:00 | 3770 | 2122.5 | 924 | 0 | 38 | 925 | 35 | 3734 | 431.18 | 185 | 1039 | 0 | 0 | 1 | 0
12:30 | 3743.5 | 2084.25 | 924 | 0 | 39 | 1005.5 | 35 | 3870.5 | 371.935 | 189 | 1158 | 0 | 0 | 8.5 | 0
13:00 | 3717 | 2046 | 924 | 0 | 40 | 1086 | 35 | 4007 | 312.69 | 193 | 1277 | 0 | 0 | 16 | 0
13:30 | 3716 | 1991 | 924 | 0 | 40 | 1071 | 37.5 | 3932.5 | 378.035 | 198 | 1307 | 0 | 0 | 33 | 0
14:00 | 3715 | 1936 | 924 | 0 | 40 | 1056 | 40 | 3858 | 443.38 | 203 | 1337 | 0 | 0 | 50 | 0
14:30 | 3764.5 | 1946.5 | 923.5 | 0 | 40 | 1060.23 | 40 | 3877.5 | 340.07 | 178.5 | 1320.5 | 0 | 0 | 56.5 | 0
15:00 | 3814 | 1957 | 923 | 0 | 40 | 1064.46 | 40 | 3897 | 236.76 | 154 | 1304 | 0 | 0 | 63 | 0
15:30 | 3766.5 | 1950.5 | 923.5 | 0 | 36 | 1039.055 | 40 | 3846.5 | 219.205 | 174 | 1241.5 | 0 | 0 | 59 | 0
16:00 | 3719 | 1944 | 924 | 0 | 32 | 1013.65 | 40 | 3796 | 201.65 | 194 | 1179 | 0 | 0 | 55 | 0
16:30 | 3679.5 | 1930 | 924 | 0 | 27 | 1020.545 | 40 | 3831 | 148.845 | 224.5 | 1141.5 | 0 | 0 | 53 | 0
17:00 | 3640 | 1916 | 924 | 0 | 22 | 1027.44 | 40 | 3866 | 96.04 | 255 | 1104 | 0 | 0 | 51 | 0
17:30 | 3684.5 | 1886.25 | 924 | 0 | 17 | 999.87 | 40 | 3855 | 56.255 | 291 | 1039.5 | 0 | 0 | 42.5 | 0
18:00 | 3729 | 1856.5 | 924 | 0 | 12 | 972.3 | 40 | 3844 | 16.47 | 327 | 975 | 0 | 0 | 34 | 0
18:30 | 3777 | 1972.75 | 923.5 | 0 | 21 | 1119.86 | 40 | 3956 | 8.235 | 375.5 | 1094.5 | 0 | 0 | 34 | 0
19:00 | 3825 | 2089 | 923 | 0 | 30 | 1267.42 | 40 | 4068 | 0 | 424 | 1214 | 0 | 0 | 34 | 0
19:30 | 3528 | 2015 | 876 | 0 | 36 | 1416.08 | 40 | 4426 | 0 | 455 | 1402 | 0 | 0 | 25 | 0
20:00 | 3591 | 1947 | 876 | 0 | 36 | 1291.37 | 40 | 4309 | 0 | 436 | 1267 | 0 | 0 | 29 | 0
20:30 | 3650.5 | 2034.75 | 900 | 0 | 36 | 1173.185 | 40 | 4169.5 | 0 | 425.5 | 1165 | 0 | 0 | 24.5 | 0
21:00 | 3710 | 2122.5 | 924 | 0 | 36 | 1055 | 40 | 4030 | 0 | 415 | 1063 | 0 | 0 | 20 | 0
21:30 | 3707.5 | 2115 | 924 | 0 | 37 | 939.5 | 40 | 3832.5 | 0 | 356.5 | 914.5 | 0 | 0 | 15.5 | 0
22:00 | 3705 | 2107.5 | 924 | 0 | 38 | 824 | 40 | 3635 | 0 | 298 | 766 | 0 | 0 | 11 | 0
22:30 | 3677 | 2117.5 | 924 | 0 | 38 | 824 | 40 | 3368.5 | 0 | 247.5 | 724.5 | 0 | 0 | 13 | 0
23:00 | 3649 | 2127.5 | 924 | 0 | 38 | 824 | 40 | 3102 | 0 | 197 | 683 | 0 | 0 | 15 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 17-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 04:00 | 367 | 12:00 | Payra | 414 | 07:00 | 407 | 01:00
Ashuganj | N/A | N/A | N/A | N/A | Rahanpur | 417 | 02:00 | 398 | 19:30
Bhulta | 404 | 06:00 | 366 | 12:00 | Rampal | 400 | 23:00 | 385 | 13:00
Bibiana | 394 | 05:00 | 385 | 12:00
BIPTC | 402 | 08:00 | 391 | 00:00
Bogura | 409 | 02:00 | 386 | 19:00
Gopalganj | 394 | 07:00 | 381 | 13:00
Kaliakoir | 375 | 22:00 | 262 | 16:00
Madunaghat | 391 | 23:00 | 383 | 01:00
Meghnaghat | 386 | 07:00 | 371 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 225 | 07:00 | 212 | 12:00 | Keranigonj | 223 | 07:00 | 210 | 15:00
AKSML | 228 | 19:30 | 221 | 01:00 | Khulna(S) | 232 | 23:00 | 216 | 00:00
Aminbazar | 225 | 04:00 | 214 | 11:00 | Madunaghat | 231 | 22:00 | 224 | 01:00
Ashuganj | 234 | 05:00 | 220 | 10:00 | Madunaghat-400 | 231 | 23:00 | 226 | 01:00
Ashuganj-400 | 229 | 07:00 | 221 | 11:00 | Maniknagar | 221 | 07:00 | 210 | 15:00
Baghabari | 237 | 06:00 | 226 | 12:00 | Meghnaghat | 228 | 07:00 | 220 | 11:00
Barapukuria | 231 | 01:00 | 218 | 19:00 | Meghnaghat-400 | 223 | 07:00 | 214 | 15:00
Barapukuria-230 | 231 | 01:00 | 218 | 19:00 | Mirsorai | 224 | 07:00 | 219 | 00:00
Barishal | 236 | 09:00 | 226 | 19:00 | Rajshahi | 235 | 05:00 | 222 | 12:00
Bheramara | 234 | 21:00 | 221 | 12:00 | Rampal | 231 | 22:00 | 216 | 00:00
Bhulta | 235 | 06:00 | 210 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 07:00 | 218 | 13:00 | Rampura | 234 | 06:00 | 207 | 11:00
BIPTC | 237 | 21:00 | 222 | 12:00 | Shikalbaha | 227 | 09:00 | 223 | 00:00
Bogura | 239 | 01:00 | 223 | 19:00 | Shyampur | 222 | 07:00 | 212 | 12:00
Bogura-400 | 240 | 01:00 | 223 | 19:00 | Siddhirganj | 222 | 07:00 | 213 | 12:00
Borhanuddin | 242 | 20:00 | 232 | 22:00 | Sirajgonj | 241 | 06:00 | 233 | 12:00
BSRM | 226 | 07:00 | 218 | 00:00 | Sreepur | 232 | 06:00 | 220 | 12:00
Cumilla(N) | 222 | 07:00 | 213 | 15:00 | Tongi | 228 | 06:00 | 215 | 07:00
Faridpur | 231 | 07:00 | 222 | 19:00
Fenchuganj | 229 | 06:00 | 221 | 14:00
Ghorashal | 230 | 08:00 | 220 | 11:00
Ghorashal-230 | 234 | 06:00 | 212 | 10:00
Gopalganj | 233 | 07:00 | 224 | 19:30
GPH | 227 | 07:00 | 222 | 01:00
Haripur | 221 | 07:00 | 212 | 15:00
Hasnabad | 222 | 06:00 | 211 | 11:00
Hathazari | 231 | 22:00 | 224 | 00:00
Ishurdi | 236 | 06:00 | 224 | 12:00
Jhenaidah | 233 | 22:00 | 216 | 00:00
Kaliakoir | 231 | 05:00 | 217 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 05:00 | 127 | 09:00 | Madartek | 139 | 04:00 | 126 | 09:00
Agargaon | 136 | 07:00 | 125 | 12:00 | Madunaghat | 130 | 13:00 | 126 | 00:00
Agrabad | 131 | 22:00 | 126 | 00:00 | Magura | 140 | 21:00 | 124 | 00:00
AKS | 129 | 00:00 | 125 | 01:00 | Mahasthangarh | 140 | 03:00 | 128 | 19:00
Aminbazar | 132 | 04:00 | 124 | 11:00 | Manikganj | 132 | 03:00 | 120 | 12:00
Amnura | 137 | 02:00 | 128 | 19:00 | Maniknagar | 134 | 07:00 | 126 | 13:00
Ashuganj | 139 | 06:00 | 133 | 10:00 | Matarbari | 125 | 10:00 | 106 | 00:00
Bagerhat | 139 | 23:00 | 116 | 00:00 | Matuail | 128.7 | 07:00 | 123 | 13:00
Bajitpur | 134 | 06:00 | 126 | 00:00 | Millgate | 158 | 17:00 | 123 | 12:00
Bakulia | 132 | 14:00 | 127 | 00:00 | Mirpur | 132 | 07:00 | 122 | 12:00
Banani | 141 | 06:00 | 125 | 09:00 | Mirzapur | 136 | 04:00 | 127 | 12:00
Bangabhaban | 134 | 07:00 | 125 | 15:00 | Mithapukur | 137 | 02:00 | 125 | 18:00
Barapukuria | 142 | 01:00 | 126 | 18:00 | MI_Cement | 129 | 06:00 | 122.5 | 15:00
Barguna | 133 | 08:00 | 129 | 00:00 | Modern | 0 | 0:00 | 0 | 0:00
Barishal | 130 | 10:00 | 122 | 19:00 | Mogbazar | 142 | 05:00 | 125 | 09:00
Barishal-230 | 130 | 07:00 | 123 | 19:00 | Mongla | 139 | 23:00 | 117 | 00:00
Baroaulia | 132 | 23:00 | 128 | 00:00 | Motijheel | 134 | 07:00 | 125 | 15:00
Baroirhat | 130 | 17:00 | 119 | 00:00 | Muktagacha | 137 | 00:00 | 129 | 15:00
Bashundhara | 140 | 05:00 | 123 | 12:00 | Munshiganj | 126 | 00:00 | 122 | 11:00
BashundharaCement | 128 | 04:00 | 122 | 15:00 | Muradnagar | 127 | 07:00 | 118 | 15:00
Beanibazar | 133 | 04:00 | 125 | 19:00 | Mymensingh | 136 | 00:00 | 117 | 19:00
Benapole | 136 | 23:00 | 115 | 00:00 | Naogaon | 141 | 01:00 | 128 | 19:00
Bhaluka | 133 | 05:00 | 123 | 12:00 | Narail | 140 | 21:00 | 123 | 00:00
Bhandaria | 125 | 09:00 | 108 | 22:00 | Narinda | 134 | 07:00 | 126 | 13:00
Bhangura | 137 | 06:00 | 129 | 12:00 | Narshingdi | 132 | 05:00 | 113 | 13:00
Bheramara | 139 | 21:00 | 132 | 00:00 | Natore | 138 | 05:00 | 128 | 19:00
Bheramara(GK) | 138 | 20:00 | 131 | 00:00 | Nawabganj | 133 | 06:00 | 124 | 12:00
Bhulta | 121 | 07:00 | 116 | 21:00 | Netrakona | 128 | 21:00 | 116 | 11:00
Bog-Sherpur | 139 | 00:00 | 128 | 19:00 | New | 137 | 04:00 | 124 | 12:00
Bogura | 141 | 02:00 | 131 | 19:00 | Niamatpur | 139 | 06:00 | 132 | 19:30
Bogura-230 | 142 | 01:00 | 132 | 19:00 | Noapara | 138 | 23:00 | 119 | 00:00
Brahmanbaria | 135 | 06:00 | 120 | 12:00 | Pabna | 137 | 06:00 | 129 | 12:00
Cantonment | 136 | 07:00 | 125 | 12:00 | Palashbari | 137 | 02:00 | 123 | 19:00
Chandina | 129 | 07:00 | 122 | 15:00 | Panchagarh | 136 | 01:00 | 121 | 14:00
Chandpur | 130 | 08:00 | 120 | 00:00 | Patuakhali | 134 | 09:00 | 129 | 21:00
Chandraghona | 130 | 07:00 | 127 | 00:00 | Payra | 136 | 07:00 | 132 | 00:00
Chapai | 137 | 02:00 | 128 | 19:00 | PHP | 126 | 09:00 | 116 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 07:00 | 123 | 13:00 | Postogola | 133 | 02:00 | 126 | 12:00
Chauddagram | 127 | 08:00 | 117 | 00:00 | Purbachal | 140 | 05:00 | 125 | 09:00
Chhatak | 132 | 05:00 | 122 | 19:00 | Purbasadipur | 135 | 00:00 | 120 | 13:00
Chowmuhani | 124 | 08:00 | 111 | 00:00 | Rahanpur | 139 | 02:00 | 132 | 19:00
Chuadanga | 141 | 21:00 | 122 | 00:00 | Rahanpur-400 | 140 | 02:00 | 133 | 19:00
Coxsbazar | 122 | 07:00 | 107 | 00:00 | Rahim | 131 | 03:00 | 123 | 13:00
Cumilla(N) | 129 | 07:00 | 121 | 15:00 | Rajbari | 136 | 23:00 | 127 | 01:00
Cumilla(S) | 135 | 06:00 | 120 | 15:00 | Rajendrapur | 136 | 06:00 | 123 | 13:00
Daudkandi | 125 | 06:00 | 118 | 12:00 | Rajshahi | 137 | 02:00 | 129 | 13:00
Dhaka | 140 | 04:00 | 125 | 09:00 | Rajshahi-230 | 137 | 05:00 | 1 | 00:00
Dhamrai | 139 | 07:00 | 126 | 12:00 | Ramganj | 125 | 09:00 | 112 | 00:00
Dhanmondi | 140.5 | 05:00 | 126 | 10:00 | Rampur | 130 | 10:00 | 126 | 00:00
Dohazari | 129 | 10:00 | 120 | 00:00 | Rampura | 141 | 05:00 | 125 | 09:00
Faridpur | 136 | 22:00 | 130 | 00:00 | Rangamati | 130 | 19:30 | 126 | 00:00
Fatullah | 130 | 06:00 | 123 | 15:00 | Rangpur | 135 | 02:00 | 122 | 18:00
Fenchuganj | 137 | 06:00 | 132 | 12:00 | Ruppur | 139 | 06:00 | 132 | 12:00
Feni | 126 | 09:00 | 114 | 00:00 | Saidpur | 137 | 01:00 | 122 | 18:00
Ghatail | 137 | 00:00 | 122 | 15:00 | Satkhira | 140 | 23:00 | 115 | 00:00
Ghorashal | 141 | 06:00 | 130 | 12:00 | Satmasjid | 135 | 06:00 | 124 | 13:00
Goalpara | 141 | 23:00 | 123 | 00:00 | Savar | 131 | 07:00 | 122 | 12:00
Gollamari | 139 | 22:00 | 124 | 00:00 | SevenRings | 142 | 06:00 | 130 | 10:00
Gopalganj | 138 | 23:00 | 126 | 00:00 | ShahCement | 130 | 07:00 | 123 | 13:00
Gopalganj-400 | 136 | 07:00 | 130 | 00:00 | Shahjadpur | 139 | 03:00 | 131 | 12:00
Gulshan | 140 | 05:00 | 125 | 09:00 | Shahjibazar | 136 | 06:00 | 124 | 13:00
Halishahar | 132 | 17:00 | 127 | 00:00 | Shahmirpur | 133 | 17:00 | 127 | 02:00
Haripur | 130 | 07:00 | 123 | 15:00 | Shariatpur | 135 | 23:00 | 125 | 01:00
HaripurSBU | 130 | 07:00 | 124 | 12:00 | Sherpur | 140 | 22:00 | 121 | 05:00
Hasnabad | 132 | 04:00 | 126 | 12:00 | Shikalbaha | 121 | 10:00 | 116 | 00:00
Hathazari | 134 | 22:00 | 130 | 12:00 | Shikalbaha-230 | 133 | 13:00 | 128 | 01:00
Ishurdi | 140 | 06:00 | 133 | 12:00 | Shitalakhya | 129.5 | 07:00 | 122.5 | 15:00
Jaldhaka | 137 | 01:00 | 119 | 18:00 | Sholosohor | 131 | 10:00 | 125 | 00:00
Jamalpur | 140 | 03:00 | 122 | 05:00 | Shyampur | 126 | 08:00 | 121 | 15:00
Jashore | 138 | 23:00 | 117 | 00:00 | Shyampur-230 | 130 | 07:00 | 123 | 12:00
Jhenaidah | 140 | 22:00 | 119 | 00:00 | Siddhirganj | 130 | 07:00 | 124 | 12:00
Jhenaidah-230 | 140 | 21:00 | 126 | 00:00 | Sirajganj | 138 | 00:00 | 126 | 19:00
Joydebpur | 138 | 07:00 | 125 | 18:30 | Sonargaon | 126 | 00:00 | 121 | 12:00
Joypurhat | 140 | 01:00 | 126 | 19:30 | Sreemongol | 135 | 05:00 | 126 | 12:00
Juldah | 132 | 18:00 | 128 | 00:00 | Sreepur | 133 | 06:00 | 127 | 19:00
Kabirpur | 137 | 07:00 | 120 | 12:00 | Srinagar | 133 | 06:00 | 124 | 12:00
Kachua | 128 | 08:00 | 118 | 00:00 | SSM | 134 | 22:00 | 132 | 00:00
Kaliakoir | 139 | 04:00 | 130 | 12:00 | Sunamganj | 130 | 02:00 | 122 | 19:00
Kallyanpur | 133 | 07:00 | 123 | 12:00 | Sylhet | 133 | 03:00 | 127 | 00:00
Kalurghat | 129 | 13:00 | 126 | 00:00 | Sylhet-132 | 132 | 03:00 | 128 | 00:00
Kamrangirchar | 132 | 06:00 | 123 | 12:00 | Tangail | 134 | 00:00 | 124 | 12:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 138 | 01:00 | 123 | 14:00
Kasba | 127 | 07:00 | 118 | 15:00 | TK | 129 | 11:00 | 127 | 00:00
Kazla | 133 | 07:00 | 125 | 13:00 | Tongi | 137 | 06:00 | 128 | 11:00
Keranigonj | 134 | 07:00 | 125 | 12:00 | Ullahpara | 139 | 05:00 | 128 | 19:00
Khagrachori | 129 | 09:00 | 125 | 00:00 | Ullon | 140 | 05:00 | 125 | 09:00
Khulna | 140 | 23:00 | 122 | 00:00 | Uttara | 131 | 06:00 | 121 | 12:00
Khulna(S) | 139 | 23:00 | 125 | 00:00 | UttaraNew | 131 | 05:00 | 122 | 12:00
Khulshi | 129 | 09:00 | 125 | 00:00 | Zigatola | 134 | 22:00 | 123 | 13:00
Kishoreganj | 132 | 05:00 | 123 | 16:00
Kodda | 136 | 06:00 | 123 | 14:00
KSRM | 132 | 17:00 | 128 | 00:00
Kulaura | 136 | 07:00 | 130 | 13:00
Kurigram | 134 | 03:00 | 118 | 18:00
Kushtia | 139 | 21:00 | 125 | 00:00
Lalbag | 133 | 04:00 | 123 | 12:00
Lalmonirhat | 133 | 03:00 | 120 | 19:00
Madanganj | 128 | 04:00 | 122 | 15:00
Madaripur | 136 | 23:00 | 128 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division