## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 18-05-2025 | [28 empty] | Date: | 18-05-2025 | [28 empty] | Date: | 18-05-2025 | [28 empty] | Date: | 18-05-2025 | [28 empty] | Date: | 18-05-2025 | [16 empty] | Date: | 18-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 17 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 274 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 16.8 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 9 | 34 | 78 | 0 | 100 | 48 | 0 | 40 | 0 | 22 | 260 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 5 | 0 | 8 | 0 | 353 | 330 | 47 | 182 | 36 | 92 | 90 | 120 | 13 | 6 | 108 | 36 | 34 | 0 | 0 | 300 | 320 | 301 | 35 | 30 | 0 | 151 | 5 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 45 | 45 | 0 | 0 | 0 | 12 | 6491.8 | 923 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 105 | 220 | 0 | 179 | 838 | 0 | 5002 | 11493.8 | 76.91
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 68 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 270 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 16.8 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 3 | 34 | 78 | 0 | 100 | 36 | 0 | 40 | 0 | 22 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 5 | 0 | 8 | 0 | 355 | 330 | 5 | 183 | 5 | 50 | 90 | 17 | 9 | 6 | 17 | 20 | 0 | 0 | 0 | 295 | 320 | 300 | 34 | 30 | 0 | 134 | 0 | 0 | 11 | 30 | 0 | 18 | 169 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 5895.8 | 924 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 100 | 220 | 0 | 179 | 895 | 0 | 5044 | 10939.8 | 76.9
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 302 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 17 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 0 | 34 | 78 | 0 | 100 | 48 | 0 | 40 | 0 | 22 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710 | 0 | 5 | 0 | 8 | 0 | 354 | 330 | 5 | 202 | 5 | 16 | 90 | 17 | 9 | 14 | 17 | 30 | 0 | 0 | 0 | 305 | 320 | 332 | 34 | 30 | 0 | 131 | 0 | 0 | 11 | 20 | 0 | 18 | 170 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 5935 | 924 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 0 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 2 | 100 | 220 | 0 | 179 | 750 | 0 | 4904 | 10839 | 76.9
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 65 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 298 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 17 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 4 | 34 | 78 | 0 | 100 | 48 | 0 | 39 | 0 | 22 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 0 | 5 | 0 | 8 | 0 | 354 | 330 | 5 | 197 | 5 | 28 | 90 | 24 | 9 | 14 | 34 | 30 | 0 | 0 | 0 | 310 | 320 | 311 | 34 | 30 | 0 | 143 | 0 | 0 | 11 | 20 | 0 | 18 | 173 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 5985 | 924 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 752 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 5 | 100 | 220 | 0 | 179 | 752 | 0 | 4943 | 10928 | 76.9
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 17 | 68 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 268 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 17 | 18 | 0 | 430 | 0 | 0 | 0 | 150 | 9 | 17 | 78 | 0 | 100 | 24 | 0 | 39 | 0 | 22 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640 | 0 | 5 | 0 | 8 | 0 | 354 | 330 | 5 | 182 | 5 | 34 | 90 | 34 | 9 | 14 | 34 | 28 | 0 | 0 | 0 | 295 | 320 | 303 | 34 | 30 | 0 | 129 | 8 | 0 | 11 | 20 | 0 | 18 | 173 | 0 | 8 | 55 | 0 | 0 | 0 | 12 | 5785 | 924 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 751 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 5 | 90 | 220 | 0 | 179 | 650 | 0 | 4830 | 10615 | 76.9
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 68 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 293 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 17 | 18 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 36 | 12 | 0 | 38 | 0 | 22 | 283 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 0 | 5 | 0 | 8 | 0 | 353 | 330 | 5 | 193 | 5 | 34 | 90 | 17 | 9 | 8 | 17 | 28 | 0 | 0 | 0 | 295 | 320 | 313 | 34 | 30 | 0 | 133 | 8 | 0 | 11 | 20 | 0 | 18 | 173 | 0 | 8 | 55 | 0 | 0 | 0 | 12 | 5568 | 924 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 753 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 130 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 5 | 100 | 220 | 0 | 179 | 598 | 0 | 4746 | 10314 | 76.9
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 17 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 301 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 2 | 0 | 17 | 19 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 35 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 0 | 5 | 0 | 8 | 0 | 300 | 330 | 5 | 202 | 5 | 34 | 90 | 17 | 9 | 3 | 17 | 30 | 0 | 4 | 0 | 285 | 320 | 329 | 34 | 30 | 0 | 133 | 8 | 0 | 11 | 20 | 0 | 18 | 173 | 0 | 8 | 55 | 0 | 0 | 3.68 | 12 | 5451.68 | 924 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.45 | 750 | 0 | 821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3.62 | 130 | 0 | 130 | 0 | 0 | 0 | 380 | 0 | 0.29 | 0 | 164 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 8 | 0.03 | 12 | 150 | 5 | 100 | 220 | 0 | 179 | 600 | 0 | 4782.59 | 10234.27 | 76.9
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 48 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 293 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 7 | 0 | 17 | 19 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 31 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 0 | 18 | 0 | 8 | 0 | 300 | 330 | 23 | 191 | 29 | 34 | 90 | 17 | 9 | 14 | 17 | 28 | 0 | 21 | 0 | 295 | 320 | 300 | 35 | 30 | 0 | 147 | 8 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 24 | 65 | 0 | 1 | 12.92 | 12 | 5695.92 | 925 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.23 | 748 | 0 | 819 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 13.83 | 130 | 0 | 130 | 0 | 0 | 0 | 390 | 0 | 1.11 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 67 | 0.04 | 48 | 200 | 0 | 100 | 220 | 0 | 180 | 605 | 0 | 4964.81 | 10660.73 | 76.9
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 52 | 48 | 0 | 0 | 11 | 0 | 0 | 0 | 320 | 311 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 8 | 17 | 17 | 19 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 39 | 0 | 5 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 627 | 0 | 51 | 0 | 8 | 0 | 310 | 335 | 49 | 208 | 32 | 34 | 90 | 17 | 9 | 14 | 17 | 28 | 0 | 34 | 0 | 300 | 320 | 352 | 35 | 30 | 0 | 151 | 8 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 24 | 85 | 0 | 1 | 27.92 | 12 | 5954.92 | 877 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.33 | 748 | 0 | 818.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 18.65 | 130 | 0 | 130 | 0 | 0 | 0 | 410 | 0 | 1.49 | 0 | 158 | 0 | 0 | 3 | 0 | 0 | 0 | 0.8 | 60 | 0.19 | 80 | 200 | 4 | 110 | 180 | 0 | 178 | 605 | 0 | 4993.48 | 10948.4 | 76.9
09:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 76 | 62 | 0 | 0 | 35 | 0 | 0 | 0 | 350 | 292 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 10 | 17 | 17 | 19 | 0 | 430 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 40 | 0 | 2 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 702 | 0 | 51 | 0 | 8 | 0 | 355 | 345 | 48 | 195 | 36 | 34 | 90 | 19 | 10 | 14 | 17 | 28 | 0 | 41 | 0 | 315 | 320 | 301 | 35 | 30 | 0 | 156 | 8 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 24 | 85 | 0 | 1 | 38.22 | 12 | 6272.22 | 877 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.91 | 747 | 0 | 820.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 26.05 | 140 | 0 | 130 | 0 | 0 | 0 | 386 | 0 | 2.7 | 0 | 155 | 0 | 0 | 24 | 0 | 0 | 0 | 2.3 | 76 | 0.27 | 110 | 200 | 6 | 110 | 215 | 0 | 216 | 660 | 0 | 5248.36 | 11520.58 | 76.91
10:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 104 | 48 | 0 | 0 | 35 | 12 | 0 | 0 | 350 | 312 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 12 | 17 | 17 | 17 | 0 | 430 | 0 | 0 | 0 | 150 | 28 | 0 | 0 | 0 | 12 | 0 | 4 | 40 | 0 | 2 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 807 | 0 | 51 | 0 | 36 | 0 | 344 | 345 | 47 | 210 | 27 | 43 | 90 | 34 | 9 | 14 | 34 | 26 | 0 | 51 | 0 | 315 | 320 | 369 | 35 | 30 | 0 | 156 | 8 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 24 | 85 | 0 | 2 | 44.52 | 12 | 6624.52 | 924 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.38 | 745 | 0 | 822.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 44.91 | 165 | 0 | 130 | 0 | 0 | 0 | 408 | 0 | 3.18 | 0 | 161 | 0 | 0 | 20 | 0 | 0 | 0 | 3.4 | 180 | 0.41 | 110 | 200 | 6 | 100 | 220 | 0 | 216 | 700 | 0 | 5455.64 | 12080.16 | 76.91
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 104 | 48 | 0 | 0 | 35 | 45 | 0 | 0 | 380 | 303 | 0 | 0 | 10 | 0 | 295 | 0 | 0 | 15 | 26 | 16 | 17 | 0 | 430 | 0 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 57 | 12 | 2 | 40 | 0 | 2 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 901 | 0 | 51 | 0 | 36 | 0 | 344 | 345 | 48 | 204 | 28 | 52 | 80 | 36 | 9 | 14 | 57 | 26 | 0 | 47 | 0 | 320 | 320 | 333 | 35 | 6 | 0 | 156 | 8 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 24 | 87 | 0 | 2 | 51.85 | 12 | 6775.85 | 924 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.93 | 784 | 0 | 822.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 29.15 | 168 | 0 | 130 | 0 | 0 | 0 | 404 | 0 | 2.92 | 0 | 162 | 0 | 0 | 33 | 0 | 0 | 0 | 2 | 202 | 0.41 | 110 | 250 | 5 | 100 | 220 | 0 | 216 | 790 | 0 | 5669.5 | 12445.35 | 76.91
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 14 | 17 | 112 | 48 | 0 | 0 | 35 | 70 | 0 | 0 | 380 | 307 | 0 | 0 | 17 | 0 | 283 | 0 | 0 | 13 | 52 | 16 | 17 | 0 | 480 | 0 | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 88 | 24 | 3 | 40 | 0 | 2 | 512 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 985 | 0 | 51 | 0 | 36 | 0 | 344 | 345 | 44 | 203 | 28 | 69 | 80 | 80 | 9 | 14 | 70 | 32 | 0 | 68 | 0 | 315 | 0 | 355 | 35 | 20 | 0 | 153 | 8 | 0 | 83 | 30 | 0 | 16 | 171 | 0 | 55 | 123 | 0 | 2 | 46.31 | 12 | 6990.31 | 924 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.07 | 868 | 0 | 916.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 58.37 | 163 | 0 | 137 | 0 | 0 | 0 | 393 | 0 | 5.6 | 0 | 164 | 0 | 0 | 22 | 0 | 0 | 0 | 2.4 | 155 | 0.3 | 110 | 293 | 4 | 100 | 220 | 0 | 213 | 940 | 0 | 6069 | 13059.31 | 76.91
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 42 | 17 | 113 | 80 | 15 | 0 | 45 | 108 | 0 | 0 | 380 | 295 | 0 | 0 | 35 | 0 | 282 | 0 | 0 | 15 | 70 | 16 | 17 | 0 | 480 | 0 | 0 | 0 | 150 | 25 | 3 | 0 | 0 | 100 | 74 | 3 | 40 | 0 | 7 | 512 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 1058 | 0 | 51 | 13 | 36 | 0 | 350 | 345 | 44 | 191 | 28 | 84 | 80 | 102 | 9 | 14 | 105 | 32 | 0 | 50 | 0 | 310 | 0 | 347 | 35 | 20 | 0 | 151 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 0 | 65 | 122 | 0 | 1 | 20.15 | 12 | 7345.15 | 924 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.48 | 958 | 0 | 1057.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 0 | 42.44 | 163 | 0 | 162 | 0 | 0 | 0 | 336 | 0 | 2.67 | 0 | 166 | 0 | 0 | 33 | 0 | 0 | 0 | 7.9 | 111 | 0.17 | 110 | 307 | 10 | 100 | 220 | 0 | 213 | 1050 | 0 | 6324.22 | 13669.37 | 76.91
14:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 17 | 115 | 80 | 15 | 0 | 55 | 108 | 0 | 0 | 350 | 297 | 0 | 0 | 35 | 0 | 282 | 0 | 0 | 28 | 90 | 16 | 17 | 0 | 480 | 0 | 0 | 0 | 150 | 17 | 34 | 0 | 0 | 100 | 74 | 4 | 40 | 0 | 2 | 565 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 1061 | 0 | 51 | 24 | 36 | 0 | 330 | 345 | 47 | 193 | 28 | 90 | 75 | 136 | 11 | 14 | 105 | 36 | 0 | 50 | 0 | 310 | 0 | 349 | 35 | 20 | 0 | 151 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 0 | 66 | 123 | 0 | 1 | 12.06 | 11 | 7471.06 | 924 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.49 | 993 | 0 | 1205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 32.29 | 161 | 0 | 163 | 0 | 0 | 0 | 327 | 0 | 4.68 | 0 | 168 | 0 | 0 | 19 | 0 | 0 | 0 | 3.1 | 93 | 0.59 | 110 | 307 | 9 | 120 | 220 | 0 | 214 | 1000 | 0 | 6384.15 | 13855.21 | 76.91
15:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 54 | 17 | 113 | 95 | 15 | 0 | 55 | 108 | 0 | 0 | 350 | 283 | 0 | 0 | 35 | 0 | 284 | 0 | 0 | 13 | 90 | 16.5 | 17 | 0 | 480 | 0 | 0 | 0 | 150 | 11 | 34 | 10 | 0 | 100 | 88 | 3 | 40 | 0 | 0 | 562 | 0 | 0 | 0 | 1 | 51 | 0 | 0 | 0 | 0 | 1160 | 0 | 51 | 30 | 36 | 0 | 346 | 345 | 48 | 196 | 28 | 90 | 70 | 139 | 22 | 14 | 105 | 36 | 0 | 42 | 0 | 315 | 0 | 355 | 35 | 40 | 0 | 152 | 8 | 0 | 82 | 25 | 0 | 16 | 172 | 0 | 65 | 119 | 0 | 2 | 7.61 | 11 | 7632.11 | 924 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.19 | 1010 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 45.06 | 160 | 0 | 163 | 0 | 0 | 0 | 381 | 0 | 3.13 | 0 | 165 | 0 | 0 | 8 | 0 | 0 | 0 | 4.2 | 140 | 0.36 | 110 | 307 | 10 | 116 | 220 | 0 | 215 | 987 | 0 | 6448.94 | 14081.05 | 76.91
16:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 17 | 113 | 95 | 15 | 0 | 55 | 108 | 0 | 2 | 350 | 296 | 0 | 0 | 35 | 0 | 289 | 0 | 0 | 12 | 125 | 8.5 | 17 | 0 | 380 | 0 | 0 | 0 | 150 | 9 | 34 | 56 | 0 | 100 | 100 | 1 | 38 | 0 | 0 | 480 | 0 | 0 | 0 | 16 | 34 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 36 | 0 | 345 | 345 | 48 | 198 | 28 | 90 | 70 | 150 | 27 | 14 | 105 | 34 | 8 | 17 | 5 | 310 | 0 | 364 | 35 | 40 | 0 | 151 | 8 | 0 | 80 | 25 | 0 | 16 | 172 | 0 | 65 | 120 | 0 | 0 | 22.47 | 11 | 7631.97 | 924 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.36 | 1010 | 0 | 1213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 14.62 | 157 | 0 | 160 | 0 | 0 | 0 | 384 | 0 | 1.81 | 0 | 163 | 0 | 0 | 5 | 0 | 0 | 0 | 0.9 | 85 | 0.25 | 110 | 307 | 10 | 120 | 220 | 0 | 214 | 977 | 0 | 6320.94 | 13952.91 | 76.91
17:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 54 | 17 | 113 | 95 | 15 | 0 | 55 | 108 | 0 | 14 | 350 | 283 | 0 | 0 | 35 | 0 | 271 | 0 | 0 | 8 | 125 | 16.5 | 17 | 0 | 380 | 0 | 0 | 0 | 150 | 10 | 34 | 72 | 0 | 100 | 100 | 0 | 37 | 0 | 2 | 360 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 1224 | 2 | 51 | 88 | 36 | 0 | 346 | 345 | 50 | 185 | 32 | 89 | 70 | 155 | 29 | 14 | 105 | 28 | 16 | 21 | 37 | 305 | 0 | 348 | 35 | 40 | 0 | 151 | 8 | 0 | 82 | 28 | 0 | 16 | 172 | 0 | 65 | 129 | 0 | 1 | 8.24 | 11 | 7544.74 | 924 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.39 | 1015 | 0 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 11.08 | 154 | 0 | 164 | 0 | 0 | 0 | 365 | 0 | 1.02 | 0 | 158 | 0 | 0 | 3 | 0 | 0 | 0 | 0.6 | 13 | 0.09 | 16 | 307 | 10 | 110 | 220 | 0 | 213 | 986 | 0 | 6090.18 | 13634.92 | 76.91
18:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 54 | 17 | 118 | 95 | 15 | 0 | 55 | 108 | 0 | 20 | 300 | 290 | 0 | 0 | 35 | 0 | 271 | 0 | 0 | 0 | 125 | 16.5 | 17 | 0 | 340 | 0 | 0 | 0 | 150 | 0 | 34 | 72 | 0 | 50 | 50 | 0 | 36 | 0 | 2 | 360 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 1155 | 0 | 51 | 100 | 36 | 0 | 300 | 335 | 49 | 187 | 30 | 90 | 80 | 155 | 29 | 14 | 105 | 26 | 16 | 2 | 37 | 300 | 0 | 302 | 34 | 40 | 0 | 130 | 8 | 0 | 82 | 30 | 0 | 16 | 171 | 0 | 94 | 145 | 0 | 0 | 1.31 | 11 | 7215.81 | 924 | 170 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9.25 | 962 | 3 | 1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 153 | 0 | 160 | 0 | 0 | 0 | 321 | 0 | 0.22 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.03 | 16 | 224 | 9 | 90 | 180 | 0 | 214 | 905 | 0 | 5720.7 | 12936.51 | 76.92
19:00 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 54 | 17 | 131 | 142 | 65 | 0 | 55 | 162 | 0 | 30 | 420 | 290 | 0 | 0 | 35 | 0 | 288 | 0 | 0 | 0 | 160 | 16.5 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 34 | 72 | 0 | 100 | 100 | 0 | 36 | 0 | 2 | 570 | 21 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 113 | 36 | 0 | 345 | 340 | 50 | 202 | 34 | 90 | 80 | 163 | 28 | 14 | 114 | 30 | 16 | 0 | 38 | 310 | 0 | 348 | 35 | 40 | 0 | 144 | 0 | 0 | 82 | 30 | 0 | 16 | 171 | 9 | 94 | 158 | 0 | 0 | 0 | 11 | 8255.5 | 877 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 17 | 1308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 185 | 0 | 0 | 0 | 397 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 293 | 11 | 116 | 220 | 0 | 214 | 910 | 0 | 6061 | 14316.5 | 76.92
19:30 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 17 | 131 | 145 | 110 | 15 | 55 | 162 | 0 | 32 | 350 | 303 | 0 | 0 | 35 | 0 | 272 | 0 | 0 | 0 | 160 | 16.5 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 1 | 34 | 72 | 0 | 100 | 100 | 0 | 36 | 0 | 2 | 561 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 100 | 36 | 0 | 354 | 345 | 50 | 186 | 34 | 90 | 80 | 180 | 38 | 14 | 114 | 30 | 25 | 0 | 38 | 305 | 0 | 337 | 34 | 40 | 0 | 147 | 8 | 0 | 82 | 30 | 0 | 18 | 171 | 54.5 | 103 | 158 | 0 | 0 | 0 | 11 | 8273 | 877 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 17 | 1415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 188 | 0 | 0 | 0 | 321 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 116 | 180 | 0 | 213 | 1150 | 0 | 6399 | 14672
20:00 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 54 | 17 | 131 | 130 | 45 | 10 | 55 | 162 | 0 | 35 | 350 | 304 | 0 | 0 | 35 | 0 | 288 | 0 | 0 | 0 | 160 | 16.5 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 2 | 34 | 72 | 0 | 100 | 100 | 0 | 37 | 0 | 4 | 563 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 36 | 0 | 354 | 345 | 52 | 196 | 35 | 89 | 80 | 176 | 38 | 14 | 114 | 38 | 25 | 0 | 39 | 300 | 0 | 320 | 34 | 40 | 0 | 134 | 8 | 0 | 82 | 30 | 0 | 18 | 171 | 54.5 | 103 | 158 | 0 | 0 | 0 | 12 | 8132 | 878 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 17 | 1407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 190 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 120 | 180 | 0 | 214 | 1150 | 0 | 6417 | 14549 | 76.92
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 22 | 17 | 131 | 130 | 15 | 0 | 55 | 126 | 0 | 16 | 400 | 280 | 0 | 0 | 17 | 0 | 267 | 0 | 0 | 0 | 160 | 16.5 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 6 | 34 | 72 | 0 | 100 | 48 | 0 | 39 | 0 | 10 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 20 | 36 | 0 | 355 | 345 | 55 | 182 | 36 | 90 | 80 | 189 | 38 | 14 | 114 | 38 | 25 | 0 | 39 | 310 | 20 | 302 | 35 | 40 | 0 | 131 | 8 | 0 | 82 | 30 | 0 | 18 | 171 | 0 | 55 | 105 | 0 | 0 | 0 | 12 | 7755.5 | 924 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 17 | 1415.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 192 | 0 | 0 | 0 | 317 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 254 | 1150 | 0 | 6498.49 | 14253.99 | 76.92
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 17 | 131 | 130 | 0 | 0 | 55 | 90 | 0 | 16 | 400 | 294 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 160 | 16 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 11 | 34 | 72 | 0 | 100 | 48 | 0 | 40 | 0 | 19 | 563 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 325 | 345 | 55 | 201 | 36 | 90 | 80 | 200 | 39 | 14 | 114 | 40 | 25 | 0 | 39 | 310 | 25 | 307 | 35 | 40 | 0 | 139 | 8 | 0 | 82 | 28 | 0 | 18 | 171 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 7694 | 923 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 17 | 1265.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 100 | 220 | 0 | 289 | 1100 | 0 | 6287.06 | 13981.06 | 76.92
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 17 | 116 | 97 | 0 | 0 | 17 | 54 | 0 | 0 | 400 | 301 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 52 | 16 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 7 | 34 | 72 | 0 | 100 | 48 | 0 | 40 | 0 | 27 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 320 | 345 | 55 | 204 | 33 | 90 | 80 | 180 | 39 | 14 | 114 | 38 | 25 | 0 | 39 | 305 | 15 | 334 | 35 | 40 | 0 | 133 | 8 | 0 | 82 | 28 | 0 | 18 | 171 | 0 | 8 | 45 | 0 | 0 | 0 | 12 | 7343 | 923 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 17 | 1266.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 150 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 220 | 0 | 289 | 1101 | 0 | 6309.21 | 13652.21 | 76.92
Total KWH | 24192 | 763200 | 411360 | 0 | 0 | 0 | 0 | 0 | 8348400 | 0 | 0 | 491760 | 432360 | 2332944 | 1752000 | 233095 | 19022 | 774185 | 1365120 | 0 | 145920 | 8995500 | 7169978 | 0 | 0 | 334998 | 0 | 6914430 | 0 | 0 | 175918 | 1484400 | 397800 | 421920 | 0 | 10251363.64 | 0 | 0 | 0 | 3700000 | 175680 | 502972 | 930768 | 0 | 1752960 | 1055040 | 22938 | 929520 | 0 | 286560 | 9920000 | 23418 | 0 | 3360 | 96048 | 239199 | 0 | 0 | 0 | 0 | 22756361 | 2565 | 917664 | 598836 | 635636 | 0 | 8476100 | 8218000 | 897120 | 4805000 | 586584 | 1586880 | 1973100 | 2356800 | 442680 | 291900 | 1681500 | 744960 | 208018 | 414418 | 286016 | 7468000 | 3855800 | 8330000 | 819000 | 688440 | 0 | 3434318 | 155568 | 0 | 1521600 | 645888 | 0 | 416000 | 4564620 | 87480 | 1171200 | 2251200 | 0 | 11050 | 296250 | 282240 | 166757120.64 | 22196363 | 4464288 | 0 | 0 | 1920 | 0 | 0 | 0 | 0 | 0 | 0 | 416880 | 21410910 | 102240 | 24855403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 748921 | 0 | 360752 | 3623545 | 0 | 3857064 | 0 | 0 | 0 | 8935709 | 0 | 31320 | 0 | 3995000 | 0 | 0 | 179916 | 0 | 0 | 0 | 30205.08 | 1163520 | 3511.5 | 1129536 | 5978000 | 162086 | 2462000 | 5323810 | 0 | 5090909 | 21655272.73 | 0 | 138179081.31 | 304936201.95

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 19-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-05-2025 | during | 19-05-2025 | during | 19-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 343 | 337 | 400.75 | 400.75 | 372 | 372 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 350 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 307 | 303 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 283 | 272 | 335 | 335 | 320 | 320 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 14 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 145 | 133 | 133 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 55 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 16.5 | 30 | 30 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 17 | 17 | 22 | 22 | 19 | 19 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 16 | 52.19 | 52.19 | 34 | 34 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 110 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 112 | 131 | 135 | 135 | 149 | 149 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 62 | 62 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 32 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 70 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 13 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 480 | 400 | 584 | 584 | 500 | 500 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2280 | 2695.5 | 4658.54 | 4720.54 | 3307.02 | 3369.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 17 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 9 | 0 | 9 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 36 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 1 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 0 | 72 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 2 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 90 | 90 | Engine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 3 | 0 | 4.65 | 0 | 4.65 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 985 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 1 | 18 | 0 | 18 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 512 | 561 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1813 | 2314 | 3378.37 | 3369.72 | 3360.37 | 3351.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 203 | 186 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 345 | 345 | 345 | 345 | 345 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 28 | 34 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 50 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 36 | 36 | 195 | 195 | 82 | 82 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 100 | 150 | 150 | 138 | 138 | Engine Problem
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 38 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 80 | 180 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 30 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 25 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 17.75 | 17.75 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 90 | 115 | 115 | 92 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 68 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1473 | 1765 | 2449.24 | 2399.24 | 2126.3 | 2076.3
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 18-05-2025 | during | 19-05-2025 | during | 19-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 123 | 158 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 103 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.31 | 0 | 47 | 0 | 47 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 11 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 54.5 | 54.5 | 54.5 | 35 | 35 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 238.31 | 326.5 | 598.1 | 549 | 371.1 | 322
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 35 | 34 | 35 | 35 | 35 | 35 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 40 | 40 | 40 | 30 | 30 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 147 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 82 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 171 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 16 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 355 | 337 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 0 | 0 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1186 | 1172 | 1610 | 1610 | 1505 | 1505
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 877 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 186 | 170 | 410 | 410 | 231 | 231 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | -
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 104.07 | 0 | 70.5 | 0 | 70.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 868 | 1104 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2082.07 | 2168 | 3582.7 | 3512.2 | 3298.71 | 3228.21
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 213 | 213 | 620 | 620 | 450 | 450 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 110 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 4 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 100 | 116 | 125 | 125 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 940 | 1150 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 293 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.3 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1880.3 | 1993 | 2787.12 | 2786.12 | 2572.12 | 2571.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 163 | 153 | 214 | 214 | 180 | 180 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 137 | 188 | 220 | 220 | 200 | 200 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0.01 | 0.01 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 393 | 321 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.6 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 916.26 | 1415 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 58.37 | 0 | 50 | 0 | 50 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 90 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 1763.23 | 2077 | 3184.17 | 3028.87 | 2868.39 | 2713.09
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 164 | 161 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.4 | 0 | 0.6 | 0 | 0.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 0 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 22 | 0 | 20.5 | 0 | 20.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 155 | 0 | 143 | 0 | 161.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 343.4 | 161 | 576.1 | 412 | 594.31 | 412
System Total |  |  |  |  | 27566.2 | 28624.082 | 13059.31 | 14672 | 22824.34 | 22387.69 | 20003.32 | 19548.46
Forecast Scenario (19-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12530 |  | 0 |  | 12530
|  |  |  | 1:00 | 12330 |  | 0 |  | 12330
|  |  |  | 2:00 | 11530 |  | 0 |  | 11530
|  |  |  | 3:00 | 11360 |  | 0 |  | 11360
|  |  |  | 4:00 | 11220 |  | 0 |  | 11220
|  |  |  | 5:00 | 10800 |  | 0 |  | 10800
|  |  |  | 6:00 | 10300 |  | 0 |  | 10300
|  |  |  | 7:00 | 10330 |  | 0 |  | 10330
|  |  |  | 8:00 | 10710 |  | 0 |  | 10710
|  |  |  | 9:00 | 11540 |  | 0 |  | 11540
|  |  |  | 10:00 | 11990 |  | 0 |  | 11990
|  |  |  | 11:00 | 12470 |  | 0 |  | 12470
|  |  |  | 12:00 | 13200 |  | 0 |  | 13200
|  |  |  | 13:00 | 13650 |  | 0 |  | 13650
|  |  |  | 14:00 | 13600 |  | 0 |  | 13600
|  |  |  | 15:00 | 13490 |  | 0 |  | 13490
|  |  |  | 16:00 | 13090 |  | 0 |  | 13090
|  |  |  | 17:00 | 12940 |  | 0 |  | 12940
|  |  |  | 18:00 | 12730 |  | 0 |  | 12730
|  |  |  | 18:30 | 13300 |  | 0 |  | 13300
|  |  |  | 19:00 | 13910 |  | 0 |  | 13910
|  |  |  | 19:30 | 14210 |  | 0 |  | 14210
|  |  |  | 20:00 | 13820 |  | 0 |  | 13820
|  |  |  | 21:00 | 13410 |  | 0 |  | 13410
|  |  |  | 22:00 | 12340 |  | 0 |  | 12340
|  |  |  | 23:00 | 11600 |  | 0 |  | 11600
Probable Maximum Temperature: |  |  | 32.60°C
Probable Maximum Demand at Day Peak: |  |  | 13200.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14210.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14210.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 294.89 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:29 hrs on 19-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 18-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13059.31 | MW | 12:00 Hr. | Energy Generated |  |  | 304.9362 |  | MKWHr.
| Day Peak Demand |  |  | 13087.53 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.744 |  | MKWHr.
| Evening Peak Generation |  |  | 14672 | MW | 19:30 Hr. | Energy Demand |  |  | 305.6802 |  | MKWHr.
| Evening Peak Demand |  |  | 14750 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33.5 |  | °C
| Minimum Generation of the Day |  |  | 10234.27 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 999.63 |  | MMCFD
| Maximum Generation of the Day |  |  | 14672 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.3243 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.4994 | 0 | 10.5646 | 0 | 0 | 0.17592 | 0 | 0 | 53.2399 | Gas | 134.0148 | Gas | 485452887.2488
| Chattogram Zone |  |  | 3.9866 | 32.6764 | 4.6038 | 0 | 0.92952 | 0.025503 | 0 | 0.17568 | 42.3974 | Coal | 90.8065 | Coal | 613757649.9965
| Cumilla Zone |  |  | 26.8011 | 0 | 7.1607 | 0 | 0 | 0.41442 | 0.74496 | 0 | 35.1212 | HFO | 27.3549 | HFO | 514118403.17
| Mymensingh Zone |  |  | 0 | 0 | 3.7921 | 0 | 0 | 0.3073 | 0 | 0 | 4.0994 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 31.8992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.8992 | Hydro | 0.92952 | Hydro | 92952
| Khulna Zone |  |  | 4.4643 | 21.4109 | 0.10416 | 0 | 0 | 0.41688 | 22.1964 | 0 | 48.5926 | Solar | 3.8582 | Solar | 62429185.5838
| Barishal Zone |  |  | 7.9479 | 32.7242 | 1.1295 | 0 | 0 | 0.0035115 | 0 | 0 | 41.8051 | Import | 47.7967 | Import | 250096949.81
| Rajshahi Zone |  |  | 16.4163 | 0 | 0 | 0 | 0 | 1.141 | 24.8554 | 0 | 42.4127 | Wind | 0.17568 | Wind | 2571955.2
| Rangpur Zone |  |  | 0 | 3.995 | 0 | 0 | 0 | 1.3736 | 0 | 0 | 5.3686
| Total |  |  | 134.0148 | 90.8065 | 27.3549 | 0 | 0.92952 | 3.8582 | 47.7967 | 0.17568 | 304.9362
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 485452887.2488 |  | Hydro | 92952
|  |  |  | Coal | 613757649.9965 |  | Solar | 62429185.5838
|  |  |  | HFO | 514118403.17 |  | Import | 250096949.81
|  |  |  | HSD | 0 |  | Wind | 2571955.2
[5 empty] | Total: | 192,85,19,983 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.1964 | Peak Hr Flow | 877.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47782600.1 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.8554 | Peak Hr Flow | 1415.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 816 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.74496 | Peak Hr Flow | 30.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 998 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.7967 | Peak Hr Flow | 2322.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 35 |  | 5656
|  |  |  | Chattogram |  | 0 |  | 1505
|  |  |  | Cumilla |  | 0 |  | 1359
|  |  |  | Mymensingh |  | 40 |  | 1203
|  |  |  | Sylhet |  | 0 |  | 585
|  |  |  | Khulna |  | 0 |  | 1796
|  |  |  | Barishal |  | 0 |  | 449
|  |  |  | Rajshahi |  | 0 |  | 1425
|  |  |  | Rangpur |  | 0 |  | 242
|  |  |  | Total |  | 75 |  | 14220
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 735.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:12 | Natore 132/33kV S/S Rajlanka is restored.
| 08:20 | 10:18 | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to Neutral Point Connect to new
earthing mesh.
| 08:20 | 10:18 | Haripur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to Neutral Point Connect to new
earthing mash.
| 09:23 | 21:18 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Scheduled S/D Due to CB & Isoalator upgrading by
BPDB
| 09:23 | 16:51 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to 132 KV GIS line bay extension
work.
| 09:24 | 16:50 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to 132 KV GIS line bay extension
work.
| 09:53 |  | Madunaghat 132/33kV S/S TR-1(507T) LT Scheduled S/D Due to For Painting Work.
| 09:53 |  | Madunaghat 132/33kV S/S TR-1(507T) HT Scheduled S/D Due to For Painting Work
| 10:18 | 11:29 | Jaldhaka 132/33kV S/S 406T-1 LT Forced S/D Due to Domer -02 | [7 empty] | 12.0MW load
interrup.
| 10:18 | 11:29 | Jaldhaka 132/33kV S/S 406T-1 HT Forced S/D Due to Domer-02 | [7 empty] | 12.0MW load
interrup.
| 10:23 | 12:21 | Haripur 230/132kV S/S Auto TR-3 HT Scheduled S/D Due to Neutral Point Connect to new
earthing mash.
| 10:23 | 12:21 | Haripur 230/132kV S/S Auto TR-3 LT Scheduled S/D Due to Neutral Point Connect to new
earthing mash.
| 10:24 | 10:35 | Goalpara 132/33kV S/S T-5 LT Tripped showing Micom P127 relays Due to Due to 33 kV | [7 empty] | 16.0MW load
|  |  | Senerbazar Feeder Fault. | [7 empty] | interrup.
| 10:24 | 10:35 | Goalpara 132/33kV S/S T-6 LT Tripped showing Micom P127 relays Due to Due to 33 kV | [7 empty] | 16.0MW load
|  |  | Senerbazar Feeder Fault | [7 empty] | interrup.
| 11:14 | 18:38 | Bogura-Mahasthangar (New)) 132 kV Ckt-2 Scheduled S/D from Mahasthangarh 132/33kV end Due
to Bogura grid. and from Bogura 132/33kV end Due to breakar change
| 11:45 | 13:34 | Palashbari 132/33kV S/S TR3-424T LT Forced S/D Due to Oil leakage
| 11:45 |  | Bibiyana South 400MW CCPP tripped.
| 11:45 |  | Bibiyana South 400 MW Tripped with remarks:- GT
| 11:46 | 13:32 | Palashbari 132/33kV S/S TR3-424T HT Forced S/D Due to Oil leakage
| 11:46 |  | Bibiyana South 400 MW Tripped with remarks:- ST
| 12:26 | 21:04 | Haripur 230/132kV S/S Auto TR-2 HT Scheduled S/D Due to Neutral Point Connect to new
earthing mesh
| 12:26 | 21:04 | Haripur 230/132kV S/S Auto TR-2 LT Scheduled S/D Due to Neutral Point Connect to new
earthing mesh
| 14:24 | 15:28 | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to T-3 33KV Bus Isolator Loop change work for
Isolator loop Burnt.
| 14:25 | 15:26 | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to T-3 33KV Bus loop change for the reason off
33kv Bus loop Burnt
| 14:30 | 15:58 | Barishal 230/132kV S/S ATR-1 LT Scheduled S/D Due to Oil leakage repair.
| 14:33 | 14:49 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Scheduled S/D Due to For 33 kV GCB gas refill.
| 14:33 | 14:48 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Scheduled S/D Due to For 33 kV GCB gas refill.
| 14:33 | 15:59 | Barishal 230/132kV S/S ATR-1 HT Scheduled S/D Due to Oil repair
| 16:08 | 17:38 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to Wzpdcl 33kV h-3 feeder bus side red hot | [7 empty] | 6.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 16:09 | 17:37 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to Wzpdcl 33kV h-3 feeder bus side red hot | [7 empty] | 6.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 18:44 | 21:15 | Aggreko-keraniganj 132kV Ckt-1 Tripped from Keranigonj 230/132/33kV end showing distance
relay relays Due to Distance relay operated.
| 19:24 |  | Bibiyana South 400 MW Synchronized with remarks:- GT
| 19:30 |  | Evening peak Generation is 14671 MW
| 19:43 |  | Bibiyana South 400 MW Tripped with remarks:- GT
| 20:20 |  | Bibiyana South 400 MW Synchronized with remarks:- GT
| 22:20 | 01:04 | Chapai 132/33kV S/S T-2 (415T) LT Forced S/D Due to red hot maintenance
| 22:35 |  | Chhatak 132/33kV S/S T-3 LT Scheduled S/D Due to 132KV T-3 Transformer CB(423B) hydraulic | [7 empty] | 6.0MW load
|  |  | oil leakage and low pressure. | [7 empty] | interrup.
| 22:40 | 01:02 | Chapai 132/33kV S/S T-2 (415T) HT Forced S/D Due to red hot maintenance
| 23:31 |  | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to 132KV T-3 Transformer CB(423B) hydraulic | [7 empty] | 6.0MW load
|  |  | oil leakage and low pressure. | [7 empty] | interrup.
| 23:43 | 00:45 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to Red hot maintenance (7 no pbs | [7 empty] | 50.0MW load
|  |  | feeder) | [7 empty] | interrup.
| 23:43 | 00:44 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Forced S/D Due to Red hot maintenance (pbs 7 no | [7 empty] | 50.0MW load
|  |  | feeder) | [7 empty] | interrup.
| 23:45 | 00:27 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-3 (50/75 MVA) HT Tripped showing OSR | [7 empty] | 45.0MW load
|  |  | relays Due to OSR | [7 empty] | interrup.
| 02:42 |  | Naogaon 132/33kV S/S T-3 LT Tripped showing O/C (a,b phase), 1st Stage U/F relays Due to | [7 empty] | 20.0MW load
|  |  | Atrai 33KV PBS feeder Incoming DS loop Cut-off from 33KV T-3 Bus(B & Y Phase). | [7 empty] | interrup.
| 04:03 |  | Ruppur 132/11kV S/S TR-01 HT Tripped showing Diff:. R,Y,B & K31,K32 relays Due to Under | [7 empty] | 2.8MW load
|  |  | Frequency Relay Not Connected. | [7 empty] | interrup.
| 05:45 |  | Mithapukur ---PS.CPRL ckt-1 Trip [CPRL End CB trip, Zone-1, Phase-B trip]
| 06:00 |  | Minimum generation 11729 MW
| 06:10 |  | Mithapukur ---PS.CPRL ckt-1 Syn
| 06:50 |  | Naogaon 132/33kV S/S T-3 HT Forced S/D Due to Atrai PBS 33KV feeder Bus DS connecting R &
Y Phase loop Maintenance.
| 06:50 |  | Naogaon 132/33kV S/S T-3 LT Forced S/D Due to Atrai PBS 33KV feeder Bus DS connecting R & | [7 empty] | 27.0MW load
|  |  | Y Phase loop Maintenance. | [7 empty] | interrup.
| 07:01 |  | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
| 07:12 |  | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to Tr1 33 kv bus section ds | [7 empty] | 150.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 07:12 |  | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to Tr1 33 kv bus section ds | [7 empty] | 150.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 07:18 |  | Kabirpur 132/33kV S/S XFR, T-I LT Scheduled S/D Due to Tr1 33 kv bus section ds | [7 empty] | 150.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 07:19 |  | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Tr1 33 kv bus section ds | [7 empty] | 150.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 07:27 |  | Feni 132/33kV S/S T-1(405T) HT Scheduled S/D Due to 33 kV CT loop maintenance work
| 07:27 |  | Feni 132/33kV S/S T-1(405T) LT Scheduled S/D Due to 33 kV CT loop maintenance work
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 18-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 337 | 8348400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8995500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 303 | 7169978 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 19022 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 272 | 6914430 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 24192 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 491760 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 1752000 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 55 | 774185 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 334998 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16.5 | 397800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 421920 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 411360 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 110 | 233095 | Liquid fuel shortage
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2332944 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 763200 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 32 | 145920 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1365120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 175918 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432360 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 10251363.64 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1484400 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2695.5 | 53239865.64
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3700000 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 17 | 96048 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 2565 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 3360 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 36 | 929520 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 239199 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 72 | 930768 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 502972 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1752960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 286560 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Engine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 22938 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1055040 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 23418 | Engine Problem
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 22756361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 1 | 175680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 561 | 9920000 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2314 | 42397389
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 186 | 4805000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8476100 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 345 | 8218000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 34 | 586584 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 897120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 36 | 635636 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 917664 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 100 | 598836 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 38 | 286016 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1973100 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 2356800 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 30 | 744960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 25 | 208018 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 291900 | Schedule Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1681500 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 442680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1586880 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 414418 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1765 | 35121212
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 158 | 2251200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 103 | 1171200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 296250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 11 | 282240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 87480 | 33kV Feeder Problem
Mymensingh Area Total |  |  |  |  | 654.21 | 326.5 | 4099420
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 34 | 819000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 688440 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 147 | 3434318 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 645888 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1521600 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 171 | 4564620 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 416000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 155568 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7468000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 337 | 8330000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 0 | 3855800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1172 | 31899234
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 877 | 22196363 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 1920 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 170 | 4464288 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 102240 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 416880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1104 | 21410910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2168 | 48592601
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 213 | 5090909 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 1129536 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 162086 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 116 | 2462000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1150 | 21655272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 180 | 5323810 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5978000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3511.5 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1993 | 41805125.23
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 153 | 3623545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 188 | 3857064 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 321 | 8935709 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1415 | 24855403 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 360752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 748921 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2077 | 42412714
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | -
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 3995000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 0 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 30205.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 0 | 0 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 179916 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1163520 | -
Rangpur Area Total |  |  |  |  | 950 | 161 | 5368641.08
Eastern Grid Total |  |  |  |  | 16921.242 | 8273 | 166757120.64
Western Grid Total |  |  |  |  | 11702.84 | 6399 | 138179081.31
National Grid Total |  |  |  |  | 28624.082 | 14672 | 304936201.95
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 18-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10233.16 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3911.6 | MW
i) Dhaka area |  |  | 5621.03 |  | MW | i) Khulna area |  |  |  | 1796 | MW
ii) Chattogram area |  |  | 1505 |  | MW | ii) Barishal area |  |  |  | 448.6 | MW
iii) Cumilla area |  |  | 1359.13 |  | MW | iii) Rajshahi area |  |  |  | 1425 | MW
iv) Mymensingh area |  |  | 1163 |  | MW | iv) Rangpur area |  |  |  | 242 | MW
v) Sylhet area |  |  | 585 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14144.76 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 84 | 19:00 | 133 | Patuakhali | 84 | 00:00
2 | AKSML | 129.5 | 13:00 | 68 | Jaldhaka | 54 | 18:00 | 134 | Payra | 38 | 00:00
3 | Aftabnagar | 64 | 13:00 | 69 | Jamalpur | 112 | 19:00 | 135 | Postogola | 58 | 13:00
4 | Agargaon | 130 | 15:00 | 70 | Jashore | 142 | 19:30 | 136 | Purbachal | 20 | 22:00
5 | Agrabad | 96 | 15:00 | 71 | Jhenaidah | 130 | 22:00 | 137 | Purbasadipur | 107 | 13:00
6 | Amnura | 29 | 19:30 | 72 | Joydebpur | 165 | 19:00 | 138 | Rahanpur | 27 | 20:00
7 | Ashuganj | 98 | 22:00 | 73 | Joypurhat | 47 | 18:30 | 139 | Rahim | 44 | 15:00
8 | BSRM | 196 | 22:00 | 74 | Juldah | 15 | 10:00 | 140 | Rajbari | 87 | 19:30
9 | Bagerhat | 86 | 23:00 | 75 | KSRM | 23.5 | 10:00 | 141 | Rajendrapur | 142 | 19:30
10 | Bajitpur | 49 | 22:00 | 76 | Kabirpur | 286 | 09:00 | 142 | Rajshahi | 122 | 22:00
11 | Bakulia | 110 | 19:00 | 77 | Kachua | 95 | 22:00 | 143 | Rajshahi-230 | 82 | 22:00
12 | Banani | 52 | 13:00 | 78 | Kallyanpur | 102 | 19:00 | 144 | Ramganj | 120 | 22:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kalurghat | 52 | 19:00 | 145 | Rampur | 47 | 00:00
14 | Barapukuria | 53 | 10:00 | 80 | Kamrangirchar | 69 | 19:00 | 146 | Rangamati | 16 | 19:00
15 | Barguna | 18 | 12:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 128 | 12:00
16 | Barishal | 105 | 13:00 | 82 | Kasba | 35 | 21:00 | 148 | Ruppur | 7.2 | 16:00
17 | Barishal-230 | 104 | 19:00 | 83 | Kazla | 99 | 20:00 | 149 | SSM | 12 | 00:00
18 | Baroaulia | 60 | 12:00 | 84 | Keranigonj | 82 | 19:30 | 150 | Saidpur | 97 | 14:00
19 | Baroirhat | 64 | 00:00 | 85 | Khagrachori | 30 | 19:30 | 151 | Satkhira | 133 | 21:00
20 | Bashundhara | 193 | 16:00 | 86 | Khulna | 83 | 12:00 | 152 | Satmasjid | 106 | 19:00
21 | BashundharaCement | 7 | 00:00 | 87 | Khulshi | 181 | 16:00 | 153 | Savar | 235 | 19:00
22 | Beanibazar | 72 | 22:00 | 88 | Kishoreganj | 143 | 19:30 | 154 | SevenRings | 17.76 | 16:00
23 | Benapole | 72 | 19:30 | 89 | Kodda | 310 | 18:00 | 155 | ShahCement | 34 | 07:00
24 | Bhaluka | 172 | 19:00 | 90 | Kulaura | 45 | 19:00 | 156 | Shahjadpur | 83 | 19:30
25 | Bhandaria | 54 | 13:00 | 91 | Kurigram | 46 | 18:30 | 157 | Shahjibazar | 121 | 19:30
26 | Bhangura | 39 | 21:00 | 92 | Kushtia | 152 | 23:00 | 158 | Shahmirpur | 57 | 00:00
27 | Bheramara(GK) | 70 | 22:00 | 93 | Lalbag | 78 | 13:00 | 159 | Shariatpur | 86 | 21:00
28 | Bhulta | 242 | 16:00 | 94 | Lalmonirhat | 49 | 18:30 | 160 | Sherpur | 130 | 19:00
29 | Bog-Sherpur | 66 | 20:00 | 95 | MI_Cement | 15.5 | 13:00 | 161 | Shikalbaha | 31 | 18:30
30 | Bogura | 154 | 20:00 | 96 | Madanganj | 44 | 23:00 | 162 | Shitalakhya | 87.7 | 12:00
31 | Borhanuddin | 102 | 00:00 | 97 | Madaripur | 110 | 23:00 | 163 | Sholosohor | 47 | 15:00
32 | Brahmanbaria | 130 | 23:00 | 98 | Madartek | 91.06 | 23:00 | 164 | Shyampur | 196 | 13:00
33 | Cantonment | 146 | 13:00 | 99 | Madunaghat | 57 | 19:00 | 165 | Siddhirganj | 119 | 16:00
34 | Chandina | 22.13 | 23:00 | 100 | Magura | 65 | 20:00 | 166 | Sirajganj | 122 | 21:00
35 | Chandpur | 76 | 21:00 | 101 | Mahasthangarh | 74 | 19:00 | 167 | Sonargaon | 115 | 22:00
36 | Chandraghona | 36 | 19:00 | 102 | Manikganj | 140 | 22:00 | 168 | Sreemongol | 83 | 19:00
37 | Chapai | 63 | 19:00 | 103 | Maniknagar | 88 | 13:00 | 169 | Sreepur | 106 | 19:30
38 | Charsaidpur | 31 | 15:00 | 104 | Matarbari | 51 | 00:00 | 170 | Srinagar | 47.58 | 22:00
39 | Chauddagram | 73 | 22:00 | 105 | Matuail | 65 | 12:00 | 171 | Sunamganj | 56 | 21:00
40 | Chhatak | 39 | 22:00 | 106 | Millgate | 128 | 16:00 | 172 | Sylhet | 46 | 00:00
41 | Chowmuhani | 234 | 19:30 | 107 | Mirpur | 122 | 15:00 | 173 | Sylhet-132 | 124 | 19:30
42 | Chuadanga | 107 | 23:00 | 108 | Mirsorai | 10 | 00:00 | 174 | TK | 34.5 | 23:00
43 | Coxsbazar | 133 | 00:00 | 109 | Mirzapur | 48 | 22:00 | 175 | Tangail | 180 | 19:00
44 | Cumilla(N) | 148 | 15:00 | 110 | Mithapukur | 56 | 18:00 | 176 | Thakurgaon | 65 | 14:00
45 | Cumilla(S) | 168 | 16:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 114 | 21:00
46 | Daudkandi | 130 | 21:00 | 112 | Mogbazar | 154.3 | 15:00 | 178 | Ullahpara | 39 | 19:30
47 | Dhaka | 88 | 12:00 | 113 | Mongla | 44 | 19:00 | 179 | Ullon | 39 | 22:00
48 | Dhamrai | 140 | 19:00 | 114 | Motijheel | 39 | 19:00 | 180 | Uttara | 87 | 16:00
49 | Dhanmondi | 138 | 14:00 | 115 | Muktagacha | 37 | 21:00 | 181 | UttaraNew | 60 | 23:00
50 | Dohazari | 106 | 00:00 | 116 | Munshiganj | 111 | 22:00 | 182 | Zigatola | 72 | 13:00
51 | Faridpur | 162 | 22:00 | 117 | Muradnagar | 28 | 19:00
52 | Fatullah | 101 | 15:00 | 118 | Mymensingh | 215 | 20:00
53 | Fenchuganj | 38 | 20:00 | 119 | Naogaon | 130 | 19:30
54 | Feni | 122 | 23:00 | 120 | Narail | 59 | 19:30
55 | GPH | 93 | 01:00 | 121 | Narinda | 82 | 16:00
56 | Ghatail | 80 | 20:00 | 122 | Narshingdi | 179 | 22:00
57 | Ghorashal | 18 | 15:00 | 123 | Natore | 161 | 21:00
58 | Ghorashal-230 | 105 | 21:00 | 124 | Nawabganj | 58.2 | 22:00
59 | Goalpara | 36 | 07:00 | 125 | Netrakona | 107 | 21:00
60 | Gollamari | 92 | 13:00 | 126 | New | 88 | 12:00
61 | Gopalganj | 104 | 19:30 | 127 | Niamatpur | 67 | 19:30
62 | Gulshan | 88 | 15:00 | 128 | Noapara | 50 | 19:30
63 | Halishahar | 75 | 09:00 | 129 | PHP | 8 | 18:30
64 | HaripurSBU | 173 | 23:00 | 130 | Pabna | 126 | 21:00
65 | Hasnabad | 98 | 13:00 | 131 | Palashbari | 58 | 19:00
66 | Hathazari | 84 | 19:00 | 132 | Panchagarh | 45 | 21:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 18-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 11493.8 | 0 |  | 11493.8
1:00 | 10939.8 | 0 |  | 10939.8
2:00 | 10839 | 0 |  | 10839
3:00 | 10928 | 0 |  | 10928
4:00 | 10615 | 0 |  | 10615
5:00 | 10314 | 0 |  | 10314
6:00 | 10234.27 | 0 |  | 10234.27
7:00 | 10660.73 | 26 |  | 10687.9
8:00 | 10948.4 | 24 |  | 10973.4
9:00 | 11520.58 | 26 |  | 11547.58
10:00 | 12080.16 | 32 |  | 12113.16
11:00 | 12445.35 | 27 |  | 12473.35
12:00 | 13059.31 | 27 |  | 13087.53
13:00 | 13669.37 | 23 |  | 13693.37
14:00 | 13855.21 | 35 |  | 13892.21
15:00 | 14081.05 | 49 |  | 14132.05
16:00 | 13952.91 | 68 |  | 14023.91
17:00 | 13634.92 | 97 |  | 13735.92
18:00 | 12936.51 | 43 |  | 12981.51
19:00 | 14316.5 | 23 |  | 14340.5
19:30 | 14672 | 75 |  | 14750
20:00 | 14549 | 97 |  | 14650
21:00 | 14253.99 | 54 |  | 14309.99
22:00 | 13981.06 | 47 |  | 14030.06
23:00 | 13652.21 | 46 |  | 13700.21
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 18-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6491.8 | 5002 | 11493.8 | DAILY GENERATION CURVE
00:30 | 6193.8 | 5023 | 11216.8
01:00 | 5895.8 | 5044 | 10939.8 | 18-05-2025
01:30 | 5915.4 | 4974 | 10889.4
02:00 | 5935 | 4904 | 10839
02:30 | 5960 | 4923.5 | 10883.5
03:00 | 5985 | 4943 | 10928
03:30 | 5885 | 4886.5 | 10771.5
04:00 | 5785 | 4830 | 10615
04:30 | 5676.5 | 4788 | 10464.5
05:00 | 5568 | 4746 | 10314
05:30 | 5509.84 | 4764.295 | 10274.135
06:00 | 5451.68 | 4782.59 | 10234.27
06:30 | 5573.8 | 4873.7 | 10447.5
07:00 | 5695.92 | 4964.81 | 10660.73
07:30 | 5825.42 | 4979.145 | 10804.565
08:00 | 5954.92 | 4993.48 | 10948.4
08:30 | 6113.57 | 5120.92 | 11234.49
09:00 | 6272.22 | 5248.36 | 11520.58
09:30 | 6448.37 | 5352 | 11800.37
10:00 | 6624.52 | 5455.64 | 12080.16
10:30 | 6700.185 | 5562.57 | 12262.755
11:00 | 6775.85 | 5669.5 | 12445.35
11:30 | 6883.08 | 5869.25 | 12752.33
12:00 | 6990.31 | 6069 | 13059.31
12:30 | 7167.73 | 6196.61 | 13364.34
13:00 | 7345.15 | 6324.22 | 13669.37
13:30 | 7408.105 | 6354.185 | 13762.29
14:00 | 7471.06 | 6384.15 | 13855.21
14:30 | 7551.585 | 6416.545 | 13968.13
15:00 | 7632.11 | 6448.94 | 14081.05
15:30 | 7632.04 | 6384.94 | 14016.98
16:00 | 7631.97 | 6320.94 | 13952.91
16:30 | 7588.355 | 6205.56 | 13793.915
17:00 | 7544.74 | 6090.18 | 13634.92
17:30 | 7380.275 | 5905.44 | 13285.715
18:00 | 7215.81 | 5720.7 | 12936.51
18:30 | 7735.655 | 5890.85 | 13626.505
19:00 | 8255.5 | 6061 | 14316.5
19:30 | 8273 | 6399 | 14672
20:00 | 8132 | 6417 | 14549
20:30 | 7943.75 | 6457.745 | 14401.495 |  | Executive Engineer
21:00 | 7755.5 | 6498.49 | 14253.99 |  | Network Operation Division
21:30 | 7724.75 | 6392.775 | 14117.525
22:00 | 7694 | 6287.06 | 13981.06
22:30 | 7518.5 | 6298.135 | 13816.635
23:00 | 7343 | 6309.21 | 13652.21

## En-Curve
QF-LDC-12
Date | 18-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3538 | 2015.8 | 923 | 0 | 36 | 823 | 40 | 3199 | 0 | 186 | 724 | 0 | 0 | 9 | 0 | DAILY ENERGY CURVE
00:30 | 3513 | 1938.3 | 923.5 | 0 | 28 | 823.5 | 40 | 3192 | 0 | 177.5 | 575 | 0 | 0 | 6 | 0 | 18-05-2025
01:00 | 3488 | 1860.8 | 924 | 0 | 20 | 824 | 40 | 3185 | 0 | 169 | 426 | 0 | 0 | 3 | 0
01:30 | 3533.5 | 1885.4 | 924 | 0 | 25 | 825 | 40 | 3080 | 0 | 169 | 406 | 0 | 0 | 1.5 | 0 | Energy Generated | 304.9362 |  | MKWHr
02:00 | 3579 | 1910 | 924 | 0 | 30 | 826 | 40 | 2975 | 0 | 169 | 386 | 0 | 0 | 0 | 0 | Energy not Served | 0.744 |  | MKWHr
02:30 | 3591 | 1918 | 924 | 0 | 30 | 824.5 | 39.5 | 2974 | 0 | 169 | 411.5 | 0 | 0 | 2 | 0 | Total Energy Requirement | 305.6802 |  | MKWHr
03:00 | 3603 | 1926 | 924 | 0 | 30 | 823 | 39 | 2973 | 0 | 169 | 437 | 0 | 0 | 4 | 0
03:30 | 3558.5 | 1900.5 | 924 | 0 | 29 | 822 | 39 | 2915.5 | 0 | 160.5 | 416 | 0 | 0 | 6.5 | 0
04:00 | 3514 | 1875 | 924 | 0 | 28 | 821 | 39 | 2858 | 0 | 152 | 395 | 0 | 0 | 9 | 0
04:30 | 3546 | 1851.5 | 924 | 0 | 28 | 819.5 | 38.5 | 2808 | 0 | 104.5 | 340 | 0 | 0 | 4.5 | 0
05:00 | 3578 | 1828 | 924 | 0 | 28 | 818 | 38 | 2758 | 0 | 57 | 285 | 0 | 0 | 0 | 0
05:30 | 3573.5 | 1801.5 | 924 | 0 | 29 | 819.5 | 37.5 | 2756.5 | 16.135 | 58.5 | 258 | 0 | 0 | 0 | 0
06:00 | 3569 | 1775 | 924 | 0 | 30 | 821 | 37 | 2755 | 32.27 | 60 | 231 | 0 | 0 | 0 | 0
06:30 | 3562.5 | 1835.5 | 924.5 | 0 | 29 | 820 | 37.5 | 2818 | 93 | 66.5 | 261 | 0 | 0 | 0 | 13
07:00 | 3556 | 1896 | 925 | 0 | 28 | 819 | 38 | 2881 | 153.73 | 73 | 291 | 0 | 0 | 0 | 26
07:30 | 3630 | 1908 | 901 | 0 | 28 | 818.51 | 38.5 | 2878.5 | 196.055 | 81.5 | 324.5 | 0 | 0 | 0 | 25
08:00 | 3704 | 1920 | 877 | 0 | 28 | 818.02 | 39 | 2876 | 238.38 | 90 | 358 | 0 | 0 | 0 | 24
08:30 | 3691 | 1967 | 877 | 0 | 28 | 819.075 | 39.5 | 2982 | 304.915 | 127.5 | 398.5 | 0 | 0 | 0 | 25
09:00 | 3678 | 2014 | 877 | 0 | 28 | 820.13 | 40 | 3088 | 371.45 | 165 | 439 | 0 | 0 | 0 | 26
09:30 | 3731.5 | 2039 | 900.5 | 0 | 27 | 821.245 | 40 | 3162 | 422.125 | 158 | 485 | 0 | 0 | 14 | 29
10:00 | 3785 | 2064 | 924 | 0 | 26 | 822.36 | 40 | 3236 | 472.8 | 151 | 531 | 0 | 0 | 28 | 32
10:30 | 3746.5 | 2076.5 | 924 | 0 | 26 | 822.225 | 40 | 3367 | 492.03 | 150.5 | 599 | 0 | 0 | 19 | 29.5
11:00 | 3708 | 2089 | 924 | 0 | 26 | 822.09 | 40 | 3498 | 511.26 | 150 | 667 | 0 | 0 | 10 | 27
11:30 | 3545 | 2109.5 | 924 | 0 | 29 | 869.175 | 40 | 3736.5 | 540.655 | 163 | 786.5 | 0 | 0 | 9 | 27
12:00 | 3382 | 2130 | 924 | 0 | 32 | 916.26 | 40 | 3975 | 570.05 | 176 | 906 | 0 | 0 | 8 | 27
12:30 | 3351.5 | 2125.5 | 924 | 0 | 32 | 986.91 | 40 | 4119.5 | 512.43 | 202.5 | 1053.5 | 0 | 0 | 16.5 | 25
13:00 | 3321 | 2121 | 924 | 0 | 32 | 1057.56 | 40 | 4264 | 454.81 | 229 | 1201 | 0 | 0 | 25 | 23
13:30 | 3314 | 2105.5 | 924 | 0 | 34 | 1131.28 | 40 | 4286 | 419.01 | 237 | 1250.5 | 0 | 0 | 21 | 29
14:00 | 3307 | 2090 | 924 | 0 | 36 | 1205 | 40 | 4308 | 383.21 | 245 | 1300 | 0 | 0 | 17 | 35
14:30 | 3358 | 2086.25 | 924 | 0 | 36 | 1212 | 40 | 4357 | 369.38 | 257.5 | 1314 | 0 | 0 | 14 | 42
15:00 | 3409 | 2082.5 | 924 | 0 | 36 | 1219 | 40 | 4406 | 355.55 | 270 | 1328 | 0 | 0 | 11 | 49
15:30 | 3409.5 | 2031 | 924 | 0 | 35 | 1216 | 39 | 4390.5 | 292.48 | 313 | 1356.5 | 0 | 0 | 10 | 58.5
16:00 | 3410 | 1979.5 | 924 | 0 | 34 | 1213 | 38 | 4375 | 229.41 | 356 | 1385 | 0 | 0 | 9 | 68
16:30 | 3379.5 | 1977.5 | 924 | 0 | 31 | 1214.5 | 37.5 | 4319 | 163.915 | 380 | 1357.5 | 0 | 0 | 9.5 | 82.5
17:00 | 3349 | 1975.5 | 924 | 0 | 28 | 1216 | 37 | 4263 | 98.42 | 404 | 1330 | 0 | 0 | 10 | 97
17:30 | 3260.5 | 1900 | 924 | 0 | 27 | 1211 | 36.5 | 4124.5 | 59.215 | 422 | 1316 | 0 | 0 | 5 | 70
18:00 | 3172 | 1824.5 | 924 | 0 | 26 | 1206 | 36 | 3986 | 20.01 | 440 | 1302 | 0 | 0 | 0 | 43
18:30 | 3321 | 1944 | 900.5 | 0 | 28 | 1257 | 36 | 4186 | 10.005 | 477 | 1467 | 0 | 0 | 0 | 33
19:00 | 3470 | 2063.5 | 877 | 0 | 30 | 1308 | 36 | 4386 | 0 | 514 | 1632 | 0 | 0 | 0 | 23
19:30 | 3336 | 1972.5 | 877 | 0 | 30 | 1415 | 36 | 4720 | 0 | 517 | 1767.5 | 0 | 0 | 1 | 75
20:00 | 3370 | 1959.5 | 878 | 0 | 38 | 1407 | 37 | 4725 | 0 | 503 | 1629.5 | 0 | 0 | 2 | 97
20:30 | 3337 | 2000.5 | 901 | 0 | 38 | 1411.245 | 38 | 4748 | 0 | 503 | 1420.75 | 0 | 0 | 4 | 75.5
21:00 | 3304 | 2041.5 | 924 | 0 | 38 | 1415.49 | 39 | 4771 | 0 | 503 | 1212 | 0 | 0 | 6 | 54
21:30 | 3320 | 2056.25 | 923.5 | 0 | 39 | 1340.275 | 39.5 | 4740 | 0 | 503 | 1147.5 | 0 | 0 | 8.5 | 50.5
22:00 | 3336 | 2071 | 923 | 0 | 40 | 1265.06 | 40 | 4709 | 0 | 503 | 1083 | 0 | 0 | 11 | 47
22:30 | 3351 | 2073.5 | 923 | 0 | 39 | 1265.635 | 40 | 4709.5 | 0 | 423.5 | 982.5 | 0 | 0 | 9 | 46.5
23:00 | 3366 | 2076 | 923 | 0 | 38 | 1266.21 | 40 | 4710 | 0 | 344 | 882 | 0 | 0 | 7 | 46
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 18-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 04:00 | 366 | 16:00 | Payra | 414 | 03:00 | 407 | 12:00
Ashuganj | 397 | 5:00 | 366 | 15:00 | Rahanpur | 413 | 04:00 | 397 | 19:30
Bhulta | 391 | 05:00 | 362 | 15:00 | Rampal | 402 | 00:00 | 384 | 15:00
Bibiana | 393 | 01:00 | 380 | 16:00
BIPTC | 404 | 09:00 | 394 | 00:00
Bogura | 404 | 04:00 | 385 | 16:00
Gopalganj | 396 | 04:00 | 379 | 19:00
Kaliakoir | 376 | 05:00 | 356 | 15:00
Madunaghat | 396 | 04:00 | 385 | 16:00
Meghnaghat | 386 | 04:00 | 371 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 04:00 | 211 | 15:00 | Keranigonj | 222 | 04:00 | 209 | 15:00
AKSML | 230 | 03:00 | 223 | 12:00 | Khulna(S) | 232 | 00:00 | 22 | 07:00
Aminbazar | 222 | 01:00 | 212 | 16:00 | Madunaghat | 235 | 05:00 | 226 | 15:00
Ashuganj | 229 | 00:00 | 216 | 15:00 | Madunaghat-400 | 235 | 05:00 | 227 | 12:00
Ashuganj-400 | 229 | 00:00 | 216 | 15:00 | Maniknagar | 220 | 05:00 | 209 | 15:00
Baghabari | 234 | 02:00 | 223 | 15:00 | Meghnaghat | 228 | 05:00 | 220 | 10:00
Barapukuria | 227 | 04:00 | 216 | 14:00 | Meghnaghat-400 | 223 | 04:00 | 214 | 15:00
Barapukuria-230 | 227 | 04:00 | 216 | 14:00 | Mirsorai | 227 | 02:00 | 219 | 16:00
Barishal | 239 | 05:00 | 226 | 22:00 | Rajshahi | 232 | 01:00 | 221 | 19:00
Bheramara | 230 | 00:00 | 222 | 12:00 | Rampal | 231 | 00:00 | 215 | 19:00
Bhulta | 227 | 04:00 | 208 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 04:00 | 217 | 15:00 | Rampura | 226 | 04:00 | 206 | 15:00
BIPTC | 233 | 00:00 | 222 | 12:00 | Shikalbaha | 233 | 05:00 | 223 | 15:00
Bogura | 233 | 04:00 | 222 | 16:00 | Shyampur | 222 | 04:00 | 210 | 15:00
Bogura-400 | 233 | 06:00 | 222 | 16:00 | Siddhirganj | 222 | 02:00 | 21 | 08:00
Borhanuddin | 243 | 05:00 | 233 | 22:00 | Sirajgonj | 238 | 00:00 | 231 | 15:00
BSRM | 228 | 04:00 | 218 | 12:00 | Sreepur | 226 | 00:00 | 216 | 15:00
Cumilla(N) | 220 | 00:00 | 211 | 15:00 | Tongi | 224 | 05:00 | 207 | 15:00
Faridpur | 234 | 04:00 | 221 | 19:00
Fenchuganj | 227 | 01:00 | 221 | 15:00
Ghorashal | 230 | 00:00 | 220 | 10:00
Ghorashal-230 | 226 | 04:00 | 115 | 21:00
Gopalganj | 236 | 05:00 | 224 | 19:00
GPH | 231 | 04:00 | 222 | 15:00
Haripur | 221 | 04:00 | 128 | 08:00
Hasnabad | 221 | 05:00 | 210 | 15:00
Hathazari | 232 | 03:00 | 224 | 15:00
Ishurdi | 233 | 05:00 | 217 | 19:00
Jhenaidah | 231 | 00:00 | 214 | 19:00
Kaliakoir | 230 | 05:00 | 215 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 00:00 | 125 | 15:00 | Madartek | 138 | 04:00 | 125 | 15:00
Agargaon | 136 | 04:00 | 125 | 15:00 | Madunaghat | 135 | 04:00 | 126 | 23:00
Agrabad | 134 | 03:00 | 127 | 15:00 | Magura | 136 | 01:00 | 121 | 19:00
AKS | 130 | 05:00 | 126 | 08:00 | Mahasthangarh | 136 | 04:00 | 126 | 16:00
Aminbazar | 131 | 01:00 | 124 | 11:00 | Manikganj | 130 | 03:00 | 118 | 16:00
Amnura | 134 | 00:00 | 127 | 19:00 | Maniknagar | 133 | 03:00 | 125 | 12:00
Ashuganj | 136 | 00:00 | 130 | 15:00 | Matarbari | 130 | 06:00 | 111 | 00:00
Bagerhat | 138 | 00:00 | 115 | 19:00 | Matuail | 128.8 | 04:00 | 121 | 15:00
Bajitpur | 132 | 02:00 | 124 | 13:00 | Millgate | 135 | 03:00 | 122 | 15:00
Bakulia | 134 | 04:00 | 126 | 19:00 | Mirpur | 130 | 02:00 | 122 | 12:00
Banani | 138 | 00:00 | 126 | 15:00 | Mirzapur | 133 | 00:00 | 126 | 14:00
Bangabhaban | 133 | 03:00 | 125 | 15:00 | Mithapukur | 134 | 04:00 | 123 | 14:00
Barapukuria | 135 | 04:00 | 124 | 14:00 | MI_Cement | 130 | 04:00 | 122 | 12:00
Barguna | 135 | 05:00 | 130 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 135 | 00:00 | 123 | 22:00 | Mogbazar | 140 | 04:00 | 124 | 18:00
Barishal-230 | 135 | 01:00 | 123 | 21:00 | Mongla | 139 | 00:00 | 116 | 19:00
Baroaulia | 132 | 00:00 | 129 | 12:00 | Motijheel | 133 | 03:00 | 125 | 15:00
Baroirhat | 126 | 00:00 | 118 | 14:00 | Muktagacha | 136 | 02:00 | 127 | 19:00
Bashundhara | 140 | 04:00 | 119 | 15:00 | Munshiganj | 128 | 04:00 | 121 | 12:00
BashundharaCement | 128 | 04:00 | 121 | 15:00 | Muradnagar | 127 | 01:00 | 118 | 15:00
Beanibazar | 133 | 02:00 | 125 | 15:00 | Mymensingh | 138 | 22:00 | 115 | 19:00
Benapole | 136 | 00:00 | 115 | 19:00 | Naogaon | 136 | 06:00 | 127 | 14:00
Bhaluka | 130 | 03:00 | 122 | 15:00 | Narail | 135 | 00:00 | 120 | 19:00
Bhandaria | 134 | 00:00 | 116 | 21:00 | Narinda | 133 | 03:00 | 125 | 12:00
Bhangura | 135 | 05:00 | 127 | 21:00 | Narshingdi | 127 | 07:00 | 115 | 15:00
Bheramara | 137 | 00:00 | 130 | 15:00 | Natore | 134 | 03:00 | 126 | 19:30
Bheramara(GK) | 137 | 00:00 | 130 | 15:00 | Nawabganj | 133 | 04:00 | 122 | 16:00
Bhulta | 121 | 03:00 | 114 | 16:00 | Netrakona | 127 | 00:00 | 116 | 20:00
Bog-Sherpur | 136 | 03:00 | 128 | 19:30 | New | 135 | 03:00 | 122 | 15:00
Bogura | 139 | 07:00 | 132 | 14:00 | Niamatpur | 137 | 03:00 | 130 | 19:30
Bogura-230 | 139 | 04:00 | 131 | 16:00 | Noapara | 138 | 00:00 | 119 | 19:00
Brahmanbaria | 129 | 06:00 | 120 | 15:00 | Pabna | 135 | 04:00 | 127 | 19:00
Cantonment | 135 | 03:00 | 125 | 15:00 | Palashbari | 133 | 03:00 | 122 | 15:00
Chandina | 128 | 01:00 | 120 | 15:00 | Panchagarh | 137 | 18:00 | 120 | 14:00
Chandpur | 128 | 18:00 | 10 | 00:00 | Patuakhali | 135 | 02:00 | 130 | 19:00
Chandraghona | 134 | 05:00 | 127 | 15:00 | Payra | 136 | 04:00 | 132 | 21:00
Chapai | 134 | 02:00 | 127 | 15:00 | PHP | 126 | 01:00 | 117 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 03:00 | 122 | 12:00 | Postogola | 132 | 05:00 | 125 | 12:00
Chauddagram | 124 | 00:00 | 116 | 12:00 | Purbachal | 140 | 05:00 | 125 | 15:00
Chhatak | 132 | 01:00 | 122 | 21:00 | Purbasadipur | 132 | 18:00 | 116 | 14:00
Chowmuhani | 127 | 00:00 | 109 | 15:00 | Rahanpur | 138 | 05:00 | 131 | 20:00
Chuadanga | 136 | 00:00 | 119 | 19:00 | Rahanpur-400 | 138 | 04:00 | 132 | 19:30
Coxsbazar | 130 | 06:00 | 110 | 19:00 | Rahim | 128 | 06:00 | 122 | 15:00
Cumilla(N) | 141 | 12:00 | 120 | 15:00 | Rajbari | 137 | 05:00 | 125 | 19:00
Cumilla(S) | 134 | 04:00 | 118 | 15:00 | Rajendrapur | 132 | 00:00 | 115 | 15:00
Daudkandi | 123 | 00:00 | 115 | 14:00 | Rajshahi | 135 | 03:00 | 126 | 19:00
Dhaka | 139 | 02:00 | 125 | 16:00 | Rajshahi-230 | 134 | 03:00 | 121 | 19:00
Dhamrai | 135 | 05:00 | 125 | 15:00 | Ramganj | 125 | 00:00 | 112 | 15:00
Dhanmondi | 139 | 02:00 | 125 | 16:00 | Rampur | 134 | 04:00 | 127 | 11:00
Dohazari | 132 | 07:00 | 123 | 13:00 | Rampura | 138 | 03:00 | 126 | 15:00
Faridpur | 136 | 00:00 | 128 | 19:00 | Rangamati | 133 | 03:00 | 126 | 15:00
Fatullah | 130 | 04:00 | 122 | 15:00 | Rangpur | 133 | 19:00 | 121 | 16:00
Fenchuganj | 135 | 00:00 | 131 | 20:00 | Ruppur | 137 | 04:00 | 131 | 19:00
Feni | 125 | 01:00 | 118 | 15:00 | Saidpur | 132 | 18:30 | 119 | 16:00
Ghatail | 132 | 00:00 | 124 | 19:00 | Satkhira | 138 | 00:00 | 116 | 19:00
Ghorashal | 136 | 01:00 | 126 | 16:00 | Satmasjid | 135 | 04:00 | 124 | 16:00
Goalpara | 140 | 00:00 | 122 | 19:00 | Savar | 128 | 06:00 | 122 | 12:00
Gollamari | 139 | 00:00 | 124 | 19:00 | SevenRings | 135 | 01:00 | 125 | 15:00
Gopalganj | 138 | 00:00 | 124 | 19:00 | ShahCement | 129 | 03:00 | 122 | 12:00
Gopalganj-400 | 137 | 00:00 | 129 | 19:00 | Shahjadpur | 137 | 00:00 | 131 | 19:00
Gulshan | 138 | 05:00 | 126 | 15:00 | Shahjibazar | 131 | 07:00 | 123 | 23:00
Halishahar | 135 | 04:00 | 13 | 07:00 | Shahmirpur | 132 | 02:00 | 129 | 10:00
Haripur | 129 | 04:00 | 123 | 11:00 | Shariatpur | 138 | 00:00 | 124 | 19:00
HaripurSBU | 128 | 00:00 | 123 | 11:00 | Sherpur | 140 | 21:00 | 132 | 14:00
Hasnabad | 132 | 04:00 | 125 | 12:00 | Shikalbaha | 124 | 03:00 | 118 | 10:00
Hathazari | 136 | 04:00 | 129 | 15:00 | Shikalbaha-230 | 136 | 05:00 | 129 | 18:00
Ishurdi | 138 | 04:00 | 131 | 19:00 | Shitalakhya | 130 | 04:00 | 122 | 12:00
Jaldhaka | 132 | 18:30 | 118 | 13:00 | Sholosohor | 135 | 04:00 | 126 | 23:00
Jamalpur | 141 | 22:00 | 134 | 14:00 | Shyampur | 127 | 01:00 | 125 | 08:00
Jashore | 138 | 00:00 | 116 | 19:00 | Shyampur-230 | 130 | 04:00 | 122 | 12:00
Jhenaidah | 137 | 00:00 | 118 | 22:00 | Siddhirganj | 129 | 00:00 | 122 | 15:00
Jhenaidah-230 | 137 | 00:00 | 124 | 19:00 | Sirajganj | 133 | 00:00 | 125 | 21:00
Joydebpur | 132 | 03:00 | 118 | 14:00 | Sonargaon | 127 | 00:00 | 120 | 14:00
Joypurhat | 135 | 05:00 | 124 | 16:00 | Sreemongol | 131 | 03:00 | 124 | 15:00
Juldah | 135 | 03:00 | 129 | 09:00 | Sreepur | 133 | 18:00 | 125 | 15:00
Kabirpur | 132 | 01:00 | 118 | 15:00 | Srinagar | 134 | 01:00 | 123 | 15:00
Kachua | 129 | 00:00 | 119 | 09:00 | SSM | 134 | 00:00 | 129 | 12:00
Kaliakoir | 138 | 04:00 | 128 | 14:00 | Sunamganj | 132 | 01:00 | 122 | 19:00
Kallyanpur | 132 | 04:00 | 123 | 15:00 | Sylhet | 134 | 02:00 | 127 | 14:00
Kalurghat | 132 | 04:00 | 127 | 12:00 | Sylhet-132 | 132 | 01:00 | 128 | 14:00
Kamrangirchar | 133 | 05:00 | 123 | 15:00 | Tangail | 131 | 00:00 | 124 | 11:00
Kaptai | 135 | 5:00 | 130 | 11:00 | Thakurgaon | 137 | 18:00 | 120 | 14:00
Kasba | 126 | 00:00 | 117 | 15:00 | TK | 131 | 07:00 | 127 | 11:00
Kazla | 133 | 05:00 | 124 | 16:00 | Tongi | 134 | 01:00 | 124 | 15:00
Keranigonj | 133 | 04:00 | 124 | 15:00 | Ullahpara | 137 | 03:00 | 126 | 20:00
Khagrachori | 133 | 04:00 | 125 | 13:00 | Ullon | 138 | 00:00 | 126 | 15:00
Khulna | 140 | 00:00 | 121 | 19:00 | Uttara | 131 | 05:00 | 121 | 16:00
Khulna(S) | 140 | 00:00 | 124 | 19:00 | UttaraNew | 131 | 05:00 | 121 | 16:00
Khulshi | 133 | 05:00 | 126 | 15:00 | Zigatola | 133 | 04:00 | 123 | 16:00
Kishoreganj | 129 | 00:00 | 121 | 14:00
Kodda | 130 | 04:00 | 117 | 15:00
KSRM | 133 | 00:00 | 127 | 11:00
Kulaura | 136 | 01:00 | 130 | 15:00
Kurigram | 133 | 19:00 | 122 | 12:00
Kushtia | 137 | 00:00 | 124 | 21:00
Lalbag | 133 | 04:00 | 123 | 12:00
Lalmonirhat | 128 | 22:00 | 121 | 15:00
Madanganj | 128 | 04:00 | 121 | 15:00
Madaripur | 138 | 00:00 | 126 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division