## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 20-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-05-2025 | during | 20-05-2025 | during | 20-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 362 | 369 | 400.75 | 400.75 | 371 | 371 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 380 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 301 | 304 | 335 | 335 | 312 | 312 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 289 | 295 | 335 | 335 | 312 | 312 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 7 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 144 | 149.36 | 149.36 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16.5 | 16 | 30 | 30 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 17 | 15 | 22 | 22 | 19 | 19 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 16 | 52.19 | 52.19 | 34 | 34 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 131 | 135 | 135 | 135 | 135 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 50 | 50 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 30 | 104 | 104 | 104 | 104 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 108 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 8 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 450 | 584 | 584 | 480 | 480 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2269.5 | 2738 | 4674.9 | 4736.9 | 3245.02 | 3307.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 30 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 37 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 8 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 10 | 70 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 0 | 34 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 0 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 80 | 108 | 108 | 90 | 90 | Engine Problem
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 5 | 0 | 3 | 0 | 3 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1100 | 1124 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 27 | 0 | 45 | 6 | 45 | 6 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 571 | 543 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 2035 | 2276 | 3412.72 | 3375.72 | 3394.72 | 3357.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 202 | 203 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 345 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 345 | 335 | 335 | 335 | 345 | 345 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 28 | 28 | 46.94 | 46.94 | 36 | 36 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 50 | 54 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 36 | 8 | 195 | 195 | 36 | 36 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 50 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 40 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 155 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 34 | 36 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 15 | 17.75 | 17.75 | 14 | 14 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 39 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 70 | 90 | 115 | 115 | 92 | 92 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 74 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1598 | 1662 | 2439.24 | 2389.24 | 2088.55 | 2038.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 19-05-2025 | during | 20-05-2025 | during | 20-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 32 | 168 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 16 | 102 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 5.96 | 0 | 33 | 0 | 33 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 67.96 | 336.5 | 584.1 | 549 | 376.6 | 341.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 35 | 34 | 35 | 35 | 35 | 35 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 40 | 40 | 40 | 40 | 40 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 139 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 64 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 173 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 8 | 8 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 342 | 343 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 210 | 15 | 210 | 210 | 210 | 210 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1375 | 1192 | 1502 | 1502 | 1405 | 1405
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 927 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 185 | 170 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 17 | 17 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 104.4 | 0 | 84 | 0 | 84 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 708 | 1036 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 1924.4 | 2103 | 3596.2 | 3512.2 | 3193.21 | 3109.21
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 286 | 285 | 400 | 500 | 450 | 450 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 90 | 115 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 900 | 1170 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 270 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.6 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1811.6 | 2071 | 2572.12 | 2671.12 | 2572.12 | 2571.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 32 | 32 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 150 | 151 | 214 | 214 | 168 | 168 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 163 | 220 | 220 | 192 | 192 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 409 | 340 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 98 | 98 | 98 | 98 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.31 | 0 | 5.3 | 0 | 5.3 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 818 | 1354.25 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 45.15 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 113 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 1678.46 | 2008.25 | 3206.17 | 3039.87 | 2859.79 | 2693.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 169 | 165 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.4 | 0 | 2.6 | 0 | 2.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 19 | 0 | 18.5 | 0 | 18.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 80 | 0 | 121.81 | 0 | 121.81 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 269.4 | 343 | 554.91 | 412 | 554.91 | 412
System Total |  |  |  |  | 27566.2 | 28624.082 | 13029.32 | 14729.75 | 22542.36 | 22188.05 | 19689.92 | 19235.61
Forecast Scenario (20-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13630 |  | 0 |  | 13630
|  |  |  | 1:00 | 13430 |  | 0 |  | 13430
|  |  |  | 2:00 | 13120 |  | 0 |  | 13120
|  |  |  | 3:00 | 12780 |  | 0 |  | 12780
|  |  |  | 4:00 | 12520 |  | 0 |  | 12520
|  |  |  | 5:00 | 12160 |  | 0 |  | 12160
|  |  |  | 6:00 | 11770 |  | 0 |  | 11770
|  |  |  | 7:00 | 11780 |  | 0 |  | 11780
|  |  |  | 8:00 | 11760 |  | 0 |  | 11760
|  |  |  | 9:00 | 11760 |  | 0 |  | 11760
|  |  |  | 10:00 | 12380 |  | 0 |  | 12380
|  |  |  | 11:00 | 12830 |  | 0 |  | 12830
|  |  |  | 12:00 | 13120 |  | 0 |  | 13120
|  |  |  | 13:00 | 13050 |  | 0 |  | 13050
|  |  |  | 14:00 | 12860 |  | 0 |  | 12860
|  |  |  | 15:00 | 13030 |  | 0 |  | 13030
|  |  |  | 16:00 | 13100 |  | 0 |  | 13100
|  |  |  | 17:00 | 12830 |  | 0 |  | 12830
|  |  |  | 18:00 | 12640 |  | 0 |  | 12640
|  |  |  | 18:30 | 13200 |  | 0 |  | 13200
|  |  |  | 19:00 | 13950 |  | 0 |  | 13950
|  |  |  | 19:30 | 14770 |  | 0 |  | 14770
|  |  |  | 20:00 | 14610 |  | 0 |  | 14610
|  |  |  | 21:00 | 14720 |  | 0 |  | 14720
|  |  |  | 22:00 | 14090 |  | 0 |  | 14090
|  |  |  | 23:00 | 13800 |  | 0 |  | 13800
Probable Maximum Temperature: |  |  | 32.10°C
Probable Maximum Demand at Day Peak: |  |  | 13120.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14770.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14770.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 311.72 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 07:57 hrs on 20-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 19-05-2025 | [28 empty] | Date: | 19-05-2025 | [28 empty] | Date: | 19-05-2025 | [28 empty] | Date: | 19-05-2025 | [28 empty] | Date: | 19-05-2025 | [16 empty] | Date: | 19-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 0 | 17 | 102 | 97 | 0 | 0 | 17 | 17 | 0 | 0 | 400 | 290 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 52 | 16 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 3 | 34 | 63 | 0 | 80 | 24 | 0 | 40 | 0 | 30 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 320 | 345 | 55 | 192 | 34 | 91 | 80 | 180 | 15 | 14 | 114 | 38 | 25 | 0 | 15 | 320 | 110 | 331 | 35 | 40 | 0 | 135 | 8 | 0 | 82 | 28 | 0 | 18 | 171 | 0 | 18 | 66 | 0 | 0 | 0 | 8 | 7288 | 924 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 17 | 1268.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 150 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 220 | 0 | 290 | 1100 | 0 | 6285.67 | 13573.67 | 76.92
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 102 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 278 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 52 | 16 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 34 | 40 | 0 | 80 | 24 | 0 | 40 | 0 | 30 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 320 | 345 | 53 | 183 | 34 | 91 | 80 | 180 | 9 | 14 | 114 | 38 | 25 | 0 | 0 | 310 | 210 | 301 | 35 | 40 | 0 | 134 | 0 | 0 | 82 | 28 | 0 | 18 | 170 | 0 | 24 | 95 | 0 | 0 | 0 | 12 | 7246 | 926 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 984 | 17 | 1212.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 150 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 290 | 1096 | 0 | 6131.59 | 13377.59 | 76.92
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 42 | 17 | 107 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 292 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 34 | 40 | 0 | 80 | 24 | 0 | 40 | 0 | 20 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1185 | 0 | 51 | 0 | 36 | 0 | 320 | 345 | 52 | 197 | 34 | 72 | 90 | 170 | 9 | 14 | 114 | 36 | 25 | 0 | 0 | 295 | 210 | 331 | 35 | 40 | 0 | 128 | 0 | 0 | 82 | 28 | 0 | 18 | 173 | 0 | 24 | 85 | 0 | 0 | 0 | 12 | 7172 | 926 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 954 | 0 | 1069.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 150 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 100 | 220 | 0 | 291 | 1000 | 0 | 5876.8 | 13048.8 | 76.92
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 17 | 121 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 288 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 34 | 16 | 0 | 80 | 24 | 0 | 40 | 0 | 30 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 36 | 0 | 320 | 345 | 52 | 188 | 33 | 70 | 90 | 170 | 9 | 14 | 114 | 36 | 25 | 0 | 0 | 300 | 210 | 301 | 35 | 40 | 0 | 130 | 0 | 0 | 82 | 28 | 0 | 18 | 174 | 0 | 24 | 85 | 0 | 0 | 0 | 12 | 6986 | 926 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 907 | 0 | 1019.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 150 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 220 | 0 | 291 | 960 | 0 | 5722.97 | 12708.97 | 76.92
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 17 | 121 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 273 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 34 | 0 | 0 | 80 | 24 | 0 | 40 | 0 | 30 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 36 | 0 | 320 | 345 | 53 | 182 | 33 | 69 | 90 | 170 | 9 | 14 | 114 | 32 | 25 | 0 | 0 | 300 | 210 | 331 | 34 | 40 | 0 | 129 | 0 | 0 | 82 | 28 | 0 | 18 | 174 | 0 | 24 | 75 | 0 | 0 | 0 | 12 | 6931 | 925 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 827 | 0 | 925.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 150 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 11 | 90 | 220 | 0 | 291 | 940 | 0 | 5525.13 | 12456.13 | 76.92
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 17 | 121 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 297 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 420 | 0 | 0 | 0 | 150 | 0 | 34 | 0 | 0 | 36 | 12 | 0 | 40 | 0 | 30 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 0 | 51 | 0 | 36 | 0 | 320 | 345 | 53 | 198 | 33 | 69 | 90 | 155 | 9 | 14 | 114 | 34 | 25 | 0 | 0 | 310 | 210 | 301 | 34 | 40 | 0 | 137 | 0 | 0 | 82 | 28 | 0 | 18 | 173 | 0 | 24 | 75 | 0 | 0 | 0 | 12 | 6870 | 925 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 813 | 0 | 821.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 150 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 100 | 220 | 0 | 289 | 800 | 0 | 5241.72 | 12111.72 | 76.92
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 0 | 17 | 123 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 296 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 2 | 0 | 17 | 17 | 0 | 420 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 893 | 1 | 51 | 0 | 36 | 0 | 320 | 345 | 53 | 198 | 33 | 69 | 90 | 136 | 9 | 14 | 114 | 30 | 0 | 3 | 0 | 310 | 210 | 320 | 34 | 40 | 0 | 134 | 0 | 0 | 82 | 28 | 0 | 18 | 174 | 0 | 24 | 75 | 0 | 0 | 2.7 | 12 | 6543.7 | 925 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | 784 | 0 | 827.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2.63 | 163 | 0 | 150 | 0 | 0 | 0 | 341 | 0 | 0.22 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.02 | 0 | 200 | 11 | 100 | 220 | 0 | 287 | 800 | 0 | 5187.28 | 11730.98 | 76.92
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 17 | 131 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 308 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 5 | 0 | 17 | 17 | 0 | 420 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 28 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 809 | 6 | 51 | 0 | 36 | 0 | 320 | 345 | 53 | 202 | 31 | 68 | 90 | 120 | 9 | 14 | 88 | 28 | 0 | 10 | 0 | 315 | 210 | 333 | 36 | 40 | 0 | 145 | 0 | 0 | 82 | 30 | 0 | 18 | 174 | 0 | 24 | 105 | 0 | 1 | 9.03 | 12 | 6533.03 | 926 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.52 | 763 | 0 | 824.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 7.2 | 166 | 0 | 150 | 0 | 0 | 0 | 365 | 0 | 0.38 | 0 | 163 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 3 | 0.17 | 0 | 200 | 6 | 100 | 220 | 0 | 287 | 800 | 0 | 5217.11 | 11750.14 | 76.92
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 131 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 311 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 16 | 0 | 17 | 17 | 0 | 420 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 38 | 0 | 2 | 408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 11 | 51 | 0 | 36 | 0 | 351 | 345 | 52 | 207 | 33 | 70 | 90 | 100 | 9 | 14 | 70 | 32 | 0 | 45 | 0 | 315 | 210 | 338 | 35 | 40 | 0 | 139 | 6 | 0 | 82 | 30 | 0 | 18 | 174 | 0 | 24 | 85 | 0 | 1 | 13.53 | 12 | 6495.53 | 881 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.83 | 762 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 10.2 | 165 | 0 | 175 | 0 | 0 | 0 | 371 | 0 | 0.63 | 0 | 168 | 0 | 0 | 3 | 0 | 0 | 0 | 0.7 | 5 | 0.2 | 0 | 200 | 9 | 110 | 220 | 0 | 287 | 750 | 0 | 5216.56 | 11712.09 | 76.92
09:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 0 | 17 | 132 | 48 | 0 | 0 | 17 | 45 | 0 | 0 | 420 | 298 | 0 | 0 | 0 | 0 | 281 | 0 | 0 | 15 | 52 | 16.7 | 17 | 0 | 350 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 48 | 0 | 2 | 40 | 0 | 2 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 846 | 15 | 51 | 0 | 36 | 0 | 300 | 330 | 50 | 189 | 28 | 69 | 85 | 119 | 9 | 14 | 114 | 32 | 0 | 28 | 0 | 300 | 210 | 301 | 35 | 40 | 0 | 150 | 6 | 0 | 79 | 20 | 0 | 18 | 174 | 0 | 24 | 85 | 0 | 0 | 26.13 | 12 | 6539.83 | 881 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 706 | 0 | 814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 38.82 | 150 | 0 | 181 | 0 | 0 | 0 | 325 | 0 | 3.44 | 0 | 166 | 0 | 0 | 5 | 0 | 0 | 0 | 0.7 | 20 | 0.31 | 0 | 250 | 8 | 114 | 180 | 0 | 286 | 780 | 0 | 5180.27 | 11720.1 | 76.92
10:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 0 | 17 | 131 | 48 | 0 | 0 | 35 | 70 | 0 | 0 | 420 | 294 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 30 | 52 | 16.5 | 17 | 0 | 350 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 48 | 0 | 4 | 40 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 17 | 51 | 0 | 36 | 0 | 341 | 330 | 51 | 210 | 28 | 69 | 85 | 136 | 9 | 14 | 114 | 30 | 0 | 30 | 0 | 310 | 210 | 341 | 35 | 39 | 0 | 147 | 6 | 0 | 79 | 30 | 0 | 18 | 174 | 0 | 24 | 85 | 0 | 0 | 17.37 | 12 | 6951.87 | 926 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.75 | 708 | 0 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 7.51 | 150 | 0 | 140 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 172 | 0 | 0 | 8 | 0 | 0 | 0 | 0.7 | 69 | 0.21 | 0 | 250 | 7 | 92 | 220 | 0 | 286 | 740 | 0 | 5349.17 | 12301.04 | 76.92
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 0 | 17 | 132 | 48 | 0 | 0 | 35 | 108 | 0 | 0 | 420 | 302 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 17 | 52 | 16.5 | 17 | 0 | 420 | 0 | 0 | 0 | 150 | 7 | 0 | 1 | 0 | 88 | 24 | 5 | 40 | 0 | 2 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 18 | 51 | 0 | 36 | 0 | 346 | 345 | 49 | 187 | 28 | 69 | 80 | 136 | 9 | 14 | 114 | 30 | 0 | 74 | 0 | 300 | 210 | 310 | 35 | 38 | 0 | 146 | 6 | 0 | 79 | 30 | 0 | 18 | 174 | 0 | 16 | 45 | 0 | 0 | 0.92 | 11 | 7240.42 | 927 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.66 | 707 | 0 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 28.72 | 150 | 0 | 140 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 170 | 0 | 0 | 13 | 0 | 0 | 0 | 1.1 | 136 | 0.8 | 0 | 307 | 8 | 100 | 220 | 0 | 285 | 825 | 0 | 5513.28 | 12753.7 | 76.92
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 7 | 17 | 131 | 48 | 0 | 0 | 35 | 108 | 0 | 0 | 400 | 301 | 0 | 0 | 17 | 0 | 289 | 0 | 0 | 8 | 17 | 16.5 | 17 | 0 | 420 | 0 | 0 | 0 | 150 | 27 | 0 | 10 | 0 | 88 | 24 | 5 | 40 | 0 | 2 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 18 | 51 | 10 | 36 | 0 | 345 | 345 | 50 | 202 | 28 | 70 | 80 | 136 | 9 | 14 | 114 | 34 | 0 | 74 | 0 | 305 | 210 | 342 | 35 | 38 | 0 | 139 | 8 | 0 | 76 | 30 | 0 | 18 | 174 | 0 | 16 | 32 | 0 | 2 | 5.96 | 12 | 7345.46 | 927 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.4 | 708 | 0 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 45.15 | 150 | 0 | 140 | 0 | 0 | 0 | 409 | 0 | 3.31 | 0 | 169 | 0 | 0 | 19 | 0 | 0 | 0 | 1.4 | 80 | 0.6 | 0 | 307 | 8 | 90 | 220 | 0 | 286 | 900 | 0 | 5683.86 | 13029.32 | 76.92
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 17 | 131 | 48 | 0 | 0 | 35 | 108 | 0 | 0 | 400 | 282 | 0 | 0 | 17 | 0 | 282 | 0 | 0 | 13 | 17 | 16 | 15 | 0 | 380 | 0 | 0 | 0 | 150 | 26 | 0 | 16 | 0 | 88 | 70 | 5 | 40 | 0 | 2 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 18 | 51 | 20 | 36 | 0 | 300 | 345 | 51 | 191 | 28 | 90 | 75 | 136 | 9 | 14 | 114 | 36 | 0 | 42 | 0 | 300 | 210 | 372 | 35 | 39 | 0 | 148 | 8 | 0 | 77 | 30 | 0 | 18 | 174 | 12 | 45 | 55 | 0 | 2 | 13.54 | 12 | 7317.54 | 927 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.95 | 714 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 48.33 | 161 | 0 | 185 | 0 | 0 | 0 | 329 | 0 | 4.01 | 0 | 169 | 0 | 0 | 12 | 0 | 0 | 0 | 3.4 | 72 | 0.32 | 0 | 250 | 9 | 96 | 180 | 0 | 287 | 920 | 0 | 5680.01 | 12997.55 | 76.92
14:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 0 | 112 | 52 | 0 | 0 | 35 | 108 | 0 | 0 | 400 | 280 | 0 | 0 | 17 | 0 | 282 | 0 | 0 | 30 | 17 | 16 | 15 | 0 | 380 | 0 | 0 | 0 | 150 | 29 | 0 | 17 | 0 | 100 | 88 | 3 | 40 | 0 | 4 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1050 | 17 | 51 | 20 | 36 | 0 | 300 | 335 | 48 | 187 | 28 | 89 | 75 | 136 | 9 | 14 | 114 | 36 | 0 | 70 | 0 | 305 | 210 | 363 | 35 | 39 | 0 | 131 | 8 | 0 | 0 | 0 | 0 | 18 | 172 | 0 | 65 | 105 | 0 | 1 | 27.83 | 12 | 7142.83 | 928 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.63 | 722 | 0 | 910.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 27.96 | 158 | 0 | 188 | 0 | 0 | 0 | 323 | 0 | 2.5 | 0 | 166 | 0 | 0 | 5 | 0 | 0 | 0 | 3.5 | 48 | 0.76 | 0 | 250 | 9 | 90 | 180 | 0 | 288 | 1000 | 0 | 5679.22 | 12822.05 | 76.92
15:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 17 | 7 | 112 | 64 | 0 | 0 | 35 | 108 | 0 | 0 | 400 | 304 | 0 | 0 | 17 | 0 | 312 | 0 | 0 | 0 | 17 | 16 | 15 | 0 | 380 | 0 | 0 | 0 | 150 | 27 | 0 | 40 | 0 | 100 | 88 | 1 | 40 | 0 | 2 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 13 | 51 | 20 | 36 | 0 | 355 | 300 | 44 | 205 | 29 | 90 | 70 | 136 | 9 | 6 | 114 | 24 | 0 | 37 | 0 | 310 | 210 | 360 | 34 | 40 | 0 | 142 | 6 | 0 | 40 | 28 | 0 | 18 | 172 | 1 | 65 | 105 | 0 | 2 | 37.09 | 12 | 7291.09 | 926 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.76 | 727 | 0 | 911.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 24.66 | 156 | 0 | 189 | 0 | 0 | 0 | 359 | 0 | 2.23 | 0 | 165 | 0 | 0 | 23 | 0 | 0 | 0 | 2.2 | 72 | 0.64 | 0 | 250 | 10 | 100 | 205 | 0 | 287 | 982 | 0 | 5671.13 | 12962.22 | 76.92
16:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 17 | 17 | 112 | 80 | 0 | 0 | 17 | 108 | 0 | 0 | 330 | 286 | 0 | 0 | 17 | 0 | 278 | 0 | 0 | 7 | 17 | 15.8 | 15 | 0 | 562 | 0 | 0 | 0 | 150 | 22 | 0 | 46 | 0 | 88 | 88 | 2 | 40 | 0 | 2 | 457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 8 | 51 | 20 | 36 | 0 | 354 | 335 | 48 | 192 | 28 | 90 | 70 | 136 | 22 | 13 | 114 | 28 | 0 | 23 | 0 | 305 | 50 | 326 | 35 | 40 | 0 | 142 | 8 | 0 | 61 | 28 | 0 | 18 | 172 | 17 | 65 | 124 | 0 | 1 | 24.97 | 12 | 7235.77 | 927 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.08 | 812 | 0 | 1028.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 15.44 | 154 | 0 | 165 | 0 | 0 | 0 | 389 | 0 | 1.64 | 0 | 168 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 112 | 0.2 | 0 | 250 | 10 | 90 | 210 | 0 | 288 | 982 | 0 | 5808.08 | 13043.85 | 76.92
17:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 17 | 17 | 112 | 80 | 15 | 0 | 17 | 108 | 0 | 0 | 330 | 284 | 0 | 0 | 17 | 0 | 266 | 0 | 0 | 3 | 17 | 16 | 15 | 0 | 588 | 0 | 0 | 0 | 150 | 17 | 10 | 62 | 0 | 88 | 88 | 1 | 40 | 0 | 2 | 455 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 3 | 51 | 20 | 8 | 0 | 354 | 335 | 51 | 177 | 31 | 90 | 70 | 136 | 36 | 0 | 114 | 24 | 0 | 6 | 0 | 310 | 15 | 310 | 35 | 40 | 0 | 131 | 8 | 0 | 61 | 30 | 0 | 18 | 172 | 17 | 74 | 132 | 0 | 0 | 6.85 | 12 | 7124.85 | 927 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.14 | 812 | 0 | 1019.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 4.98 | 152 | 0 | 161 | 0 | 0 | 0 | 343 | 0 | 0.38 | 0 | 165 | 0 | 0 | 6 | 0 | 0 | 0 | 1.9 | 14 | 0.07 | 0 | 250 | 9 | 100 | 215 | 0 | 289 | 987 | 0 | 5663.43 | 12788.28 | 76.91
18:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 17 | 17 | 119 | 95 | 15 | 0 | 35 | 90 | 0 | 7 | 300 | 290 | 0 | 0 | 17 | 0 | 277 | 0 | 0 | 1 | 17 | 16 | 15 | 0 | 588 | 0 | 0 | 12 | 150 | 12 | 17 | 70 | 0 | 100 | 100 | 0 | 38 | 0 | 2 | 420 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 0 | 51 | 20 | 8 | 0 | 320 | 300 | 55 | 192 | 31 | 68 | 80 | 100 | 37 | 15 | 88 | 26 | 0 | 3 | 0 | 300 | 15 | 364 | 34 | 40 | 0 | 129 | 8 | 0 | 64 | 30 | 0 | 18 | 173 | 17 | 85 | 132 | 0 | 0 | 1.61 | 12 | 7034.61 | 926 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.23 | 814 | 5 | 1117.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91 | 140 | 0 | 140 | 0 | 0 | 0 | 338 | 0 | 0.1 | 0 | 167 | 0 | 0 | 1 | 34 | 0 | 0 | 0.2 | 2 | 0 | 0 | 200 | 9 | 90 | 180 | 0 | 284 | 950 | 0 | 5568.45 | 12603.06 | 76.91
19:00 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 20 | 17 | 131 | 120 | 55 | 11 | 35 | 162 | 0 | 18 | 340 | 266 | 0 | 0 | 30 | 0 | 267 | 0 | 0 | 0 | 90 | 16 | 15 | 0 | 588 | 0 | 0 | 45 | 150 | 3 | 34 | 70 | 0 | 100 | 88 | 0 | 37 | 0 | 4 | 570 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 51 | 30 | 8 | 0 | 356 | 335 | 55 | 182 | 28 | 73 | 80 | 104 | 39 | 15 | 114 | 38 | 8 | 0 | 23 | 315 | 15 | 300 | 35 | 40 | 0 | 146 | 8 | 0 | 64 | 30 | 0 | 18 | 173 | 17 | 102 | 159 | 0 | 0 | 0 | 12 | 7813 | 881 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 936 | 17 | 1119.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 163 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 0 | 50 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 301 | 11 | 105 | 205 | 0 | 285 | 1000 | 0 | 6082.78 | 13895.78 | 76.91
19:30 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 54 | 17 | 131 | 144 | 145 | 0 | 35 | 144 | 0 | 30 | 380 | 304 | 0 | 0 | 35 | 0 | 295 | 0 | 0 | 0 | 90 | 16 | 15 | 0 | 450 | 0 | 0 | 80 | 150 | 0 | 34 | 70 | 0 | 100 | 100 | 0 | 37 | 0 | 0 | 543 | 0 | 0 | 30 | 0 | 8 | 0 | 0 | 0 | 0 | 1124 | 0 | 51 | 50 | 8 | 0 | 356 | 335 | 54 | 203 | 28 | 90 | 80 | 155 | 39 | 15 | 114 | 36 | 8 | 0 | 40 | 315 | 15 | 343 | 34 | 40 | 0 | 152 | 8 | 0 | 64 | 30 | 0 | 18 | 173 | 54.5 | 102 | 168 | 0 | 0 | 0 | 12 | 8204.5 | 880 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1036 | 17 | 1354.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 163 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 165 | 0 | 70 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 11 | 115 | 220 | 0 | 285 | 1170 | 0 | 6525.25 | 14729.75
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 17 | 131 | 144 | 145 | 0 | 35 | 90 | 0 | 36 | 380 | 300 | 0 | 0 | 35 | 0 | 286 | 0 | 0 | 0 | 90 | 16 | 15 | 0 | 450 | 0 | 0 | 72 | 150 | 0 | 34 | 70 | 0 | 100 | 72 | 0 | 37 | 0 | 5 | 544 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 51 | 20 | 8 | 0 | 356 | 335 | 54 | 197 | 28 | 90 | 80 | 149 | 39 | 15 | 114 | 36 | 8 | 0 | 40 | 305 | 45 | 330 | 35 | 35 | 0 | 152 | 8 | 0 | 64 | 30 | 0 | 18 | 173 | 48 | 83 | 160 | 0 | 0 | 0 | 12 | 7996 | 880 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 1402.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 165 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 166 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 11 | 115 | 220 | 0 | 285 | 1170 | 0 | 6567.2 | 14563.2 | 76.91
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 41 | 17 | 131 | 145 | 145 | 0 | 17 | 72 | 0 | 47 | 400 | 276 | 0 | 0 | 17 | 0 | 266 | 0 | 0 | 0 | 108 | 16 | 15 | 0 | 480 | 0 | 0 | 50 | 150 | 3 | 34 | 70 | 0 | 100 | 72 | 0 | 38 | 0 | 7 | 543 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 20 | 8 | 0 | 356 | 335 | 54 | 182 | 28 | 90 | 80 | 155 | 39 | 15 | 114 | 34 | 8 | 0 | 40 | 310 | 55 | 315 | 34 | 39 | 0 | 152 | 8 | 0 | 64 | 30 | 0 | 18 | 173 | 35 | 83 | 170 | 0 | 0 | 0 | 12 | 7968 | 927 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 1421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 177 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 165 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 105 | 220 | 0 | 286 | 1170 | 0 | 6719 | 14687 | 76.9
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 17 | 131 | 145 | 30 | 0 | 17 | 35 | 0 | 16 | 400 | 306 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 108 | 16 | 15 | 0 | 480 | 0 | 0 | 36 | 150 | 8 | 34 | 70 | 0 | 100 | 72 | 0 | 39 | 0 | 15 | 504 | 0 | 0 | 33 | 5 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 54 | 203 | 28 | 90 | 70 | 155 | 38 | 15 | 114 | 38 | 8 | 0 | 40 | 310 | 60 | 332 | 35 | 40 | 0 | 154 | 8 | 0 | 64 | 27 | 0 | 18 | 173 | 17 | 83 | 171 | 0 | 0 | 0 | 12 | 7769 | 927 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1059 | 0 | 1412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 178 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 166 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 284 | 1120 | 0 | 6670 | 14439 | 76.9
23:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 17 | 17 | 131 | 145 | 30 | 0 | 17 | 35 | 0 | 16 | 400 | 305 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 108 | 16.5 | 15 | 0 | 480 | 0 | 0 | 24 | 150 | 8 | 34 | 70 | 0 | 100 | 72 | 0 | 40 | 0 | 18 | 501 | 0 | 0 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 55 | 197 | 28 | 90 | 70 | 155 | 39 | 15 | 114 | 38 | 8 | 0 | 40 | 315 | 60 | 333 | 35 | 40 | 0 | 153 | 8 | 0 | 64 | 25 | 0 | 18 | 173 | 17 | 83 | 168 | 0 | 0 | 0 | 12 | 7739.5 | 927 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 1417 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 165 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 253 | 1112 | 0 | 6626 | 14365.5 | 76.9
Total KWH | 22320 | 780480 | 400800 | 0 | 0 | 0 | 0 | 0 | 8578800 | 0 | 0 | 291960 | 409320 | 2988144 | 2020800 | 480491 | 19956 | 487479 | 1369440 | 0 | 134400 | 9299500 | 7107753 | 0 | 0 | 204249 | 0 | 6925512 | 0 | 0 | 137553 | 907200 | 393000 | 370440 | 0 | 10802727.27 | 0 | 0 | 266880 | 3700000 | 185760 | 393122 | 775296 | 0 | 1766400 | 1110720 | 30164 | 940920 | 0 | 313920 | 11774545 | 0 | 0 | 216480 | 22280.4 | 17563 | 0 | 0 | 0 | 0 | 25194543 | 144720 | 1223744 | 279345 | 685818 | 0 | 8412500 | 8148000 | 1240800 | 4803000 | 740520 | 1907520 | 1923890 | 3483840 | 450240 | 311210 | 2636820 | 782400 | 186091 | 434282 | 203200 | 7481000 | 3541300 | 8247000 | 826000 | 894840 | 0 | 3404209 | 122592 | 0 | 1662720 | 662880 | 0 | 434000 | 3584260 | 239040 | 1171200 | 2536800 | 0 | 10250 | 202410 | 294240 | 174153598.67 | 22223273 | 4466304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 522000 | 20327270 | 56640 | 24887108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570720 | 0 | 265496 | 3878636 | 0 | 4128173 | 0 | 0 | 0 | 8701527 | 0 | 22440 | 0 | 4080000 | 0 | 242416 | 113835 | 487459 | 0 | 0 | 19830.84 | 747360 | 4233 | 0 | 6436000 | 234633 | 2450000 | 5275680 | 0 | 6850224 | 23531636.36 | 0 | 140522894.2 | 314676492.87

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 19-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13029.32 | MW | 12:00 Hr. | Energy Generated |  |  | 314.6765 |  | MKWHr.
| Day Peak Demand |  |  | 13123.32 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.292 |  | MKWHr.
| Evening Peak Generation |  |  | 14729.75 | MW | 19:30 Hr. | Energy Demand |  |  | 315.9685 |  | MKWHr.
| Evening Peak Demand |  |  | 14775.75 | MW | 19:30 Hr. | Maximum Temperature |  |  | 34.2 |  | °C
| Minimum Generation of the Day |  |  | 11712.09 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 1015.21 |  | MMCFD
| Maximum Generation of the Day |  |  | 14729.75 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.3552 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.4777 | 0 | 10.517 | 0 | 0 | 0.13755 | 0 | 0 | 54.1323 | Gas | 134.9769 | Gas | 491176731.1159
| Chattogram Zone |  |  | 4.0139 | 36.9691 | 4.5687 | 0 | 0.94092 | 0.17488 | 0 | 0.18576 | 46.8533 | Coal | 98.1942 | Coal | 652016345.088
| Cumilla Zone |  |  | 27.4895 | 0 | 9.1471 | 0 | 0 | 0.43428 | 0.7824 | 0 | 37.8532 | HFO | 29.2606 | HFO | 551731987.838
| Mymensingh Zone |  |  | 0 | 0 | 4.2413 | 0 | 0 | 0.21266 | 0 | 0 | 4.4539 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.8608 | Hydro | 0.94092 | Hydro | 94092
| Khulna Zone |  |  | 4.4663 | 20.3273 | 0.05664 | 0 | 0 | 0.522 | 22.2233 | 0 | 47.5955 | Solar | 3.2253 | Solar | 51332796.5324
| Barishal Zone |  |  | 7.9603 | 36.8179 | 0 | 0 | 0 | 0.004233 | 0 | 0 | 44.7824 | Import | 47.8928 | Import | 250758060.01
| Rajshahi Zone |  |  | 16.7083 | 0 | 0 | 0 | 0 | 0.85866 | 24.8871 | 0 | 42.4541 | Wind | 0.18576 | Wind | 2719526.4
| Rangpur Zone |  |  | 0 | 4.08 | 0.72988 | 0 | 0 | 0.88103 | 0 | 0 | 5.6909
| Total |  |  | 134.9769 | 98.1942 | 29.2606 | 0 | 0.94092 | 3.2253 | 47.8928 | 0.18576 | 314.6765
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 491176731.1159 |  | Hydro | 94092
|  |  |  | Coal | 652016345.088 |  | Solar | 51332796.5324
|  |  |  | HFO | 551731987.838 |  | Import | 250758060.01
|  |  |  | HSD | 0 |  | Wind | 2719526.4
[5 empty] | Total: | 199,98,29,538 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2233 | Peak Hr Flow | 880.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 46052309.19 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.8871 | Peak Hr Flow | 1354.25 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 792 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.7824 | Peak Hr Flow | 36.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1070 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.8928 | Peak Hr Flow | 2270.25 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 44 |  | 5518
|  |  |  | Chattogram |  | 0 |  | 1524
|  |  |  | Cumilla |  | 0 |  | 1370
|  |  |  | Mymensingh |  | 0 |  | 1083
|  |  |  | Sylhet |  | 0 |  | 533
|  |  |  | Khulna |  | 0 |  | 1464
|  |  |  | Barishal |  | 0 |  | 468
|  |  |  | Rajshahi |  | 0 |  | 1381
|  |  |  | Rangpur |  | 0 |  | 849
|  |  |  | Total |  | 44 |  | 14190
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 435.09
|  |  |  | Total Unavailable Capacity |  |  |  | 735.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:20 | 08:20 | Niamatpur 132/33kV S/S 132 kV Rahanpur Ckt-2 Tripped showing Distance Relay CB Line :
Auto reclosing Z1: operate phs A relays Due to Poesha feeder trial এ o/c & E/F signal
এসে ট্রিপ করে ।
| 08:24 | 08:48 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing REF 630 relays Due to Under | [7 empty] | 30.0MW load
|  |  | Frequency | [7 empty] | interrup.
| 08:24 | 08:49 | Benapole 132/33kV S/S Transformer-2(416T) LT Tripped showing REF 630 relays Due to Under | [7 empty] | 20.0MW load
|  |  | Frequency | [7 empty] | interrup.
| 08:25 | 08:58 | Mongla 132/33kV S/S T-1 LT Tripped showing No relays Due to CB Open Because of Black out | [7 empty] | 41.0MW load
interrup.
| 08:25 |  | About 345 MW interruption occurred under Bagerhat, Mongla, Satkhira, Goalpara, Khulna
(C), Noapara & Benapole S/S up to 8:42 hrs as 132 kv buses at Khulna (S) got tripped
operating bus bar protection trip. Khulna (S) 132 kv buses were switched on at 10:00 hr &
Satkhira S/S got power.
| 08:27 |  | Khulna(S) 230/132kV S/S Capacitor Bank 1 & 2 Tripped showing PROTECTION RELAY relays.
| 08:27 | 11:20 | Gallamari- Khulna (S) 132kV Ckt-2 Tripped from Khulna(S) 230/132kV end showing BBP/BFP | [7 empty] | 23.0MW load
|  |  | BAY UNIT relays. | [7 empty] | interrup. Khulna(S)
230/132kV end
| 08:27 | 11:20 | Gallamari- Khulna (S) 132kV Ckt-1 Tripped from Khulna(S) 230/132kV end showing BBP/BFP | [7 empty] | 23.0MW load
|  |  | BAY UNIT relays. | [7 empty] | interrup. Khulna(S)
230/132kV end
| 08:27 | 10:09 | Khulna (S)-Satkhira 132kV Ckt-2 Tripped from Khulna(S) 230/132kV end showing BBP/BFP BAY | [7 empty] | 51.0MW load
|  |  | UNIT relays. | [7 empty] | interrup. Khulna(S)
230/132kV end
| 08:27 | 10:00 | Khulna (S)-Satkhira 132kV Ckt-1 Tripped from Khulna(S) 230/132kV end showing BBP/BFP BAY | [7 empty] | 51.0MW load
|  |  | UNIT relays. | [7 empty] | interrup. Khulna(S)
230/132kV end
| 08:27 | 09:59 | Khulna(C )-Khulna (S) 132kV Ckt-2 Tripped from Khulna(S) 230/132kV end showing BBP/BFP | [7 empty] | 107.0MW load
|  |  | BAY UNIT relays. | [7 empty] | interrup. Khulna(S)
230/132kV end
| 08:27 | 11:08 | Khulna(S) 230/132kV S/S TR-3 HT Tripped showing BUSBER PROTECTION TRIP relays. | [7 empty] | 143.0MW load
interrup.
| 08:27 | 11:09 | Khulna(S) 230/132kV S/S TR-3 LT Tripped showing BUSBER PROTECTION relays. | [7 empty] | 143.0MW load
interrup.
| 08:27 | 09:51 | Khulna(S) 230/132kV S/S TR-2 LT Tripped showing BBP/BFP BAY UNIT relays. | [7 empty] | 111.0MW load
interrup.
| 08:27 | 09:55 | Khulna(S) 230/132kV S/S TR-1 LT Tripped showing BBP/BFP BAY UNIT relays. | [7 empty] | 111.0MW load
interrup.
| 08:27 | 09:55 | Khulna(C )-Khulna (S) 132kV Ckt-1 Tripped from Khulna(S) 230/132kV end showing BBP/BFP | [7 empty] | 107.0MW load
|  |  | BAY UNIT relays. | [7 empty] | interrup. Khulna(S)
230/132kV end
|  | 08:35 | Feni 132/33kV S/S T-1(405T) HT is restored.
|  | 08:35 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 08:56 | 08:59 | Mongla 132/33kV S/S 100MW ERBL Solar PS Tripped showing No relays Due to CB Open | [7 empty] | 68.0MW load
|  |  | instruction by ALDC Due to Black out. | [7 empty] | interrup.
|  | 09:10 | Kabirpur 132/33kV S/S XFR, T-I HT is restored.
|  | 09:11 | Kabirpur 132/33kV S/S XFR, T-I LT is restored.
|  | 09:11 | Kabirpur 132/33kV S/S XFR, T-3 HT is restored.
| 09:12 | 16:38 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Bay extension work at
Rajendrapur grid.
|  | 09:12 | Kabirpur 132/33kV S/S XFR, T-3 LT is restored.
| 09:12 | 16:41 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to Bay extension work at
Rajendrapur grid.
| 09:23 | 10:09 | Khulna (S)-Satkhira 132kV Ckt-2 Forced S/D from Satkhira 132/33kV end Due to Khulna south | [7 empty] | 55.0MW load
|  |  | grid maintenance work | [7 empty] | interrup. Satkhira
132/33kV end
| 09:23 | 10:01 | Khulna (S)-Satkhira 132kV Ckt-1 Forced S/D from Satkhira 132/33kV end Due to Khulna south | [7 empty] | 55.0MW load
|  |  | grid maintenance work | [7 empty] | interrup. Satkhira
132/33kV end
| 09:40 | 17:51 | Dhamrai-Kaliakoir 132 kV Ckt-2 Forced S/D from Kaliakoir 400/230/132kV end Due to By NLDC
and from Dhamrai 132/33kV end Due to Project work.15 MW Load shifted by manikgonj grid
|  | 10:17 | Naogaon 132/33kV S/S T-3 LT is restored.
|  | 10:18 | Naogaon 132/33kV S/S T-3 HT is restored.
|  | 10:20 | Rangpur-Saidpur 132kV Ckt-2 is restored.
|  | 10:20 | Rangpur-Saidpur 132kV Ckt-2 is restored.
|  | 11:24 | Ruppur 132/11kV S/S TR-01 HT is restored.
| 11:29 | 19:16 | Bogura-Mahasthangar (New)) 132 kV Ckt-2 Scheduled S/D from Mahasthangarh 132/33kV end Due
to CB Replacement work. and from Bogura 132/33kV end Due to Breaker change
| 12:00 |  | Day Peak Gen. 13029 MW
|  | 12:56 | Chhatak 132/33kV S/S T-3 HT is restored.
|  | 13:05 | Chhatak 132/33kV S/S T-3 LT is restored.
| 13:08 | 16:20 | Kurigram-Rangpur 132kV Ckt-1 Forced S/D from Kurigram 132/33kV end Due to Signal | [7 empty] | 30.0MW load
|  |  | checking & annunciator | [7 empty] | interrup. Kurigram
132/33kV end
| 13:38 | 14:05 | Shahjibazar 132/33kV S/S SPCL 86 MW Tripped showing MICOM P121 Relay relays Due to Heavy
Rain stormy weather, CT blust from 86 MW power plant.
| 13:38 | 14:07 | Shahjibazar 132/33kV S/S BPDB 60 MW Tripped showing CB Tripping Relay relays Due to Heavy
Rain stormy weather, CT blust from 86 MW power plant.
| 14:18 | 14:50 | Fenchuganj-Sreemangal 132kV Ckt-1 Tripped from Sreemongol 132/33kV end showing Distance
Relay , relays Due to Stormy weather and from Fenchuganj 230/132/33kV end showing
REL670 REC650 relays Due to Bad weather
| 15:09 | 15:36 | Rajbari 132/33kV S/S Transformer-3 LT Tripped showing 86.1 & 86.2 operated. relays Due to | [7 empty] | 7.0MW load
|  |  | O/C, | [7 empty] | interrup.
|  | 15:54 | Dhamrai 132/33kV S/S Main Bus-1 is restored.
| 17:39 | 21:09 | Gopalganj(N)-Madaripur 132kV Ckt-3 Tripped from Madaripur 132/33kV end showing Distance
Relay relays Due to A-B-N Trip ABC Over Current Earth Fault Z-1, 1.388 km A-
9732, B- 9827, C - 238.7 and from Gopalganj 400/132kV end showing Distance relay relays
Due to Phase to phase fault
| 19:30 |  | Evening peak generation 14729 MW
|  | 21:27 | Gopalganj 400/132kV S/S 400kV Bus-01 is restored.
| 06:00 |  | Minimum Generation is 12256 MW
| 06:04 | 07:05 | Gulshan 132/33kV S/S MT-2 LT Scheduled S/D Due to Aux-01 transformer maintenance work
| 06:05 | 06:59 | Gulshan 132/33kV S/S MT-2 HT Scheduled S/D Due to Aux-01 transformer maintenance work
| 06:37 | 06:52 | Chandina 132/33kV S/S TR-3 HT Tripped showing K86L, lock out relay 1&2 both, F87T1, | [7 empty] | 13.0MW load
|  |  | F87T2, F87BB, BCU relays Due to PBS-01, over current & earth fault | [7 empty] | interrup.
| 06:37 | 06:52 | Chandina 132/33kV S/S TR-3 LT Tripped showing K86L1 & K86L2 lock out 1&2, F-51 relays | [7 empty] | 13.0MW load
|  |  | Due to PBS-1, over current, Earth Fault. | [7 empty] | interrup.
| 06:47 |  | Bhaluka 132/33kV S/S Transformer- 01 HT Forced S/D Due to 33 kv bus section-01-bus loop( | [7 empty] | 60.0MW load
|  |  | sokhipur feeder) red hot | [7 empty] | interrup.
| 06:47 |  | Bhaluka 132/33kV S/S Transformer- 01 LT Forced S/D Due to 33 kv bus section-01bus loop( | [7 empty] | 60.0MW load
|  |  | sokhipur feeder) red hot | [7 empty] | interrup.
| 07:09 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to 33kV DS of T-1A R-Phase Red
Hot Manitenance.
| 07:09 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to 33kV DS of T-1A R-Phase Red | [7 empty] | 40.0MW load
|  |  | Hot Manitenance. | [7 empty] | interrup.
| 07:17 |  | Jhenaidah-Jhenaidah(New) 132kV Ckt-3 Forced S/D from Jhenaidah 230/132kV end Due to Red
Hot maintenance
| 07:18 |  | Jhenaidah 132/33kV S/S Jhenaidah1-Jhenaidah2,132kV Circuit-3(L5) Forced S/D Due to 132kV
Jhenaidah-230kV Jhenaidah CKT-3 (L-5) Red Hot Manitenance at Jhenaidah 230kV SS End.
| 07:22 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Underground cable replacement
| 07:23 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Underground cable replacement
| 07:26 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Underground cable replacement | [7 empty] | 27.0MW load
|  |  | at 33kV Bus section-1 | [7 empty] | interrup.
| 07:27 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Underground cable replacement | [7 empty] | 27.0MW load
interrup.
| 07:28 |  | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 19-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 369 | 8578800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 380 | 9299500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 304 | 7107753 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 19956 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 295 | 6925512 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 22320 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 291960 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 2020800 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 487479 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 204249 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 393000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 370440 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 400800 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 480491 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 131 | 2988144 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 780480 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 30 | 134400 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1369440 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 137553 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 409320 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 450 | 10802727.27 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 907200 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2738 | 54132324.27
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3700000 | Unit #1 Under Maintenance, Unit#2 Running at 100MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 22280.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 144720 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 216480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 940920 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 8 | 17563 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 70 | 775296 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 34 | 393122 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1766400 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 313920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 266880 | Engine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 30164 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1110720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1124 | 25194543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 185760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 543 | 11774545 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2276 | 46853313.4
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 203 | 4803000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8412500 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 8148000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 28 | 740520 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 54 | 1240800 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 685818 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1223744 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 50 | 279345 | Engine Problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 40 | 203200 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1923890 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 155 | 3483840 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 36 | 782400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 186091 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 311210 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2636820 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 39 | 450240 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 90 | 1907520 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 434282 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1662 | 37853220
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 10250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 168 | 2536800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 102 | 1171200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 202410 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 294240 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 54.5 | 239040 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 336.5 | 4453940
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 34 | 826000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 894840 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3404209 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 662880 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 64 | 1662720 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 3584260 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 434000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 122592 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7481000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 343 | 8247000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 15 | 3541300 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1192 | 30860801
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 22223273 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 170 | 4466304 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 56640 | -
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 522000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1036 | 20327270 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 2103 | 47595487
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 285 | 6850224 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 234633 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 115 | 2450000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1170 | 23531636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5275680 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 270 | 6436000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4233 | -
Barishal Area Total |  |  |  |  | 3585.1 | 2071 | 44782406.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 151 | 3878636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 163 | 4128173 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 340 | 8701527 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 22440 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1354.25 | 24887108 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 265496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 570720 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 2008.25 | 42454100
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 165 | 4080000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 487459 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 19830.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 242416 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 113835 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 747360 | -
Rangpur Area Total |  |  |  |  | 950 | 343 | 5690900.84
Eastern Grid Total |  |  |  |  | 16921.242 | 8204.5 | 174153598.67
Western Grid Total |  |  |  |  | 11702.84 | 6525.25 | 140522894.2
National Grid Total |  |  |  |  | 28624.082 | 14729.75 | 314676492.87
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 19-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9983.54 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4162.2 | MW
i) Dhaka area |  |  | 5473.71 |  | MW | i) Khulna area |  |  |  | 1464.2 | MW
ii) Chattogram area |  |  | 1524 |  | MW | ii) Barishal area |  |  |  | 467.8 | MW
iii) Cumilla area |  |  | 1369.83 |  | MW | iii) Rajshahi area |  |  |  | 1381.2 | MW
iv) Mymensingh area |  |  | 1083 |  | MW | iv) Rangpur area |  |  |  | 849 | MW
v) Sylhet area |  |  | 533 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14145.74 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 81 | 00:00 | 133 | Patuakhali | 86.6 | 22:00
2 | AKSML | 128.7 | 06:00 | 68 | Jaldhaka | 68 | 19:30 | 134 | Payra | 36 | 22:00
3 | Aftabnagar | 68 | 13:00 | 69 | Jamalpur | 116 | 19:30 | 135 | Postogola | 63 | 13:00
4 | Agargaon | 140 | 13:00 | 70 | Jashore | 148 | 13:00 | 136 | Purbachal | 18 | 00:00
5 | Agrabad | 102 | 16:00 | 71 | Jhenaidah | 126 | 00:00 | 137 | Purbasadipur | 109 | 20:00
6 | Amnura | 31 | 20:00 | 72 | Joydebpur | 155 | 18:00 | 138 | Rahanpur | 25 | 23:00
7 | Ashuganj | 98 | 01:00 | 73 | Joypurhat | 54 | 19:00 | 139 | Rahim | 45 | 17:00
8 | BSRM | 195 | 23:00 | 74 | Juldah | 14 | 07:00 | 140 | Rajbari | 82 | 00:00
9 | Bagerhat | 83 | 00:00 | 75 | KSRM | 27 | 09:00 | 141 | Rajendrapur | 131 | 19:30
10 | Bajitpur | 46 | 00:00 | 76 | Kabirpur | 286 | 10:00 | 142 | Rajshahi | 110 | 00:00
11 | Bakulia | 114 | 19:00 | 77 | Kachua | 86 | 00:00 | 143 | Rajshahi-230 | 81 | 13:00
12 | Banani | 58 | 12:00 | 78 | Kallyanpur | 105 | 12:00 | 144 | Ramganj | 118 | 23:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 26 | 09:00 | 145 | Rampur | 46 | 23:00
14 | Barapukuria | 57 | 21:00 | 80 | Kamrangirchar | 70 | 12:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 24 | 21:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 137 | 19:30
16 | Barishal | 111 | 20:00 | 82 | Kasba | 35 | 00:00 | 148 | Ruppur | 7.8 | 15:00
17 | Barishal-230 | 100 | 18:30 | 83 | Kazla | 105 | 13:00 | 149 | SSM | 12 | 00:00
18 | Baroaulia | 66 | 14:00 | 84 | Keranigonj | 87 | 14:00 | 150 | Saidpur | 96 | 19:00
19 | Baroirhat | 65 | 19:30 | 85 | Khagrachori | 30 | 19:00 | 151 | Satkhira | 132 | 21:00
20 | Bashundhara | 197 | 12:00 | 86 | Khulna | 73 | 12:00 | 152 | Satmasjid | 114 | 13:00
21 | BashundharaCement | 10 | 16:00 | 87 | Khulshi | 190 | 13:00 | 153 | Savar | 236 | 09:00
22 | Beanibazar | 70 | 00:00 | 88 | Kishoreganj | 116 | 21:00 | 154 | SevenRings | 15.68 | 18:00
23 | Benapole | 69 | 00:00 | 89 | Kodda | 308 | 18:00 | 155 | ShahCement | 28 | 04:00
24 | Bhaluka | 150 | 10:00 | 90 | Kulaura | 41 | 00:00 | 156 | Shahjadpur | 82 | 20:00
25 | Bhandaria | 57 | 22:00 | 91 | Kurigram | 56 | 19:00 | 157 | Shahjibazar | 115 | 02:00
26 | Bhangura | 34 | 00:00 | 92 | Kushtia | 153 | 00:00 | 158 | Shahmirpur | 60 | 00:00
27 | Bheramara(GK) | 68 | 00:00 | 93 | Lalbag | 74 | 11:00 | 159 | Shariatpur | 83 | 00:00
28 | Bhulta | 238 | 10:00 | 94 | Lalmonirhat | 50 | 19:30 | 160 | Sherpur | 132 | 19:30
29 | Bog-Sherpur | 64 | 20:00 | 95 | MI_Cement | 14 | 12:00 | 161 | Shikalbaha | 35 | 14:00
30 | Bogura | 157 | 20:00 | 96 | Madanganj | 44 | 00:00 | 162 | Shitalakhya | 88.9 | 12:00
31 | Borhanuddin | 99 | 23:00 | 97 | Madaripur | 107 | 22:00 | 163 | Sholosohor | 48 | 16:00
32 | Brahmanbaria | 126 | 00:00 | 98 | Madartek | 87.84 | 00:00 | 164 | Shyampur | 182 | 01:00
33 | Cantonment | 154 | 12:00 | 99 | Madunaghat | 57 | 22:00 | 165 | Siddhirganj | 125 | 12:00
34 | Chandina | 20.7 | 00:00 | 100 | Magura | 62 | 00:00 | 166 | Sirajganj | 108 | 20:00
35 | Chandpur | 70 | 00:00 | 101 | Mahasthangarh | 74 | 23:00 | 167 | Sonargaon | 126 | 00:00
36 | Chandraghona | 37 | 20:00 | 102 | Manikganj | 139 | 10:00 | 168 | Sreemongol | 77 | 00:00
37 | Chapai | 69 | 22:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 108 | 19:30
38 | Charsaidpur | 50 | 12:00 | 104 | Matarbari | 48 | 19:00 | 170 | Srinagar | 44.33 | 23:00
39 | Chauddagram | 70 | 00:00 | 105 | Matuail | 66 | 12:00 | 171 | Sunamganj | 52 | 19:30
40 | Chhatak | 33 | 19:30 | 106 | Millgate | 123 | 12:00 | 172 | Sylhet | 38 | 00:00
41 | Chowmuhani | 229 | 20:00 | 107 | Mirpur | 123 | 12:00 | 173 | Sylhet-132 | 115 | 00:00
42 | Chuadanga | 108 | 01:00 | 108 | Mirsorai | 12 | 13:00 | 174 | TK | 36 | 23:00
43 | Coxsbazar | 130 | 20:00 | 109 | Mirzapur | 44 | 00:00 | 175 | Tangail | 163 | 21:00
44 | Cumilla(N) | 140 | 19:30 | 110 | Mithapukur | 56 | 20:00 | 176 | Thakurgaon | 79 | 19:30
45 | Cumilla(S) | 171 | 14:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 127 | 11:00
46 | Daudkandi | 131 | 20:00 | 112 | Mogbazar | 162.9 | 12:00 | 178 | Ullahpara | 35 | 19:00
47 | Dhaka | 72 | 12:00 | 113 | Mongla | 44 | 12:00 | 179 | Ullon | 40 | 20:00
48 | Dhamrai | 138 | 19:00 | 114 | Motijheel | 43 | 12:00 | 180 | Uttara | 84 | 12:00
49 | Dhanmondi | 150 | 12:00 | 115 | Muktagacha | 30 | 20:00 | 181 | UttaraNew | 60 | 12:00
50 | Dohazari | 107 | 21:00 | 116 | Munshiganj | 110 | 00:00 | 182 | Zigatola | 76 | 12:00
51 | Faridpur | 158 | 00:00 | 117 | Muradnagar | 27 | 21:00
52 | Fatullah | 103 | 12:00 | 118 | Mymensingh | 192 | 19:30
53 | Fenchuganj | 39 | 19:30 | 119 | Naogaon | 122 | 21:00
54 | Feni | 123 | 19:00 | 120 | Narail | 54 | 00:00
55 | GPH | 89 | 11:00 | 121 | Narinda | 91 | 13:00
56 | Ghatail | 76 | 19:30 | 122 | Narshingdi | 174 | 00:00
57 | Ghorashal | 18 | 00:00 | 123 | Natore | 136 | 21:00
58 | Ghorashal-230 | 96 | 01:00 | 124 | Nawabganj | 54 | 00:00
59 | Goalpara | 34 | 00:00 | 125 | Netrakona | 116 | 22:00
60 | Gollamari | 90 | 13:00 | 126 | New | 89.4 | 11:00
61 | Gopalganj | 94.5 | 00:00 | 127 | Niamatpur | 64 | 22:00
62 | Gulshan | 94 | 11:00 | 128 | Noapara | 44 | 14:00
63 | Halishahar | 75 | 11:00 | 129 | PHP | 9 | 18:30
64 | HaripurSBU | 184 | 12:00 | 130 | Pabna | 119 | 00:00
65 | Hasnabad | 85 | 14:00 | 131 | Palashbari | 94 | 19:30
66 | Hathazari | 88 | 19:00 | 132 | Panchagarh | 54 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 19-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13573.67 | 54 |  | 13630.1
1:00 | 13377.59 | 51 |  | 13430.59
2:00 | 13048.8 | 71 |  | 13123
3:00 | 12708.97 | 69 |  | 12780.97
4:00 | 12456.13 | 61 |  | 12520.13
5:00 | 12111.72 | 47 |  | 12160.72
6:00 | 11730.98 | 39 |  | 11771.74
7:00 | 11750.14 | 35 |  | 11786.72
8:00 | 11712.09 | 49 |  | 11763.09
9:00 | 11720.1 | 41 |  | 11763.1
10:00 | 12301.04 | 78 |  | 12383.04
11:00 | 12753.7 | 76 |  | 12832.7
12:00 | 13029.32 | 90 |  | 13123.32
13:00 | 12997.55 | 53 |  | 13052.55
14:00 | 12822.05 | 41 |  | 12865.05
15:00 | 12962.22 | 68 |  | 13033.22
16:00 | 13043.85 | 57 |  | 13103.85
17:00 | 12788.28 | 44 |  | 12834.28
18:00 | 12603.06 | 37 |  | 12642.06
19:00 | 13895.78 | 53 |  | 13950.78
19:30 | 14729.75 | 44 |  | 14775.75
20:00 | 14563.2 | 45 |  | 14610.2
21:00 | 14687 | 36 |  | 14725
22:00 | 14439 | 49 |  | 14490
23:00 | 14365.5 | 48 |  | 14415.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 19-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7288 | 6285.67 | 13573.67 | DAILY GENERATION CURVE
00:30 | 7267 | 6208.63 | 13475.63
01:00 | 7246 | 6131.59 | 13377.59 | 19-05-2025
01:30 | 7209 | 6004.195 | 13213.195
02:00 | 7172 | 5876.8 | 13048.8
02:30 | 7079 | 5799.885 | 12878.885
03:00 | 6986 | 5722.97 | 12708.97
03:30 | 6958.5 | 5624.05 | 12582.55
04:00 | 6931 | 5525.13 | 12456.13
04:30 | 6900.5 | 5383.425 | 12283.925
05:00 | 6870 | 5241.72 | 12111.72
05:30 | 6706.85 | 5214.5 | 11921.35
06:00 | 6543.7 | 5187.28 | 11730.98
06:30 | 6538.365 | 5202.195 | 11740.56
07:00 | 6533.03 | 5217.11 | 11750.14
07:30 | 6514.28 | 5216.835 | 11731.115
08:00 | 6495.53 | 5216.56 | 11712.09
08:30 | 6517.68 | 5198.415 | 11716.095
09:00 | 6539.83 | 5180.27 | 11720.1
09:30 | 6745.85 | 5264.72 | 12010.57
10:00 | 6951.87 | 5349.17 | 12301.04
10:30 | 7096.145 | 5431.225 | 12527.37
11:00 | 7240.42 | 5513.28 | 12753.7
11:30 | 7292.94 | 5598.57 | 12891.51
12:00 | 7345.46 | 5683.86 | 13029.32
12:30 | 7331.5 | 5681.935 | 13013.435
13:00 | 7317.54 | 5680.01 | 12997.55
13:30 | 7230.185 | 5679.615 | 12909.8
14:00 | 7142.83 | 5679.22 | 12822.05
14:30 | 7216.96 | 5675.175 | 12892.135
15:00 | 7291.09 | 5671.13 | 12962.22
15:30 | 7263.43 | 5739.605 | 13003.035
16:00 | 7235.77 | 5808.08 | 13043.85
16:30 | 7180.31 | 5735.755 | 12916.065
17:00 | 7124.85 | 5663.43 | 12788.28
17:30 | 7079.73 | 5615.94 | 12695.67
18:00 | 7034.61 | 5568.45 | 12603.06
18:30 | 7423.805 | 5825.615 | 13249.42
19:00 | 7813 | 6082.78 | 13895.78
19:30 | 8204.5 | 6525.25 | 14729.75
20:00 | 7996 | 6567.2 | 14563.2
20:30 | 7982 | 6643.1 | 14625.1 |  | Executive Engineer
21:00 | 7968 | 6719 | 14687 |  | Network Operation Division
21:30 | 7868.5 | 6694.5 | 14563
22:00 | 7769 | 6670 | 14439
22:30 | 7754.25 | 6648 | 14402.25
23:00 | 7739.5 | 6626 | 14365.5

## En-Curve
QF-LDC-12
Date | 19-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3417 | 2085 | 924 | 0 | 38 | 1268.67 | 40 | 4704 | 0 | 303 | 791 | 0 | 0 | 3 | 54 | DAILY ENERGY CURVE
00:30 | 3422 | 2068.5 | 925 | 0 | 38 | 1240.63 | 40 | 4665.5 | 0 | 284 | 790.5 | 0 | 0 | 1.5 | 52.5 | 19-05-2025
01:00 | 3427 | 2052 | 926 | 0 | 38 | 1212.59 | 40 | 4627 | 0 | 265 | 790 | 0 | 0 | 0 | 51
01:30 | 3475.5 | 2042.5 | 926 | 0 | 37 | 1141.195 | 40 | 4518 | 0 | 247.5 | 785.5 | 0 | 0 | 0 | 61 | Energy Generated | 314.6765 |  | MKWHr
02:00 | 3524 | 2033 | 926 | 0 | 36 | 1069.8 | 40 | 4409 | 0 | 230 | 781 | 0 | 0 | 0 | 71 | Energy not Served | 1.292 |  | MKWHr
02:30 | 3486 | 2032 | 926 | 0 | 36 | 1044.885 | 40 | 4346 | 0 | 202 | 766 | 0 | 0 | 0 | 70 | Total Energy Requirement | 315.9685 |  | MKWHr
03:00 | 3448 | 2031 | 926 | 0 | 36 | 1019.97 | 40 | 4283 | 0 | 174 | 751 | 0 | 0 | 0 | 69
03:30 | 3452.5 | 2032 | 925.5 | 0 | 34 | 972.55 | 40 | 4233 | 0 | 147.5 | 745.5 | 0 | 0 | 0 | 65
04:00 | 3457 | 2033 | 925 | 0 | 32 | 925.13 | 40 | 4183 | 0 | 121 | 740 | 0 | 0 | 0 | 61
04:30 | 3485.5 | 2074 | 925 | 0 | 33 | 873.425 | 40 | 4027.5 | 0 | 121 | 704.5 | 0 | 0 | 0 | 54
05:00 | 3514 | 2115 | 925 | 0 | 34 | 821.72 | 40 | 3872 | 0 | 121 | 669 | 0 | 0 | 0 | 47
05:30 | 3531.5 | 2115 | 925 | 0 | 32 | 824.425 | 40 | 3705 | 10.425 | 114 | 624 | 0 | 0 | 0 | 43
06:00 | 3549 | 2115 | 925 | 0 | 30 | 827.13 | 40 | 3538 | 20.85 | 107 | 579 | 0 | 0 | 0 | 39
06:30 | 3579.5 | 2123.5 | 925.5 | 0 | 29 | 825.885 | 39 | 3484.5 | 50.175 | 107 | 576.5 | 0 | 0 | 0 | 37
07:00 | 3610 | 2132 | 926 | 0 | 28 | 824.64 | 38 | 3431 | 79.5 | 107 | 574 | 0 | 0 | 0 | 35
07:30 | 3651 | 2121.5 | 903.5 | 0 | 30 | 822.32 | 38 | 3409 | 135.795 | 74 | 546 | 0 | 0 | 0 | 42
08:00 | 3692 | 2111 | 881 | 0 | 32 | 820 | 38 | 3387 | 192.09 | 41 | 518 | 0 | 0 | 0 | 49
08:30 | 3586.5 | 2044.35 | 881 | 0 | 32 | 817 | 39 | 3392 | 211.245 | 108.5 | 604.5 | 0 | 0 | 0 | 45
09:00 | 3481 | 1977.7 | 881 | 0 | 32 | 814 | 40 | 3397 | 230.4 | 176 | 691 | 0 | 0 | 0 | 41
09:30 | 3547 | 1999.1 | 903.5 | 0 | 31 | 818 | 40 | 3476.5 | 298.97 | 176 | 720.5 | 0 | 0 | 0 | 59.5
10:00 | 3613 | 2020.5 | 926 | 0 | 30 | 822 | 40 | 3556 | 367.54 | 176 | 750 | 0 | 0 | 0 | 78
10:30 | 3528.5 | 2053.5 | 926.5 | 0 | 30 | 819.5 | 40 | 3735 | 437.37 | 176.5 | 777 | 0 | 0 | 3.5 | 77
11:00 | 3444 | 2086.5 | 927 | 0 | 30 | 817 | 40 | 3914 | 507.2 | 177 | 804 | 0 | 0 | 7 | 76
11:30 | 3533 | 2075 | 927 | 0 | 32 | 817.5 | 40 | 3977.5 | 493.51 | 164 | 815 | 0 | 0 | 17 | 83
12:00 | 3622 | 2063.5 | 927 | 0 | 34 | 818 | 40 | 4041 | 479.82 | 151 | 826 | 0 | 0 | 27 | 90
12:30 | 3588.5 | 2016.25 | 927 | 0 | 35 | 867.5 | 40 | 3993 | 464.685 | 154 | 901 | 0 | 0 | 26.5 | 71.5
13:00 | 3555 | 1969 | 927 | 0 | 36 | 917 | 40 | 3945 | 449.55 | 157 | 976 | 0 | 0 | 26 | 53
13:30 | 3518.5 | 1923 | 927.5 | 0 | 36 | 913.935 | 40 | 3938.5 | 441.365 | 142 | 1001.5 | 0 | 0 | 27.5 | 47
14:00 | 3482 | 1877 | 928 | 0 | 36 | 910.87 | 40 | 3932 | 433.18 | 127 | 1027 | 0 | 0 | 29 | 41
14:30 | 3557.5 | 1922 | 927 | 0 | 30 | 911.255 | 40 | 3925 | 375.38 | 144.5 | 1031.5 | 0 | 0 | 28 | 54.5
15:00 | 3633 | 1967 | 926 | 0 | 24 | 911.64 | 40 | 3918 | 317.58 | 162 | 1036 | 0 | 0 | 27 | 68
15:30 | 3527.5 | 2030.9 | 926.5 | 0 | 26 | 970.18 | 40 | 3963.5 | 270.955 | 173 | 1050 | 0 | 0 | 24.5 | 62.5
16:00 | 3422 | 2094.8 | 927 | 0 | 28 | 1028.72 | 40 | 4009 | 224.33 | 184 | 1064 | 0 | 0 | 22 | 57
16:30 | 3348.5 | 2086.9 | 927 | 0 | 26 | 1024.34 | 40 | 4001 | 153.825 | 197 | 1092 | 0 | 0 | 19.5 | 50.5
17:00 | 3275 | 2079 | 927 | 0 | 24 | 1019.96 | 40 | 3993 | 83.32 | 210 | 1120 | 0 | 0 | 17 | 44
17:30 | 3247 | 2054.5 | 926.5 | 0 | 25 | 1068.485 | 39 | 3899 | 46.685 | 242.5 | 1132.5 | 0 | 0 | 14.5 | 40.5
18:00 | 3219 | 2030 | 926 | 0 | 26 | 1117.01 | 38 | 3805 | 10.05 | 275 | 1145 | 0 | 0 | 12 | 37
18:30 | 3279.5 | 2068.5 | 903.5 | 0 | 32 | 1118.395 | 37.5 | 4094.5 | 5.025 | 340 | 1363 | 0 | 0 | 7.5 | 45
19:00 | 3340 | 2107 | 881 | 0 | 38 | 1119.78 | 37 | 4384 | 0 | 405 | 1581 | 0 | 0 | 3 | 53
19:30 | 3408 | 2063 | 880 | 0 | 36 | 1354.25 | 37 | 4593 | 0 | 446 | 1912.5 | 0 | 0 | 0 | 44
20:00 | 3400 | 2054 | 880 | 0 | 36 | 1402.2 | 37 | 4583 | 0 | 446 | 1725 | 0 | 0 | 0 | 45
20:30 | 3429.5 | 2070 | 903.5 | 0 | 35 | 1411.6 | 37.5 | 4632 | 0 | 455.5 | 1649 | 0 | 0 | 1.5 | 40.5
21:00 | 3459 | 2086 | 927 | 0 | 34 | 1421 | 38 | 4681 | 0 | 465 | 1573 | 0 | 0 | 3 | 36
21:30 | 3495 | 2106.5 | 927 | 0 | 36 | 1416.5 | 38.5 | 4635.5 | 0 | 465 | 1437.5 | 0 | 0 | 5.5 | 42.5
22:00 | 3531 | 2127 | 927 | 0 | 38 | 1412 | 39 | 4590 | 0 | 465 | 1302 | 0 | 0 | 8 | 49
22:30 | 3522.5 | 2130.75 | 927 | 0 | 38 | 1414.5 | 39.5 | 4569 | 0 | 456.5 | 1296.5 | 0 | 0 | 8 | 48.5
23:00 | 3514 | 2134.5 | 927 | 0 | 38 | 1417 | 40 | 4548 | 0 | 448 | 1291 | 0 | 0 | 8 | 48
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 19-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 06:00 | 368 | 00:00 | Payra | 412 | 05:00 | 407 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Rahanpur | 414 | 09:00 | 392 | 21:00
Bhulta | 390 | 05:00 | 368 | 12:00 | Rampal | 401 | 10:00 | 385 | 21:00
Bibiana | 389 | 03:00 | 384 | 00:00
BIPTC | 404 | 08:00 | 395 | 21:00
Bogura | 406 | 09:00 | 380 | 21:00
Gopalganj | 392 | 07:00 | 381 | 00:00
Kaliakoir | 373 | 07:00 | 360 | 00:00
Madunaghat | 391 | 06:00 | 383 | 13:00
Meghnaghat | 381 | 06:00 | 373 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 220 | 06:00 | 211 | 12:00 | Keranigonj | 218 | 06:00 | 209 | 12:00
AKSML | 229 | 05:00 | 221 | 12:00 | Khulna(S) | 234 | 09:00 | 214 | 22:00
Aminbazar | 220 | 05:00 | 212 | 12:00 | Madunaghat | 230 | 18:00 | 225 | 00:00
Ashuganj | 229 | 06:00 | 219 | 19:00 | Madunaghat-400 | 230 | 06:00 | 225 | 13:00
Ashuganj-400 | 229 | 06:00 | 219 | 19:00 | Maniknagar | 216 | 06:00 | 208 | 12:00
Baghabari | 234 | 05:00 | 223 | 18:30 | Meghnaghat | 223 | 07:00 | 220 | 00:00
Barapukuria | 230 | 02:00 | 215 | 21:00 | Meghnaghat-400 | 220 | 05:00 | 214 | 12:00
Barapukuria-230 | 230 | 02:00 | 215 | 21:00 | Mirsorai | 225 | 06:00 | 218 | 01:00
Barishal | 235 | 06:00 | 228 | 00:00 | Rajshahi | 234 | 03:00 | 219 | 19:30
Bheramara | 234 | 02:00 | 221 | 13:00 | Rampal | 232 | 09:00 | 216 | 21:00
Bhulta | 227 | 05:00 | 209 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 223 | 06:00 | 219 | 00:00 | Rampura | 225 | 04:00 | 208 | 12:00
BIPTC | 236 | 03:00 | 221 | 19:30 | Shikalbaha | 229 | 17:00 | 222 | 12:00
Bogura | 234 | 05:00 | 219 | 19:30 | Shyampur | 218 | 06:00 | 210 | 12:00
Bogura-400 | 235 | 09:00 | 220 | 19:30 | Siddhirganj | 218 | 07:00 | 211 | 12:00
Borhanuddin | 239 | 07:00 | 234 | 00:00 | Sirajgonj | 239 | 04:00 | 231 | 19:30
BSRM | 224 | 04:00 | 218 | 00:00 | Sreepur | 226 | 05:00 | 218 | 19:00
Cumilla(N) | 219 | 05:00 | 213 | 00:00 | Tongi | 222 | 07:00 | 206 | 11:00
Faridpur | 230 | 06:00 | 222 | 00:00
Fenchuganj | 226 | 08:00 | 221 | 19:00
Ghorashal | 230 | 03:00 | 220 | 00:00
Ghorashal-230 | 225 | 06:00 | 212 | 12:00
Gopalganj | 232 | 06:00 | 224 | 00:00
GPH | 227 | 04:00 | 221 | 00:00
Haripur | 217 | 07:00 | 210 | 12:00
Hasnabad | 218 | 06:00 | 210 | 12:00
Hathazari | 230 | 18:00 | 224 | 10:00
Ishurdi | 236 | 08:00 | 223 | 19:30
Jhenaidah | 230 | 09:00 | 216 | 13:00
Kaliakoir | 230 | 19:30 | 219 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 05:00 | 126 | 12:00 | Madartek | 137 | 04:00 | 124 | 12:00
Agargaon | 132 | 04:00 | 125 | 12:00 | Madunaghat | 131 | 18:00 | 126 | 00:00
Agrabad | 131 | 18:00 | 12 | 02:00 | Magura | 135 | 08:00 | 123 | 13:00
AKS | 128 | 18:00 | 125 | 00:00 | Mahasthangarh | 138 | 09:00 | 125 | 19:00
Aminbazar | 129 | 05:00 | 124 | 00:00 | Manikganj | 130 | 06:00 | 120 | 12:00
Amnura | 136 | 07:00 | 125 | 22:00 | Maniknagar | 130 | 03:00 | 123 | 12:00
Ashuganj | 136 | 06:00 | 132 | 19:00 | Matarbari | 116 | 09:00 | 108 | 22:00
Bagerhat | 133 | 18:00 | 116 | 22:00 | Matuail | 126 | 06:00 | 121 | 11:00
Bajitpur | 134 | 12:00 | 124 | 22:00 | Millgate | 134 | 05:00 | 123 | 12:00
Bakulia | 131 | 18:00 | 127 | 10:00 | Mirpur | 128 | 07:00 | 122 | 12:00
Banani | 139 | 05:00 | 111 | 18:00 | Mirzapur | 133 | 11:00 | 127 | 00:00
Bangabhaban | 130 | 04:00 | 123 | 12:00 | Mithapukur | 137 | 06:00 | 124 | 18:00
Barapukuria | 138 | 02:00 | 124 | 21:00 | MI_Cement | 127 | 05:00 | 121 | 12:00
Barguna | 134 | 06:00 | 129 | 19:00 | Modern | 0 | 0:00 | 0 | 0:00
Barishal | 130 | 06:00 | 123 | 23:00 | Mogbazar | 140 | 05:00 | 125 | 12:00
Barishal-230 | 131 | 07:00 | 124 | 22:00 | Mongla | 135 | 10:00 | 118 | 22:00
Baroaulia | 132 | 18:00 | 127 | 15:00 | Motijheel | 130 | 04:00 | 123 | 12:00
Baroirhat | 125 | 18:00 | 118 | 00:00 | Muktagacha | 136 | 11:00 | 127 | 00:00
Bashundhara | 139 | 07:00 | 124 | 11:00 | Munshiganj | 125 | 05:00 | 120 | 11:00
BashundharaCement | 126 | 03:00 | 120 | 12:00 | Muradnagar | 123 | 17:00 | 118 | 01:00
Beanibazar | 131 | 02:00 | 126 | 00:00 | Mymensingh | 136 | 09:00 | 116 | 19:30
Benapole | 134 | 18:00 | 118 | 22:00 | Naogaon | 138 | 09:00 | 124 | 19:30
Bhaluka | 133 | 12:00 | 124 | 19:00 | Narail | 136 | 18:00 | 124 | 13:00
Bhandaria | 125 | 06:00 | 115 | 22:00 | Narinda | 130 | 03:00 | 123 | 12:00
Bhangura | 134 | 03:00 | 127 | 19:30 | Narshingdi | 130 | 14:00 | 114 | 12:00
Bheramara | 138 | 08:00 | 131 | 20:00 | Natore | 135 | 08:00 | 126 | 19:30
Bheramara(GK) | 137 | 08:00 | 131 | 20:00 | Nawabganj | 132 | 05:00 | 18 | 09:00
Bhulta | 119 | 20:00 | 112 | 12:00 | Netrakona | 132 | 12:00 | 115 | 19:30
Bog-Sherpur | 137 | 06:00 | 126 | 19:30 | New | 135 | 07:00 | 124 | 12:00
Bogura | 140 | 09:00 | 128 | 21:00 | Niamatpur | 138 | 08:00 | 128 | 21:00
Bogura-230 | 140 | 09:00 | 129 | 19:30 | Noapara | 135 | 18:00 | 122 | 21:00
Brahmanbaria | 129 | 07:00 | 121 | 00:00 | Pabna | 135 | 08:00 | 127 | 19:30
Cantonment | 133 | 06:00 | 124 | 12:00 | Palashbari | 135 | 07:00 | 121 | 21:00
Chandina | 125 | 06:00 | 121 | 00:00 | Panchagarh | 133 | 04:00 | 120 | 10:00
Chandpur | 125 | 09:00 | 120 | 23:00 | Patuakhali | 133 | 09:00 | 130 | 21:00
Chandraghona | 130 | 18:00 | 127 | 00:00 | Payra | 135 | 03:00 | 132 | 19:30
Chapai | 134 | 09:00 | 126 | 22:00 | PHP | 123 | 17:00 | 116 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 126 | 04:00 | 121 | 11:00 | Postogola | 129 | 04:00 | 124 | 12:00
Chauddagram | 122 | 17:00 | 116 | 00:00 | Purbachal | 138 | 04:00 | 126 | 11:00
Chhatak | 130 | 13:00 | 124 | 23:00 | Purbasadipur | 132 | 04:00 | 119 | 13:00
Chowmuhani | 117 | 18:00 | 111 | 01:00 | Rahanpur | 138 | 05:00 | 131 | 19:00
Chuadanga | 139 | 03:00 | 122 | 13:00 | Rahanpur-400 | 139 | 08:00 | 130 | 21:00
Coxsbazar | 117 | 18:00 | 109 | 00:00 | Rahim | 126 | 05:00 | 123 | 00:00
Cumilla(N) | 126 | 18:00 | 120 | 00:00 | Rajbari | 133 | 06:00 | 126 | 00:00
Cumilla(S) | 133 | 03:00 | 119 | 00:00 | Rajendrapur | 133 | 05:00 | 119 | 17:00
Daudkandi | 121 | 14:00 | 115 | 00:00 | Rajshahi | 135 | 03:00 | 126 | 19:30
Dhaka | 138 | 06:00 | 126 | 12:00 | Rajshahi-230 | 135 | 03:00 | 120 | 21:00
Dhamrai | 132 | 05:00 | 126 | 10:00 | Ramganj | 120 | 18:00 | 112 | 23:00
Dhanmondi | 139 | 06:00 | 125 | 12:00 | Rampur | 131 | 18:00 | 125 | 10:00
Dohazari | 126 | 18:00 | 121 | 00:00 | Rampura | 138 | 04:00 | 125 | 12:00
Faridpur | 135 | 18:00 | 128 | 00:00 | Rangamati | 129 | 06:00 | 125 | 00:00
Fatullah | 127 | 05:00 | 122 | 12:00 | Rangpur | 136 | 05:00 | 121 | 21:00
Fenchuganj | 134 | 05:00 | 131 | 00:00 | Ruppur | 137 | 03:00 | 130 | 19:30
Feni | 124 | 18:00 | 117 | 22:00 | Saidpur | 133 | 05:00 | 120 | 18:00
Ghatail | 135 | 11:00 | 124 | 00:00 | Satkhira | 133 | 18:00 | 117 | 22:00
Ghorashal | 137 | 07:00 | 130 | 22:00 | Satmasjid | 132 | 05:00 | 125 | 13:00
Goalpara | 137 | 10:00 | 123 | 23:00 | Savar | 127 | 06:00 | 122 | 00:00
Gollamari | 136 | 18:00 | 123 | 11:00 | SevenRings | 137 | 07:00 | 127 | 19:00
Gopalganj | 136 | 18:00 | 126 | 11:00 | ShahCement | 126 | 04:00 | 121 | 11:00
Gopalganj-400 | 135 | 06:00 | 130 | 00:00 | Shahjadpur | 137 | 03:00 | 130 | 19:30
Gulshan | 138 | 04:00 | 126 | 11:00 | Shahjibazar | 131 | 07:00 | 123 | 00:00
Halishahar | 133 | 18:00 | 126 | 00:00 | Shahmirpur | 134 | 18:00 | 127 | 12:00
Haripur | 126 | 07:00 | 121 | 12:00 | Shariatpur | 132 | 06:00 | 126 | 00:00
HaripurSBU | 126 | 04:00 | 121 | 12:00 | Sherpur | 140 | 10:00 | 130 | 00:00
Hasnabad | 129 | 04:00 | 124 | 12:00 | Shikalbaha | 121 | 18:00 | 116 | 00:00
Hathazari | 133 | 21:00 | 129 | 10:00 | Shikalbaha-230 | 131 | 18:30 | 128 | 11:00
Ishurdi | 139 | 08:00 | 131 | 19:00 | Shitalakhya | 127 | 05:00 | 121 | 12:00
Jaldhaka | 133 | 05:00 | 118 | 13:00 | Sholosohor | 131 | 04:00 | 125 | 12:00
Jamalpur | 140 | 04:00 | 129 | 00:00 | Shyampur | 127 | 18:00 | 124 | 11:00
Jashore | 132 | 10:00 | 118 | 13:00 | Shyampur-230 | 127 | 06:00 | 122 | 12:00
Jhenaidah | 136 | 09:00 | 121 | 00:00 | Siddhirganj | 127 | 06:00 | 122 | 11:00
Jhenaidah-230 | 136 | 04:00 | 126 | 12:00 | Sirajganj | 135 | 09:00 | 124 | 19:30
Joydebpur | 135 | 03:00 | 122 | 16:00 | Sonargaon | 124 | 03:00 | 118 | 13:00
Joypurhat | 137 | 08:00 | 122 | 19:30 | Sreemongol | 132 | 14:00 | 125 | 00:00
Juldah | 134 | 18:00 | 127 | 00:00 | Sreepur | 134 | 12:00 | 126 | 19:30
Kabirpur | 132 | 08:00 | 120 | 12:00 | Srinagar | 130 | 05:00 | 123 | 12:00
Kachua | 123 | 17:00 | 118 | 22:00 | SSM | 132 | 00:00 | 130 | 13:00
Kaliakoir | 138 | 07:00 | 131 | 00:00 | Sunamganj | 129 | 00:00 | 123 | 19:00
Kallyanpur | 129 | 06:00 | 123 | 12:00 | Sylhet | 131 | 02:00 | 127 | 19:00
Kalurghat | 129 | 04:00 | 126 | 00:00 | Sylhet-132 | 131 | 07:00 | 128 | 20:00
Kamrangirchar | 130 | 06:00 | 122 | 12:00 | Tangail | 135 | 11:00 | 124 | 00:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 136 | 05:00 | 121 | 13:00
Kasba | 123 | 18:00 | 118 | 00:00 | TK | 131 | 18:00 | 125 | 00:00
Kazla | 130 | 00:00 | 123 | 12:00 | Tongi | 135 | 07:00 | 126 | 11:00
Keranigonj | 130 | 04:00 | 123 | 12:00 | Ullahpara | 135 | 05:00 | 126 | 19:30
Khagrachori | 129 | 18:00 | 124 | 12:00 | Ullon | 138 | 05:00 | 126 | 12:00
Khulna | 135 | 10:00 | 122 | 22:00 | Uttara | 128 | 06:00 | 24 | 21:00
Khulna(S) | 136 | 10:00 | 125 | 21:00 | UttaraNew | 128 | 05:00 | 122 | 11:00
Khulshi | 129 | 18:00 | 124 | 12:00 | Zigatola | 130 | 06:00 | 123 | 12:00
Kishoreganj | 133 | 12:00 | 123 | 20:00
Kodda | 138 | 18:30 | 121 | 16:00
KSRM | 131 | 21:00 | 127 | 00:00
Kulaura | 133 | 05:00 | 130 | 00:00
Kurigram | 134 | 05:00 | 120 | 13:00
Kushtia | 134 | 09:00 | 126 | 00:00
Lalbag | 135 | 18:30 | 122 | 11:00
Lalmonirhat | 133 | 06:00 | 120 | 18:30
Madanganj | 126 | 03:00 | 120 | 12:00
Madaripur | 133 | 07:00 | 128 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division