## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 21-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-05-2025 | during | 21-05-2025 | during | 21-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 174.8 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 342 | 320 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 400 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 286 | 297 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 75.24 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 273 | 278 | 335 | 335 | 301.5 | 301.5 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 10 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 149 | 149.36 | 149.36 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 15 | 30 | 30 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 22 | 22 | 17 | 17 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 17 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 145 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 95 | 135 | 135 | 135 | 135 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 400 | 350 | 584 | 584 | 584 | 584 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 0 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6085.764 | 2249 | 2383 | 5260.9 | 5319.9 | 3895.02 | 3954.02
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 12 | 0 | 18 | 0 | 18 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 126.5 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 94 | 4 | 3 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 98 | 17 | 17 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 85 | 92 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 2 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 7 | 2 | 0 | 4.96 | 0 | 4.96 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 48 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1000 | 1103 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 30 | 8 | 26 | 18 | 26 | 18 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 570 | 501 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4915.22 | 1968 | 2034 | 3395.68 | 3387.72 | 3395.68 | 3387.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 200 | 196 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 338 | 358 | 353.35 | 353.35 | 353.35 | 353.35
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 335 | 330 | 330 | 330 | 330
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.94 | 24 | 35 | 46.94 | 46.94 | 31 | 31 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 49 | 54 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 10 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 122 | 34 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 24 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 6 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 52 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 38 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 50 | 115 | 115 | 92 | 92 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 51 | 0 | 65 | 0 | 65 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2897.48 | 1460 | 1329 | 2449.24 | 2384.24 | 2243.55 | 2178.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 20-05-2025 | during | 21-05-2025 | during | 21-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 140 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 85 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 3.21 | 0 | 33 | 0 | 33 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 137.21 | 237 | 584.1 | 549 | 376.6 | 341.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 80 | 35 | 35 | 35 | 35 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 140 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 47.998 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66.57 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 63 | 80 | 83 | 83 | 64 | 64 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 225 | 174 | 173 | 170 | 170 | 174 | 174 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 315 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 326 | 356 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2368.568 | 1457 | 1513 | 1610 | 1610 | 1501 | 1501
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 926 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 50 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 100 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 149 | 147 | 410 | 410 | 200 | 200 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 0.01 | 0.01 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 103 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 855 | 858 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3686.2 | 2033 | 1885 | 3582.2 | 3512.2 | 3252.21 | 3182.21
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 1320 | 290 | 285 | 450 | 600 | 450 | 450 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 8 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 193.1 | 120 | 100 | 125 | 125 | 113 | 113 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 800 | 980 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 215 | 220 | 220 | 220 | 198 | 198 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.3 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 3585.1 | 1683.3 | 1903 | 2617.12 | 2766.12 | 2543.12 | 2542.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 47 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 66 | 0 | 0 | 32 | 32 | 26 | 26 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 35.09 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 45.49 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 165 | 165 | 214 | 214 | 181 | 181 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 152 | 170 | 220 | 220 | 189 | 189 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 350 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 46 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 959.2 | 1157 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.86 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 98 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3481.54 | 1853.06 | 1842 | 3205.07 | 3038.87 | 3124.07 | 2957.87
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 50 | 50 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 116 | 134 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 3.7 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 18.5 | 0 | 18.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 4 | 0 | 121.8 | 0 | 121.8 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 153.7 | 239 | 608.9 | 462 | 558.9 | 412
System Total |  |  |  |  | 27566.2 | 28624.082 | 12994.27 | 13365 | 23313.21 | 23030.05 | 20890.15 | 20456.99
Forecast Scenario (21-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 13180 |  | 0 |  | 12800
|  |  |  | 1:00 | 12980 |  | 0 |  | 12680
|  |  |  | 2:00 | 12670 |  | 0 |  | 12370
|  |  |  | 3:00 | 12330 |  | 0 |  | 12030
|  |  |  | 4:00 | 12070 |  | 0 |  | 11770
|  |  |  | 5:00 | 11710 |  | 0 |  | 11410
|  |  |  | 6:00 | 11320 |  | 0 |  | 11020
|  |  |  | 7:00 | 11330 |  | 0 |  | 11030
|  |  |  | 8:00 | 11310 |  | 0 |  | 11010
|  |  |  | 9:00 | 11610 |  | 0 |  | 11610
|  |  |  | 10:00 | 12230 |  | 0 |  | 12230
|  |  |  | 11:00 | 12680 |  | 0 |  | 12680
|  |  |  | 12:00 | 12970 |  | 0 |  | 12970
|  |  |  | 13:00 | 12900 |  | 0 |  | 12900
|  |  |  | 14:00 | 12710 |  | 0 |  | 12710
|  |  |  | 15:00 | 12880 |  | 0 |  | 12880
|  |  |  | 16:00 | 12950 |  | 0 |  | 12950
|  |  |  | 17:00 | 12680 |  | 0 |  | 12680
|  |  |  | 18:00 | 12490 |  | 0 |  | 12490
|  |  |  | 18:30 | 13050 |  | 0 |  | 13050
|  |  |  | 19:00 | 13800 |  | 0 |  | 13800
|  |  |  | 19:30 | 14620 |  | 0 |  | 14620
|  |  |  | 20:00 | 14460 |  | 0 |  | 14460
|  |  |  | 21:00 | 14570 |  | 0 |  | 14570
|  |  |  | 22:00 | 14340 |  | 0 |  | 14340
|  |  |  | 23:00 | 14260 |  | 0 |  | 14260
Probable Maximum Temperature: |  |  | 32.50°C
Probable Maximum Demand at Day Peak: |  |  | 12970.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 14620.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14320.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 301.93 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:35 hrs on 21-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 20-05-2025 | [28 empty] | Date: | 20-05-2025 | [28 empty] | Date: | 20-05-2025 | [28 empty] | Date: | 20-05-2025 | [28 empty] | Date: | 20-05-2025 | [16 empty] | Date: | 20-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 174.800 MW | 97.700 MW | 400.750 MW | 40.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 93.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 98.000 MW | 94.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 7.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 126.500 MW | 126.500 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.940 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 47.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 80.000 MW | 90.000 MW | 11.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.570 MW | 330.000 MW | 20.000 MW | 225.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 50.000 MW | 100.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 47.000 MW | 71.000 MW | 113.000 MW | 66.000 MW | 104.000 MW | 113.000 MW | 45.490 MW | 52.200 MW | 100.000 MW | 46.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 11.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 193.100 MW | 220.000 MW | 220.000 MW | 1320.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 17 | 131 | 145 | 30 | 0 | 17 | 35 | 0 | 16 | 400 | 285 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 0 | 108 | 16.5 | 15 | 0 | 480 | 0 | 0 | 24 | 150 | 11 | 34 | 70 | 0 | 100 | 72 | 0 | 40 | 0 | 20 | 504 | 0 | 0 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 55 | 184 | 31 | 90 | 80 | 155 | 17 | 15 | 114 | 36 | 8 | 0 | 40 | 310 | 60 | 304 | 36 | 40 | 0 | 153 | 8 | 0 | 64 | 25 | 0 | 18 | 171 | 17 | 83 | 160 | 0 | 0 | 0 | 12 | 7622.5 | 928 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1059 | 0 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 166 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 250 | 1104 | 0 | 6602 | 14224.5 | 76.9
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 121 | 80 | 30 | 0 | 17 | 0 | 0 | 16 | 400 | 282 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 0 | 108 | 17 | 15 | 0 | 480 | 0 | 0 | 0 | 150 | 16 | 34 | 48 | 0 | 100 | 72 | 0 | 40 | 0 | 21 | 502 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 51 | 0 | 8 | 0 | 357 | 330 | 55 | 193 | 31 | 75 | 80 | 155 | 9 | 15 | 114 | 34 | 25 | 0 | 40 | 300 | 60 | 311 | 36 | 40 | 0 | 130 | 8 | 0 | 64 | 25 | 0 | 18 | 172 | 17 | 18 | 122 | 0 | 0 | 0 | 12 | 7219 | 927 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1039 | 0 | 1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 107 | 220 | 0 | 250 | 1102 | 0 | 6405 | 13624 | 76.89
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 17 | 95 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 287 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 108 | 17 | 15 | 0 | 480 | 0 | 0 | 0 | 150 | 21 | 34 | 0 | 0 | 100 | 72 | 0 | 40 | 0 | 21 | 502 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 8 | 0 | 357 | 330 | 55 | 192 | 31 | 74 | 90 | 155 | 9 | 15 | 114 | 34 | 25 | 0 | 0 | 305 | 119 | 311 | 36 | 40 | 0 | 131 | 8 | 0 | 64 | 25 | 0 | 18 | 172 | 0 | 18 | 123 | 0 | 0 | 0 | 12 | 7116 | 927 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 979 | 0 | 1164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 180 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 250 | 1050 | 0 | 6113 | 13229 | 76.89
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 17 | 78 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 280 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 108 | 17 | 15 | 0 | 480 | 0 | 0 | 0 | 150 | 19 | 34 | 0 | 0 | 100 | 72 | 0 | 40 | 0 | 22 | 505 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 55 | 191 | 31 | 73 | 90 | 155 | 9 | 15 | 114 | 32 | 25 | 0 | 0 | 310 | 125 | 312 | 36 | 40 | 0 | 135 | 8 | 0 | 64 | 28 | 0 | 18 | 172 | 0 | 18 | 123 | 0 | 0 | 0 | 12 | 7112 | 926 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958 | 0 | 1026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 115 | 220 | 0 | 249 | 996 | 0 | 5840 | 12952 | 76.89
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 78 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 287 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 52 | 17 | 15 | 0 | 480 | 0 | 0 | 0 | 150 | 13 | 34 | 0 | 0 | 100 | 48 | 0 | 40 | 0 | 22 | 504 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 55 | 197 | 31 | 72 | 90 | 155 | 9 | 15 | 114 | 32 | 25 | 0 | 0 | 315 | 150 | 331 | 36 | 40 | 0 | 135 | 8 | 0 | 64 | 28 | 0 | 18 | 172 | 0 | 18 | 115 | 0 | 0 | 0 | 12 | 6937 | 926 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 916 | 0 | 1027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 115 | 220 | 0 | 250 | 1000 | 0 | 5811 | 12748 | 76.89
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 17 | 78 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 262 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 52 | 17 | 15 | 0 | 480 | 0 | 0 | 0 | 150 | 15 | 34 | 0 | 0 | 100 | 48 | 0 | 40 | 0 | 23 | 502 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 8 | 0 | 356 | 330 | 55 | 182 | 31 | 70 | 90 | 155 | 9 | 15 | 114 | 32 | 25 | 0 | 0 | 305 | 260 | 302 | 36 | 40 | 0 | 131 | 8 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 18 | 123 | 0 | 0 | 0 | 12 | 6866 | 927 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 917 | 0 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 174 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 11 | 105 | 220 | 0 | 248 | 950 | 0 | 5657 | 12523 | 76.88
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 17 | 78 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 285 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 2 | 52 | 17 | 15 | 0 | 480 | 0 | 0 | 0 | 150 | 16 | 34 | 0 | 0 | 70 | 48 | 1 | 40 | 0 | 32 | 502 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 808 | 1 | 51 | 0 | 8 | 0 | 300 | 330 | 55 | 186 | 31 | 63 | 90 | 155 | 9 | 15 | 114 | 30 | 25 | 4 | 0 | 295 | 320 | 303 | 36 | 40 | 0 | 128 | 8 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 19 | 122 | 0 | 0 | 2.11 | 12 | 6776.11 | 926 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.58 | 854 | 0 | 1021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 3.62 | 174 | 0 | 163 | 0 | 0 | 0 | 350 | 0 | 0.3 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 200 | 11 | 115 | 220 | 0 | 248 | 851 | 0 | 5484.55 | 12260.66 | 76.88
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 0 | 17 | 78 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 287 | 0 | 0 | 0 | 0 | 268 | 0 | 0 | 8 | 52 | 17 | 16 | 0 | 480 | 0 | 0 | 0 | 150 | 12 | 17 | 0 | 0 | 70 | 48 | 2 | 38 | 0 | 30 | 505 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 808 | 6 | 51 | 0 | 8 | 0 | 300 | 330 | 54 | 194 | 31 | 65 | 90 | 155 | 9 | 8 | 114 | 34 | 25 | 20 | 0 | 305 | 320 | 303 | 36 | 40 | 0 | 130 | 8 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 56 | 112 | 0 | 1 | 11.06 | 12 | 6832.06 | 926 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 811 | 0 | 1031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 171 | 0 | 156 | 0 | 0 | 0 | 350 | 0 | 0.6 | 0 | 118 | 0 | 0 | 1 | 0 | 0 | 0 | 0.8 | 0 | 0.13 | 0 | 200 | 9 | 105 | 220 | 0 | 283 | 850 | 0 | 5437.13 | 12269.19 | 76.88
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 78 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 296 | 0 | 0 | 0 | 0 | 293 | 0 | 0 | 11 | 35 | 17 | 16 | 0 | 400 | 0 | 0 | 0 | 150 | 21 | 17 | 0 | 0 | 70 | 48 | 3 | 38 | 0 | 4 | 505 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 810 | 11 | 51 | 0 | 8 | 0 | 300 | 330 | 54 | 198 | 31 | 72 | 80 | 155 | 9 | 8 | 114 | 30 | 25 | 39 | 0 | 295 | 320 | 335 | 36 | 40 | 0 | 128 | 5 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 65 | 121 | 0 | 0 | 20.25 | 12 | 6752.25 | 878 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.12 | 811 | 0 | 925.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 25.36 | 171 | 0 | 165 | 0 | 0 | 0 | 300 | 0 | 2.32 | 0 | 143 | 0 | 0 | 7 | 0 | 0 | 0 | 0.7 | 12 | 0.4 | 0 | 200 | 7 | 115 | 220 | 0 | 290 | 820 | 0 | 5359.59 | 12111.84 | 76.87
09:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 17 | 80 | 80 | 0 | 0 | 12 | 0 | 0 | 0 | 400 | 297 | 0 | 0 | 0 | 0 | 295 | 0 | 0 | 20 | 35 | 16 | 16 | 0 | 400 | 0 | 0 | 0 | 150 | 39 | 17 | 0 | 0 | 70 | 48 | 4 | 38 | 0 | 2 | 502 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 803 | 17 | 51 | 0 | 8 | 0 | 345 | 330 | 52 | 200 | 23 | 73 | 80 | 155 | 9 | 15 | 114 | 30 | 25 | 40 | 0 | 320 | 320 | 360 | 36 | 38 | 0 | 147 | 6 | 0 | 63 | 30 | 0 | 18 | 174 | 0 | 45 | 75 | 0 | 0 | 8.65 | 12 | 6993.65 | 878 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 809 | 0 | 917.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 40.05 | 172 | 0 | 181 | 0 | 0 | 0 | 350 | 0 | 2.21 | 0 | 125 | 0 | 0 | 22 | 0 | 0 | 0 | 0.5 | 32 | 0.46 | 0 | 200 | 8 | 115 | 220 | 0 | 291 | 800 | 0 | 5408.87 | 12402.52 | 76.87
10:00 | 0 | 34 | 28 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 110 | 32 | 0 | 0 | 30 | 54 | 0 | 0 | 400 | 289 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 27 | 52 | 16 | 16 | 0 | 400 | 0 | 0 | 0 | 150 | 26 | 17 | 0 | 0 | 70 | 24 | 5 | 39 | 0 | 2 | 506 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 904 | 18 | 51 | 0 | 8 | 0 | 341 | 330 | 51 | 200 | 25 | 72 | 80 | 136 | 9 | 15 | 70 | 30 | 8 | 69 | 0 | 310 | 320 | 364 | 35 | 39 | 0 | 151 | 0 | 0 | 63 | 30 | 0 | 18 | 174 | 0 | 45 | 55 | 0 | 0 | 0.16 | 12 | 7023.16 | 926 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 808 | 0 | 923.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 9.59 | 173 | 0 | 182 | 0 | 0 | 0 | 414 | 0 | 2.02 | 0 | 117 | 0 | 0 | 19 | 0 | 0 | 0 | 0.3 | 46 | 0.5 | 0 | 250 | 7 | 120 | 220 | 0 | 291 | 800 | 0 | 5616.94 | 12640.1 | 76.87
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 17 | 114 | 32 | 0 | 0 | 35 | 100 | 0 | 0 | 400 | 294 | 0 | 0 | 0 | 0 | 273 | 0 | 0 | 22 | 52 | 16 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 17 | 17 | 0 | 0 | 70 | 24 | 5 | 40 | 0 | 2 | 568 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1000 | 16 | 51 | 0 | 8 | 0 | 342 | 330 | 50 | 189 | 27 | 72 | 80 | 129 | 9 | 6 | 70 | 24 | 8 | 34 | 0 | 310 | 320 | 360 | 35 | 39 | 0 | 153 | 0 | 0 | 62 | 30 | 0 | 18 | 174 | 0 | 45 | 55 | 0 | 2 | 0.61 | 12 | 7150.61 | 926 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 809 | 0 | 955.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 3.05 | 173 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 0.53 | 0 | 117 | 0 | 0 | 2 | 0 | 0 | 0 | 7.9 | 35 | 0.8 | 0 | 250 | 8 | 120 | 215 | 0 | 289 | 800 | 0 | 5578.82 | 12729.43 | 76.86
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 10 | 17 | 131 | 32 | 0 | 0 | 35 | 162 | 0 | 0 | 400 | 286 | 0 | 0 | 17 | 0 | 273 | 0 | 0 | 19 | 17 | 16 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 30 | 17 | 4 | 0 | 85 | 48 | 2 | 40 | 0 | 2 | 570 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1000 | 12 | 51 | 10 | 8 | 0 | 338 | 330 | 49 | 200 | 24 | 72 | 80 | 122 | 9 | 6 | 70 | 32 | 8 | 51 | 0 | 295 | 320 | 326 | 35 | 40 | 0 | 156 | 0 | 0 | 63 | 30 | 0 | 18 | 174 | 0 | 45 | 75 | 0 | 2 | 3.21 | 12 | 7271.21 | 926 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 855 | 0 | 959.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 0 | 64.86 | 165 | 0 | 152 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 116 | 0 | 0 | 30 | 0 | 0 | 0 | 3.7 | 4 | 0.3 | 0 | 250 | 8 | 120 | 215 | 0 | 290 | 800 | 0 | 5723.06 | 12994.27 | 76.86
13:00 | 0 | 52 | 33 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 14 | 17 | 115 | 16 | 0 | 0 | 35 | 162 | 0 | 0 | 350 | 261 | 0 | 0 | 0 | 0 | 267 | 0 | 0 | 33 | 0 | 16 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 49 | 17 | 30 | 0 | 89 | 48 | 2 | 40 | 0 | 2 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 16 | 51 | 0 | 8 | 0 | 355 | 330 | 46 | 181 | 32 | 72 | 75 | 120 | 9 | 0 | 17 | 28 | 0 | 10 | 0 | 290 | 320 | 335 | 35 | 39 | 0 | 158 | 0 | 0 | 64 | 30 | 0 | 18 | 174 | 0 | 16 | 85 | 0 | 0 | 49.58 | 12 | 7104.58 | 927 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 835 | 0 | 969.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 59.92 | 149 | 0 | 153 | 0 | 0 | 0 | 414 | 0 | 4.84 | 0 | 117 | 0 | 0 | 28 | 0 | 0 | 0 | 5.9 | 54 | 0.78 | 0 | 250 | 8 | 110 | 215 | 0 | 289 | 760 | 0 | 5638.79 | 12743.37 | 76.86
14:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 0 | 17 | 0 | 80 | 40 | 0 | 0 | 35 | 162 | 0 | 0 | 400 | 312 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 27 | 0 | 15.8 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 45 | 17 | 31 | 0 | 76 | 48 | 2 | 40 | 0 | 4 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 0 | 8 | 0 | 328 | 305 | 50 | 211 | 32 | 73 | 70 | 82 | 9 | 6 | 34 | 30 | 1 | 14 | 0 | 300 | 320 | 405 | 35 | 40 | 0 | 157 | 6 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 8 | 86 | 0 | 0 | 2.41 | 12 | 6986.21 | 927 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 761 | 0 | 961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 1.32 | 168 | 0 | 175 | 0 | 0 | 0 | 414 | 0 | 0.08 | 0 | 111 | 0 | 0 | 11 | 0 | 0 | 0 | 5.5 | 180 | 0.44 | 0 | 200 | 8 | 120 | 215 | 0 | 289 | 700 | 0 | 5472.34 | 12458.55 | 76.85
15:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 17 | 8 | 74 | 48 | 0 | 0 | 35 | 162 | 0 | 0 | 400 | 297 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 10 | 35 | 15.8 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 50 | 17 | 31 | 0 | 76 | 12 | 2 | 40 | 0 | 0 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 6 | 51 | 0 | 8 | 0 | 356 | 330 | 54 | 202 | 32 | 88 | 70 | 96 | 9 | 6 | 106 | 26 | 20 | 7 | 0 | 300 | 320 | 365 | 35 | 40 | 0 | 159 | 6 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 24 | 104 | 0 | 0 | 1.47 | 12 | 7118.27 | 926 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 762 | 0 | 984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 163 | 0 | 172 | 0 | 0 | 0 | 370 | 0 | 0.19 | 0 | 142 | 0 | 0 | 17 | 0 | 0 | 0 | 5.5 | 146 | 0.13 | 0 | 250 | 8 | 120 | 215 | 0 | 386 | 766 | 0 | 5684.82 | 12803.09 | 76.85
16:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 17 | 17 | 85 | 48 | 0 | 0 | 35 | 90 | 0 | 0 | 400 | 306 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 35 | 15.8 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 40 | 17 | 31 | 0 | 76 | 12 | 0 | 40 | 0 | 0 | 407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 8 | 51 | 0 | 8 | 0 | 356 | 330 | 54 | 205 | 32 | 90 | 70 | 68 | 9 | 3 | 88 | 26 | 8 | 7 | 0 | 310 | 320 | 380 | 35 | 40 | 0 | 138 | 0 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 24 | 105 | 0 | 0 | 2.53 | 12 | 6866.33 | 926 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 760 | 0 | 858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.14 | 159 | 0 | 170 | 0 | 0 | 0 | 370 | 0 | 0.01 | 0 | 132 | 0 | 0 | 13 | 0 | 0 | 0 | 2.3 | 94 | 0.04 | 0 | 200 | 9 | 120 | 216 | 0 | 281 | 750 | 0 | 5223.49 | 12089.82 | 76.85
17:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 1 | 100 | 48 | 0 | 0 | 35 | 90 | 0 | 0 | 400 | 293 | 0 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 35 | 15.8 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 43 | 17 | 31 | 0 | 76 | 48 | 1 | 40 | 0 | 2 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 2 | 51 | 0 | 8 | 0 | 356 | 330 | 54 | 188 | 29 | 35 | 70 | 34 | 26 | 5 | 52 | 18 | 8 | 2 | 0 | 305 | 320 | 305 | 35 | 40 | 0 | 145 | 0 | 0 | 64 | 30 | 0 | 18 | 172 | 0 | 45 | 96 | 0 | 1 | 0.42 | 12 | 6664.22 | 926 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 760 | 0 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 2.29 | 165 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 0.17 | 0 | 134 | 0 | 0 | 6 | 0 | 0 | 0 | 1.8 | 47 | 0.12 | 0 | 200 | 9 | 100 | 216 | 0 | 281 | 744 | 0 | 5249.38 | 11913.6 | 76.84
18:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 17 | 17 | 112 | 48 | 0 | 0 | 35 | 54 | 0 | 0 | 400 | 298 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 1 | 90 | 15.2 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 11 | 17 | 31 | 0 | 76 | 48 | 0 | 40 | 0 | 2 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 915 | 0 | 51 | 3 | 8 | 0 | 305 | 300 | 52 | 196 | 32 | 35 | 80 | 17 | 37 | 3 | 52 | 20 | 8 | 0 | 0 | 305 | 320 | 300 | 34 | 40 | 0 | 151 | 0 | 0 | 64 | 30 | 0 | 18 | 173 | 0 | 75 | 122 | 0 | 0 | 3.19 | 12 | 6684.39 | 927 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 762 | 0 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.85 | 164 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 0.25 | 0 | 162 | 0 | 0 | 1 | 0 | 0 | 0 | 0.3 | 3 | 0.03 | 0 | 200 | 9 | 100 | 180 | 0 | 287 | 743 | 0 | 5143.43 | 11827.82 | 76.84
19:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 17 | 17 | 99 | 147 | 15 | 0 | 35 | 100 | 0 | 16 | 400 | 294 | 0 | 0 | 17 | 0 | 270 | 0 | 0 | 0 | 90 | 15 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 7 | 17 | 31 | 0 | 92 | 100 | 0 | 40 | 0 | 2 | 504 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 51 | 10 | 8 | 0 | 357 | 310 | 54 | 200 | 34 | 39 | 80 | 18 | 38 | 6 | 52 | 28 | 8 | 0 | 0 | 310 | 320 | 349 | 35 | 40 | 0 | 146 | 0 | 0 | 80 | 30 | 0 | 18 | 173 | 0 | 75 | 125 | 0 | 0 | 0 | 12 | 7399 | 881 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 824 | 0 | 1068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 138 | 0 | 35 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 11 | 100 | 220 | 0 | 284 | 775 | 0 | 5625 | 13024 | 76.84
19:30 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 17 | 95 | 149 | 145 | 0 | 35 | 108 | 0 | 0 | 400 | 297 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 90 | 15 | 15 | 0 | 350 | 0 | 0 | 0 | 150 | 8 | 17 | 3 | 0 | 92 | 100 | 0 | 40 | 0 | 2 | 501 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 51 | 0 | 8 | 0 | 358 | 335 | 54 | 196 | 35 | 50 | 80 | 34 | 38 | 6 | 52 | 24 | 8 | 0 | 0 | 315 | 320 | 356 | 35 | 40 | 0 | 140 | 6 | 0 | 80 | 30 | 0 | 18 | 173 | 0 | 85 | 140 | 0 | 0 | 0 | 12 | 7496 | 880 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 858 | 0 | 1157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 170 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 134 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 220 | 0 | 285 | 980 | 0 | 5869 | 13365
20:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 17 | 95 | 149 | 145 | 0 | 35 | 108 | 0 | 0 | 400 | 303 | 0 | 0 | 0 | 0 | 271 | 0 | 0 | 0 | 90 | 15 | 15 | 0 | 350 | 0 | 0 | 0 | 150 | 15 | 17 | 0 | 0 | 95 | 100 | 0 | 38 | 0 | 4 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 0 | 43 | 0 | 8 | 0 | 357 | 330 | 54 | 189 | 35 | 34 | 80 | 17 | 39 | 6 | 17 | 42 | 8 | 0 | 0 | 315 | 320 | 380 | 34 | 40 | 0 | 133 | 6 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 65 | 123 | 0 | 0 | 0 | 12 | 7397 | 880 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 857 | 0 | 1175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 170 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 137 | 0 | 68 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 220 | 0 | 309 | 987 | 0 | 5952 | 13349 | 76.83
21:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 95 | 149 | 0 | 0 | 35 | 35 | 0 | 0 | 400 | 302 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 90 | 15 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 7 | 17 | 0 | 0 | 95 | 62 | 0 | 37 | 0 | 9 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151 | 0 | 43 | 0 | 8 | 0 | 358 | 335 | 54 | 187 | 35 | 38 | 70 | 21 | 39 | 14 | 52 | 36 | 8 | 0 | 0 | 300 | 320 | 290 | 34 | 40 | 0 | 144 | 6 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 45 | 123 | 0 | 0 | 0 | 12 | 7089 | 928 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 908 | 0 | 1318.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 156 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 157 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 120 | 220 | 0 | 382 | 962 | 0 | 6193.32 | 13282.32 | 76.83
22:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 17 | 95 | 149 | 0 | 0 | 35 | 0 | 0 | 0 | 400 | 310 | 0 | 0 | 0 | 0 | 302 | 0 | 0 | 0 | 70 | 15 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 15 | 17 | 0 | 0 | 70 | 12 | 0 | 38 | 0 | 15 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093 | 0 | 43 | 0 | 8 | 0 | 322 | 300 | 54 | 206 | 35 | 68 | 70 | 51 | 38 | 14 | 52 | 38 | 8 | 0 | 0 | 295 | 320 | 231 | 35 | 40 | 0 | 131 | 6 | 0 | 83 | 30 | 0 | 18 | 173 | 0 | 45 | 123 | 0 | 0 | 0 | 12 | 6876 | 927 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 866 | 0 | 1327.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 158 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 167 | 0 | 72 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 8 | 120 | 180 | 0 | 396 | 998 | 0 | 6186.74 | 13062.74 | 76.82
23:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 102 | 149 | 0 | 0 | 35 | 0 | 0 | 0 | 400 | 305 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 70 | 15 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 4 | 17 | 0 | 0 | 70 | 12 | 0 | 39 | 0 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 0 | 43 | 0 | 8 | 0 | 320 | 300 | 54 | 208 | 35 | 68 | 70 | 51 | 38 | 14 | 52 | 34 | 8 | 0 | 0 | 320 | 320 | 328 | 36 | 40 | 0 | 143 | 6 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 45 | 123 | 0 | 0 | 0 | 12 | 6944 | 927 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 1313.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 159 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 168 | 0 | 72 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 9 | 130 | 180 | 0 | 407 | 1000 | 0 | 6152.36 | 13096.36 | 76.82
Total KWH | 0 | 723840 | 415680 | 0 | 0 | 0 | 0 | 0 | 8287200 | 0 | 0 | 156240 | 396720 | 2325456 | 1903200 | 237360 | 0 | 581707 | 1293120 | 0 | 33600 | 9362500 | 7065600 | 0 | 0 | 51000 | 0 | 6874285 | 0 | 0 | 175864 | 1426800 | 385800 | 357120 | 0 | 10400454.55 | 0 | 0 | 13440 | 3700000 | 532800 | 512699 | 253632 | 0 | 2015040 | 1167360 | 26559 | 946680 | 0 | 228480 | 11512727.27 | 0 | 0 | 19200 | 102951 | 0 | 0 | 0 | 0 | 0 | 23367270 | 114885 | 1105072 | 56872 | 217455 | 0 | 8493900 | 7946000 | 1269600 | 4757000 | 745920 | 1649280 | 1877690 | 2560320 | 423360 | 233710 | 1917480 | 729600 | 387648 | 331827 | 66768 | 7428000 | 6649000 | 8382000 | 823000 | 886440 | 0 | 3407973 | 106848 | 0 | 1622400 | 695424 | 0 | 432000 | 4572140 | 22320 | 968400 | 2584800 | 0 | 5400 | 112530 | 292080 | 170727526.82 | 22241455 | 3824640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 519840 | 20240000 | 0 | 24369818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 643630 | 0 | 195008 | 4081455 | 0 | 4259982 | 0 | 0 | 0 | 9658327 | 0 | 14880 | 0 | 3536000 | 0 | 359612 | 165793 | 500438 | 0 | 0 | 40770.12 | 709200 | 3709 | 0 | 5629000 | 206984 | 2702000 | 5283390 | 0 | 7199280 | 21790545.45 | 0 | 138175756.57 | 308903283.39

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 20-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12994.27 | MW | 12:00 Hr. | Energy Generated |  |  | 308.9033 |  | MKWHr.
| Day Peak Demand |  |  | 13042.27 | MW | 12:00 Hr. | Energy Unserverd |  |  | 1.107 |  | MKWHr.
| Evening Peak Generation |  |  | 13365 | MW | 19:30 Hr. | Energy Demand |  |  | 310.0103 |  | MKWHr.
| Evening Peak Demand |  |  | 13406 | MW | 19:30 Hr. | Maximum Temperature |  |  | 33 |  | °C
| Minimum Generation of the Day |  |  | 11913.6 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 1010.92 |  | MMCFD
| Maximum Generation of the Day |  |  | 14224.5 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.0322 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 42.733 | 0 | 9.5447 | 0 | 0 | 0.17586 | 0 | 0 | 52.4535 | Gas | 138.3298 | Gas | 503985456.1135
| Chattogram Zone |  |  | 3.9285 | 34.88 | 4.0843 | 0 | 0.94668 | 0.14144 | 0 | 0.5328 | 44.5137 | Coal | 93.2748 | Coal | 594942314.5415
| Cumilla Zone |  |  | 26.6463 | 0 | 7.0617 | 0 | 0 | 0.33183 | 0.7296 | 0 | 34.7695 | HFO | 25.4184 | HFO | 473017240.8
| Mymensingh Zone |  |  | 0 | 0 | 3.8676 | 0 | 0 | 0.11793 | 0 | 0 | 3.9855 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.0052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.0052 | Hydro | 0.94668 | Hydro | 94668
| Khulna Zone |  |  | 3.8246 | 20.24 | 0 | 0 | 0 | 0.51984 | 22.2415 | 0 | 46.8259 | Solar | 3.0599 | Solar | 49030465.7432
| Barishal Zone |  |  | 8.1924 | 34.6188 | 0 | 0 | 0 | 0.003709 | 0 | 0 | 42.8149 | Import | 47.3409 | Import | 234481147.54
| Rajshahi Zone |  |  | 17.9998 | 0 | 0 | 0 | 0 | 0.85352 | 24.3698 | 0 | 43.2231 | Wind | 0.5328 | Wind | 7800192
| Rangpur Zone |  |  | 0 | 3.536 | 0.86005 | 0 | 0 | 0.91576 | 0 | 0 | 5.3118
| Total |  |  | 138.3298 | 93.2748 | 25.4184 | 0 | 0.94668 | 3.0599 | 47.3409 | 0.5328 | 308.9033
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 503985456.1135 |  | Hydro | 94668
|  |  |  | Coal | 594942314.5415 |  | Solar | 49030465.7432
|  |  |  | HFO | 473017240.8 |  | Import | 234481147.54
|  |  |  | HSD | 0 |  | Wind | 7800192
[5 empty] | Total: | 186,33,51,484 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2415 | Peak Hr Flow | 880.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 37452072.83 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.3698 | Peak Hr Flow | 1157.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 548 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.7296 | Peak Hr Flow | 24.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 926 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.3409 | Peak Hr Flow | 2061.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 39 |  | 5144
|  |  |  | Chattogram |  | 0 |  | 1515
|  |  |  | Cumilla |  | 0 |  | 933
|  |  |  | Mymensingh |  | 0 |  | 993
|  |  |  | Sylhet |  | 0 |  | 475
|  |  |  | Khulna |  | 0 |  | 1395
|  |  |  | Barishal |  | 0 |  | 421
|  |  |  | Rajshahi |  | 0 |  | 1252
|  |  |  | Rangpur |  | 0 |  | 864
|  |  |  | Total |  | 39 |  | 12992
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 35.09
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Nababganj 55 MW PP (Southern power ) |  |  | 55
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
[7 empty] | 4 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 490.09
|  |  |  | Total Unavailable Capacity |  |  |  | 790.09
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:34 | 09:47 | Ishwardi-Natore 132kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to Line
parameter test and from Natore 132/33kV end Due to Parameter test ( Ishurdi end)
|  | 09:02 | Bhaluka 132/33kV S/S Transformer- 01 HT is restored.
|  | 09:05 | Bhaluka 132/33kV S/S Transformer- 01 LT is restored.
| 09:12 | 18:03 | Dhamrai-Kaliakoir 132 kV Ckt-2 Project Work S/D from Dhamrai 132/33kV end Due to Bay
extension work and from Kaliakoir 400/230/132kV end Due to By NLDC
|  | 09:20 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
|  | 09:20 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
| 09:22 | 16:46 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to Bay extension Project work
| 09:22 | 16:46 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Bay extension Project work
|  | 09:35 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
| 09:36 | 18:53 | Bogura-Mahasthangar (New)) 132 kV Ckt-2 Project Work S/D from Mahasthangarh 132/33kV end
Due to Bogura 132 kv Grid Work Purpose and from Bogura 132/33kV end Due to 132kv Circuit Breaker Change.
|  | 09:36 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
|  | 10:04 | Jhenaidah-Jhenaidah(New) 132kV Ckt-3 is restored.
|  | 10:05 | Jhenaidah 132/33kV S/S Jhenaidah1-Jhenaidah2,132kV Circuit-3(L5) is restored.
|  | 10:05 | Jhenaidah 132/33kV S/S Jhenaidah1-Jhenaidah2,132kV Circuit-3(L5) is restored.
| 10:48 | 12:04 | Ruppur 132/11kV S/S TR-01 HT Tripped showing Differential relay relays Due to Under
Frequency Relay Not Connected.
| 10:56 | 12:16 | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to T-1 Shut Down Due To Energy Meter Change.
| 11:06 | 12:14 | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to T-1 Shut Down Due To Energy Meter Change.
|  | 11:16 | Faridpur 132/33kV S/S Transformer-3 HT is restored.
|  | 11:19 | Faridpur 132/33kV S/S Transformer-3 LT is restored.
| 12:00 |  | Day Peak Generation: 12992 MW.
| 12:31 | 13:52 | Bogura 132/33kV S/S Transformer-2 LT Scheduled S/D Due to T-2 Shut Down Due To Energy Meter Change.
| 12:32 | 13:52 | Bogura 132/33kV S/S Transformer-2 HT Scheduled S/D Due to T-2 Shut Down Due To Energy Meter Change.
| 12:33 | 22:50 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Scheduled S/D Due to CB & Isolation upgrading by BPDB
| 13:48 | 15:27 | Palashbari 132/33kV S/S TR4-434T HT Forced S/D Due to Due to T4 Transformer 33 kV Breaker
R phase Connector Change
| 13:48 | 15:27 | Palashbari 132/33kV S/S TR4-434T LT Forced S/D Due to Due to T4 Transformer 33 kV Breaker
R phase Connector Change.
| 16:40 | 17:56 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to 33 KV PBS FEEDER RED HOT MAINTENANCE | [7 empty] | 10.0MW load interrup.
| 16:41 | 17:54 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to 33 KV PBS FEEDER RED HOT MAINTENANCE | [7 empty] | 10.0MW load interrup.
| 18:00 | 19:55 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Scheduled S/D Due to 33 Companygonj Feeder Bus
DS Bus side red hot
| 18:23 | 20:10 | Ghorashal 230kV S/S TARFO-2 HT Tripped showing Siprotec relays Due to 33 kv pbs outgoing | [7 empty] | 78.0MW load
|  |  | -1 DS insulator ceack | [7 empty] | interrup.
| 18:24 | 20:10 | Ghorashal 230kV S/S TARFO-2 LT Tripped showing siemens relays Due to 33 kv pbs outgoing | [7 empty] | 74.0MW load
|  |  | -1 DS insulator ceack | [7 empty] | interrup.
| 19:30 |  | Evening Peak Gen. 13365 MW
| 19:58 |  | Patuakhali 1320 MW (RNPL) Unit-1 was synchronized.
|  | 21:06 | Gopalganj 400/132kV S/S 400kV Bus-02 is restored.
| 23:40 |  | Borhanuddin 230/33KV Transformer(PDB) S/D Due to Abnormal Noise. | [7 empty] | 23MW load interrup.
| 23:57 |  | Borhanuddin 230/33KV Transformer(Power Grid) Tripped. | [7 empty] | 70MW load interrup.
| 02:51 |  | Borhanuddin 230/33KV Transformer(Power Grid) Restored. | [7 empty] | 70MW load interrup.
| 05:53 |  | Haripur-Meghnaghat 230kV Ckt-1 Scheduled S/D from Haripur 230/132kV end Due to Line DS Y
phase Changing Work
| 06:30 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 06:48 |  | Chowmuhani-Ramganj 132 kV Ckt-1 Project Work S/D from Chowmuhani 132/33kV end Due to
Temporary Jumper Remove from Ramgonj -1 to Chowmuhoni Maijdi
| 07:33 |  | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to ৩৩ কেভি ইনকামার-০২ এর আইসোলেটরের উপরে | [7 empty] | 10.0MW load
|  |  | রেড হট হওয়ায়। | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 20-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 174.8 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 40 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 320 | 8287200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 9362500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 297 | 7065600 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 75.24 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 22 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 93 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 278 | 6874285 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 156240 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 149 | 1903200 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 581707 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 51000 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 385800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 357120 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 415680 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 145 | 237360 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 95 | 2325456 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 723840 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 33600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1293120 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 175864 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 396720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 350 | 10400454.55 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 0 | 0 | Schedule Outage
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1426800 | -
Dhaka Area Total |  |  |  |  | 6085.764 | 2383 | 52453546.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3700000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 102951 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 114885 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 19200 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 946680 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 126.5 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 94 | 3 | 253632 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 98 | 17 | 512699 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 92 | 2015040 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 228480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 13440 | Engine Problem
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 7 | 0 | 26559 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1167360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1103 | 23367270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 8 | 532800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 501 | 11512727.27 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4915.22 | 2034 | 44513723.27
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 196 | 4757000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 358 | 8493900 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 7946000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.94 | 35 | 745920 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 54 | 1269600 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1105072 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 56872 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 47 | 0 | 66768 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1877690 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 2560320 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 24 | 729600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 387648 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 6 | 233710 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1917480 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 423360 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 50 | 1649280 | Liquid fuel shortage
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 331827 | -
Cumilla Area Total |  |  |  |  | 2897.48 | 1329 | 34769502
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 5400 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 140 | 2584800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 968400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 112530 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 292080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 22320 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 237 | 3985530
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 80 | 35 | 823000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 886440 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 140 | 3407973 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 47.998 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66.57 | 30 | 695424 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1622400 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 225 | 173 | 4572140 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 106848 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7428000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 356 | 8382000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 6649000 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2368.568 | 1513 | 35005225
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 22241455 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 50 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 100 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 147 | 3824640 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 519840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 858 | 20240000 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3686.2 | 1885 | 46825935
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 1320 | 285 | 7199280 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 206984 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 193.1 | 100 | 2702000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 980 | 21790545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5283390 | Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5629000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3709 | -
Barishal Area Total |  |  |  |  | 3585.1 | 1903 | 42814908.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 47 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 66 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 35.09 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 45.49 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 165 | 4081455 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 170 | 4259982 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 9658327 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 46 | 0 | 0 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 14880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1157 | 24369818 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 195008 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 643630 | -
Rajshahi Area Total |  |  |  |  | 3481.54 | 1842 | 43223100
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 134 | 3536000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 500438 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 40770.12 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 359612 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 165793 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 709200 | -
Rangpur Area Total |  |  |  |  | 950 | 239 | 5311813.12
Eastern Grid Total |  |  |  |  | 16921.242 | 7496 | 170727526.82
Western Grid Total |  |  |  |  | 11702.84 | 5869 | 138175756.57
National Grid Total |  |  |  |  | 28624.082 | 13365 | 308903283.39
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 20-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9021.09 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3931.6 | MW
i) Dhaka area |  |  | 5105.46 |  | MW | i) Khulna area |  |  |  | 1394.8 | MW
ii) Chattogram area |  |  | 1515 |  | MW | ii) Barishal area |  |  |  | 421 | MW
iii) Cumilla area |  |  | 932.63 |  | MW | iii) Rajshahi area |  |  |  | 1251.8 | MW
iv) Mymensingh area |  |  | 993 |  | MW | iv) Rangpur area |  |  |  | 864 | MW
v) Sylhet area |  |  | 475 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12952.69 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 80 | 13:00 | 133 | Patuakhali | 85.4 | 00:00
2 | AKSML | 117 | 13:00 | 68 | Jaldhaka | 73 | 20:00 | 134 | Payra | 36 | 22:00
3 | Aftabnagar | 68 | 12:00 | 69 | Jamalpur | 100 | 19:30 | 135 | Postogola | 64 | 13:00
4 | Agargaon | 143 | 13:00 | 70 | Jashore | 144 | 19:30 | 136 | Purbachal | 18 | 00:00
5 | Agrabad | 100 | 16:00 | 71 | Jhenaidah | 118 | 20:00 | 137 | Purbasadipur | 118 | 19:30
6 | Amnura | 32 | 22:00 | 72 | Joydebpur | 157 | 11:00 | 138 | Rahanpur | 26 | 01:00
7 | Ashuganj | 97 | 00:00 | 73 | Joypurhat | 52 | 00:00 | 139 | Rahim | 53 | 09:00
8 | BSRM | 202 | 12:00 | 74 | Juldah | 14 | 08:00 | 140 | Rajbari | 66 | 15:00
9 | Bagerhat | 86 | 19:00 | 75 | KSRM | 20 | 19:30 | 141 | Rajendrapur | 127 | 00:00
10 | Bajitpur | 44 | 01:00 | 76 | Kabirpur | 289 | 09:00 | 142 | Rajshahi | 104 | 00:00
11 | Bakulia | 114 | 19:30 | 77 | Kachua | 81 | 00:00 | 143 | Rajshahi-230 | 84 | 13:00
12 | Banani | 58 | 11:00 | 78 | Kallyanpur | 105 | 12:00 | 144 | Ramganj | 110 | 00:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 28 | 16:00 | 145 | Rampur | 47 | 00:00
14 | Barapukuria | 57 | 21:00 | 80 | Kamrangirchar | 72 | 12:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 24 | 20:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 132 | 20:00
16 | Barishal | 114 | 19:30 | 82 | Kasba | 31 | 00:00 | 148 | Ruppur | 7.4 | 08:00
17 | Barishal-230 | 96 | 00:00 | 83 | Kazla | 107 | 13:00 | 149 | SSM | 14 | 00:00
18 | Baroaulia | 58 | 00:00 | 84 | Keranigonj | 87 | 19:00 | 150 | Saidpur | 100 | 19:30
19 | Baroirhat | 63 | 00:00 | 85 | Khagrachori | 24 | 00:00 | 151 | Satkhira | 147 | 22:00
20 | Bashundhara | 198 | 12:00 | 86 | Khulna | 78 | 19:30 | 152 | Satmasjid | 110 | 13:00
21 | BashundharaCement | 14 | 15:00 | 87 | Khulshi | 197 | 19:00 | 153 | Savar | 236 | 12:00
22 | Beanibazar | 64 | 00:00 | 88 | Kishoreganj | 114 | 00:00 | 154 | SevenRings | 17.91 | 12:00
23 | Benapole | 70 | 19:00 | 89 | Kodda | 310 | 18:00 | 155 | ShahCement | 29 | 03:00
24 | Bhaluka | 149 | 10:00 | 90 | Kulaura | 38 | 19:30 | 156 | Shahjadpur | 74 | 09:00
25 | Bhandaria | 58 | 22:00 | 91 | Kurigram | 58 | 19:00 | 157 | Shahjibazar | 113 | 22:00
26 | Bhangura | 30 | 20:00 | 92 | Kushtia | 142 | 15:00 | 158 | Shahmirpur | 56 | 00:00
27 | Bheramara(GK) | 58 | 13:00 | 93 | Lalbag | 71 | 11:00 | 159 | Shariatpur | 78 | 00:00
28 | Bhulta | 237 | 10:00 | 94 | Lalmonirhat | 55 | 19:00 | 160 | Sherpur | 122 | 19:00
29 | Bog-Sherpur | 62 | 00:00 | 95 | MI_Cement | 16.7 | 11:00 | 161 | Shikalbaha | 30 | 00:00
30 | Bogura | 148 | 01:00 | 96 | Madanganj | 48 | 13:00 | 162 | Shitalakhya | 91 | 12:00
31 | Borhanuddin | 103 | 00:00 | 97 | Madaripur | 99 | 00:00 | 163 | Sholosohor | 50 | 16:00
32 | Brahmanbaria | 119 | 00:00 | 98 | Madartek | 84.14 | 00:00 | 164 | Shyampur | 178 | 07:00
33 | Cantonment | 156 | 12:00 | 99 | Madunaghat | 59 | 19:00 | 165 | Siddhirganj | 122 | 15:00
34 | Chandina | 25.62 | 12:00 | 100 | Magura | 54 | 20:00 | 166 | Sirajganj | 94 | 20:00
35 | Chandpur | 69 | 00:00 | 101 | Mahasthangarh | 74 | 00:00 | 167 | Sonargaon | 115 | 00:00
36 | Chandraghona | 36 | 19:30 | 102 | Manikganj | 125 | 15:00 | 168 | Sreemongol | 65 | 00:00
37 | Chapai | 67 | 00:00 | 103 | Maniknagar | 90 | 13:00 | 169 | Sreepur | 102 | 10:00
38 | Charsaidpur | 47 | 00:00 | 104 | Matarbari | 50 | 05:00 | 170 | Srinagar | 41.34 | 00:00
39 | Chauddagram | 64 | 00:00 | 105 | Matuail | 70 | 13:00 | 171 | Sunamganj | 50 | 00:00
40 | Chhatak | 29 | 00:00 | 106 | Millgate | 132 | 10:00 | 172 | Sylhet | 37 | 17:00
41 | Chowmuhani | 210 | 07:00 | 107 | Mirpur | 125 | 12:00 | 173 | Sylhet-132 | 100 | 19:00
42 | Chuadanga | 104 | 14:00 | 108 | Mirsorai | 11 | 09:00 | 174 | TK | 35.5 | 00:00
43 | Coxsbazar | 139 | 19:30 | 109 | Mirzapur | 40 | 07:00 | 175 | Tangail | 144 | 19:30
44 | Cumilla(N) | 131 | 00:00 | 110 | Mithapukur | 48 | 19:30 | 176 | Thakurgaon | 96 | 20:00
45 | Cumilla(S) | 159 | 12:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 118 | 11:00
46 | Daudkandi | 119 | 00:00 | 112 | Mogbazar | 145.2 | 13:00 | 178 | Ullahpara | 30 | 19:30
47 | Dhaka | 76 | 12:00 | 113 | Mongla | 36 | 19:30 | 179 | Ullon | 40 | 21:00
48 | Dhamrai | 136 | 06:00 | 114 | Motijheel | 43 | 11:00 | 180 | Uttara | 88 | 12:00
49 | Dhanmondi | 148 | 13:00 | 115 | Muktagacha | 27 | 19:00 | 181 | UttaraNew | 59 | 12:00
50 | Dohazari | 115 | 19:30 | 116 | Munshiganj | 101 | 00:00 | 182 | Zigatola | 76 | 13:00
51 | Faridpur | 138 | 22:00 | 117 | Muradnagar | 28 | 23:00
52 | Fatullah | 104 | 10:00 | 118 | Mymensingh | 178 | 00:00
53 | Fenchuganj | 32 | 00:00 | 119 | Naogaon | 117 | 00:00
54 | Feni | 115 | 00:00 | 120 | Narail | 56 | 20:00
55 | GPH | 94 | 18:00 | 121 | Narinda | 90 | 13:00
56 | Ghatail | 66 | 07:00 | 122 | Narshingdi | 173 | 00:00
57 | Ghorashal | 15 | 10:00 | 123 | Natore | 133 | 00:00
58 | Ghorashal-230 | 93 | 22:00 | 124 | Nawabganj | 50.6 | 13:00
59 | Goalpara | 42 | 21:00 | 125 | Netrakona | 108 | 00:00
60 | Gollamari | 88 | 12:00 | 126 | New | 90.1 | 15:00
61 | Gopalganj | 93 | 21:00 | 127 | Niamatpur | 62 | 22:00
62 | Gulshan | 134 | 13:00 | 128 | Noapara | 48 | 20:00
63 | Halishahar | 90 | 15:00 | 129 | PHP | 8 | 01:00
64 | HaripurSBU | 197 | 11:00 | 130 | Pabna | 114 | 22:00
65 | Hasnabad | 87 | 13:00 | 131 | Palashbari | 89 | 19:30
66 | Hathazari | 84 | 00:00 | 132 | Panchagarh | 59 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 20-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14224.5 | 92 |  | 14320.5
1:00 | 13624 | 53 |  | 13679
2:00 | 13229 | 49 |  | 13280
3:00 | 12952 | 46 |  | 13000
4:00 | 12748 | 45 |  | 12795
5:00 | 12523 | 40 |  | 12565
6:00 | 12260.66 | 26 |  | 12287.66
7:00 | 12269.19 | 10 |  | 12279.19
8:00 | 12111.84 | 106 |  | 12222.84
9:00 | 12402.52 | 86 |  | 12492.52
10:00 | 12640.1 | 50 |  | 12692.1
11:00 | 12729.43 | 52 |  | 12783.43
12:00 | 12994.27 | 46 |  | 13042.27
13:00 | 12743.37 | 49 |  | 12794.37
14:00 | 12458.55 | 32 |  | 12491.55
15:00 | 12803.09 | 28 |  | 12832.09
16:00 | 12089.82 | 31 |  | 12121.82
17:00 | 11913.6 | 37 |  | 11952.6
18:00 | 11827.82 | 42 |  | 11871.82
19:00 | 13024 | 44 |  | 13070
19:30 | 13365 | 39 |  | 13406
20:00 | 13349 | 39 |  | 13390
21:00 | 13282.32 | 36 |  | 13319.94
22:00 | 13062.74 | 36 |  | 13100.74
23:00 | 13096.36 | 32 |  | 13129.36
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 20-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7622.5 | 6602 | 14224.5 | DAILY GENERATION CURVE
00:30 | 7420.75 | 6503.5 | 13924.25
01:00 | 7219 | 6405 | 13624 | 20-05-2025
01:30 | 7167.5 | 6259 | 13426.5
02:00 | 7116 | 6113 | 13229
02:30 | 7114 | 5976.5 | 13090.5
03:00 | 7112 | 5840 | 12952
03:30 | 7024.5 | 5825.5 | 12850
04:00 | 6937 | 5811 | 12748
04:30 | 6901.5 | 5734 | 12635.5
05:00 | 6866 | 5657 | 12523
05:30 | 6821.055 | 5570.775 | 12391.83
06:00 | 6776.11 | 5484.55 | 12260.66
06:30 | 6804.085 | 5460.84 | 12264.925
07:00 | 6832.06 | 5437.13 | 12269.19
07:30 | 6792.155 | 5398.36 | 12190.515
08:00 | 6752.25 | 5359.59 | 12111.84
08:30 | 6872.95 | 5384.23 | 12257.18
09:00 | 6993.65 | 5408.87 | 12402.52
09:30 | 7008.405 | 5512.905 | 12521.31
10:00 | 7023.16 | 5616.94 | 12640.1
10:30 | 7086.885 | 5597.88 | 12684.765
11:00 | 7150.61 | 5578.82 | 12729.43
11:30 | 7210.91 | 5650.94 | 12861.85
12:00 | 7271.21 | 5723.06 | 12994.27
12:30 | 7187.895 | 5680.925 | 12868.82
13:00 | 7104.58 | 5638.79 | 12743.37
13:30 | 7045.395 | 5555.565 | 12600.96
14:00 | 6986.21 | 5472.34 | 12458.55
14:30 | 7052.24 | 5578.58 | 12630.82
15:00 | 7118.27 | 5684.82 | 12803.09
15:30 | 6992.3 | 5454.155 | 12446.455
16:00 | 6866.33 | 5223.49 | 12089.82
16:30 | 6765.275 | 5236.435 | 12001.71
17:00 | 6664.22 | 5249.38 | 11913.6
17:30 | 6674.305 | 5196.405 | 11870.71
18:00 | 6684.39 | 5143.43 | 11827.82
18:30 | 7041.695 | 5384.215 | 12425.91
19:00 | 7399 | 5625 | 13024
19:30 | 7496 | 5869 | 13365
20:00 | 7397 | 5952 | 13349
20:30 | 7243 | 6072.66 | 13315.66 |  | Executive Engineer
21:00 | 7089 | 6193.32 | 13282.32 |  | Network Operation Division
21:30 | 6982.5 | 6190.03 | 13172.53
22:00 | 6876 | 6186.74 | 13062.74
22:30 | 6910 | 6169.55 | 13079.55
23:00 | 6944 | 6152.36 | 13096.36

## En-Curve
QF-LDC-12
Date | 20-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3450 | 2111.5 | 928 | 0 | 36 | 1408 | 40 | 4540 | 0 | 439 | 1261 | 0 | 0 | 11 | 92 | DAILY ENERGY CURVE
00:30 | 3446.5 | 2094.25 | 927.5 | 0 | 35 | 1362 | 40 | 4507 | 0 | 387 | 1111.5 | 0 | 0 | 13.5 | 72.5 | 20-05-2025
01:00 | 3443 | 2077 | 927 | 0 | 34 | 1316 | 40 | 4474 | 0 | 335 | 962 | 0 | 0 | 16 | 53
01:30 | 3489.5 | 2082.5 | 927 | 0 | 34 | 1240 | 40 | 4412 | 0 | 291 | 892 | 0 | 0 | 18.5 | 51 | Energy Generated | 308.9033 |  | MKWHr
02:00 | 3536 | 2088 | 927 | 0 | 34 | 1164 | 40 | 4350 | 0 | 247 | 822 | 0 | 0 | 21 | 49 | Energy not Served | 1.107 |  | MKWHr
02:30 | 3540 | 2089.5 | 926.5 | 0 | 33 | 1095 | 40 | 4286.5 | 0 | 247 | 813 | 0 | 0 | 20 | 47.5 | Total Energy Requirement | 310.0103 |  | MKWHr
03:00 | 3544 | 2091 | 926 | 0 | 32 | 1026 | 40 | 4223 | 0 | 247 | 804 | 0 | 0 | 19 | 46
03:30 | 3575.5 | 2097 | 926 | 0 | 32 | 1026.5 | 40 | 4130.5 | 0 | 219 | 787.5 | 0 | 0 | 16 | 45.5
04:00 | 3607 | 2103 | 926 | 0 | 32 | 1027 | 40 | 4038 | 0 | 191 | 771 | 0 | 0 | 13 | 45
04:30 | 3574.5 | 2084 | 926.5 | 0 | 32 | 1024.5 | 40 | 3975 | 0 | 191 | 774 | 0 | 0 | 14 | 42.5
05:00 | 3542 | 2065 | 927 | 0 | 32 | 1022 | 40 | 3912 | 0 | 191 | 777 | 0 | 0 | 15 | 40
05:30 | 3549.5 | 2074.5 | 926.5 | 0 | 31 | 1021.5 | 40 | 3770.5 | 13.33 | 191 | 758.5 | 0 | 0 | 15.5 | 33
06:00 | 3557 | 2084 | 926 | 0 | 30 | 1021 | 40 | 3629 | 26.66 | 191 | 740 | 0 | 0 | 16 | 26
06:30 | 3546.5 | 2085.5 | 926 | 0 | 32 | 1026 | 39 | 3602 | 56.925 | 182.5 | 754.5 | 0 | 0 | 14 | 18
07:00 | 3536 | 2087 | 926 | 0 | 34 | 1031 | 38 | 3575 | 87.19 | 174 | 769 | 0 | 0 | 12 | 10
07:30 | 3561.5 | 1980 | 902 | 0 | 32 | 978.345 | 38 | 3577 | 158.17 | 165.5 | 781.5 | 0 | 0 | 16.5 | 58
08:00 | 3587 | 1873 | 878 | 0 | 30 | 925.69 | 38 | 3579 | 229.15 | 157 | 794 | 0 | 0 | 21 | 106
08:30 | 3666.5 | 1947 | 878 | 0 | 30 | 921.67 | 38 | 3554.5 | 249.01 | 174 | 768.5 | 0 | 0 | 30 | 96
09:00 | 3746 | 2021 | 878 | 0 | 30 | 917.65 | 38 | 3530 | 268.87 | 191 | 743 | 0 | 0 | 39 | 86
09:30 | 3770.5 | 2010 | 902 | 0 | 30 | 920.59 | 38.5 | 3603 | 305.72 | 177 | 731.5 | 0 | 0 | 32.5 | 68
10:00 | 3795 | 1999 | 926 | 0 | 30 | 923.53 | 39 | 3676 | 342.57 | 163 | 720 | 0 | 0 | 26 | 50
10:30 | 3782 | 1994.5 | 926 | 0 | 27 | 939.535 | 39.5 | 3754.5 | 294.73 | 161.5 | 744 | 0 | 0 | 21.5 | 51
11:00 | 3769 | 1990 | 926 | 0 | 24 | 955.54 | 40 | 3833 | 246.89 | 160 | 768 | 0 | 0 | 17 | 52
11:30 | 3724.5 | 1980 | 926 | 0 | 28 | 957.37 | 40 | 3857 | 319.98 | 153.5 | 852 | 0 | 0 | 23.5 | 49
12:00 | 3680 | 1970 | 926 | 0 | 32 | 959.2 | 40 | 3881 | 393.07 | 147 | 936 | 0 | 0 | 30 | 46
12:30 | 3673.5 | 1927 | 926.5 | 0 | 30 | 964.275 | 40 | 3851 | 396.045 | 147.5 | 873.5 | 0 | 0 | 39.5 | 47.5
13:00 | 3667 | 1884 | 927 | 0 | 28 | 969.35 | 40 | 3821 | 399.02 | 148 | 811 | 0 | 0 | 49 | 49
13:30 | 3735.5 | 1947.9 | 927 | 0 | 29 | 965.175 | 40 | 3643.5 | 359.885 | 139 | 767 | 0 | 0 | 47 | 40.5
14:00 | 3804 | 2011.8 | 927 | 0 | 30 | 961 | 40 | 3466 | 320.75 | 130 | 723 | 0 | 0 | 45 | 32
14:30 | 3780 | 2005.3 | 926.5 | 0 | 28 | 972.5 | 40 | 3587 | 309.52 | 151.5 | 783 | 0 | 0 | 47.5 | 30
15:00 | 3756 | 1998.8 | 926 | 0 | 26 | 984 | 40 | 3708 | 298.29 | 173 | 843 | 0 | 0 | 50 | 28
15:30 | 3742.5 | 1994.3 | 926 | 0 | 26 | 921 | 40 | 3569 | 220.155 | 173 | 789.5 | 0 | 0 | 45 | 29.5
16:00 | 3729 | 1989.8 | 926 | 0 | 26 | 858 | 40 | 3430 | 142.02 | 173 | 736 | 0 | 0 | 40 | 31
16:30 | 3686 | 1986.3 | 926 | 0 | 22 | 861 | 40 | 3427 | 133.41 | 173 | 705.5 | 0 | 0 | 41.5 | 34
17:00 | 3643 | 1982.8 | 926 | 0 | 18 | 864 | 40 | 3424 | 124.8 | 173 | 675 | 0 | 0 | 43 | 37
17:30 | 3610.5 | 1968 | 926.5 | 0 | 19 | 864 | 40 | 3428.5 | 71.71 | 218 | 697.5 | 0 | 0 | 27 | 39.5
18:00 | 3578 | 1953.2 | 927 | 0 | 20 | 864 | 40 | 3433 | 18.62 | 263 | 720 | 0 | 0 | 11 | 42
18:30 | 3633 | 1982.6 | 904 | 0 | 24 | 966 | 40 | 3673 | 9.31 | 308.5 | 876.5 | 0 | 0 | 9 | 43
19:00 | 3688 | 2012 | 881 | 0 | 28 | 1068 | 40 | 3913 | 0 | 354 | 1033 | 0 | 0 | 7 | 44
19:30 | 3656 | 1970 | 880 | 0 | 24 | 1157 | 40 | 4168 | 0 | 328 | 1134 | 0 | 0 | 8 | 39
20:00 | 3657 | 1966 | 880 | 0 | 42 | 1175 | 38 | 4203 | 0 | 325 | 1048 | 0 | 0 | 15 | 39
20:30 | 3660 | 1989.5 | 904 | 0 | 39 | 1246.66 | 37.5 | 4170.5 | 0 | 325 | 932.5 | 0 | 0 | 11 | 37.5
21:00 | 3663 | 2013 | 928 | 0 | 36 | 1318.32 | 37 | 4138 | 0 | 325 | 817 | 0 | 0 | 7 | 36
21:30 | 3618.5 | 1995 | 927.5 | 0 | 37 | 1323.03 | 37.5 | 4115.5 | 0 | 315 | 792.5 | 0 | 0 | 11 | 36
22:00 | 3574 | 1977 | 927 | 0 | 38 | 1327.74 | 38 | 4093 | 0 | 305 | 768 | 0 | 0 | 15 | 36
22:30 | 3635.5 | 1986 | 927 | 0 | 36 | 1320.55 | 38.5 | 4059 | 0 | 296 | 771.5 | 0 | 0 | 9.5 | 34
23:00 | 3697 | 1995 | 927 | 0 | 34 | 1313.36 | 39 | 4025 | 0 | 287 | 775 | 0 | 0 | 4 | 32
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 20-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 381 | 18:00 | 368 | 11:00 | Payra | 414 | 14:00 | 407 | 00:00
Ashuganj | 393 | 5:00 | 368 | 10:00 | Rahanpur | 413 | 06:00 | 396 | 00:00
Bhulta | 387 | 05:00 | 365 | 11:00 | Rampal | 399 | 18:00 | 387 | 00:00
Bibiana | 394 | 18:30 | 385 | 00:00
BIPTC | 404 | 08:00 | 393 | 13:00
Bogura | 404 | 06:00 | 385 | 00:00
Gopalganj | 394 | 18:00 | 382 | 00:00
Kaliakoir | 373 | 18:30 | 360 | 11:00
Madunaghat | 392 | 06:00 | 385 | 00:00
Meghnaghat | 384 | 18:00 | 373 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 222 | 18:30 | 211 | 11:00 | Keranigonj | 220 | 18:30 | 209 | 11:00
AKSML | 230 | 18:30 | 221 | 12:00 | Khulna(S) | 227 | 18:00 | 216 | 00:00
Aminbazar | 222 | 18:00 | 213 | 12:00 | Madunaghat | 230 | 06:00 | 226 | 11:00
Ashuganj | 228 | 07:00 | 220 | 00:00 | Madunaghat-400 | 231 | 07:00 | 226 | 01:00
Ashuganj-400 | 220 | 5:00 | 216 | 10:00 | Maniknagar | 217 | 06:00 | 208 | 11:00
Baghabari | 234 | 05:00 | 225 | 00:00 | Meghnaghat | 226 | 18:30 | 219 | 10:00
Barapukuria | 228 | 04:00 | 215 | 19:30 | Meghnaghat-400 | 222 | 18:00 | 214 | 11:00
Barapukuria-230 | 226 | 5:00 | 215 | 19:00 | Mirsorai | 225 | 08:00 | 218 | 15:00
Barishal | 239 | 01:00 | 228 | 00:00 | Rajshahi | 236 | 05:00 | 224 | 00:00
Bheramara | 234 | 05:00 | 225 | 00:00 | Rampal | 227 | 18:30 | 217 | 00:00
Bhulta | 225 | 05:00 | 209 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 18:30 | 219 | 00:00 | Rampura | 223 | 05:00 | 206 | 11:00
BIPTC | 236 | 04:00 | 225 | 00:00 | Shikalbaha | 229 | 07:00 | 222 | 15:00
Bogura | 232 | 06:00 | 223 | 00:00 | Shyampur | 220 | 18:30 | 210 | 11:00
Bogura-400 | 234 | 06:00 | 223 | 19:30 | Siddhirganj | 219 | 20:00 | 212 | 11:00
Borhanuddin | 240 | 17:00 | 234 | 00:00 | Sirajgonj | 238 | 06:00 | 230 | 02:00
BSRM | 227 | 18:00 | 218 | 11:00 | Sreepur | 228 | 18:30 | 219 | 00:00
Cumilla(N) | 222 | 18:00 | 212 | 11:00 | Tongi | 225 | 19:30 | 209 | 11:00
Faridpur | 233 | 18:00 | 223 | 00:00
Fenchuganj | 227 | 08:00 | 221 | 01:00
Ghorashal | 225 | 00:00 | 220 | 09:00
Ghorashal-230 | 224 | 18:30 | 209 | 11:00
Gopalganj | 234 | 18:30 | 225 | 00:00
GPH | 228 | 18:00 | 222 | 11:00
Haripur | 219 | 18:00 | 210 | 11:00
Hasnabad | 220 | 18:00 | 210 | 10:00
Hathazari | 231 | 06:00 | 224 | 11:00
Ishurdi | 237 | 03:00 | 227 | 00:00
Jhenaidah | 229 | 05:00 | 220 | 00:00
Kaliakoir | 229 | 20:00 | 218 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 06:00 | 124 | 11:00 | Madartek | 136 | 06:00 | 124 | 11:00
Agargaon | 133 | 05:00 | 125 | 11:00 | Madunaghat | 131 | 09:00 | 127 | 11:00
Agrabad | 131 | 06:00 | 126 | 10:00 | Magura | 135 | 05:00 | 126 | 14:00
AKS | 130 | 04:00 | 125 | 15:00 | Mahasthangarh | 136 | 06:00 | 129 | 01:00
Aminbazar | 131 | 17:00 | 124 | 09:00 | Manikganj | 130 | 18:30 | 119 | 11:00
Amnura | 136 | 18:30 | 125 | 00:00 | Maniknagar | 131 | 06:00 | 123 | 12:00
Ashuganj | 136 | 06:00 | 133 | 00:00 | Matarbari | 120 | 09:00 | 109 | 21:00
Bagerhat | 127 | 07:00 | 118 | 00:00 | Matuail | 128 | 18:00 | 121 | 11:00
Bajitpur | 132 | 12:00 | 126 | 01:00 | Millgate | 134 | 20:00 | 123 | 10:00
Bakulia | 133 | 07:00 | 126 | 15:00 | Mirpur | 129 | 16:00 | 122 | 10:00
Banani | 137 | 04:00 | 125 | 11:00 | Mirzapur | 134 | 18:30 | 128 | 02:00
Bangabhaban | 131 | 04:00 | 123 | 11:00 | Mithapukur | 134 | 05:00 | 124 | 19:30
Barapukuria | 136 | 04:00 | 123 | 19:30 | MI_Cement | 128 | 17:00 | 121 | 11:00
Barguna | 133 | 06:00 | 129 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 18:30 | 125 | 00:00 | Mogbazar | 135 | 02:00 | 125 | 11:00
Barishal-230 | 131 | 18:00 | 124 | 00:00 | Mongla | 128 | 09:00 | 119 | 00:00
Baroaulia | 132 | 07:00 | 127 | 15:00 | Motijheel | 131 | 04:00 | 123 | 11:00
Baroirhat | 128 | 19:30 | 118 | 01:00 | Muktagacha | 135 | 00:00 | 131 | 07:00
Bashundhara | 137 | 04:00 | 122 | 11:00 | Munshiganj | 128 | 18:00 | 121 | 11:00
BashundharaCement | 128 | 18:00 | 120 | 12:00 | Muradnagar | 129 | 18:30 | 120 | 00:00
Beanibazar | 133 | 08:00 | 126 | 00:00 | Mymensingh | 137 | 08:00 | 118 | 00:00
Benapole | 129 | 18:30 | 118 | 20:00 | Naogaon | 135 | 10:00 | 127 | 00:00
Bhaluka | 133 | 18:30 | 124 | 14:00 | Narail | 136 | 05:00 | 126 | 14:00
Bhandaria | 126 | 18:00 | 115 | 00:00 | Narinda | 131 | 6:00 | 123 | 12:00
Bhangura | 134 | 04:00 | 129 | 00:00 | Narshingdi | 130 | 13:00 | 115 | 10:00
Bheramara | 138 | 05:00 | 132 | 14:00 | Natore | 135 | 17:00 | 127 | 00:00
Bheramara(GK) | 137 | 06:00 | 132 | 00:00 | Nawabganj | 132 | 18:00 | 123 | 11:00
Bhulta | 120 | 18:00 | 113 | 12:00 | Netrakona | 131 | 10:00 | 118 | 00:00
Bog-Sherpur | 136 | 06:00 | 129 | 00:00 | New | 134 | 20:00 | 124 | 11:00
Bogura | 138 | 18:30 | 132 | 00:00 | Niamatpur | 136 | 06:00 | 129 | 00:00
Bogura-230 | 138 | 06:00 | 132 | 00:00 | Noapara | 132 | 18:30 | 123 | 00:00
Brahmanbaria | 130 | 13:00 | 121 | 00:00 | Pabna | 136 | 16:00 | 130 | 00:00
Cantonment | 133 | 05:00 | 125 | 11:00 | Palashbari | 134 | 06:00 | 123 | 19:30
Chandina | 130 | 18:30 | 122 | 00:00 | Panchagarh | 135 | 21:00 | 120 | 19:30
Chandpur | 131 | 16:00 | 119 | 23:00 | Patuakhali | 133 | 06:00 | 129 | 00:00
Chandraghona | 131 | 07:00 | 126 | 15:00 | Payra | 135 | 07:00 | 132 | 00:00
Chapai | 134 | 18:00 | 126 | 00:00 | PHP | 127 | 16:00 | 117 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 18:00 | 121 | 11:00 | Postogola | 131 | 18:00 | 125 | 10:00
Chauddagram | 128 | 18:30 | 116 | 00:00 | Purbachal | 138 | 05:00 | 124 | 11:00
Chhatak | 132 | 09:00 | 124 | 00:00 | Purbasadipur | 130 | 04:00 | 117 | 19:30
Chowmuhani | 125 | 16:00 | 111 | 01:00 | Rahanpur | 137 | 05:00 | 132 | 00:00
Chuadanga | 133 | 05:00 | 123 | 14:00 | Rahanpur-400 | 138 | 06:00 | 132 | 00:00
Coxsbazar | 119 | 07:00 | 109 | 19:00 | Rahim | 128 | 18:00 | 122 | 12:00
Cumilla(N) | 130 | 18:30 | 121 | 00:00 | Rajbari | 136 | 17:00 | 128 | 00:00
Cumilla(S) | 134 | 23:00 | 120 | 00:00 | Rajendrapur | 133 | 06:00 | 118 | 11:00
Daudkandi | 128 | 18:30 | 117 | 12:00 | Rajshahi | 135 | 05:00 | 128 | 00:00
Dhaka | 138 | 05:00 | 125 | 11:00 | Rajshahi-230 | 136 | 07:00 | 121 | 00:00
Dhamrai | 134 | 18:30 | 126 | 10:00 | Ramganj | 127 | 16:00 | 112 | 00:00
Dhanmondi | 137 | 05:00 | 125 | 11:00 | Rampur | 130 | 06:00 | 126 | 11:00
Dohazari | 127 | 09:00 | 121 | 19:00 | Rampura | 137 | 05:00 | 124 | 11:00
Faridpur | 137 | 18:00 | 130 | 00:00 | Rangamati | 130 | 06:00 | 125 | 15:00
Fatullah | 129 | 18:00 | 122 | 11:00 | Rangpur | 134 | 06:00 | 120 | 19:30
Fenchuganj | 136 | 13:00 | 132 | 00:00 | Ruppur | 138 | 04:00 | 133 | 00:00
Feni | 126 | 16:00 | 117 | 00:00 | Saidpur | 133 | 05:00 | 118 | 19:30
Ghatail | 134 | 18:30 | 127 | 21:00 | Satkhira | 128 | 05:00 | 117 | 22:00
Ghorashal | 135 | 13:00 | 127 | 11:00 | Satmasjid | 133 | 06:00 | 125 | 11:00
Goalpara | 134 | 18:30 | 124 | 00:00 | Savar | 130 | 17:00 | 121 | 11:00
Gollamari | 134 | 18:30 | 127 | 00:00 | SevenRings | 134 | 06:00 | 126 | 11:00
Gopalganj | 135 | 18:30 | 127 | 00:00 | ShahCement | 128 | 18:00 | 121 | 11:00
Gopalganj-400 | 136 | 18:00 | 130 | 00:00 | Shahjadpur | 136 | 05:00 | 132 | 01:00
Gulshan | 137 | 04:00 | 125 | 11:00 | Shahjibazar | 132 | 13:00 | 123 | 00:00
Halishahar | 133 | 07:00 | 124 | 15:00 | Shahmirpur | 133 | 07:00 | 128 | 15:00
Haripur | 127 | 06:00 | 122 | 11:00 | Shariatpur | 136 | 18:30 | 127 | 00:00
HaripurSBU | 128 | 18:00 | 122 | 11:00 | Sherpur | 140 | 08:00 | 124 | 01:00
Hasnabad | 130 | 19:00 | 124 | 11:00 | Shikalbaha | 121 | 05:00 | 116 | 00:00
Hathazari | 135 | 06:00 | 131 | 00:00 | Shikalbaha-230 | 133 | 07:00 | 127 | 15:00
Ishurdi | 139 | 08:00 | 132 | 00:00 | Shitalakhya | 128 | 17:00 | 121 | 11:00
Jaldhaka | 130 | 06:00 | 115 | 19:30 | Sholosohor | 131 | 05:00 | 126 | 11:00
Jamalpur | 142 | 09:00 | 127 | 01:00 | Shyampur | 128 | 18:30 | 121 | 12:00
Jashore | 131 | 18:00 | 121 | 12:00 | Shyampur-230 | 129 | 18:00 | 122 | 11:00
Jhenaidah | 135 | 05:00 | 123 | 14:00 | Siddhirganj | 128 | 17:00 | 122 | 11:00
Jhenaidah-230 | 136 | 18:30 | 128 | 13:00 | Sirajganj | 133 | 18:30 | 128 | 00:00
Joydebpur | 134 | 13:00 | 121 | 11:00 | Sonargaon | 127 | 18:00 | 120 | 10:00
Joypurhat | 134 | 06:00 | 126 | 00:00 | Sreemongol | 133 | 13:00 | 125 | 00:00
Juldah | 133 | 05:00 | 128 | 15:00 | Sreepur | 134 | 18:30 | 127 | 00:00
Kabirpur | 135 | 18:30 | 120 | 11:00 | Srinagar | 132 | 18:00 | 124 | 11:00
Kachua | 128 | 16:00 | 118 | 23:00 | SSM | 132 | 00:00 | 130 | 14:00
Kaliakoir | 138 | 18:30 | 130 | 11:00 | Sunamganj | 131 | 09:00 | 123 | 00:00
Kallyanpur | 131 | 19:30 | 124 | 09:00 | Sylhet | 133 | 08:00 | 127 | 00:00
Kalurghat | 130 | 18:00 | 126 | 00:00 | Sylhet-132 | 132 | 07:00 | 129 | 00:00
Kamrangirchar | 131 | 18:00 | 122 | 12:00 | Tangail | 132 | 18:30 | 127 | 23:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 136 | 21:00 | 121 | 19:30
Kasba | 128 | 18:30 | 119 | 00:00 | TK | 130 | 04:00 | 127 | 20:00
Kazla | 130 | 05:00 | 123 | 12:00 | Tongi | 135 | 19:30 | 126 | 11:00
Keranigonj | 131 | 05:00 | 124 | 11:00 | Ullahpara | 135 | 05:00 | 129 | 00:00
Khagrachori | 131 | 22:00 | 125 | 11:00 | Ullon | 138 | 06:00 | 124 | 11:00
Khulna | 131 | 18:00 | 123 | 22:00 | Uttara | 129 | 17:00 | 121 | 11:00
Khulna(S) | 134 | 18:00 | 126 | 22:00 | UttaraNew | 130 | 18:30 | 122 | 10:00
Khulshi | 131 | 06:00 | 125 | 15:00 | Zigatola | 131 | 06:00 | 130 | 19:00
Kishoreganj | 132 | 18:30 | 124 | 00:00
Kodda | 135 | 19:30 | 120 | 14:00
KSRM | 132 | 05:00 | 127 | 14:00
Kulaura | 135 | 13:00 | 131 | 00:00
Kurigram | 132 | 01:00 | 119 | 19:30
Kushtia | 135 | 09:00 | 127 | 14:00
Lalbag | 132 | 06:00 | 122 | 11:00
Lalmonirhat | 132 | 06:00 | 120 | 18:00
Madanganj | 128 | 18:00 | 120 | 12:00
Madaripur | 136 | 18:30 | 129 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division