## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 21-05-2025 | [28 empty] | Date: | 21-05-2025 | [28 empty] | Date: | 21-05-2025 | [28 empty] | Date: | 21-05-2025 | [28 empty] | Date: | 21-05-2025 | [16 empty] | Date: | 21-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [16 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 180.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1200.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 40.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 17 | 113 | 112 | 0 | 0 | 35 | 0 | 0 | 0 | 400 | 282 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 70 | 15.5 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 8 | 17 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 23 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1054 | 0 | 51 | 0 | 8 | 0 | 320 | 300 | 54 | 187 | 34 | 68 | 70 | 61 | 17 | 14 | 70 | 34 | 8 | 0 | 0 | 310 | 320 | 289 | 36 | 40 | 0 | 136 | 6 | 0 | 83 | 30 | 0 | 18 | 171 | 0 | 55 | 123 | 0 | 0 | 0 | 8 | 6815.5 | 927 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 819 | 0 | 1301.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 158 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 166 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 9 | 110 | 180 | 0 | 401 | 998 | 0 | 6030.91 | 12846.41 | 76.81
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 17 | 100 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 277 | 0 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 52 | 15.5 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 5 | 0 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 22 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 51 | 0 | 8 | 0 | 320 | 305 | 54 | 183 | 34 | 68 | 70 | 68 | 15 | 14 | 70 | 28 | 8 | 0 | 0 | 300 | 320 | 289 | 36 | 39 | 0 | 129 | 6 | 0 | 83 | 30 | 0 | 18 | 172 | 0 | 18 | 124 | 0 | 0 | 0 | 12 | 6500.5 | 927 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 803 | 0 | 1205.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 160 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 10 | 110 | 180 | 0 | 420 | 996 | 0 | 5897.09 | 12397.59 | 76.81
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 83 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 287 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 34 | 15.5 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 5 | 0 | 0 | 0 | 48 | 0 | 0 | 40 | 0 | 22 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1003 | 0 | 51 | 0 | 8 | 0 | 320 | 305 | 55 | 194 | 34 | 68 | 80 | 68 | 9 | 14 | 70 | 30 | 0 | 0 | 0 | 305 | 320 | 310 | 36 | 39 | 0 | 133 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 18 | 124 | 0 | 0 | 0 | 12 | 6472.5 | 926 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 1011.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 160 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 10 | 120 | 180 | 0 | 420 | 940 | 0 | 5529.05 | 12001.55 | 76.81
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 17 | 68 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 287 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 15.5 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 40 | 0 | 23 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 51 | 0 | 8 | 0 | 320 | 305 | 55 | 190 | 34 | 68 | 80 | 68 | 9 | 14 | 70 | 30 | 0 | 0 | 0 | 310 | 320 | 306 | 36 | 39 | 0 | 130 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 18 | 122 | 0 | 0 | 0 | 12 | 6334.5 | 926 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 962.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 160 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 10 | 110 | 180 | 0 | 424 | 880 | 0 | 5417.45 | 11751.95 | 76.8
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 68 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 304 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 17 | 15.5 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 11 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 24 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 51 | 0 | 8 | 0 | 320 | 305 | 55 | 206 | 34 | 50 | 80 | 34 | 9 | 14 | 70 | 30 | 0 | 0 | 0 | 310 | 320 | 322 | 36 | 39 | 0 | 134 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 18 | 123 | 0 | 0 | 0 | 12 | 6318.5 | 926 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 916.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 160 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 10 | 120 | 180 | 0 | 425 | 821 | 0 | 5330.12 | 11648.62 | 76.8
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 68 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 283 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 17 | 15.5 | 15 | 0 | 400 | 0 | 0 | 0 | 150 | 26 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 23 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 855 | 0 | 51 | 0 | 8 | 0 | 320 | 305 | 55 | 190 | 34 | 50 | 80 | 34 | 9 | 14 | 70 | 28 | 0 | 0 | 0 | 315 | 320 | 301 | 36 | 39 | 0 | 136 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 27 | 114 | 0 | 0 | 0 | 12 | 6203.5 | 927 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 775 | 0 | 910.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 160 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 9 | 120 | 180 | 0 | 424 | 797 | 0 | 5312.94 | 11516.44 | 76.8
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 17 | 68 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 294 | 0 | 0 | 0 | 0 | 292 | 0 | 0 | 1 | 17 | 15.5 | 15 | 0 | 300 | 0 | 0 | 0 | 150 | 16 | 0 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 26 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 691 | 0 | 51 | 2 | 8 | 0 | 359 | 335 | 55 | 204 | 34 | 45 | 90 | 46 | 9 | 14 | 70 | 26 | 8 | 5 | 0 | 310 | 320 | 333 | 36 | 39 | 0 | 135 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 27 | 114 | 0 | 0 | 1.24 | 12 | 6054.74 | 926 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 766 | 0 | 911.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.99 | 140 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 168 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0.04 | 0 | 170 | 8 | 120 | 180 | 0 | 422 | 698 | 0 | 5145.84 | 11200.58 | 76.79
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 17 | 81 | 64 | 0 | 18 | 0 | 0 | 0 | 18 | 300 | 294 | 84 | 0 | 0 | 0 | 294 | 0 | 0 | 6 | 17 | 0 | 15 | 0 | 300 | 0 | 0 | 0 | 150 | 14 | 0 | 0 | 0 | 12 | 0 | 1 | 40 | 0 | 20 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655 | 0 | 51 | 38 | 8 | 0 | 358 | 345 | 55 | 204 | 34 | 50 | 90 | 85 | 9 | 14 | 70 | 28 | 16 | 10 | 0 | 315 | 320 | 333 | 36 | 39 | 0 | 138 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 74 | 114 | 0 | 0 | 3.26 | 12 | 6353.26 | 926 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8 | 764 | 0 | 913.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10.75 | 140 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 0.48 | 0 | 165 | 0 | 0 | 4 | 0 | 0 | 0 | 1.7 | 14 | 0.16 | 0 | 170 | 8 | 120 | 180 | 0 | 424 | 689 | 0 | 5184.58 | 11537.84 | 76.79
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 17 | 95 | 64 | 0 | 45 | 14 | 0 | 0 | 40 | 300 | 300 | 66 | 0 | 0 | 0 | 293 | 0 | 0 | 13 | 17 | 15 | 15 | 0 | 300 | 0 | 0 | 0 | 150 | 16 | 0 | 0 | 0 | 12 | 0 | 2 | 40 | 0 | 5 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655 | 0 | 51 | 76 | 8 | 0 | 355 | 335 | 55 | 203 | 33 | 50 | 80 | 85 | 9 | 14 | 70 | 26 | 16 | 17 | 0 | 320 | 320 | 333 | 36 | 39 | 0 | 139 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 74 | 114 | 0 | 1 | 6.56 | 12 | 6479.56 | 879 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.79 | 756 | 0 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 17.31 | 140 | 0 | 140 | 0 | 0 | 0 | 320 | 0 | 1.17 | 0 | 166 | 0 | 0 | 3 | 0 | 0 | 0 | 2.2 | 72 | 0.35 | 0 | 170 | 8 | 120 | 180 | 0 | 426 | 695 | 0 | 5249.82 | 11729.38 | 76.79
09:00 | 8 | 17 | 33 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 52 | 17 | 95 | 64 | 0 | 55 | 17 | 0 | 0 | 48 | 300 | 314 | 64 | 0 | 0 | 0 | 324 | 0 | 0 | 18 | 17 | 15 | 15 | 0 | 300 | 0 | 0 | 0 | 150 | 37 | 0 | 0 | 0 | 12 | 0 | 3 | 37 | 0 | 2 | 424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655 | 1 | 51 | 50 | 8 | 0 | 351 | 335 | 55 | 204 | 32 | 50 | 80 | 85 | 9 | 14 | 70 | 28 | 16 | 48 | 0 | 315 | 320 | 370 | 36 | 40 | 0 | 146 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 74 | 114 | 0 | 1 | 6.65 | 12 | 6681.65 | 879 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.31 | 755 | 0 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 18.7 | 145 | 0 | 170 | 0 | 0 | 0 | 370 | 0 | 1.95 | 0 | 139 | 0 | 0 | 5 | 0 | 0 | 0 | 2.2 | 46 | 0.32 | 0 | 170 | 6 | 120 | 220 | 0 | 480 | 697 | 0 | 5439.48 | 12121.13 | 76.79
10:00 | 8 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 28 | 17 | 110 | 64 | 0 | 0 | 35 | 0 | 0 | 16 | 420 | 311 | 0 | 0 | 0 | 0 | 287 | 0 | 0 | 28 | 17 | 14.5 | 15 | 0 | 330 | 0 | 0 | 0 | 150 | 26 | 0 | 0 | 0 | 12 | 0 | 5 | 38 | 0 | 2 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 4 | 51 | 10 | 16 | 0 | 351 | 335 | 52 | 197 | 34 | 50 | 80 | 68 | 9 | 14 | 70 | 28 | 0 | 12 | 0 | 320 | 320 | 375 | 36 | 40 | 0 | 158 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 74 | 114 | 0 | 1 | 9.58 | 12 | 6816.08 | 927 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.35 | 755 | 0 | 964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 28.05 | 168 | 0 | 174 | 0 | 0 | 0 | 414 | 0 | 3.29 | 0 | 138 | 0 | 0 | 8 | 0 | 0 | 0 | 3.5 | 57 | 0.69 | 0 | 224 | 0 | 120 | 220 | 0 | 615 | 732 | 0 | 5851.88 | 12667.96 | 76.79
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 54 | 17 | 114 | 48 | 0 | 0 | 35 | 50 | 0 | 0 | 420 | 303 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 34 | 17 | 14.5 | 15 | 0 | 330 | 0 | 0 | 0 | 150 | 11 | 0 | 0 | 0 | 15 | 0 | 5 | 40 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 9 | 51 | 10 | 16 | 0 | 342 | 335 | 48 | 197 | 34 | 50 | 75 | 51 | 9 | 14 | 46 | 28 | 0 | 11 | 0 | 300 | 320 | 382 | 36 | 40 | 0 | 158 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 74 | 114 | 0 | 2 | 11.3 | 12 | 6813.8 | 927 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 37.38 | 755 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 44.38 | 172 | 0 | 176 | 0 | 0 | 0 | 414 | 0 | 5.25 | 0 | 140 | 0 | 0 | 6 | 0 | 0 | 0 | 4.9 | 94 | 0.25 | 0 | 307 | 7 | 120 | 220 | 0 | 615 | 746 | 0 | 6180.16 | 12993.96 | 76.79
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 54 | 17 | 113 | 48 | 0 | 0 | 35 | 145 | 0 | 0 | 420 | 307 | 0 | 0 | 5 | 0 | 298 | 0 | 0 | 34 | 17 | 14.5 | 15 | 0 | 420 | 0 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 70 | 25 | 5 | 39 | 0 | 2 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 18 | 51 | 18 | 16 | 0 | 353 | 335 | 48 | 207 | 34 | 52 | 70 | 48 | 9 | 0 | 49 | 32 | 0 | 24 | 0 | 310 | 336 | 388 | 39 | 40 | 0 | 155 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 78 | 114 | 0 | 2 | 17.13 | 12 | 7415.63 | 927 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22.84 | 763 | 0 | 1139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 56.68 | 171 | 0 | 171 | 0 | 0 | 0 | 414 | 0 | 4.44 | 0 | 138 | 0 | 0 | 13 | 0 | 0 | 0 | 6.8 | 74 | 0.09 | 0 | 307 | 7 | 120 | 220 | 0 | 617 | 744 | 0 | 6180.85 | 13596.48 | 76.79
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 54 | 17 | 113 | 64 | 45 | 9 | 35 | 155 | 0 | 15 | 420 | 288 | 20 | 0 | 17 | 0 | 266 | 0 | 0 | 32 | 17 | 14.5 | 15 | 0 | 420 | 0 | 0 | 0 | 150 | 2 | 0 | 2 | 0 | 70 | 36 | 4 | 40 | 0 | 6 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 12 | 51 | 30 | 36 | 0 | 356 | 335 | 50 | 182 | 34 | 71 | 70 | 59 | 9 | 14 | 59 | 34 | 0 | 15 | 0 | 305 | 320 | 350 | 36 | 40 | 0 | 151 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 78 | 114 | 0 | 2 | 32.3 | 12 | 7531.8 | 928 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27.53 | 760 | 0 | 1323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 59.79 | 168 | 0 | 169 | 0 | 0 | 0 | 320 | 0 | 2.69 | 0 | 138 | 0 | 0 | 27 | 0 | 0 | 0 | 5.1 | 52 | 0.32 | 0 | 307 | 7 | 110 | 220 | 0 | 616 | 700 | 0 | 6184.43 | 13716.23 | 76.79
14:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 17 | 113 | 64 | 45 | 15 | 35 | 158 | 0 | 31 | 420 | 294 | 80 | 0 | 25 | 0 | 300 | 0 | 0 | 28 | 17 | 14.5 | 16 | 0 | 350 | 0 | 0 | 0 | 150 | 0 | 17 | 23 | 0 | 70 | 36 | 2 | 40 | 0 | 2 | 571 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1053 | 16 | 51 | 30 | 8 | 0 | 351 | 335 | 52 | 207 | 34 | 72 | 70 | 68 | 9 | 11 | 60 | 30 | 0 | 25 | 30 | 315 | 320 | 339 | 36 | 40 | 0 | 141 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 77 | 112 | 0 | 2 | 25 | 11 | 7626.5 | 927 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 96.59 | 767 | 0 | 1313.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 27.45 | 166 | 0 | 168 | 0 | 0 | 0 | 370 | 0 | 1.44 | 0 | 156 | 0 | 0 | 15 | 0 | 0 | 0 | 2 | 124 | 0.12 | 0 | 307 | 9 | 100 | 220 | 0 | 613 | 700 | 0 | 6294.89 | 13921.39 | 76.79
15:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 0 | 114 | 64 | 15 | 15 | 35 | 162 | 0 | 31 | 420 | 307 | 20 | 0 | 35 | 0 | 268 | 0 | 0 | 21 | 35 | 14.5 | 0 | 0 | 350 | 0 | 0 | 0 | 150 | 4 | 17 | 25 | 0 | 88 | 48 | 3 | 40 | 0 | 2 | 571 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1157 | 11 | 51 | 20 | 0 | 0 | 320 | 335 | 50 | 209 | 34 | 72 | 70 | 84 | 9 | 13 | 72 | 34 | 16 | 38 | 37 | 305 | 320 | 301 | 34 | 40 | 0 | 148 | 0 | 0 | 80 | 30 | 0 | 18 | 174 | 0 | 77 | 91 | 0 | 2 | 22.7 | 11 | 7600.2 | 928 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 73.63 | 765 | 0 | 1317.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 0 | 27.79 | 161 | 0 | 163 | 0 | 0 | 0 | 350 | 0 | 0.49 | 0 | 158 | 0 | 0 | 20 | 0 | 0 | 0 | 4.9 | 77 | 0.04 | 0 | 287 | 9 | 110 | 220 | 0 | 641 | 742 | 0 | 6268.63 | 13868.83 | 76.79
16:00 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 45 | 0 | 113 | 64 | 15 | 15 | 35 | 90 | 0 | 31 | 380 | 273 | 20 | 0 | 17 | 0 | 265 | 0 | 0 | 14 | 35 | 14.5 | 0 | 0 | 350 | 0 | 0 | 0 | 150 | 6 | 17 | 38 | 0 | 88 | 48 | 1 | 40 | 0 | 2 | 500 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 1000 | 4 | 51 | 10 | 0 | 0 | 320 | 300 | 10 | 182 | 30 | 73 | 70 | 107 | 9 | 14 | 92 | 30 | 16 | 32 | 39 | 295 | 320 | 300 | 35 | 40 | 0 | 128 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 77 | 81 | 0 | 0 | 7.76 | 11 | 7037.26 | 927 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 57.23 | 758 | 0 | 1218.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 25.88 | 159 | 0 | 159 | 0 | 0 | 0 | 350 | 0 | 1.63 | 0 | 159 | 0 | 0 | 4 | 0 | 0 | 0 | 3.6 | 47 | 0.17 | 0 | 200 | 9 | 110 | 220 | 0 | 687 | 670 | 0 | 5958.72 | 12995.98 | 76.79
17:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 35 | 0 | 112 | 64 | 15 | 15 | 35 | 35 | 0 | 31 | 380 | 291 | 30 | 0 | 0 | 0 | 275 | 0 | 0 | 3 | 35 | 14.5 | 0 | 0 | 350 | 0 | 0 | 0 | 150 | 15 | 34 | 38 | 0 | 88 | 48 | 0 | 40 | 0 | 2 | 500 | 0 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 51 | 10 | 0 | 0 | 320 | 300 | 10 | 191 | 35 | 72 | 70 | 124 | 12 | 9 | 100 | 30 | 16 | 9 | 40 | 300 | 320 | 300 | 35 | 40 | 0 | 130 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 77 | 91 | 0 | 0 | 3.67 | 12 | 7019.17 | 927 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 11.26 | 765 | 0 | 1118.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 10.98 | 159 | 0 | 157 | 0 | 0 | 0 | 350 | 0 | 0.88 | 0 | 162 | 0 | 0 | 1 | 0 | 0 | 0 | 0.6 | 29 | 0.08 | 0 | 200 | 9 | 110 | 220 | 0 | 612 | 652 | 0 | 5665.02 | 12684.19 | 76.8
18:00 | 16 | 54 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 35 | 0 | 112 | 64 | 15 | 15 | 35 | 35 | 0 | 31 | 380 | 288 | 10 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 52 | 4.5 | 10 | 0 | 300 | 0 | 0 | 0 | 150 | 17 | 34 | 38 | 0 | 88 | 48 | 0 | 40 | 0 | 4 | 500 | 0 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 975 | 0 | 51 | 10 | 0 | 0 | 320 | 300 | 10 | 185 | 35 | 72 | 70 | 120 | 27 | 12 | 95 | 32 | 16 | 3 | 40 | 295 | 320 | 300 | 35 | 40 | 0 | 128 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 77 | 118 | 0 | 0 | 1.35 | 12 | 7017.85 | 928 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8.31 | 760 | 0 | 1120.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98 | 159 | 0 | 157 | 0 | 0 | 0 | 350 | 0 | 0.15 | 0 | 162 | 0 | 30 | 0 | 24 | 0 | 0 | 0 | 8 | 0.07 | 0 | 200 | 8 | 110 | 220 | 0 | 602 | 650 | 0 | 5644.86 | 12662.71 | 76.81
19:00 | 16 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 42 | 12 | 113 | 138 | 15 | 15 | 35 | 72 | 0 | 32 | 350 | 316 | 60 | 0 | 17 | 0 | 266 | 0 | 0 | 0 | 65 | 14.5 | 16 | 0 | 400 | 0 | 0 | 10 | 150 | 17 | 34 | 38 | 0 | 90 | 48 | 0 | 40 | 0 | 6 | 575 | 0 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 1175 | 0 | 51 | 10 | 0 | 0 | 327 | 335 | 10 | 186 | 33 | 72 | 70 | 136 | 36 | 15 | 106 | 38 | 16 | 0 | 39 | 300 | 320 | 323 | 35 | 40 | 0 | 135 | 6 | 0 | 83 | 30 | 0 | 18 | 175 | 0 | 96 | 141 | 0 | 0 | 0 | 12 | 7787.5 | 878 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 825 | 17 | 1275.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 159 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 159 | 0 | 70 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 11 | 110 | 220 | 0 | 599 | 732 | 0 | 6111.53 | 13899.03 | 76.82
19:30 | 0 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 17 | 113 | 149 | 0 | 0 | 35 | 35 | 0 | 16 | 350 | 321 | 50 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 90 | 14.5 | 16 | 0 | 400 | 0 | 0 | 0 | 150 | 31 | 34 | 39 | 0 | 90 | 48 | 0 | 40 | 0 | 6 | 500 | 0 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 191 | 33 | 72 | 70 | 158 | 37 | 15 | 114 | 34 | 8 | 0 | 39 | 310 | 320 | 361 | 35 | 40 | 0 | 141 | 6 | 0 | 83 | 30 | 0 | 18 | 175 | 0 | 107 | 141 | 0 | 0 | 0 | 12 | 7818.5 | 879 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 873 | 17 | 1260.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 163 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 154 | 0 | 45 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 590 | 950 | 0 | 6443.58 | 14262.08 | 76.82
20:00 | 0 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 54 | 17 | 113 | 149 | 0 | 0 | 35 | 35 | 0 | 16 | 350 | 290 | 45 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 108 | 14.5 | 16 | 0 | 400 | 0 | 0 | 0 | 150 | 41 | 34 | 39 | 0 | 90 | 36 | 0 | 40 | 0 | 14 | 500 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 0 | 0 | 353 | 335 | 10 | 182 | 35 | 72 | 80 | 154 | 38 | 15 | 114 | 38 | 8 | 0 | 39 | 295 | 320 | 363 | 36 | 40 | 0 | 134 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 115 | 141 | 0 | 0 | 0 | 12 | 7777.5 | 879 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 806 | 17 | 1268.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 164 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 158 | 10 | 70 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 540 | 990 | 0 | 6416.98 | 14194.48 | 76.83
21:00 | 0 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 33 | 17 | 113 | 112 | 0 | 0 | 24 | 17 | 0 | 0 | 350 | 251 | 46 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 125 | 14.5 | 16 | 0 | 450 | 0 | 0 | 0 | 150 | 25 | 34 | 39 | 0 | 90 | 12 | 0 | 37 | 0 | 18 | 550 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1185 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 182 | 35 | 80 | 80 | 150 | 38 | 14 | 114 | 38 | 0 | 0 | 39 | 280 | 320 | 363 | 36 | 40 | 0 | 138 | 6 | 0 | 83 | 28 | 0 | 18 | 175 | 0 | 115 | 141 | 0 | 0 | 0 | 12 | 7656.5 | 927 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 17 | 1315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 166 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 162 | 30 | 72 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 90 | 207 | 0 | 518 | 1070 | 0 | 6403 | 14059.5 | 76.84
22:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 114 | 97 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 275 | 46 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 108 | 14 | 16 | 0 | 450 | 0 | 0 | 0 | 150 | 15 | 17 | 39 | 0 | 70 | 12 | 0 | 37 | 0 | 25 | 551 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1103 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 183 | 35 | 90 | 80 | 136 | 39 | 15 | 114 | 40 | 0 | 0 | 39 | 295 | 320 | 349 | 36 | 40 | 0 | 149 | 6 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 116 | 141 | 0 | 0 | 0 | 12 | 7490 | 927 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 1215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 168 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 166 | 47 | 72 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 90 | 220 | 0 | 520 | 1000 | 0 | 6099 | 13589 | 76.85
23:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 17 | 115 | 97 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 276 | 45 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 108 | 0 | 16 | 0 | 450 | 0 | 0 | 0 | 150 | 10 | 17 | 39 | 0 | 70 | 12 | 0 | 37 | 0 | 27 | 450 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 201 | 35 | 90 | 75 | 131 | 38 | 15 | 114 | 40 | 0 | 0 | 32 | 300 | 320 | 382 | 36 | 40 | 0 | 132 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 85 | 141 | 0 | 0 | 0 | 12 | 7267 | 927 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 763 | 0 | 1112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 169 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 165 | 50 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 100 | 220 | 0 | 523 | 900 | 0 | 5875 | 13142 | 76.86
Total KWH | 31248 | 737280 | 402720 | 0 | 0 | 0 | 0 | 0 | 8496000 | 0 | 0 | 681840 | 366840 | 2449152 | 1845120 | 183415 | 262410 | 543188 | 964800 | 0 | 340800 | 8721500 | 7096378 | 589596 | 0 | 137982 | 0 | 6874494 | 0 | 0 | 218353 | 1041600 | 301800 | 319320 | 0 | 9215454.55 | 0 | 0 | 11520 | 3600000 | 353760 | 274845 | 321703 | 0 | 1317120 | 433920 | 27102 | 931680 | 0 | 304320 | 11294545.46 | 0 | 0 | 28800 | 86252.4 | 0 | 0 | 0 | 0 | 0 | 22925452 | 73710 | 1223168 | 478400 | 184000 | 0 | 8502400 | 7872000 | 887520 | 4774000 | 819936 | 1599360 | 1793570 | 2235840 | 399000 | 299830 | 1997280 | 766080 | 160906 | 280809 | 394992 | 7451000 | 7731200 | 8434000 | 848000 | 887760 | 0 | 3345873 | 53880 | 0 | 1963200 | 719424 | 0 | 433000 | 3592070 | 0 | 1617600 | 2832000 | 0 | 9200 | 171840 | 288480 | 168853638.41 | 22221090 | 3505248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306576 | 592560 | 18472727 | 53280 | 26606546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 636620 | 0 | 279744 | 4073991 | 0 | 4070445 | 0 | 0 | 0 | 8833672 | 0 | 24060 | 0 | 3845000 | 150545 | 374989 | 111542 | 485020 | 0 | 0 | 37788.84 | 699840 | 3622 | 0 | 5324000 | 211969 | 2689000 | 4800230 | 0 | 12646008 | 20190545.45 | 0 | 141246658.29 | 310100296.7

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 22-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-05-2025 | during | 22-05-2025 | during | 22-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 366 | 334 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 350 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 307 | 321 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 298 | 277 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 149 | 149.36 | 149.36 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 5 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14.5 | 14.5 | 30 | 30 | 17 | 17 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 16 | 22 | 22 | 16 | 16 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 17 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 113 | 113 | 135 | 135 | 135 | 135 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 54 | 105 | 105 | 50 | 50 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 145 | 35 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 34 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 420 | 400 | 584 | 584 | 480 | 480 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 0 | 50 | 583 | 583 | 84 | 84 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 90 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 5945.724 | 2385.5 | 2342.5 | 5260.9 | 5257.9 | 3367.77 | 3364.77
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 18 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 39 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 39 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 68 | 68 | 68 | 68 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 70 | 90 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 6 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 5 | 0 | 2.38 | 0 | 2.38 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 48 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1000 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 12 | 31 | 7 | 3 | 7 | 3 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1200 | 570 | 500 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4945.72 | 1891 | 2176 | 3366.1 | 3380.72 | 3366.1 | 3380.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 207 | 191 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 353 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 335 | 335 | 335 | 335 | 335 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 34 | 33 | 46.7 | 46.7 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 0 | 195 | 195 | 36 | 36 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 18 | 0 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 48 | 158 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 34 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 15 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 49 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 37 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 72 | 115 | 115 | 92 | 92 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 24 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1346 | 1521 | 2459 | 2389 | 2098.55 | 2028.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 21-05-2025 | during | 22-05-2025 | during | 22-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 114 | 141 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 78 | 107 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 17.13 | 0 | 33 | 0 | 33 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 223.13 | 260 | 584.1 | 549 | 376.6 | 341.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 35 | 35 | 35 | 39 | 39 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 141 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 174 | 175 | 172 | 172 | 174 | 174 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 6 | 25 | 25 | 8 | 8 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 388 | 361 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 336 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1570 | 1519 | 1614 | 1614 | 1539 | 1539
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 927 | 879 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 142 | 134 | 410 | 410 | 169 | 169 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 105 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 22.84 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 763 | 873 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1869.84 | 2008 | 3602.2 | 3512.2 | 3346.2 | 3256.2
| Patuakhali 1320 MW (RNPL) | Coal | RPCL | 660*2 | 0 | 0 | 617 | 590 | 450 | 800 | 800 | 800 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 40 | 7 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 110 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 744 | 950 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.09 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 2266 | 2266 | 2015.09 | 2188 | 2622.12 | 2971.12 | 2932.12 | 2931.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 26 | 26 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 171 | 162 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 163 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 350 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 11 | 11 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.44 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1139 | 1260.58 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 56.68 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 108 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 2064.12 | 1935.58 | 3199.02 | 3037.87 | 3140.64 | 2979.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 0 | 0 | 50 | 50 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 138 | 154 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 6.8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 45 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 74 | 0 | 85.97 | 0 | 85.97 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 231.8 | 312 | 579.57 | 462 | 529.57 | 412
System Total |  |  |  |  | 27566.2 | 27130.055 | 13596.48 | 14262.08 | 23287.01 | 23173.81 | 20696.55 | 20233.35
Forecast Scenario (22-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14455 |  | 0 |  | 14455
|  |  |  | 1:00 | 14021 |  | 0 |  | 14021
|  |  |  | 2:00 | 13569 |  | 0 |  | 13569
|  |  |  | 3:00 | 12640 |  | 0 |  | 12640
|  |  |  | 4:00 | 12305 |  | 0 |  | 12305
|  |  |  | 5:00 | 11937 |  | 0 |  | 11937
|  |  |  | 6:00 | 11567 |  | 0 |  | 11567
|  |  |  | 7:00 | 11493 |  | 0 |  | 11493
|  |  |  | 8:00 | 11483 |  | 0 |  | 11483
|  |  |  | 9:00 | 11902 |  | 0 |  | 11902
|  |  |  | 10:00 | 12223 |  | 0 |  | 12223
|  |  |  | 11:00 | 12460 |  | 0 |  | 12460
|  |  |  | 12:00 | 12699 |  | 0 |  | 12699
|  |  |  | 13:00 | 12893 |  | 0 |  | 12893
|  |  |  | 14:00 | 13202 |  | 0 |  | 13202
|  |  |  | 15:00 | 13364 |  | 0 |  | 13364
|  |  |  | 16:00 | 12983 |  | 0 |  | 12983
|  |  |  | 17:00 | 12524 |  | 0 |  | 12524
|  |  |  | 18:00 | 12122 |  | 0 |  | 12122
|  |  |  | 18:30 | 13000 |  | 0 |  | 13000
|  |  |  | 19:00 | 13529 |  | 0 |  | 13529
|  |  |  | 19:30 | 13881 |  | 0 |  | 13881
|  |  |  | 20:00 | 13671 |  | 0 |  | 13671
|  |  |  | 21:00 | 13971 |  | 0 |  | 13971
|  |  |  | 22:00 | 13571 |  | 0 |  | 13571
|  |  |  | 23:00 | 13692 |  | 0 |  | 13692
Probable Maximum Temperature: |  |  | 32.70°C
Probable Maximum Demand at Day Peak: |  |  | 12699.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 13971.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13971.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 308.276 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:24 hrs on 22-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 21-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13596.48 | MW | 12:00 Hr. | Energy Generated |  |  | 310.1003 |  | MKWHr.
| Day Peak Demand |  |  | 13648.48 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.832 |  | MKWHr.
| Evening Peak Generation |  |  | 14262.08 | MW | 19:30 Hr. | Energy Demand |  |  | 310.9323 |  | MKWHr.
| Evening Peak Demand |  |  | 14311.08 | MW | 19:30 Hr. | Maximum Temperature |  |  | 35 |  | °C
| Minimum Generation of the Day |  |  | 11200.58 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1020.13 |  | MMCFD
| Maximum Generation of the Day |  |  | 14262.08 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 5.9511 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.6145 | 0 | 9.9884 | 0 | 0 | 0.21835 | 0 | 0 | 51.8213 | Gas | 135.5192 | Gas | 493916271.3535
| Chattogram Zone |  |  | 3.9043 | 34.22 | 2.4742 | 0 | 0.93168 | 0.10081 | 0 | 0.35376 | 41.9847 | Coal | 94.8488 | Coal | 567116269.1915
| Cumilla Zone |  |  | 26.3564 | 0 | 7.2658 | 0 | 0 | 0.28081 | 0.76608 | 0 | 34.6691 | HFO | 25.6863 | HFO | 477838250.708
| Mymensingh Zone |  |  | 0 | 0 | 4.7381 | 0 | 0 | 0.18104 | 0 | 0 | 4.9191 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.4594 | Hydro | 0.93168 | Hydro | 93168
| Khulna Zone |  |  | 3.5052 | 18.4727 | 0.35986 | 0 | 0 | 0.59256 | 22.2211 | 0 | 45.1515 | Solar | 3.1668 | Solar | 50888847.8624
| Barishal Zone |  |  | 7.7012 | 38.1606 | 0 | 0 | 0 | 0.003622 | 0 | 0 | 45.8654 | Import | 49.5937 | Import | 250390810.48
| Rajshahi Zone |  |  | 16.9781 | 0 | 0 | 0 | 0 | 0.94042 | 26.6065 | 0 | 44.5251 | Wind | 0.35376 | Wind | 5179046.4
| Rangpur Zone |  |  | 0 | 3.9955 | 0.86001 | 0 | 0 | 0.84917 | 0 | 0 | 5.7047
| Total |  |  | 135.5192 | 94.8488 | 25.6863 | 0 | 0.93168 | 3.1668 | 49.5937 | 0.35376 | 310.1003
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 493916271.3535 |  | Hydro | 93168
|  |  |  | Coal | 567116269.1915 |  | Solar | 50888847.8624
|  |  |  | HFO | 477838250.708 |  | Import | 250390810.48
|  |  |  | HSD | 0 |  | Wind | 5179046.4
[5 empty] | Total: | 184,54,22,663 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2211 | Peak Hr Flow | 879.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 43957527.37 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 26.6065 | Peak Hr Flow | 1260.58 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 600 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.76608 | Peak Hr Flow | 34.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1124 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.5937 | Peak Hr Flow | 2173.58 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5119
|  |  |  | Chattogram |  | 0 |  | 1476
|  |  |  | Cumilla |  | 30 |  | 1344
|  |  |  | Mymensingh |  | 17 |  | 1068
|  |  |  | Sylhet |  | 0 |  | 500
|  |  |  | Khulna |  | 0 |  | 1580
|  |  |  | Barishal |  | 0 |  | 478
|  |  |  | Rajshahi |  | 0 |  | 1252
|  |  |  | Rangpur |  | 0 |  | 927
|  |  |  | Total |  | 47 |  | 13744
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:50 | Haripur-Meghnaghat 230kV Ckt-1 is restored.
| 08:55 | 12:44 | BIPTC S/S 10CF25 Scheduled S/D Due to Capacitor bank T1-60C current unbalance
| 09:15 | 09:52 | Bhandaria 132/33kV S/S Transformer-1 LT Forced S/D Due to 33 kV incomming Meter change by
BPDB.
|  | 09:29 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
| 09:35 | 09:50 | Bhandaria 132/33kV S/S Transformer-1 HT Forced S/D Due to 33 kV incomming Meter change by
BPDB.
| 09:36 | 17:27 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to GIS Installation of Sreepur
Bay.
| 09:37 | 17:25 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to GIS Installation of Sreepur
Bay.
| 09:41 | 18:27 | Dhamrai-Kaliakoir 132 kV Ckt-2 Project Work S/D from Kaliakoir 400/230/132kV end. and
from Dhamrai 132/33kV end Due to Dhamrai Nobinagor new line project work by EEGBPS
project.
| 09:42 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- GT
|  | 09:54 | Srinagar 132/33kV S/S Tr-02 HT is restored.
| 09:55 |  | Jashore 132/33kV S/S Cap. Bank-1 Scheduled S/D Due to R-Phase PT change
| 10:53 | 12:35 | Sreepur 230/132/33kV S/S 132 kV BUS-1 Forced S/D Due to Bird Nest Removal.
| 11:07 | 16:19 | Jashore 132/33kV S/S 132 kV Bus-A Scheduled S/D Due to 132 KV R-phase PT change work
| 12:40 | 12:55 | Faridpur 132/33kV S/S Transformer-1 LT Tripped showing 33kV Earth Fault relays. | [7 empty] | 60.0MW load
interrup.
| 12:40 | 12:55 | Faridpur 132/33kV S/S Transformer-2 LT Tripped showing 33kV Earth fault, relays Due to | [7 empty] | 60.0MW load
|  |  | 33kV PBS feeder fault. | [7 empty] | interrup.
| 12:50 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 13:14 | 13:14 | Purbasadipur-Saidpur 132kV Ckt-1 Forced S/D from Purbasadipur 132/33kV end Due to To
Check Saidpur-01 Protection Circuit
| 14:12 |  | Meghnaghat CCPP(Summit)-2 Tripped with remarks:- ST
| 14:13 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT
| 14:13 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- GT (FALSE)
|  | 14:50 | Ishwardi-Natore 132kV Ckt-2 is restored.
| 15:23 | 16:21 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Project Work S/D
| 15:35 | 17:22 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) LT Forced S/D Due to 33kV feeder Uthrail | [7 empty] | 40.0MW load
|  |  | and chirirbandor red hot maintenance | [7 empty] | interrup.
| 15:36 | 17:21 | Purbasadipur 132/33kV S/S T-3 Transformer (423T) HT Forced S/D Due to 33kV feeder Uthrail | [7 empty] | 40.0MW load
|  |  | and chirirbandor red hot maintenance | [7 empty] | interrup.
| 15:42 | 18:17 | Bogura-Mahasthangar (New)) 132 kV Ckt-2 Scheduled S/D from Mahasthangarh 132/33kV end Due
to CB Replace Work. and from Bogura 132/33kV end Due to 132kv Circuit Breaker Change.
| 15:49 | 17:19 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 15:49 | 17:19 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Scheduled S/D | [7 empty] | 20.0MW load
interrup.
| 15:50 |  | Bogura 132/33kV S/S 132KV Bus-B Scheduled S/D Due to 132kv Circuit Breaker Change.
|  | 17:05 | Ashuganj-Ghorasal 132kV Ckt-2 is restored.
| 19:30 |  | Evening Peak Generation: 14261 MW.
| 22:32 | 23:25 | Mithapukur 132/33kV S/S TR-2 (414T) LT Forced S/D Due to Red hot maintenance.
| 22:33 | 23:17 | Bogura(New)-Naogaon 132 kV Ckt-2 Tripped from Bogura 230/132kV end showing CB Open, | [7 empty] | 124.0MW load
|  |  | Phase-C, Zone-4, Location 60.25km, relays Due to Rain & Storming | [7 empty] | interrup. Bogura
230/132kV end
| 22:33 | 00:25 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Bogura 230/132kV end showing CB Open, PSB, | [7 empty] | 124.0MW load
|  |  | AR, Carrier send, Zone-1, 19.58km, Phase-C, CGT. relays Due to Rain & Storming | [7 empty] | interrup. Bogura
230/132kV end
| 22:34 | 23:25 | Mithapukur 132/33kV S/S TR-2 (414T) HT Forced S/D Due to Red hot maintenance.
| 01:37 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 04:57 |  | Meghnaghat CCPP (Summit)-2 ST tripped
| 05:14 |  | Haripur-Meghnaghat 230kV Ckt-2 Scheduled S/D from Haripur 230/132kV end Due to Line DS
Hotspot Maintenance.
| 06:00 |  | Min. Gen. 11205 MW
| 06:07 |  | Madanganj 132/33kV S/S BUS Coupler Forced S/D
| 06:11 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D Due to Due Load
management of NLDC
| 06:43 |  | Maniknagar 132/33kV S/S Transformer GT-2 HT Scheduled S/D Due to PT(Y-ph) slow oil
leakage maintenance work by DPDC. Shutdown taken by Mr. Rokonul Islam, SDE, DPDC.
| 07:28 |  | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to 33kv jamuna feeder bus loop reconnect | [7 empty] | 12.0MW load
|  |  | work. | [7 empty] | interrup.
| 07:28 |  | Jamalpur 132/33kV S/S T-2 LT Scheduled S/D Due to 33kv Jamuna feeder bus Loop re -connect | [7 empty] | 12.0MW load
|  |  | work | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 21-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 334 | 8496000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 8721500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 321 | 7096378 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 262410 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 277 | 6874494 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 31248 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 681840 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 149 | 1845120 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 543188 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 137982 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14.5 | 301800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 16 | 319320 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 402720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 183415 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 113 | 2449152 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 54 | 737280 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 340800 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 964800 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 218353 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 366840 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 400 | 9215454.55 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 50 | 589596 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 90 | 1041600 | -
Dhaka Area Total |  |  |  |  | 5945.724 | 2342.5 | 51821290.55
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3600000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 86252.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 73710 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 28800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 931680 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 321703 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 274845 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 90 | 1317120 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 6 | 304320 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 11520 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 27102 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 48 | 433920 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 22925452 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 31 | 353760 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1200 | 500 | 11294545.46 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4945.72 | 2176 | 41984729.86
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 191 | 4774000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8502400 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 7872000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 819936 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 887520 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 184000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1223168 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 478400 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 394992 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1793570 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 158 | 2235840 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 34 | 766080 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 160906 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 299830 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1997280 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 37 | 399000 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 1599360 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 280809 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1521 | 34669091
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 9200 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 141 | 2832000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 107 | 1617600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 171840 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 288480 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 260 | 4919120
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 35 | 848000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 887760 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 141 | 3345873 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 719424 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1963200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 175 | 3592070 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 433000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 6 | 53880 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7451000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 361 | 8434000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7731200 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1519 | 35459407
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 879 | 22221090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 134 | 3505248 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 53280 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 306576 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 592560 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 873 | 18472727 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2008 | 45151481
| Patuakhali 1320 MW (RNPL) |  | RPCL | 660*2 | 0 | 590 | 12646008 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 40 | 11 | 211969 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2689000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 950 | 20190545.45 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 4800230 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5324000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3622 | -
Barishal Area Total |  |  |  |  | 2266 | 2188 | 45865374.45
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 162 | 4073991 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 163 | 4070445 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 8833672 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 0 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 24060 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1260.58 | 26606546 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 279744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 636620 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1935.58 | 44525078
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 0 | 150545 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 154 | 3845000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 485020 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 37788.84 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 45 | 374989 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 111542 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 699840 | -
Rangpur Area Total |  |  |  |  | 950 | 312 | 5704724.84
Eastern Grid Total |  |  |  |  | 16761.895 | 7818.5 | 168853638.41
Western Grid Total |  |  |  |  | 10368.16 | 6443.58 | 141246658.29
National Grid Total |  |  |  |  | 27130.055 | 14262.08 | 310100296.7
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 21-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9460.79 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4237.7 | MW
i) Dhaka area |  |  | 5119.13 |  | MW | i) Khulna area |  |  |  | 1580.5 | MW
ii) Chattogram area |  |  | 1476.5 |  | MW | ii) Barishal area |  |  |  | 478.4 | MW
iii) Cumilla area |  |  | 1314.16 |  | MW | iii) Rajshahi area |  |  |  | 1251.8 | MW
iv) Mymensingh area |  |  | 1051 |  | MW | iv) Rangpur area |  |  |  | 927 | MW
v) Sylhet area |  |  | 500 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13698.49 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 83 | 21:00 | 133 | Patuakhali | 83 | 22:00
2 | AKSML | 111 | 15:00 | 68 | Jaldhaka | 80 | 20:00 | 134 | Payra | 36 | 00:00
3 | Aftabnagar | 40 | 13:00 | 69 | Jamalpur | 118 | 19:30 | 135 | Postogola | 60 | 15:00
4 | Agargaon | 143 | 13:00 | 70 | Jashore | 160 | 19:00 | 136 | Purbachal | 19 | 12:00
5 | Agrabad | 102 | 15:00 | 71 | Jhenaidah | 115 | 14:00 | 137 | Purbasadipur | 130 | 20:00
6 | Amnura | 35 | 19:30 | 72 | Joydebpur | 159 | 15:00 | 138 | Rahanpur | 23 | 00:00
7 | Ashuganj | 99 | 01:00 | 73 | Joypurhat | 54 | 19:00 | 139 | Rahim | 44 | 16:00
8 | BSRM | 210 | 07:00 | 74 | Juldah | 12.5 | 07:00 | 140 | Rajbari | 68 | 13:00
9 | Bagerhat | 89 | 21:00 | 75 | KSRM | 27 | 03:00 | 141 | Rajendrapur | 129 | 20:00
10 | Bajitpur | 49 | 22:00 | 76 | Kabirpur | 276 | 14:00 | 142 | Rajshahi | 115 | 19:00
11 | Bakulia | 111 | 19:00 | 77 | Kachua | 98 | 21:00 | 143 | Rajshahi-230 | 84 | 19:00
12 | Banani | 43.4 | 13:00 | 78 | Kallyanpur | 105 | 13:00 | 144 | Ramganj | 116 | 19:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kalurghat | 26 | 11:00 | 145 | Rampur | 41 | 00:00
14 | Barapukuria | 61 | 19:00 | 80 | Kamrangirchar | 71.7 | 13:00 | 146 | Rangamati | 18 | 19:30
15 | Barguna | 22 | 20:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 147 | 19:00
16 | Barishal | 119 | 22:00 | 82 | Kasba | 34 | 19:30 | 148 | Ruppur | 8.8 | 15:00
17 | Barishal-230 | 108 | 19:30 | 83 | Kazla | 103 | 14:00 | 149 | SSM | 14 | 01:00
18 | Baroaulia | 66 | 11:00 | 84 | Keranigonj | 105 | 12:00 | 150 | Saidpur | 108 | 19:30
19 | Baroirhat | 60 | 21:00 | 85 | Khagrachori | 26 | 23:00 | 151 | Satkhira | 151 | 21:00
20 | Bashundhara | 194 | 13:00 | 86 | Khulna | 76 | 13:00 | 152 | Satmasjid | 112 | 13:00
21 | BashundharaCement | 17 | 23:00 | 87 | Khulshi | 175 | 19:00 | 153 | Savar | 232 | 15:00
22 | Beanibazar | 58 | 19:00 | 88 | Kishoreganj | 129 | 20:00 | 154 | SevenRings | 17.44 | 05:00
23 | Benapole | 71 | 19:00 | 89 | Kodda | 307 | 08:00 | 155 | ShahCement | 29 | 13:00
24 | Bhaluka | 155 | 16:00 | 90 | Kulaura | 36 | 19:00 | 156 | Shahjadpur | 71 | 17:00
25 | Bhandaria | 55 | 00:00 | 91 | Kurigram | 56 | 20:00 | 157 | Shahjibazar | 121 | 21:00
26 | Bhangura | 33 | 14:00 | 92 | Kushtia | 144 | 16:00 | 158 | Shahmirpur | 54 | 18:00
27 | Bheramara(GK) | 58 | 17:00 | 93 | Lalbag | 70 | 12:00 | 159 | Shariatpur | 87 | 22:00
28 | Bhulta | 245 | 21:00 | 94 | Lalmonirhat | 58 | 20:00 | 160 | Sherpur | 136 | 19:00
29 | Bog-Sherpur | 64 | 19:30 | 95 | MI_Cement | 16.7 | 12:00 | 161 | Shikalbaha | 34 | 19:00
30 | Bogura | 149 | 21:00 | 96 | Madanganj | 48 | 12:00 | 162 | Shitalakhya | 92 | 15:00
31 | Borhanuddin | 88 | 22:00 | 97 | Madaripur | 114 | 23:00 | 163 | Sholosohor | 47 | 01:00
32 | Brahmanbaria | 111 | 22:00 | 98 | Madartek | 82.86 | 14:00 | 164 | Shyampur | 174 | 12:00
33 | Cantonment | 160 | 13:00 | 99 | Madunaghat | 59 | 19:00 | 165 | Siddhirganj | 136 | 08:00
34 | Chandina | 19.98 | 22:00 | 100 | Magura | 59 | 22:00 | 166 | Sirajganj | 108 | 20:00
35 | Chandpur | 68 | 21:00 | 101 | Mahasthangarh | 72 | 20:00 | 167 | Sonargaon | 117 | 11:00
36 | Chandraghona | 37 | 19:30 | 102 | Manikganj | 125 | 21:00 | 168 | Sreemongol | 66 | 22:00
37 | Chapai | 69 | 20:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 102 | 22:00
38 | Charsaidpur | 44 | 10:00 | 104 | Matarbari | 50 | 00:00 | 170 | Srinagar | 44.3 | 14:00
39 | Chauddagram | 75 | 23:00 | 105 | Matuail | 68 | 12:00 | 171 | Sunamganj | 50 | 21:00
40 | Chhatak | 28 | 19:00 | 106 | Millgate | 126 | 15:00 | 172 | Sylhet | 37 | 19:00
41 | Chowmuhani | 229 | 19:00 | 107 | Mirpur | 121.5 | 14:00 | 173 | Sylhet-132 | 109 | 20:00
42 | Chuadanga | 108 | 15:00 | 108 | Mirsorai | 11 | 15:00 | 174 | TK | 35 | 19:30
43 | Coxsbazar | 134 | 00:00 | 109 | Mirzapur | 44 | 13:00 | 175 | Tangail | 149 | 12:00
44 | Cumilla(N) | 139 | 23:00 | 110 | Mithapukur | 50 | 19:00 | 176 | Thakurgaon | 98 | 20:00
45 | Cumilla(S) | 170 | 20:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 113 | 11:00
46 | Daudkandi | 127 | 14:00 | 112 | Mogbazar | 169.5 | 14:00 | 178 | Ullahpara | 37 | 19:30
47 | Dhaka | 74 | 13:00 | 113 | Mongla | 40 | 10:00 | 179 | Ullon | 46 | 21:00
48 | Dhamrai | 134 | 00:00 | 114 | Motijheel | 43 | 13:00 | 180 | Uttara | 87 | 13:00
49 | Dhanmondi | 169 | 13:00 | 115 | Muktagacha | 30 | 19:00 | 181 | UttaraNew | 59 | 13:00
50 | Dohazari | 104 | 19:30 | 116 | Munshiganj | 100 | 22:00 | 182 | Zigatola | 78 | 15:00
51 | Faridpur | 155 | 21:00 | 117 | Muradnagar | 30 | 14:00
52 | Fatullah | 111 | 15:00 | 118 | Mymensingh | 181 | 19:00
53 | Fenchuganj | 32 | 19:00 | 119 | Naogaon | 109 | 11:00
54 | Feni | 122 | 19:00 | 120 | Narail | 62 | 23:00
55 | GPH | 93 | 14:00 | 121 | Narinda | 88 | 13:00
56 | Ghatail | 74 | 20:00 | 122 | Narshingdi | 165 | 21:00
57 | Ghorashal | 15 | 12:00 | 123 | Natore | 124 | 14:00
58 | Ghorashal-230 | 91 | 00:00 | 124 | Nawabganj | 50 | 14:00
59 | Goalpara | 46 | 23:00 | 125 | Netrakona | 117 | 21:00
60 | Gollamari | 94 | 23:00 | 126 | New | 92 | 15:00
61 | Gopalganj | 110 | 19:30 | 127 | Niamatpur | 55 | 00:00
62 | Gulshan | 138 | 13:00 | 128 | Noapara | 46 | 19:30
63 | Halishahar | 80.5 | 15:00 | 129 | PHP | 9 | 17:00
64 | HaripurSBU | 177 | 13:00 | 130 | Pabna | 125 | 13:00
65 | Hasnabad | 64 | 00:00 | 131 | Palashbari | 112 | 20:00
66 | Hathazari | 87 | 19:00 | 132 | Panchagarh | 60 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 21-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12846.41 | 24 |  | 12871.49
1:00 | 12397.59 | 32 |  | 12430.59
2:00 | 12001.55 | 32 |  | 12034.55
3:00 | 11751.95 | 32 |  | 11784.95
4:00 | 11648.62 | 26 |  | 11675.62
5:00 | 11516.44 | 24 |  | 11541.44
6:00 | 11200.58 | 69 |  | 11272.58
7:00 | 11537.84 | 39 |  | 11578.84
8:00 | 11729.38 | 36 |  | 11767.38
9:00 | 12121.13 | 35 |  | 12158.13
10:00 | 12667.96 | 43 |  | 12712.96
11:00 | 12993.96 | 42 |  | 13037.96
12:00 | 13596.48 | 50 |  | 13648.48
13:00 | 13716.23 | 40 |  | 13758.23
14:00 | 13921.39 | 87 |  | 14012.39
15:00 | 13868.83 | 63 |  | 13934.83
16:00 | 12995.98 | 41 |  | 13038.98
17:00 | 12684.19 | 0 |  | 12684.19
18:00 | 12662.71 | 0 |  | 12662.71
19:00 | 13899.03 | 35 |  | 13936.03
19:30 | 14262.08 | 47 |  | 14311.08
20:00 | 14194.48 | 0 |  | 14194.48
21:00 | 14059.5 | 30 |  | 14090.5
22:00 | 13589 | 25 |  | 13615
23:00 | 13142 | 27 |  | 13170
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 21-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 6815.5 | 6030.91 | 12846.41 | DAILY GENERATION CURVE
00:30 | 6658 | 5964 | 12622
01:00 | 6500.5 | 5897.09 | 12397.59 | 21-05-2025
01:30 | 6486.5 | 5713.07 | 12199.57
02:00 | 6472.5 | 5529.05 | 12001.55
02:30 | 6403.5 | 5473.25 | 11876.75
03:00 | 6334.5 | 5417.45 | 11751.95
03:30 | 6326.5 | 5373.785 | 11700.285
04:00 | 6318.5 | 5330.12 | 11648.62
04:30 | 6261 | 5321.53 | 11582.53
05:00 | 6203.5 | 5312.94 | 11516.44
05:30 | 6129.12 | 5229.39 | 11358.51
06:00 | 6054.74 | 5145.84 | 11200.58
06:30 | 6204 | 5165.21 | 11369.21
07:00 | 6353.26 | 5184.58 | 11537.84
07:30 | 6416.41 | 5217.2 | 11633.61
08:00 | 6479.56 | 5249.82 | 11729.38
08:30 | 6580.605 | 5344.65 | 11925.255
09:00 | 6681.65 | 5439.48 | 12121.13
09:30 | 6748.865 | 5645.68 | 12394.545
10:00 | 6816.08 | 5851.88 | 12667.96
10:30 | 6814.94 | 6016.02 | 12830.96
11:00 | 6813.8 | 6180.16 | 12993.96
11:30 | 7114.715 | 6180.505 | 13295.22
12:00 | 7415.63 | 6180.85 | 13596.48
12:30 | 7473.715 | 6182.64 | 13656.355
13:00 | 7531.8 | 6184.43 | 13716.23
13:30 | 7579.15 | 6239.66 | 13818.81
14:00 | 7626.5 | 6294.89 | 13921.39
14:30 | 7613.35 | 6281.76 | 13895.11
15:00 | 7600.2 | 6268.63 | 13868.83
15:30 | 7318.73 | 6113.675 | 13432.405
16:00 | 7037.26 | 5958.72 | 12995.98
16:30 | 7028.215 | 5811.87 | 12840.085
17:00 | 7019.17 | 5665.02 | 12684.19
17:30 | 7018.51 | 5654.94 | 12673.45
18:00 | 7017.85 | 5644.86 | 12662.71
18:30 | 7402.675 | 5878.195 | 13280.87
19:00 | 7787.5 | 6111.53 | 13899.03
19:30 | 7818.5 | 6443.58 | 14262.08
20:00 | 7777.5 | 6416.98 | 14194.48
20:30 | 7717 | 6409.99 | 14126.99 |  | Executive Engineer
21:00 | 7656.5 | 6403 | 14059.5 |  | Network Operation Division
21:30 | 7573.25 | 6251 | 13824.25
22:00 | 7490 | 6099 | 13589
22:30 | 7378.5 | 5987 | 13365.5
23:00 | 7267 | 5875 | 13142

## En-Curve
QF-LDC-12
Date | 21-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3570 | 1986.5 | 927 | 0 | 34 | 1301.91 | 40 | 4012 | 0 | 241 | 726 | 0 | 0 | 8 | 24 | DAILY ENERGY CURVE
00:30 | 3558 | 1950.5 | 927 | 0 | 31 | 1253.5 | 40 | 3985 | 0 | 199.5 | 671 | 0 | 0 | 6.5 | 28 | 21-05-2025
01:00 | 3546 | 1914.5 | 927 | 0 | 28 | 1205.09 | 40 | 3958 | 0 | 158 | 616 | 0 | 0 | 5 | 32
01:30 | 3560.5 | 1924.5 | 926.5 | 0 | 29 | 1108.07 | 40 | 3890.5 | 0 | 149 | 566.5 | 0 | 0 | 5 | 32 | Energy Generated | 310.1003 |  | MKWHr
02:00 | 3575 | 1934.5 | 926 | 0 | 30 | 1011.05 | 40 | 3823 | 0 | 140 | 517 | 0 | 0 | 5 | 32 | Energy not Served | 0.832 |  | MKWHr
02:30 | 3565 | 1933 | 926 | 0 | 30 | 986.75 | 40 | 3774 | 0 | 123 | 496.5 | 0 | 0 | 2.5 | 32 | Total Energy Requirement | 310.9323 |  | MKWHr
03:00 | 3555 | 1931.5 | 926 | 0 | 30 | 962.45 | 40 | 3725 | 0 | 106 | 476 | 0 | 0 | 0 | 32
03:30 | 3594.5 | 1942.5 | 926 | 0 | 30 | 939.285 | 40 | 3672 | 0 | 106 | 444.5 | 0 | 0 | 5.5 | 29
04:00 | 3634 | 1953.5 | 926 | 0 | 30 | 916.12 | 40 | 3619 | 0 | 106 | 413 | 0 | 0 | 11 | 26
04:30 | 3606.5 | 1945.5 | 926.5 | 0 | 29 | 913.53 | 40 | 3584 | 0 | 106 | 413 | 0 | 0 | 18.5 | 25
05:00 | 3579 | 1937.5 | 927 | 0 | 28 | 910.94 | 40 | 3549 | 0 | 106 | 413 | 0 | 0 | 26 | 24
05:30 | 3615.5 | 1866 | 926.5 | 0 | 27 | 911.225 | 40 | 3413 | 10.785 | 106 | 421.5 | 0 | 0 | 21 | 46.5
06:00 | 3652 | 1794.5 | 926 | 0 | 26 | 911.51 | 40 | 3277 | 21.57 | 106 | 430 | 0 | 0 | 16 | 69
06:30 | 3656 | 1829.75 | 926 | 0 | 27 | 912.6 | 40 | 3254.5 | 53.36 | 106 | 549 | 0 | 0 | 15 | 54
07:00 | 3660 | 1865 | 926 | 0 | 28 | 913.69 | 40 | 3232 | 85.15 | 106 | 668 | 0 | 0 | 14 | 39
07:30 | 3649 | 1860.5 | 902.5 | 0 | 27 | 913.845 | 40 | 3243 | 151.265 | 106 | 725.5 | 0 | 0 | 15 | 37.5
08:00 | 3638 | 1856 | 879 | 0 | 26 | 914 | 40 | 3254 | 217.38 | 106 | 783 | 0 | 0 | 16 | 36
08:30 | 3715.5 | 1880.5 | 879 | 0 | 27 | 913 | 38.5 | 3287 | 256.255 | 118.5 | 783.5 | 0 | 0 | 26.5 | 35.5
09:00 | 3793 | 1905 | 879 | 0 | 28 | 912 | 37 | 3320 | 295.13 | 131 | 784 | 0 | 0 | 37 | 35
09:30 | 3811.5 | 1954.25 | 903 | 0 | 28 | 938 | 37.5 | 3545 | 301.795 | 135.5 | 708.5 | 0 | 0 | 31.5 | 39
10:00 | 3830 | 2003.5 | 927 | 0 | 28 | 964 | 38 | 3770 | 308.46 | 140 | 633 | 0 | 0 | 26 | 43
10:30 | 3820.5 | 1991 | 927 | 0 | 28 | 1041.5 | 39 | 3841.5 | 342.46 | 139.5 | 642 | 0 | 0 | 18.5 | 42.5
11:00 | 3811 | 1978.5 | 927 | 0 | 28 | 1119 | 40 | 3913 | 376.46 | 139 | 651 | 0 | 0 | 11 | 42
11:30 | 3833.5 | 2022 | 927 | 0 | 30 | 1129 | 39.5 | 4026 | 381.22 | 148 | 747.5 | 0 | 0 | 11.5 | 46
12:00 | 3856 | 2065.5 | 927 | 0 | 32 | 1139 | 39 | 4139 | 385.98 | 157 | 844 | 0 | 0 | 12 | 50
12:30 | 3731.5 | 2081.5 | 927.5 | 0 | 33 | 1231 | 39.5 | 4141 | 377.355 | 166 | 921 | 0 | 0 | 7 | 45
13:00 | 3607 | 2097.5 | 928 | 0 | 34 | 1323 | 40 | 4143 | 368.73 | 175 | 998 | 0 | 0 | 2 | 40
13:30 | 3653 | 2080.5 | 927.5 | 0 | 32 | 1318.145 | 40 | 4155 | 401.665 | 191.5 | 1018.5 | 0 | 0 | 1 | 63.5
14:00 | 3699 | 2063.5 | 927 | 0 | 30 | 1313.29 | 40 | 4167 | 434.6 | 208 | 1039 | 0 | 0 | 0 | 87
14:30 | 3634.5 | 2026.5 | 927.5 | 0 | 32 | 1315.535 | 40 | 4244 | 403.575 | 221.5 | 1048 | 0 | 0 | 2 | 75
15:00 | 3570 | 1989.5 | 928 | 0 | 34 | 1317.78 | 40 | 4321 | 372.55 | 235 | 1057 | 0 | 0 | 4 | 63
15:30 | 3520.5 | 1922.5 | 927.5 | 0 | 32 | 1267.995 | 40 | 4147.5 | 309.41 | 238.5 | 1021.5 | 0 | 0 | 5 | 52
16:00 | 3471 | 1855.5 | 927 | 0 | 30 | 1218.21 | 40 | 3974 | 246.27 | 242 | 986 | 0 | 0 | 6 | 41
16:30 | 3489 | 1870.5 | 927 | 0 | 30 | 1168.215 | 40 | 3907.5 | 169.87 | 263.5 | 964 | 0 | 0 | 10.5 | 20.5
17:00 | 3507 | 1885.5 | 927 | 0 | 30 | 1118.22 | 40 | 3841 | 93.47 | 285 | 942 | 0 | 0 | 15 | 0
17:30 | 3492.5 | 1847.5 | 927.5 | 0 | 31 | 1119.285 | 40 | 3845 | 57.665 | 303.5 | 993.5 | 0 | 0 | 16 | 0
18:00 | 3478 | 1809.5 | 928 | 0 | 32 | 1120.35 | 40 | 3849 | 21.86 | 322 | 1045 | 0 | 0 | 17 | 0
18:30 | 3515 | 1901.5 | 903 | 0 | 35 | 1197.94 | 40 | 4092 | 10.93 | 396 | 1172.5 | 0 | 0 | 17 | 17.5
19:00 | 3552 | 1993.5 | 878 | 0 | 38 | 1275.53 | 40 | 4335 | 0 | 470 | 1300 | 0 | 0 | 17 | 35
19:30 | 3642 | 2004.5 | 879 | 0 | 34 | 1260.58 | 40 | 4598 | 0 | 527 | 1246 | 0 | 0 | 31 | 47
20:00 | 3635 | 1954.5 | 879 | 0 | 38 | 1268.98 | 40 | 4535 | 0 | 545 | 1258 | 0 | 0 | 41 | 0
20:30 | 3626 | 1950 | 903 | 0 | 38 | 1291.99 | 38.5 | 4573.5 | 0 | 482.5 | 1190.5 | 0 | 0 | 33 | 15
21:00 | 3617 | 1945.5 | 927 | 0 | 38 | 1315 | 37 | 4612 | 0 | 420 | 1123 | 0 | 0 | 25 | 30
21:30 | 3614.5 | 1980.75 | 927 | 0 | 39 | 1265 | 37 | 4481.5 | 0 | 394.5 | 1065 | 0 | 0 | 20 | 27.5
22:00 | 3612 | 2016 | 927 | 0 | 40 | 1215 | 37 | 4351 | 0 | 369 | 1007 | 0 | 0 | 15 | 25
22:30 | 3655 | 2001 | 927 | 0 | 40 | 1163.5 | 37 | 4202 | 0 | 357 | 970.5 | 0 | 0 | 12.5 | 26
23:00 | 3698 | 1986 | 927 | 0 | 40 | 1112 | 37 | 4053 | 0 | 345 | 934 | 0 | 0 | 10 | 27
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 21-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 07:00 | 365 | 12:00 | Payra | 414 | 17:00 | 410 | 00:00
Ashuganj | 404 | 6:00 | 363 | 11:00 | Rahanpur | 411 | 05:00 | 396 | 15:00
Bhulta | 396 | 06:00 | 361 | 11:00 | Rampal | 399 | 18:00 | 389 | 11:00
Bibiana | 393 | 05:00 | 385 | 12:00
BIPTC | 405 | 08:00 | 393 | 15:00
Bogura | 402 | 05:00 | 383 | 15:00
Gopalganj | 394 | 05:00 | 381 | 12:00
Kaliakoir | 375 | 07:00 | 356 | 12:00
Madunaghat | 394 | 07:00 | 383 | 12:00
Meghnaghat | 386 | 05:00 | 371 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 224 | 07:00 | 209 | 12:00 | Keranigonj | 222 | 07:00 | 207 | 12:00
AKSML | 230 | 18:30 | 220 | 12:00 | Khulna(S) | 228 | 18:30 | 216 | 11:00
Aminbazar | 233 | 04:00 | 210 | 11:00 | Madunaghat | 232 | 07:00 | 224 | 11:00
Ashuganj | 232 | 06:00 | 216 | 12:00 | Madunaghat-400 | 232 | 07:00 | 224 | 12:00
Ashuganj-400 | 232 | 06:00 | 216 | 12:00 | Maniknagar | 218 | 04:00 | 207 | 12:00
Baghabari | 235 | 05:00 | 224 | 14:00 | Meghnaghat | 229 | 07:00 | 217 | 12:00
Barapukuria | 226 | 03:00 | 214 | 19:30 | Meghnaghat-400 | 224 | 07:00 | 211 | 12:00
Barapukuria-230 | 226 | 03:00 | 214 | 19:30 | Mirsorai | 228 | 08:00 | 216 | 14:00
Barishal | 236 | 07:00 | 228 | 21:00 | Rajshahi | 235 | 23:00 | 222 | 11:00
Bheramara | 234 | 06:00 | 221 | 11:00 | Rampal | 227 | 08:00 | 219 | 00:00
Bhulta | 229 | 06:00 | 208 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 225 | 18:30 | 218 | 21:00 | Rampura | 228 | 06:00 | 205 | 11:00
BIPTC | 236 | 06:00 | 222 | 11:00 | Shikalbaha | 229 | 07:00 | 221 | 11:00
Bogura | 232 | 05:00 | 222 | 13:00 | Shyampur | 222 | 07:00 | 208 | 12:00
Bogura-400 | 232 | 05:00 | 221 | 19:30 | Siddhirganj | 220 | 06:00 | 211 | 12:00
Borhanuddin | 241 | 18:00 | 235 | 21:00 | Sirajgonj | 239 | 05:00 | 231 | 15:00
BSRM | 226 | 08:00 | 216 | 12:00 | Sreepur | 229 | 06:00 | 217 | 12:00
Cumilla(N) | 222 | 07:00 | 210 | 14:00 | Tongi | 227 | 04:00 | 208 | 11:00
Faridpur | 232 | 18:00 | 224 | 12:00
Fenchuganj | 229 | 09:00 | 223 | 11:00
Ghorashal | 225 | 01:00 | 210 | 12:00
Ghorashal-230 | 228 | 07:00 | 210 | 11:00
Gopalganj | 233 | 06:00 | 226 | 12:00
GPH | 228 | 08:00 | 220 | 13:00
Haripur | 219 | 05:00 | 209 | 12:00
Hasnabad | 222 | 05:00 | 208 | 12:00
Hathazari | 230 | 04:00 | 224 | 09:00
Ishurdi | 238 | 18:30 | 224 | 11:00
Jhenaidah | 228 | 05:00 | 217 | 11:00
Kaliakoir | 231 | 07:00 | 216 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 140 | 05:00 | 124 | 11:00 | Madartek | 140 | 07:00 | 125 | 14:00
Agargaon | 135 | 06:00 | 124 | 12:00 | Madunaghat | 132 | 17:00 | 125 | 12:00
Agrabad | 131 | 06:00 | 125 | 11:00 | Magura | 134 | 06:00 | 124 | 12:00
AKS | 129 | 18:00 | 124 | 14:00 | Mahasthangarh | 136 | 05:00 | 127 | 16:00
Aminbazar | 132 | 05:00 | 122 | 11:00 | Manikganj | 130 | 07:00 | 119 | 15:00
Amnura | 136 | 05:00 | 126 | 14:00 | Maniknagar | 131 | 04:00 | 122 | 12:00
Ashuganj | 137 | 06:00 | 131 | 12:00 | Matarbari | 120 | 09:00 | 108 | 23:00
Bagerhat | 127 | 17:00 | 118 | 00:00 | Matuail | 128 | 05:00 | 120.5 | 12:00
Bajitpur | 133 | 06:00 | 124 | 19:00 | Millgate | 136 | 05:00 | 121 | 12:00
Bakulia | 131 | 05:00 | 126 | 12:00 | Mirpur | 130 | 06:00 | 120 | 12:00
Banani | 140 | 06:00 | 123 | 11:00 | Mirzapur | 134 | 08:00 | 126 | 12:00
Bangabhaban | 132 | 06:00 | 122 | 12:00 | Mithapukur | 132 | 04:00 | 122 | 19:00
Barapukuria | 135 | 05:00 | 123 | 19:30 | MI_Cement | 129 | 07:00 | 121 | 12:00
Barguna | 135 | 13:00 | 131 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 18:00 | 124 | 23:00 | Mogbazar | 139 | 05:00 | 125 | 11:00
Barishal-230 | 131 | 06:00 | 125 | 21:00 | Mongla | 130 | 18:00 | 120 | 00:00
Baroaulia | 132 | 13:00 | 127 | 10:00 | Motijheel | 132 | 06:00 | 122 | 12:00
Baroirhat | 125 | 06:00 | 116 | 14:00 | Muktagacha | 135 | 06:00 | 131 | 11:00
Bashundhara | 140 | 05:00 | 122 | 11:00 | Munshiganj | 129 | 07:00 | 120 | 12:00
BashundharaCement | 128 | 07:00 | 120 | 12:00 | Muradnagar | 125 | 16:00 | 118 | 12:00
Beanibazar | 132 | 09:00 | 128 | 00:00 | Mymensingh | 136 | 08:00 | 115 | 19:30
Benapole | 129 | 18:30 | 119 | 14:00 | Naogaon | 136 | 06:00 | 126 | 14:00
Bhaluka | 132 | 05:00 | 122 | 15:00 | Narail | 134 | 05:00 | 124 | 14:00
Bhandaria | 126 | 17:00 | 115 | 22:00 | Narinda | 131 | 04:00 | 122 | 12:00
Bhangura | 135 | 03:00 | 128 | 11:00 | Narshingdi | 128 | 06:00 | 114 | 12:00
Bheramara | 137 | 06:00 | 129 | 15:00 | Natore | 137 | 23:00 | 127 | 13:00
Bheramara(GK) | 137 | 05:00 | 129 | 15:00 | Nawabganj | 133 | 07:00 | 121 | 12:00
Bhulta | 121 | 16:00 | 114 | 10:00 | Netrakona | 126 | 07:00 | 114 | 19:30
Bog-Sherpur | 136 | 05:00 | 128 | 14:00 | New | 136 | 06:00 | 122 | 11:00
Bogura | 138 | 23:00 | 131 | 14:00 | Niamatpur | 138 | 13:00 | 130 | 14:00
Bogura-230 | 138 | 04:00 | 131 | 13:00 | Noapara | 132 | 04:00 | 123 | 11:00
Brahmanbaria | 130 | 07:00 | 122 | 22:00 | Pabna | 136 | 23:00 | 127 | 15:00
Cantonment | 135 | 07:00 | 123 | 12:00 | Palashbari | 131 | 03:00 | 121 | 19:30
Chandina | 127 | 07:00 | 121 | 11:00 | Panchagarh | 133 | 21:00 | 120 | 19:30
Chandpur | 127 | 09:00 | 115 | 14:00 | Patuakhali | 134 | 06:00 | 131 | 22:00
Chandraghona | 132 | 06:00 | 31 | 07:00 | Payra | 136 | 08:00 | 132 | 05:00
Chapai | 134 | 05:00 | 126 | 19:00 | PHP | 124 | 07:00 | 115 | 14:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 08:00 | 120 | 12:00 | Postogola | 132 | 07:00 | 124 | 12:00
Chauddagram | 125 | 07:00 | 115 | 14:00 | Purbachal | 140 | 05:00 | 123 | 11:00
Chhatak | 132 | 06:00 | 126 | 14:00 | Purbasadipur | 127 | 00:00 | 116 | 19:30
Chowmuhani | 119 | 07:00 | 110 | 19:00 | Rahanpur | 137 | 04:00 | 132 | 14:00
Chuadanga | 134 | 05:00 | 122 | 15:00 | Rahanpur-400 | 137 | 04:00 | 132 | 13:00
Coxsbazar | 122 | 17:00 | 110 | 19:00 | Rahim | 129 | 07:00 | 122 | 11:00
Cumilla(N) | 128 | 06:00 | 119 | 14:00 | Rajbari | 135 | 18:00 | 128 | 22:00
Cumilla(S) | 134 | 00:00 | 118 | 14:00 | Rajendrapur | 133 | 07:00 | 118 | 12:00
Daudkandi | 125 | 16:00 | 116 | 12:00 | Rajshahi | 137 | 23:00 | 127 | 15:00
Dhaka | 140 | 06:00 | 123 | 11:00 | Rajshahi-230 | 137 | 23:00 | 120 | 14:00
Dhamrai | 134 | 05:00 | 124 | 11:00 | Ramganj | 122 | 07:00 | 109 | 14:00
Dhanmondi | 140.5 | 06:00 | 121.5 | 11:00 | Rampur | 130 | 06:00 | 125 | 12:00
Dohazari | 127 | 17:00 | 120 | 22:00 | Rampura | 140 | 06:00 | 124 | 11:00
Faridpur | 135 | 05:00 | 130 | 12:00 | Rangamati | 131 | 08:00 | 125 | 12:00
Fatullah | 130 | 06:00 | 121 | 12:00 | Rangpur | 129 | 00:00 | 120 | 19:30
Fenchuganj | 136 | 07:00 | 132 | 21:00 | Ruppur | 138 | 06:00 | 130 | 15:00
Feni | 124 | 08:00 | 113 | 14:00 | Saidpur | 131 | 05:00 | 116 | 19:30
Ghatail | 133 | 05:00 | 126 | 12:00 | Satkhira | 129 | 18:00 | 119 | 22:00
Ghorashal | 135 | 06:00 | 126 | 13:00 | Satmasjid | 135 | 07:00 | 124 | 12:00
Goalpara | 135 | 18:00 | 126 | 00:00 | Savar | 129 | 07:00 | 120 | 12:00
Gollamari | 135 | 18:00 | 12 | 08:00 | SevenRings | 137 | 07:00 | 126 | 11:00
Gopalganj | 135 | 18:30 | 128 | 00:00 | ShahCement | 129 | 08:00 | 120 | 12:00
Gopalganj-400 | 136 | 05:00 | 130 | 12:00 | Shahjadpur | 136 | 01:00 | 132 | 11:00
Gulshan | 140 | 06:00 | 124 | 11:00 | Shahjibazar | 132 | 07:00 | 124 | 23:00
Halishahar | 132 | 18:00 | 124 | 11:00 | Shahmirpur | 132 | 17:00 | 127 | 12:00
Haripur | 128 | 05:00 | 122 | 12:00 | Shariatpur | 133 | 06:00 | 127 | 21:00
HaripurSBU | 127 | 02:00 | 122 | 12:00 | Sherpur | 138 | 08:00 | 132 | 18:30
Hasnabad | 133 | 20:00 | 124 | 11:00 | Shikalbaha | 121 | 05:00 | 115 | 11:00
Hathazari | 133 | 02:00 | 128 | 15:00 | Shikalbaha-230 | 132 | 01:00 | 122 | 06:00
Ishurdi | 139 | 06:00 | 132 | 11:00 | Shitalakhya | 129 | 07:00 | 121 | 12:00
Jaldhaka | 128 | 03:00 | 115 | 19:00 | Sholosohor | 131 | 07:00 | 125 | 11:00
Jamalpur | 140 | 07:00 | 135 | 01:00 | Shyampur | 130 | 07:00 | 122 | 12:00
Jashore | 130 | 05:00 | 120 | 14:00 | Shyampur-230 | 130 | 07:00 | 120 | 12:00
Jhenaidah | 136 | 20:00 | 120 | 15:00 | Siddhirganj | 128 | 04:00 | 121 | 12:00
Jhenaidah-230 | 135 | 05:00 | 127 | 11:00 | Sirajganj | 134 | 23:00 | 126 | 15:00
Joydebpur | 135 | 17:00 | 120 | 12:00 | Sonargaon | 128 | 08:00 | 118 | 11:00
Joypurhat | 135 | 04:00 | 126 | 13:00 | Sreemongol | 132 | 07:00 | 126 | 22:00
Juldah | 132 | 17:00 | 128 | 10:00 | Sreepur | 134 | 06:00 | 126 | 14:00
Kabirpur | 134 | 19:30 | 120 | 11:00 | Srinagar | 133 | 07:00 | 121 | 12:00
Kachua | 125 | 07:00 | 115 | 14:00 | SSM | 134 | 07:00 | 132 | 00:00
Kaliakoir | 138 | 07:00 | 129 | 11:00 | Sunamganj | 130 | 06:00 | 125 | 19:30
Kallyanpur | 131 | 05:00 | 122 | 10:00 | Sylhet | 133 | 09:00 | 129 | 00:00
Kalurghat | 131 | 08:00 | 125 | 12:00 | Sylhet-132 | 132 | 04:00 | 130 | 00:00
Kamrangirchar | 133 | 06:00 | 121 | 11:00 | Tangail | 132 | 04:00 | 123 | 07:00
Kaptai | 133 | 8:00 | 129 | 13:00 | Thakurgaon | 133 | 21:00 | 118 | 19:30
Kasba | 125 | 18:30 | 117 | 12:00 | TK | 129 | 00:00 | 126 | 12:00
Kazla | 131 | 04:00 | 122 | 12:00 | Tongi | 136 | 04:00 | 125 | 11:00
Keranigonj | 133 | 07:00 | 122 | 12:00 | Ullahpara | 135 | 05:00 | 123 | 13:00
Khagrachori | 130 | 07:00 | 124 | 13:00 | Ullon | 140 | 07:00 | 123 | 11:00
Khulna | 133 | 18:00 | 124 | 00:00 | Uttara | 130 | 06:00 | 119 | 12:00
Khulna(S) | 136 | 18:30 | 127 | 00:00 | UttaraNew | 130 | 06:00 | 120 | 12:00
Khulshi | 131 | 08:00 | 124 | 12:00 | Zigatola | 133 | 07:00 | 121 | 12:00
Kishoreganj | 132 | 07:00 | 121 | 21:00
Kodda | 132 | 19:30 | 118 | 12:00
KSRM | 133 | 06:00 | 126 | 14:00
Kulaura | 135 | 07:00 | 131 | 23:00
Kurigram | 131 | 04:00 | 117 | 19:30
Kushtia | 136 | 20:00 | 124 | 15:00
Lalbag | 132 | 06:00 | 121 | 12:00
Lalmonirhat | 129 | 03:00 | 119 | 19:30
Madanganj | 128 | 07:00 | 120 | 12:00
Madaripur | 135 | 05:00 | 129 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division