## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 23-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-05-2025 | during | 23-05-2025 | during | 23-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 230 | 230 | -
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 402 | 401 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 300 | 450 | 450 | 420 | 420 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 286 | 289 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 250 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 65 | 144 | 149.36 | 149.36 | 133 | 133 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 14 | 14.5 | 30 | 30 | 15.5 | 15.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 16 | 15 | 22 | 22 | 16 | 16 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 105 | 112 | 135 | 135 | 135 | 135 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 53 | 52 | 105 | 105 | 50 | 50 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 16 | 44 | 104 | 104 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 18 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 300 | 280 | 584 | 584 | 450 | 450 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 140 | 200 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 2242 | 2528.5 | 5260.9 | 5257.9 | 4065.26 | 4062.26
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 150 | 150 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 9 | 0 | 19 | 0 | 19 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 32 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 72 | 72 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 34 | 34 | 34 | 34 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 75 | 91 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 15 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 4.74 | 0 | 4.74 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 34 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 38 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 770 | 1200 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 31 | 9 | 2 | 7 | 2 | 7 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 456 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1553 | 2291 | 3354.46 | 3350.72 | 3338.46 | 3350.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 186 | 189 | 0 | 221 | 0 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 354 | 354 | 353.35 | 353.35 | 353.35 | 353.35
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 31 | 46.7 | 46.7 | 35 | 35 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 10 | 10 | 55 | 55 | 55 | 55 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 180 | 180 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 85 | 150 | 150 | 150 | 150 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 38 | 16 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 70 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 181 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 48 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 6 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 39 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 34 | 72 | 115 | 115 | 92 | 92 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 32 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1501 | 1627 | 2213 | 2394 | 2012.55 | 2177.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 22-05-2025 | during | 23-05-2025 | during | 23-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 121 | 166 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 64 | 105 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 21.51 | 0 | 37 | 0 | 37 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 220.51 | 283 | 588.1 | 549 | 370.6 | 331.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 36 | 35 | 35 | 35 | 34 | 34 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 40 | 40 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 151 | 152 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 22 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 82 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 174 | 172 | 170 | 170 | 175 | 175 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 8 | 25 | 25 | 6 | 6 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 350 | 348 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1506 | 1492 | 1612 | 1612 | 1517 | 1517
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 927 | 880 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 157 | 131 | 410 | 410 | 176 | 176 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 105 | 0 | 105 | 105 | 105 | 105
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 101.71 | 0 | 85 | 0 | 85 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 757 | 900 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2047.71 | 1928 | 3599.2 | 3514.2 | 3350.2 | 3265.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 597 | 678 | 0 | 0 | 0 | 0 | On test
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 8 | 11 | 10.12 | 10.12 | 10.12 | 10.12 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 110 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 741 | 1130 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 110 | 110 | 220 | 220 | GT-12 Under shutdown for Offline water wash
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.26 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1936.26 | 2456 | 2062.12 | 2061.12 | 2122.12 | 2121.12
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 26 | 26 | Engine Problem
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 152 | 154 | 214 | 214 | 172 | 172 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 160 | 220 | 220 | 176 | 176 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 350 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 97 | 97 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.18 | 0 | 5.15 | 0 | 5.15 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 983 | 1456.93 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 64.16 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 115 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1903.34 | 2205.93 | 3197.02 | 3030.87 | 3059.64 | 2893.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 53 | 50 | 55 | 55 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 167 | 157 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 90 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 107 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 200 | 0 | 157.62 | 0 | 157.62 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 428 | 404 | 655.22 | 467 | 600.22 | 412
System Total |  |  |  |  | 28886.2 | 27110.055 | 13337.82 | 15215.43 | 22542.02 | 22236.81 | 20436.05 | 20130.84
Forecast Scenario (23-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14700 |  | 0 |  | 14700
|  |  |  | 1:00 | 14240 |  | 0 |  | 14240
|  |  |  | 2:00 | 13590 |  | 0 |  | 13590
|  |  |  | 3:00 | 13170 |  | 0 |  | 13170
|  |  |  | 4:00 | 12840 |  | 0 |  | 12840
|  |  |  | 5:00 | 12390 |  | 0 |  | 12390
|  |  |  | 6:00 | 10890 |  | 0 |  | 10890
|  |  |  | 7:00 | 10920 |  | 0 |  | 10920
|  |  |  | 8:00 | 11030 |  | 0 |  | 11030
|  |  |  | 9:00 | 11440 |  | 0 |  | 11440
|  |  |  | 10:00 | 11900 |  | 0 |  | 11900
|  |  |  | 11:00 | 12250 |  | 0 |  | 12250
|  |  |  | 12:00 | 12780 |  | 0 |  | 12780
|  |  |  | 13:00 | 13220 |  | 0 |  | 13220
|  |  |  | 14:00 | 12950 |  | 0 |  | 12950
|  |  |  | 15:00 | 13320 |  | 0 |  | 13320
|  |  |  | 16:00 | 12920 |  | 0 |  | 12920
|  |  |  | 17:00 | 12700 |  | 0 |  | 12700
|  |  |  | 18:00 | 12270 |  | 0 |  | 12270
|  |  |  | 18:30 | 13470 |  | 0 |  | 13470
|  |  |  | 19:00 | 14270 |  | 0 |  | 14270
|  |  |  | 19:30 | 15020 |  | 0 |  | 15020
|  |  |  | 20:00 | 15140 |  | 0 |  | 15140
|  |  |  | 21:00 | 15420 |  | 0 |  | 15420
|  |  |  | 22:00 | 15450 |  | 0 |  | 15450
|  |  |  | 23:00 | 15550 |  | 0 |  | 15550
Probable Maximum Temperature: |  |  | 32.40°C
Probable Maximum Demand at Day Peak: |  |  | 12780.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15420.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14200.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 289.67 MKWHr.
*** This report is generated digitally from Operation Information System (OIS) at 09:37 hrs on 23-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 22-05-2025 | [28 empty] | Date: | 22-05-2025 | [28 empty] | Date: | 22-05-2025 | [28 empty] | Date: | 22-05-2025 | [28 empty] | Date: | 22-05-2025 | [16 empty] | Date: | 22-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [16 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 17 | 116 | 97 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 293 | 45 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 108 | 0 | 15 | 0 | 450 | 0 | 0 | 0 | 150 | 14 | 17 | 39 | 0 | 70 | 12 | 0 | 39 | 0 | 27 | 382 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 194 | 35 | 76 | 75 | 161 | 13 | 14 | 114 | 40 | 8 | 0 | 0 | 310 | 320 | 363 | 36 | 40 | 0 | 131 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 65 | 132 | 0 | 0 | 0 | 12 | 7134 | 927 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 155 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 166 | 52 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 100 | 220 | 0 | 521 | 900 | 0 | 5709 | 12843 | 76.87
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 113 | 97 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 295 | 60 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 108 | 14 | 16 | 0 | 450 | 0 | 0 | 0 | 150 | 5 | 17 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 29 | 384 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 199 | 35 | 24 | 75 | 181 | 9 | 14 | 114 | 40 | 52.2 | 0 | 41 | 315 | 320 | 382 | 36 | 39 | 0 | 139 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 48 | 93 | 0 | 0 | 0 | 12 | 7149.2 | 918 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 777 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 141 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 163 | 52 | 35 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 100 | 220 | 0 | 522 | 900 | 0 | 5700 | 12849.2 | 76.88
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 113 | 97 | 0 | 0 | 17 | 0 | 0 | 0 | 350 | 283 | 110 | 0 | 0 | 0 | 269 | 0 | 0 | 0 | 90 | 14 | 16 | 0 | 450 | 0 | 0 | 0 | 150 | 8 | 17 | 0 | 0 | 70 | 12 | 0 | 40 | 0 | 29 | 382 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 183 | 35 | 17 | 80 | 175 | 9 | 14 | 114 | 36 | 52.2 | 0 | 41 | 300 | 320 | 324 | 36 | 39 | 0 | 130 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 49 | 93 | 0 | 0 | 0 | 12 | 7023.2 | 918 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 769 | 0 | 1017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 163 | 53 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 100 | 180 | 0 | 524 | 900 | 0 | 5615 | 12638.2 | 76.89
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 17 | 107 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 282 | 116 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 90 | 14 | 16 | 0 | 400 | 0 | 0 | 0 | 150 | 3 | 17 | 0 | 0 | 70 | 0 | 0 | 40 | 0 | 29 | 385 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 909 | 0 | 51 | 0 | 0 | 0 | 354 | 335 | 10 | 189 | 32 | 17 | 80 | 173 | 9 | 14 | 114 | 36 | 52.2 | 0 | 41 | 305 | 320 | 300 | 36 | 39 | 0 | 130 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 49 | 93 | 0 | 0 | 0 | 12 | 6804.2 | 919 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 146 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 167 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 90 | 180 | 0 | 524 | 800 | 0 | 5354 | 12158.2 | 76.9
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 85 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 298 | 135 | 0 | 0 | 0 | 287 | 0 | 0 | 0 | 70 | 14 | 16 | 0 | 350 | 0 | 0 | 0 | 150 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 30 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 0 | 0 | 300 | 335 | 10 | 200 | 32 | 17 | 80 | 176 | 9 | 14 | 114 | 36 | 52.2 | 0 | 41 | 300 | 320 | 332 | 36 | 39 | 0 | 135 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 49 | 94 | 0 | 0 | 0 | 12 | 6599.2 | 926 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 154 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 167 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 96 | 180 | 0 | 523 | 720 | 0 | 5233 | 11832.2 | 76.91
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 17 | 85 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 300 | 180 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 70 | 14 | 16 | 0 | 300 | 0 | 0 | 0 | 150 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 40 | 0 | 30 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 804 | 0 | 51 | 0 | 0 | 0 | 300 | 335 | 10 | 182 | 32 | 17 | 80 | 172 | 9 | 14 | 114 | 34 | 52.2 | 0 | 41 | 305 | 320 | 300 | 36 | 39 | 0 | 131 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 49 | 95 | 0 | 0 | 0 | 12 | 6541.2 | 927 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 154 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 171 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 90 | 180 | 0 | 522 | 680 | 0 | 5188 | 11729.2 | 76.92
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 85 | 65 | 0 | 4 | 0 | 0 | 0 | 0 | 300 | 305 | 62 | 0 | 0 | 0 | 326 | 0 | 0 | 2 | 52 | 14 | 16 | 0 | 280 | 0 | 0 | 0 | 150 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 653 | 1 | 51 | 0 | 0 | 0 | 300 | 285 | 10 | 194 | 32 | 17 | 80 | 174 | 9 | 14 | 114 | 32 | 8 | 4 | 40 | 305 | 320 | 331 | 36 | 39 | 0 | 135 | 0 | 0 | 83 | 30 | 0 | 18 | 174 | 0 | 49 | 94 | 0 | 0 | 0.53 | 12 | 6152.53 | 926 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 763 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 4.02 | 157 | 0 | 148 | 0 | 0 | 0 | 250 | 0 | 0.33 | 0 | 168 | 54 | 0 | 1 | 0 | 0 | 0 | 0 | 14 | 0.02 | 0 | 150 | 9 | 100 | 180 | 0 | 522 | 600 | 0 | 5053.37 | 11205.9 | 76.93
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 17 | 85 | 65 | 0 | 50 | 0 | 0 | 0 | 32 | 300 | 296 | 62 | 0 | 0 | 0 | 325 | 0 | 0 | 9 | 35 | 14 | 16 | 0 | 280 | 0 | 0 | 0 | 150 | 9 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 655 | 3 | 51 | 0 | 0 | 0 | 354 | 340 | 10 | 194 | 29 | 16 | 80 | 184 | 9 | 14 | 114 | 32 | 0 | 15 | 40 | 320 | 320 | 374 | 36 | 39 | 0 | 140 | 0 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 65 | 121 | 0 | 1 | 7.76 | 12 | 6484.76 | 925 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 765 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 8.81 | 160 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 1.03 | 0 | 164 | 51 | 0 | 6 | 0 | 0 | 0 | 1 | 34 | 0.17 | 0 | 150 | 7 | 96 | 180 | 0 | 521 | 593 | 0 | 5150.01 | 11634.77 | 76.94
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 85 | 65 | 0 | 55 | 1 | 0 | 0 | 32 | 300 | 313 | 62 | 0 | 0 | 0 | 320 | 0 | 0 | 12 | 35 | 14 | 16 | 0 | 280 | 0 | 0 | 0 | 150 | 17 | 17 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 5 | 51 | 0 | 0 | 0 | 347 | 340 | 10 | 211 | 29 | 16 | 80 | 175 | 9 | 15 | 114 | 30 | 0 | 9 | 39 | 315 | 320 | 405 | 36 | 39 | 0 | 135 | 0 | 0 | 82 | 30 | 0 | 18 | 173 | 0 | 65 | 122 | 0 | 1 | 8.74 | 12 | 6547.74 | 880 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 764 | 0 | 827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 19.06 | 152 | 0 | 133 | 0 | 0 | 0 | 300 | 0 | 1.73 | 0 | 162 | 54 | 0 | 11 | 0 | 0 | 0 | 1.5 | 110 | 0.25 | 0 | 150 | 6 | 100 | 180 | 0 | 524 | 589 | 0 | 5214.54 | 11762.28 | 76.95
09:00 | 0 | 53 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 88 | 65 | 0 | 55 | 29 | 0 | 0 | 32 | 300 | 312 | 58 | 0 | 0 | 0 | 318 | 0 | 0 | 9 | 35 | 14 | 16 | 0 | 280 | 0 | 0 | 0 | 120 | 54 | 10 | 0 | 0 | 0 | 0 | 4 | 39 | 0 | 2 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 51 | 0 | 0 | 0 | 300 | 340 | 10 | 205 | 29 | 16 | 70 | 174 | 9 | 6 | 114 | 40 | 0 | 14 | 39 | 305 | 320 | 400 | 36 | 39 | 0 | 140 | 0 | 0 | 82 | 30 | 0 | 18 | 174 | 0 | 45 | 104 | 0 | 1 | 26.19 | 12 | 6590.19 | 879 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 76.92 | 762 | 0 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 31.47 | 160 | 0 | 164 | 0 | 0 | 0 | 350 | 0 | 2.68 | 0 | 163 | 53 | 0 | 6 | 0 | 0 | 0 | 2.4 | 102 | 0.26 | 0 | 200 | 5 | 100 | 180 | 0 | 536 | 650 | 0 | 5486.73 | 12076.92 | 76.96
10:00 | 0 | 53 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 17 | 87 | 65 | 0 | 55 | 35 | 0 | 0 | 32 | 350 | 290 | 110 | 0 | 0 | 0 | 316 | 0 | 0 | 21 | 52 | 14 | 16 | 0 | 400 | 0 | 0 | 0 | 120 | 24 | 0 | 0 | 0 | 10 | 0 | 3 | 39 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 9 | 43 | 0 | 0 | 0 | 356 | 340 | 10 | 183 | 32 | 17 | 70 | 184 | 9 | 6 | 114 | 38 | 0 | 22 | 39 | 305 | 320 | 348 | 36 | 39 | 0 | 152 | 0 | 0 | 82 | 30 | 0 | 18 | 174 | 0 | 45 | 104 | 0 | 1 | 9.37 | 12 | 6934.37 | 927 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 72.31 | 760 | 0 | 881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 25.95 | 170 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 2.66 | 0 | 168 | 53 | 0 | 25 | 0 | 0 | 0 | 1.7 | 160 | 0.65 | 0 | 200 | 7 | 90 | 220 | 0 | 533 | 672 | 0 | 5797.27 | 12731.64 | 76.97
11:00 | 0 | 53 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 88 | 65 | 0 | 15 | 35 | 17 | 0 | 16 | 320 | 306 | 125 | 0 | 0 | 0 | 322 | 0 | 0 | 26 | 70 | 14 | 16 | 0 | 350 | 0 | 0 | 0 | 120 | 26 | 0 | 0 | 0 | 48 | 0 | 5 | 37 | 0 | 2 | 455 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 705 | 14 | 43 | 0 | 0 | 0 | 354 | 340 | 10 | 202 | 32 | 34 | 70 | 177 | 9 | 11 | 114 | 46 | 0 | 33 | 38 | 310 | 320 | 385 | 36 | 40 | 0 | 142 | 0 | 0 | 82 | 30 | 0 | 18 | 174 | 0 | 56 | 122 | 0 | 1 | 50.17 | 12 | 6990.17 | 927 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 101.68 | 759 | 0 | 874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 60.97 | 140 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 5.17 | 0 | 167 | 53 | 0 | 0 | 0 | 0 | 0 | 8 | 170 | 0.76 | 0 | 200 | 7 | 100 | 220 | 0 | 533 | 711 | 0 | 5859.58 | 12849.75 | 76.97
12:00 | 0 | 53 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 105 | 65 | 0 | 15 | 35 | 17 | 0 | 16 | 320 | 286 | 140 | 0 | 0 | 0 | 328 | 0 | 0 | 18 | 70 | 14 | 16 | 0 | 300 | 0 | 0 | 0 | 150 | 31 | 0 | 0 | 0 | 75 | 0 | 3 | 38 | 0 | 2 | 456 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 9 | 43 | 0 | 0 | 0 | 354 | 340 | 10 | 186 | 31 | 34 | 70 | 181 | 9 | 11 | 114 | 48 | 0 | 32 | 38 | 305 | 320 | 350 | 36 | 40 | 0 | 151 | 0 | 0 | 82 | 30 | 0 | 18 | 174 | 0 | 64 | 121 | 0 | 2 | 21.51 | 12 | 7022.51 | 927 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 101.71 | 757 | 0 | 983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 64.16 | 152 | 0 | 170 | 0 | 0 | 0 | 414 | 0 | 5.18 | 0 | 167 | 53 | 0 | 0 | 0 | 0 | 0 | 8 | 200 | 0.26 | 0 | 250 | 8 | 120 | 220 | 0 | 597 | 741 | 0 | 6315.31 | 13337.82 | 76.97
13:00 | 0 | 53 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 0 | 17 | 113 | 65 | 0 | 15 | 35 | 60 | 0 | 16 | 320 | 291 | 150 | 0 | 0 | 0 | 323 | 0 | 0 | 33 | 70 | 14 | 16 | 0 | 300 | 0 | 0 | 0 | 150 | 46 | 0 | 0 | 0 | 75 | 0 | 1 | 38 | 0 | 5 | 504 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 51 | 0 | 0 | 0 | 349 | 340 | 10 | 202 | 31 | 34 | 70 | 180 | 9 | 14 | 114 | 50 | 0 | 30 | 38 | 310 | 320 | 384 | 35 | 39 | 0 | 159 | 5 | 0 | 82 | 30 | 0 | 18 | 174 | 0 | 64 | 121 | 0 | 2 | 41.78 | 12 | 7322.78 | 927 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 49.21 | 758 | 0 | 1030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 36.78 | 162 | 0 | 171 | 0 | 0 | 0 | 414 | 0 | 3.7 | 0 | 166 | 52 | 0 | 9 | 0 | 0 | 0 | 8 | 165 | 0.15 | 0 | 250 | 8 | 120 | 220 | 0 | 596 | 769 | 0 | 6225.84 | 13548.62 | 76.97
14:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 0 | 17 | 112 | 65 | 0 | 15 | 35 | 72 | 0 | 16 | 320 | 285 | 150 | 0 | 0 | 0 | 300 | 0 | 0 | 23 | 70 | 14.5 | 16 | 0 | 300 | 0 | 0 | 0 | 150 | 60 | 0 | 0 | 0 | 88 | 0 | 1 | 40 | 0 | 2 | 455 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 805 | 4 | 51 | 0 | 0 | 0 | 355 | 340 | 10 | 182 | 29 | 34 | 70 | 176 | 9 | 14 | 114 | 50 | 0 | 39 | 38 | 310 | 320 | 359 | 35 | 40 | 0 | 154 | 5 | 0 | 82 | 30 | 0 | 18 | 175 | 0 | 63 | 120 | 0 | 2 | 39.96 | 11 | 7178.46 | 927 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 36.64 | 814 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 30.77 | 159 | 0 | 169 | 0 | 0 | 0 | 350 | 0 | 2.16 | 0 | 165 | 52 | 0 | 25 | 0 | 0 | 0 | 8 | 171 | 0.08 | 0 | 236 | 7 | 110 | 180 | 0 | 611 | 843 | 0 | 6350.65 | 13529.11 | 76.97
15:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 391 | 0 | 0 | 2 | 17 | 112 | 65 | 0 | 15 | 35 | 90 | 0 | 16 | 360 | 291 | 150 | 0 | 0 | 0 | 318 | 0 | 0 | 23 | 70 | 14.5 | 16 | 0 | 300 | 0 | 0 | 0 | 150 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 505 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 850 | 1 | 51 | 3 | 0 | 0 | 350 | 340 | 10 | 202 | 28 | 42 | 70 | 168 | 11 | 14 | 91 | 50 | 0 | 16 | 38 | 305 | 320 | 386 | 35 | 40 | 0 | 156 | 5 | 0 | 82 | 30 | 0 | 18 | 175 | 0 | 63 | 120 | 0 | 0 | 17.19 | 9 | 7208.69 | 927 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 61.32 | 812 | 0 | 1127.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 21.92 | 157 | 0 | 165 | 0 | 0 | 0 | 414 | 0 | 2.65 | 0 | 124 | 50 | 0 | 9 | 0 | 0 | 0 | 2.5 | 112 | 0.22 | 0 | 200 | 8 | 120 | 220 | 0 | 611 | 848 | 0 | 6290.06 | 13498.75 | 76.97
16:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 28 | 17 | 112 | 65 | 0 | 15 | 35 | 100 | 0 | 16 | 300 | 276 | 200 | 0 | 0 | 0 | 321 | 0 | 0 | 16 | 70 | 14.5 | 16 | 0 | 300 | 0 | 0 | 0 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 10 | 2 | 503 | 0 | 0 | 50 | 0 | 11 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 40 | 0 | 0 | 352 | 340 | 10 | 185 | 28 | 72 | 70 | 155 | 9 | 14 | 88 | 50 | 0 | 10 | 38 | 305 | 320 | 349 | 35 | 40 | 0 | 155 | 0 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 63 | 111 | 0 | 1 | 18.09 | 7 | 7235.59 | 927 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 27.01 | 812 | 0 | 1169.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 25.9 | 155 | 0 | 161 | 0 | 0 | 0 | 414 | 0 | 2.19 | 0 | 157 | 52 | 30 | 16 | 0 | 0 | 0 | 4.2 | 103 | 0.1 | 0 | 200 | 8 | 110 | 220 | 0 | 612 | 845 | 0 | 6312.3 | 13547.89 | 76.97
17:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 35 | 17 | 112 | 65 | 0 | 15 | 35 | 108 | 0 | 16 | 300 | 299 | 200 | 0 | 0 | 0 | 268 | 0 | 0 | 7 | 70 | 14.5 | 0 | 0 | 300 | 0 | 0 | 0 | 150 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 40 | 17 | 5 | 504 | 0 | 0 | 50 | 0 | 17 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 40 | 0 | 0 | 300 | 340 | 10 | 192 | 31 | 72 | 70 | 151 | 9 | 14 | 88 | 56 | 0 | 10 | 38 | 305 | 320 | 355 | 35 | 40 | 0 | 152 | 6 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 63 | 120 | 0 | 0 | 9.54 | 11 | 7214.04 | 926 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 27.87 | 812 | 0 | 1168.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 12.23 | 155 | 0 | 160 | 0 | 0 | 0 | 350 | 0 | 1.08 | 0 | 163 | 50 | 35 | 8 | 0 | 0 | 0 | 2.1 | 37 | 0.12 | 0 | 200 | 7 | 116 | 220 | 0 | 614 | 840 | 0 | 6153.32 | 13367.36 | 76.97
18:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 35 | 17 | 112 | 65 | 0 | 15 | 35 | 108 | 0 | 16 | 300 | 287 | 200 | 0 | 0 | 0 | 265 | 0 | 0 | 1 | 70 | 14.5 | 15 | 0 | 300 | 0 | 0 | 0 | 150 | 8 | 17 | 24 | 0 | 0 | 0 | 0 | 40 | 17 | 20 | 453 | 0 | 0 | 50 | 0 | 17 | 0 | 0 | 0 | 0 | 900 | 0 | 51 | 40 | 0 | 0 | 300 | 340 | 10 | 182 | 31 | 72 | 70 | 163 | 26 | 9 | 88 | 54 | 8 | 3 | 38 | 300 | 320 | 318 | 35 | 40 | 0 | 130 | 6 | 0 | 81 | 30 | 0 | 18 | 171 | 0 | 92 | 139 | 0 | 0 | 2.67 | 11 | 7209.17 | 926 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 7.45 | 781 | 0 | 1167.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.86 | 154 | 0 | 161 | 0 | 0 | 0 | 300 | 0 | 0.26 | 0 | 164 | 47 | 35 | 2 | 0 | 0 | 0 | 0.9 | 9 | 0.05 | 0 | 200 | 7 | 100 | 180 | 0 | 612 | 800 | 0 | 5892.75 | 13101.92 | 76.97
19:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 37 | 17 | 112 | 145 | 0 | 15 | 35 | 150 | 0 | 30 | 300 | 303 | 200 | 0 | 30 | 0 | 293 | 0 | 0 | 0 | 108 | 14.5 | 15 | 0 | 300 | 0 | 0 | 0 | 150 | 5 | 17 | 40 | 0 | 35 | 30 | 0 | 40 | 17 | 9 | 575 | 0 | 0 | 47 | 0 | 17 | 0 | 0 | 0 | 0 | 1195 | 0 | 51 | 48 | 0 | 0 | 342 | 340 | 10 | 200 | 31 | 72 | 70 | 188 | 34 | 6 | 114 | 62 | 8 | 0 | 37 | 305 | 320 | 347 | 35 | 40 | 0 | 140 | 6 | 0 | 82 | 22 | 0 | 18 | 172 | 0 | 96 | 157 | 0 | 0 | 0 | 12 | 8115.5 | 879 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 795 | 12 | 1314.4 | 0 | 0 | 0 | 11 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 160 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 47 | 70 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 676 | 850 | 0 | 6456.4 | 14571.9 | 76.97
19:30 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 54 | 17 | 112 | 144 | 0 | 0 | 35 | 162 | 0 | 44 | 300 | 289 | 200 | 0 | 35 | 0 | 250 | 0 | 0 | 0 | 108 | 14.5 | 15 | 0 | 280 | 0 | 0 | 0 | 150 | 9 | 17 | 72 | 0 | 91 | 38 | 0 | 40 | 34 | 15 | 575 | 0 | 0 | 18 | 0 | 32 | 0 | 0 | 0 | 0 | 1200 | 0 | 51 | 85 | 0 | 0 | 354 | 340 | 10 | 189 | 31 | 72 | 70 | 200 | 39 | 6 | 114 | 42 | 8 | 0 | 16 | 295 | 320 | 348 | 35 | 40 | 0 | 152 | 8 | 0 | 82 | 22 | 0 | 18 | 172 | 0 | 105 | 166 | 0 | 0 | 0 | 12 | 8221.5 | 880 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900 | 17 | 1456.93 | 0 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 160 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 157 | 50 | 107 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 678 | 1130 | 0 | 6993.93 | 15215.43
20:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 48 | 17 | 112 | 144 | 0 | 0 | 17 | 162 | 0 | 51 | 300 | 291 | 200 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 14.5 | 15 | 0 | 280 | 0 | 0 | 0 | 150 | 14 | 17 | 72 | 0 | 93 | 38 | 0 | 40 | 39 | 15 | 500 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 1132 | 0 | 51 | 70 | 0 | 0 | 354 | 340 | 10 | 182 | 31 | 72 | 80 | 200 | 40 | 11 | 114 | 42 | 8 | 0 | 0 | 295 | 320 | 355 | 35 | 40 | 0 | 151 | 8 | 0 | 82 | 25 | 0 | 18 | 171 | 0 | 105 | 166 | 0 | 0 | 0 | 12 | 8047.5 | 880 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 905 | 17 | 1452.38 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 160 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 160 | 48 | 110 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 674 | 1115 | 0 | 6934.38 | 14981.88 | 76.97
21:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 35 | 17 | 112 | 144 | 0 | 0 | 17 | 126 | 0 | 78 | 300 | 255 | 200 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 126 | 14.5 | 15 | 0 | 280 | 0 | 0 | 0 | 150 | 5 | 17 | 72 | 0 | 96 | 12 | 0 | 39 | 17 | 16 | 501 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 1226 | 0 | 51 | 10 | 0 | 0 | 354 | 340 | 10 | 182 | 31 | 72 | 80 | 200 | 38 | 14 | 114 | 42 | 8 | 0 | 0 | 300 | 320 | 349 | 29 | 40 | 0 | 154 | 8 | 0 | 82 | 25 | 0 | 18 | 171 | 0 | 96 | 167 | 0 | 0 | 0 | 12 | 7923.5 | 923 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 937 | 17 | 1454.92 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 160 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 676 | 1160 | 0 | 7126.92 | 15050.42 | 76.97
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 23 | 17 | 94 | 145 | 0 | 0 | 17 | 126 | 0 | 80 | 300 | 308 | 200 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 126 | 14.5 | 15 | 0 | 280 | 0 | 0 | 0 | 150 | 20 | 17 | 72 | 0 | 70 | 12 | 0 | 37 | 0 | 27 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 0 | 0 | 352 | 340 | 10 | 208 | 31 | 72 | 80 | 200 | 39 | 14 | 114 | 40 | 8 | 0 | 0 | 305 | 320 | 395 | 0 | 40 | 0 | 156 | 8 | 0 | 82 | 20 | 0 | 18 | 173 | 0 | 96 | 167 | 0 | 0 | 0 | 12 | 7894.5 | 884 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958 | 17 | 1463.04 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 0 | 154 | 0 | 160 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 166 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 180 | 0 | 676 | 1240 | 0 | 7124.04 | 15018.54 | 76.97
23:00 | 0 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 94 | 145 | 0 | 0 | 17 | 126 | 0 | 80 | 300 | 277 | 200 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 126 | 14 | 15 | 0 | 280 | 0 | 0 | 0 | 150 | 14 | 17 | 72 | 0 | 70 | 12 | 0 | 37 | 0 | 21 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 0 | 0 | 354 | 340 | 10 | 180 | 31 | 73 | 70 | 200 | 38 | 14 | 114 | 42 | 14 | 0 | 0 | 295 | 320 | 302 | 0 | 39 | 0 | 148 | 8 | 0 | 82 | 20 | 0 | 18 | 173 | 0 | 96 | 167 | 0 | 0 | 0 | 12 | 7639 | 879 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 22 | 1453.26 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 30 | 0 | 155 | 0 | 158 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 675 | 1244 | 0 | 7166.26 | 14805.26 | 76.97
Total KWH | 0 | 768960 | 402720 | 0 | 0 | 0 | 0 | 0 | 9406800 | 0 | 0 | 286560 | 432000 | 2439792 | 2040480 | 0 | 372748 | 555152 | 1334880 | 0 | 621120 | 7816000 | 7139869 | 3380991 | 0 | 49852 | 0 | 7076476 | 0 | 0 | 214485 | 1974000 | 340200 | 345000 | 0 | 7878181.82 | 0 | 0 | 0 | 3600000 | 426240 | 269348 | 460320 | 0 | 1104000 | 163200 | 14805 | 941580 | 135491 | 353760 | 10661818.18 | 0 | 0 | 399840 | 26231.4 | 149709 | 0 | 0 | 0 | 0 | 21610907 | 53055 | 1181472 | 292727 | 0 | 0 | 8409900 | 8154000 | 248160 | 4809000 | 748368 | 1034880 | 1784000 | 4227360 | 391440 | 280590 | 2661900 | 998400 | 384763 | 242545 | 764544 | 7430500 | 7678600 | 8926000 | 756000 | 871200 | 0 | 3466309.1 | 60336 | 0 | 1970880 | 666816 | 0 | 433000 | 4582770 | 0 | 1615200 | 2925600 | 0 | 12250 | 281030 | 277680 | 173814791.5 | 22032000 | 3552768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 826128 | 648720 | 19323637 | 123840 | 25636637 | 0 | 0 | 0 | 35136 | 0 | 234168 | 0 | 0 | 0 | 677860 | 65771 | 346000 | 3950009 | 0 | 3943655 | 0 | 0 | 0 | 8648000 | 0 | 29400 | 0 | 3958000 | 1164218 | 736201 | 132341 | 556080 | 0 | 0 | 46404.36 | 1374480 | 3315 | 0 | 5302000 | 216680 | 2592000 | 5154380 | 0 | 13962240 | 21025454.55 | 0 | 146297522.91 | 320112314.41

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 22-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13337.82 | MW | 12:00 Hr. | Energy Generated |  |  | 320.1123 |  | MKWHr.
| Day Peak Demand |  |  | 13376.82 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.981 |  | MKWHr.
| Evening Peak Generation |  |  | 15215.43 | MW | 19:30 Hr. | Energy Demand |  |  | 321.0933 |  | MKWHr.
| Evening Peak Demand |  |  | 15281.43 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.4 |  | °C
| Minimum Generation of the Day |  |  | 11205.9 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 1018.84 |  | MMCFD
| Maximum Generation of the Day |  |  | 15215.43 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.1673 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 43.3835 | 0 | 11.2783 | 0 | 0 | 0.21449 | 0 | 0 | 54.8763 | Gas | 137.8527 | Gas | 498374114.8404
| Chattogram Zone |  |  | 3.9538 | 32.2727 | 2.7081 | 0 | 0.94158 | 0.06786 | 0 | 0.42624 | 40.3703 | Coal | 97.0083 | Coal | 574664861.2885
| Cumilla Zone |  |  | 25.6155 | 0 | 9.7576 | 0 | 0 | 0.24255 | 0.9984 | 0 | 36.614 | HFO | 31.1398 | HFO | 581952971.798
| Mymensingh Zone |  |  | 0 | 0 | 4.8185 | 0 | 0 | 0.29328 | 0 | 0 | 5.1118 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 36.8424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.8424 | Hydro | 0.94158 | Hydro | 94158
| Khulna Zone |  |  | 3.5528 | 19.3236 | 0.94997 | 0 | 0 | 0.64872 | 22.032 | 0 | 46.5071 | Solar | 4.0767 | Solar | 67548019.0696
| Barishal Zone |  |  | 7.9631 | 40.2897 | 0 | 0 | 0 | 0.003315 | 0 | 0 | 48.2561 | Import | 48.667 | Import | 245360942.26
| Rajshahi Zone |  |  | 16.5417 | 0 | 0.33508 | 0 | 0 | 1.0533 | 25.6366 | 0 | 43.5666 | Wind | 0.42624 | Wind | 6240153.6
| Rangpur Zone |  |  | 0 | 5.1222 | 1.2923 | 0 | 0 | 1.5532 | 0 | 0 | 7.9677
| Total |  |  | 137.8527 | 97.0083 | 31.1398 | 0 | 0.94158 | 4.0767 | 48.667 | 0.42624 | 320.1123
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 498374114.8404 |  | Hydro | 94158
|  |  |  | Coal | 574664861.2885 |  | Solar | 67548019.0696
|  |  |  | HFO | 581952971.798 |  | Import | 245360942.26
|  |  |  | HSD | 0 |  | Wind | 6240153.6
[5 empty] | Total: | 197,42,35,220 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.032 | Peak Hr Flow | 880.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45921236.46 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.6366 | Peak Hr Flow | 1456.93 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 632 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9984 | Peak Hr Flow | 42.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 926 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.667 | Peak Hr Flow | 2378.93 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 55 |  | 5593
|  |  |  | Chattogram |  | 0 |  | 1379
|  |  |  | Cumilla |  | 0 |  | 1348
|  |  |  | Mymensingh |  | 0 |  | 1164
|  |  |  | Sylhet |  | 0 |  | 563
|  |  |  | Khulna |  | 5 |  | 1807
|  |  |  | Barishal |  | 0 |  | 441
|  |  |  | Rajshahi |  | 0 |  | 1466
|  |  |  | Rangpur |  | 3 |  | 976
|  |  |  | Total |  | 63 |  | 14737
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:34 | 09:57 | Cumilla(N) 230/132/33kV S/S 132KV T-04 HT Tripped showing TI> relays. | [7 empty] | 50.0MW load
interrup.
| 08:34 | 11:14 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Tripped showing Differential Protection | [7 empty] | 50.0MW load
|  |  | Operated Restricted Earth fault Lock Out relays Due to 33KV Under ground R-phase Cable | [7 empty] | interrup.
Blast
| 08:34 | 11:14 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Tripped showing No relays Due to 33KV Under | [7 empty] | 50.0MW load
|  |  | ground R-phase Cable Blast | [7 empty] | interrup.
| 08:34 | 09:58 | Cumilla(N) 230/132/33kV S/S 132KV T-04 LT Tripped showing No relays Due to 33KV T-03 | [7 empty] | 50.0MW load
|  |  | Under ground R-phase Cable Blast | [7 empty] | interrup.
| 08:40 | 11:25 | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D
| 08:40 | 11:25 | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D
| 08:44 | 15:39 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to 6 No.
Earthing pit maintenanc work.
|  | 08:48 | Jamalpur 132/33kV S/S T-2 LT is restored.
|  | 08:48 | Jamalpur 132/33kV S/S T-2 HT is restored.
|  | 08:59 | Haripur-Meghnaghat 230kV Ckt-2 is restored.
| 09:15 | 13:22 | Chauddagram-Feni 132 kV Ckt-2 Scheduled S/D from Chauddagram 132/33kV end Due to For
maintenance in Feni grid substation. and from Feni 132/33kV end Due to Transfer DS
maintenance work
| 09:34 | 16:11 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Bay Extension work in
Rajendrapur S/S.
| 09:34 | 16:11 | Rajendrapur 132/33kV S/S MTR-2 HT Project Work S/D Due to Bay Extension work in
Rajendrapur S/S.
| 09:34 | 16:11 | Rajendrapur 132/33kV S/S MTR-2 LT Project Work S/D Due to Bay Extension work in
Rajendrapur S/S.
| 09:40 | 13:59 | Pabna- Shahjadpur 132kV Ckt-1 Forced S/D from Pabna 132/33kV end Due to CB SF6 Gas
leakage maintenance.
| 09:57 |  | 400Kv Bus-1 S/D at Payra P/S.
| 09:58 |  | Summit Meghnaghat-2 589 MW CCPP ST was sync.
| 09:58 |  | Meghnaghat CCPP(Summit)-2 Synchronized with remarks:- ST
| 10:03 | 12:08 | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Redhot maintenance
| 10:03 | 12:08 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Red hot maintenance
|  | 10:08 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt is restored.
| 11:17 | 11:26 | Bogura(New)-Naogaon 132 kV Ckt-1 Tripped from Naogaon 132/33kV end showing TCSR-1 relays.
| 11:30 | 12:10 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to BPDB 33KV Feeder (incomer-2)
red hot maintenance.
| 11:40 | 12:15 | Lalmonirhat 132/33kV S/S T-1 (425T) HT Scheduled S/D Due to R phase red hot
| 11:40 | 12:15 | Lalmonirhat 132/33kV S/S T-1 (425T) LT Scheduled S/D Due to 33 kv R phase red hot
| 12:35 | 20:51 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Scheduled S/D Due to 33kV new CB and Isolator
installation by BPDB.
| 13:01 | 19:10 | Jashore 132/33kV S/S 132 kV Bus-A Scheduled S/D Due to For replacing R phase PT of 132 kv
Capacitor Bank.
| 13:10 | 13:56 | Purbasadipur-Saidpur 132kV Ckt-2 Tripped from Purbasadipur 132/33kV end showing Siemens
(7sa87) relays. and from Saidpur 132/33kV end showing Distance relay Signal: Phase A
Phase B relays.
| 14:40 | 15:36 | Juldah-Shahmirpur 132kV Ckt-1 Tripped from Shahmirpur 132/33kV end showing Distance | [7 empty] | 53.0MW load
|  |  | A,B,C, 3Ph, Zone 4, 7.4 km relays Due to Julda Unit 3 power plant fault. | [7 empty] | interrup.
Shahmirpur 132/33kV
end
| 14:41 | 15:36 | Juldah-Shahmirpur 132kV Ckt-2 Tripped from Shahmirpur 132/33kV end showing Distance | [7 empty] | 53.0MW load
|  |  | A,B,C, 3Ph, Zone 4, 7.6 km relays Due to Julda Unit 3 power plant fault. | [7 empty] | interrup.
Shahmirpur 132/33kV
end
|  | 15:29 | Madunaghat 132/33kV S/S TR-1(507T) HT is restored.
| 15:48 | 18:04 | Barishal(N)-Madaripur 132 kV Ckt-2 Forced S/D from Barishal 230/132kV end Due to TCS -1
fail repair
| 15:48 | 16:22 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Scheduled S/D Due to 33KV underground cable
termination work
| 15:48 | 16:22 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Scheduled S/D Due to 33KV underground cable
termination work
| 16:05 |  | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 Project Work S/D from Rangpur 132/33kV end
Due to Reconducting
| 16:14 | 17:25 | Bogura(New)-Naogaon 132 kV Ckt-1 Forced S/D from Naogaon 132/33kV end Due to Removing the
string of kite. and from Bogura 230/132kVend.
| 16:16 |  | Bogura(New)-Naogaon 132 kV Ckt-2 Forced S/D from Naogaon 132/33kV end Due to Removing the
string of kite. and from Bogura 230/132kVend.
|  | 16:16 | Naogaon-Niyamatpur 132kV Ckt-1 is restored.
|  | 17:00 | GPH 230/33kV S/S Transformer-01(D05) HT is restored.
| 17:22 |  | Naogaon-Niyamatpur 132kV Ckt-1 Forced S/D from Niamatpur 132/33kV end Due to NLDC এর
নির্দেশে CB ( 102 B ) ওপেন করা হল .
| 18:12 | 18:32 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Forced S/D Due to New energy meter installation | [7 empty] | 56.0MW load
|  |  | by energy audit56 | [7 empty] | interrup.
| 18:38 | 18:46 | Kishoreganj 132/33kV S/S Tr-3 (424T) LT Forced S/D Due to New energy meter installation | [7 empty] | 44.0MW load
|  |  | by energy audit | [7 empty] | interrup.
| 19:30 |  | peak generation 15214 MW
| 19:30 |  | Evening peak generation 15214 MW
| 20:49 | 23:45 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
Maintenance work 330MW Shahjibazar end.
| 20:56 | 22:27 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Scheduled S/D from Mirsorai 230/33kV end Due to
bashundhara 230 kv project work
| 21:08 | 23:02 | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Agargaon 230/132kV end Due to For
Earthing pit Maintenance
| 00:05 |  | Bhola Nutan Biddyut CCPP GT-12 was shutdown due to offline water wash.
| 02:35 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- ST
| 02:44 |  | Ashuganj CCPP 225 MW Shutdown with remarks:- GT
| 03:33 |  | BIPTC S/S 20DF22 Tripped showing 87.1(Differential Relay) relays Due to C1 unbalance
60/61 CPR04 tripped
| 05:38 |  | GPH-Hathazari 230kV Ckt-1 Scheduled S/D from Hathazari 230/132/33kV end.
| 05:38 |  | Hathazari 230/132/33kV S/S AKSML-02 Scheduled S/D
| 05:48 |  | GPH 230/33kV S/S HATHAZARI Scheduled S/D Due to for Hathazari line maintenance
| 06:53 |  | Ashuganj-Kishoreganj 132kV Ckt-2 Project Work S/D from Ashuganj 230/132/33kV end.
| 07:00 |  | Minimum Generation: 11902 MW.
| 07:03 |  | Haripur-Narsingdi 132kV Ckt-1 Project Work S/D from Narshingdi 132/33kV end Due to LILO
Stringing work
| 07:31 |  | APR-Hasnabad 230kV Ckt-2 Scheduled S/D from Hasnabad 230/132kV end Due to High
temperature maintenance of 71 No Tower R Phase Jumper joint.
| 07:34 |  | Shyampur 230/132kV S/S 230 kV APR (D04) Scheduled S/D Due to Red hot on red phase Jumper
Connection point of Tower no 71 of 230 kV Hasnabad -Shyampur Ckt -2 (The work will be
done by Hasnabad SS)
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 22-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 401 | 9406800 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7816000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 289 | 7139869 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 372748 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 7076476 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 286560 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 2040480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 555152 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 49852 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14.5 | 340200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 345000 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 402720 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 2439792 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 768960 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 44 | 621120 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1334880 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 214485 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432000 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 280 | 7878181.82 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 200 | 3380991 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 1974000 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2528.5 | 54876266.82
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 150 | 3600000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 26231.4 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 53055 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 399840 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 941580 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 0 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 32 | 149709 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 72 | 460320 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 269348 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 91 | 1104000 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 353760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 14805 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 135491 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 38 | 163200 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1200 | 21610907 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 9 | 426240 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 10661818.18 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2291 | 40370304.58
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 189 | 4809000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8409900 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8154000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 31 | 748368 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 10 | 248160 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1181472 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 85 | 292727 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 16 | 764544 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 70 | 1784000 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4227360 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 42 | 998400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 384763 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 6 | 280590 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2661900 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 39 | 391440 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 1034880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 242545 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1627 | 36614049
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 12250 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 166 | 2925600 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 105 | 1615200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 281030 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 277680 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 283 | 5111760
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 35 | 756000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 40 | 871200 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 152 | 3466309.1 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 22 | 666816 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1970880 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 172 | 4582770 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 433000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 60336 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7430500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8926000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7678600 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1492 | 36842411.1
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 880 | 22032000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 131 | 3552768 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 123840 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 826128 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 648720 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 900 | 19323637 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 1928 | 46507093
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 678 | 13962240 | On test
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 216680 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2592000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1130 | 21025454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5154380 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5302000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3315 | -
Barishal Area Total |  |  |  |  | 2236 | 2456 | 48256069.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 154 | 3950009 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 160 | 3943655 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 350 | 8648000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 65771 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 234168 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 35136 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29400 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1456.93 | 25636637 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 346000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 677860 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2205.93 | 43566636
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1164218 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 157 | 3958000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 556080 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 46404.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 107 | 736201 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 132341 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1374480 | -
Rangpur Area Total |  |  |  |  | 950 | 404 | 7967724.36
Eastern Grid Total |  |  |  |  | 16771.895 | 8221.5 | 173814791.5
Western Grid Total |  |  |  |  | 10338.16 | 6993.93 | 146297522.91
National Grid Total |  |  |  |  | 27110.055 | 15215.43 | 320112314.41
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 22-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9992.39 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4681.5 | MW
i) Dhaka area |  |  | 5538.1 |  | MW | i) Khulna area |  |  |  | 1801.9 | MW
ii) Chattogram area |  |  | 1378.8 |  | MW | ii) Barishal area |  |  |  | 441 | MW
iii) Cumilla area |  |  | 1348.49 |  | MW | iii) Rajshahi area |  |  |  | 1465.6 | MW
iv) Mymensingh area |  |  | 1164 |  | MW | iv) Rangpur area |  |  |  | 973 | MW
v) Sylhet area |  |  | 563 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14673.89 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 81 | 19:00 | 133 | Patuakhali | 82 | 00:00
2 | AKSML | 115 | 04:00 | 68 | Jaldhaka | 76 | 19:30 | 134 | Payra | 34 | 00:00
3 | Aftabnagar | 38 | 13:00 | 69 | Jamalpur | 133 | 20:00 | 135 | Postogola | 58 | 13:00
4 | Agargaon | 127 | 14:00 | 70 | Jashore | 146 | 20:00 | 136 | Purbachal | 20 | 19:30
5 | Agrabad | 96 | 11:00 | 71 | Jhenaidah | 135 | 21:00 | 137 | Purbasadipur | 129 | 19:30
6 | Amnura | 37 | 23:00 | 72 | Joydebpur | 158 | 19:00 | 138 | Rahanpur | 30 | 23:00
7 | Ashuganj | 111 | 01:00 | 73 | Joypurhat | 60 | 20:00 | 139 | Rahim | 46 | 08:00
8 | BSRM | 195 | 08:00 | 74 | Juldah | 13 | 16:00 | 140 | Rajbari | 82 | 21:00
9 | Bagerhat | 86 | 00:00 | 75 | KSRM | 46 | 15:00 | 141 | Rajendrapur | 138 | 20:00
10 | Bajitpur | 48 | 19:30 | 76 | Kabirpur | 271 | 21:00 | 142 | Rajshahi | 115 | 23:00
11 | Bakulia | 103 | 13:00 | 77 | Kachua | 92 | 00:00 | 143 | Rajshahi-230 | 80 | 23:00
12 | Banani | 40 | 13:00 | 78 | Kallyanpur | 99 | 19:00 | 144 | Ramganj | 118 | 21:00
13 | Bangabhaban | 16 | 10:00 | 79 | Kalurghat | 26 | 09:00 | 145 | Rampur | 43 | 00:00
14 | Barapukuria | 66 | 20:00 | 80 | Kamrangirchar | 70 | 19:00 | 146 | Rangamati | 15 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 149 | 21:00
16 | Barishal | 126 | 12:00 | 82 | Kasba | 34 | 20:00 | 148 | Ruppur | 8 | 16:00
17 | Barishal-230 | 106 | 22:00 | 83 | Kazla | 100 | 19:00 | 149 | SSM | 13 | 01:00
18 | Baroaulia | 67 | 11:00 | 84 | Keranigonj | 95 | 19:30 | 150 | Saidpur | 110 | 19:30
19 | Baroirhat | 57 | 00:00 | 85 | Khagrachori | 30 | 19:00 | 151 | Satkhira | 137 | 19:30
20 | Bashundhara | 194 | 16:00 | 86 | Khulna | 79 | 22:00 | 152 | Satmasjid | 101 | 19:00
21 | BashundharaCement | 11 | 17:00 | 87 | Khulshi | 183 | 12:00 | 153 | Savar | 216 | 16:00
22 | Beanibazar | 66 | 19:30 | 88 | Kishoreganj | 134 | 20:00 | 154 | SevenRings | 15 | 03:00
23 | Benapole | 68 | 19:30 | 89 | Kodda | 308 | 08:00 | 155 | ShahCement | 20 | 12:00
24 | Bhaluka | 157 | 21:00 | 90 | Kulaura | 40 | 19:00 | 156 | Shahjadpur | 82 | 12:00
25 | Bhandaria | 54 | 00:00 | 91 | Kurigram | 64 | 19:30 | 157 | Shahjibazar | 120 | 21:00
26 | Bhangura | 37 | 21:00 | 92 | Kushtia | 160 | 23:00 | 158 | Shahmirpur | 59 | 00:00
27 | Bheramara(GK) | 68 | 22:00 | 93 | Lalbag | 58 | 18:30 | 159 | Shariatpur | 88 | 23:00
28 | Bhulta | 241 | 14:00 | 94 | Lalmonirhat | 61 | 19:30 | 160 | Sherpur | 144 | 19:30
29 | Bog-Sherpur | 70 | 19:30 | 95 | MI_Cement | 15 | 13:00 | 161 | Shikalbaha | 29 | 00:00
30 | Bogura | 174 | 21:00 | 96 | Madanganj | 48 | 11:00 | 162 | Shitalakhya | 88 | 12:00
31 | Borhanuddin | 89 | 22:00 | 97 | Madaripur | 115 | 23:00 | 163 | Sholosohor | 48 | 12:00
32 | Brahmanbaria | 124 | 22:00 | 98 | Madartek | 84 | 23:00 | 164 | Shyampur | 194 | 11:00
33 | Cantonment | 142 | 13:00 | 99 | Madunaghat | 52 | 00:00 | 165 | Siddhirganj | 122 | 19:00
34 | Chandina | 21 | 11:00 | 100 | Magura | 66 | 19:00 | 166 | Sirajganj | 112 | 20:00
35 | Chandpur | 75 | 21:00 | 101 | Mahasthangarh | 78 | 20:00 | 167 | Sonargaon | 125 | 18:00
36 | Chandraghona | 33 | 01:00 | 102 | Manikganj | 140 | 20:00 | 168 | Sreemongol | 72 | 22:00
37 | Chapai | 68 | 21:00 | 103 | Maniknagar | 72 | 13:00 | 169 | Sreepur | 104 | 20:00
38 | Charsaidpur | 41 | 10:00 | 104 | Matarbari | 47 | 00:00 | 170 | Srinagar | 47 | 22:00
39 | Chauddagram | 73 | 22:00 | 105 | Matuail | 68 | 10:00 | 171 | Sunamganj | 56 | 19:30
40 | Chhatak | 35 | 19:30 | 106 | Millgate | 113 | 09:00 | 172 | Sylhet | 47 | 19:00
41 | Chowmuhani | 223 | 19:30 | 107 | Mirpur | 122 | 19:00 | 173 | Sylhet-132 | 103 | 20:00
42 | Chuadanga | 111 | 21:00 | 108 | Mirsorai | 11 | 10:00 | 174 | TK | 34 | 00:00
43 | Coxsbazar | 126 | 21:00 | 109 | Mirzapur | 47 | 20:00 | 175 | Tangail | 174 | 20:00
44 | Cumilla(N) | 144 | 01:00 | 110 | Mithapukur | 64 | 19:00 | 176 | Thakurgaon | 107 | 20:00
45 | Cumilla(S) | 187 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 125 | 21:00
46 | Daudkandi | 147 | 19:00 | 112 | Mogbazar | 147 | 16:00 | 178 | Ullahpara | 40 | 19:00
47 | Dhaka | 62 | 13:00 | 113 | Mongla | 44 | 19:30 | 179 | Ullon | 49 | 20:00
48 | Dhamrai | 134 | 15:00 | 114 | Motijheel | 37 | 13:00 | 180 | Uttara | 83 | 16:00
49 | Dhanmondi | 146 | 16:00 | 115 | Muktagacha | 35 | 21:00 | 181 | UttaraNew | 59 | 19:00
50 | Dohazari | 103 | 00:00 | 116 | Munshiganj | 109 | 20:00 | 182 | Zigatola | 72 | 20:00
51 | Faridpur | 167 | 22:00 | 117 | Muradnagar | 27 | 21:00
52 | Fatullah | 106 | 12:00 | 118 | Mymensingh | 200 | 21:00
53 | Fenchuganj | 35 | 18:30 | 119 | Naogaon | 134 | 21:00
54 | Feni | 117 | 19:00 | 120 | Narail | 61 | 19:30
55 | GPH | 27 | 01:00 | 121 | Narinda | 82 | 13:00
56 | Ghatail | 80 | 19:00 | 122 | Narshingdi | 174 | 19:30
57 | Ghorashal | 17 | 19:30 | 123 | Natore | 173 | 20:00
58 | Ghorashal-230 | 100 | 21:00 | 124 | Nawabganj | 58 | 22:00
59 | Goalpara | 46 | 00:00 | 125 | Netrakona | 114 | 23:00
60 | Gollamari | 94 | 00:00 | 126 | New | 90 | 21:00
61 | Gopalganj | 110 | 00:00 | 127 | Niamatpur | 72 | 22:00
62 | Gulshan | 120 | 15:00 | 128 | Noapara | 48 | 20:00
63 | Halishahar | 84 | 14:00 | 129 | PHP | 8 | 01:00
64 | HaripurSBU | 192 | 11:00 | 130 | Pabna | 126 | 19:30
65 | Hasnabad | 67 | 19:00 | 131 | Palashbari | 112 | 19:00
66 | Hathazari | 81 | 00:00 | 132 | Panchagarh | 62 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 22-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 12843 | 23 |  | 12867.04
1:00 | 12849.2 | 25 |  | 12875.2
2:00 | 12638.2 | 21 |  | 12660.2
3:00 | 12158.2 | 21 |  | 12180.2
4:00 | 11832.2 | 22 |  | 11855.2
5:00 | 11729.2 | 20 |  | 11750.2
6:00 | 11205.9 | 10 |  | 11215.9
7:00 | 11634.77 | 16 |  | 11651.77
8:00 | 11762.28 | 19 |  | 11782.28
9:00 | 12076.92 | 20 |  | 12097.92
10:00 | 12731.64 | 31 |  | 12763.64
11:00 | 12849.75 | 32 |  | 12882.75
12:00 | 13337.82 | 37 |  | 13376.82
13:00 | 13548.62 | 37 |  | 13587.62
14:00 | 13529.11 | 32 |  | 13562.11
15:00 | 13498.75 | 43 |  | 13543.75
16:00 | 13547.89 | 72 |  | 13622.89
17:00 | 13367.36 | 53 |  | 13422.36
18:00 | 13101.92 | 50 |  | 13153.92
19:00 | 14571.9 | 47 |  | 14620.9
19:30 | 15215.43 | 63 |  | 15281.43
20:00 | 14981.88 | 66 |  | 15050.88
21:00 | 15050.42 | 68 |  | 15121.42
22:00 | 15018.54 | 78 |  | 15100.54
23:00 | 14805.26 | 138 |  | 14949.26
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 22-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7134 | 5709 | 12843 | DAILY GENERATION CURVE
00:30 | 7141.6 | 5704.5 | 12846.1
01:00 | 7149.2 | 5700 | 12849.2 | 22-05-2025
01:30 | 7086.2 | 5657.5 | 12743.7
02:00 | 7023.2 | 5615 | 12638.2
02:30 | 6913.7 | 5484.5 | 12398.2
03:00 | 6804.2 | 5354 | 12158.2
03:30 | 6701.7 | 5293.5 | 11995.2
04:00 | 6599.2 | 5233 | 11832.2
04:30 | 6570.2 | 5210.5 | 11780.7
05:00 | 6541.2 | 5188 | 11729.2
05:30 | 6346.865 | 5120.685 | 11467.55
06:00 | 6152.53 | 5053.37 | 11205.9
06:30 | 6318.645 | 5101.69 | 11420.335
07:00 | 6484.76 | 5150.01 | 11634.77
07:30 | 6516.25 | 5182.275 | 11698.525
08:00 | 6547.74 | 5214.54 | 11762.28
08:30 | 6568.965 | 5350.635 | 11919.6
09:00 | 6590.19 | 5486.73 | 12076.92
09:30 | 6762.28 | 5642 | 12404.28
10:00 | 6934.37 | 5797.27 | 12731.64
10:30 | 6962.27 | 5828.425 | 12790.695
11:00 | 6990.17 | 5859.58 | 12849.75
11:30 | 7006.34 | 6087.445 | 13093.785
12:00 | 7022.51 | 6315.31 | 13337.82
12:30 | 7172.645 | 6270.575 | 13443.22
13:00 | 7322.78 | 6225.84 | 13548.62
13:30 | 7250.62 | 6288.245 | 13538.865
14:00 | 7178.46 | 6350.65 | 13529.11
14:30 | 7193.575 | 6320.355 | 13513.93
15:00 | 7208.69 | 6290.06 | 13498.75
15:30 | 7222.14 | 6301.18 | 13523.32
16:00 | 7235.59 | 6312.3 | 13547.89
16:30 | 7224.815 | 6232.81 | 13457.625
17:00 | 7214.04 | 6153.32 | 13367.36
17:30 | 7211.605 | 6023.035 | 13234.64
18:00 | 7209.17 | 5892.75 | 13101.92
18:30 | 7662.335 | 6174.575 | 13836.91
19:00 | 8115.5 | 6456.4 | 14571.9
19:30 | 8221.5 | 6993.93 | 15215.43
20:00 | 8047.5 | 6934.38 | 14981.88
20:30 | 7985.5 | 7030.65 | 15016.15 |  | Executive Engineer
21:00 | 7923.5 | 7126.92 | 15050.42 |  | Network Operation Division
21:30 | 7909 | 7125.48 | 15034.48
22:00 | 7894.5 | 7124.04 | 15018.54
22:30 | 7766.75 | 7145.15 | 14911.9
23:00 | 7639 | 7166.26 | 14805.26

## En-Curve
QF-LDC-12
Date | 22-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3611 | 2010 | 927 | 0 | 40 | 1011 | 39 | 3983 | 0 | 303 | 905 | 0 | 0 | 14 | 23 | DAILY ENERGY CURVE
00:30 | 3621 | 2033 | 922.5 | 0 | 40 | 1014 | 39.5 | 3991.5 | 0 | 295.5 | 879.6 | 0 | 0 | 9.5 | 24 | 22-05-2025
01:00 | 3631 | 2056 | 918 | 0 | 40 | 1017 | 40 | 4000 | 0 | 288 | 854.2 | 0 | 0 | 5 | 25
01:30 | 3575 | 2043 | 918 | 0 | 38 | 1017 | 40 | 3996.5 | 0 | 279 | 830.7 | 0 | 0 | 6.5 | 23 | Energy Generated | 320.1123 |  | MKWHr
02:00 | 3519 | 2030 | 918 | 0 | 36 | 1017 | 40 | 3993 | 0 | 270 | 807.2 | 0 | 0 | 8 | 21 | Energy not Served | 0.981 |  | MKWHr
02:30 | 3508 | 2010 | 918.5 | 0 | 36 | 966 | 40 | 3896 | 0 | 254 | 764.2 | 0 | 0 | 5.5 | 21 | Total Energy Requirement | 321.0933 |  | MKWHr
03:00 | 3497 | 1990 | 919 | 0 | 36 | 915 | 40 | 3799 | 0 | 238 | 721.2 | 0 | 0 | 3 | 21
03:30 | 3517 | 1983 | 922.5 | 0 | 36 | 870 | 40 | 3706 | 0 | 228 | 691.2 | 0 | 0 | 1.5 | 21.5
04:00 | 3537 | 1976 | 926 | 0 | 36 | 825 | 40 | 3613 | 0 | 218 | 661.2 | 0 | 0 | 0 | 22
04:30 | 3522 | 1960 | 926.5 | 0 | 35 | 825 | 40 | 3594.5 | 0 | 218 | 659.7 | 0 | 0 | 0 | 21
05:00 | 3507 | 1944 | 927 | 0 | 34 | 825 | 40 | 3576 | 0 | 218 | 658.2 | 0 | 0 | 0 | 20
05:30 | 3503.5 | 1855 | 926.5 | 0 | 33 | 826 | 40 | 3435.5 | 18.95 | 208.5 | 620.6 | 0 | 0 | 0 | 15
06:00 | 3500 | 1766 | 926 | 0 | 32 | 827 | 40 | 3295 | 37.9 | 199 | 583 | 0 | 0 | 0 | 10
06:30 | 3615.5 | 1769 | 925.5 | 0 | 32 | 827 | 40 | 3289.5 | 82.835 | 190.5 | 644 | 0 | 0 | 4.5 | 13
07:00 | 3731 | 1772 | 925 | 0 | 32 | 827 | 40 | 3284 | 127.77 | 182 | 705 | 0 | 0 | 9 | 16
07:30 | 3746 | 1776.5 | 902.5 | 0 | 31 | 827 | 40 | 3286 | 191.025 | 181.5 | 704 | 0 | 0 | 13 | 17.5
08:00 | 3761 | 1781 | 880 | 0 | 30 | 827 | 40 | 3288 | 254.28 | 181 | 703 | 0 | 0 | 17 | 19
08:30 | 3755.5 | 1771 | 879.5 | 0 | 35 | 829.5 | 39.5 | 3378.5 | 285.1 | 211.5 | 699 | 0 | 0 | 35.5 | 19.5
09:00 | 3750 | 1761 | 879 | 0 | 40 | 832 | 39 | 3469 | 315.92 | 242 | 695 | 0 | 0 | 54 | 20
09:30 | 3769 | 1884 | 903 | 0 | 39 | 856.5 | 39 | 3552.5 | 368.78 | 245.5 | 708 | 0 | 0 | 39 | 25.5
10:00 | 3788 | 2007 | 927 | 0 | 38 | 881 | 39 | 3636 | 421.64 | 249 | 721 | 0 | 0 | 24 | 31
10:30 | 3792 | 1982.5 | 927 | 0 | 42 | 877.5 | 38 | 3609.5 | 496.695 | 257.5 | 743 | 0 | 0 | 25 | 31.5
11:00 | 3796 | 1958 | 927 | 0 | 46 | 874 | 37 | 3583 | 571.75 | 266 | 765 | 0 | 0 | 26 | 32
11:30 | 3819 | 1933 | 927 | 0 | 47 | 928.5 | 37.5 | 3687 | 575.785 | 311 | 799.5 | 0 | 0 | 28.5 | 34.5
12:00 | 3842 | 1908 | 927 | 0 | 48 | 983 | 38 | 3791 | 579.82 | 356 | 834 | 0 | 0 | 31 | 37
12:30 | 3861.5 | 1931.5 | 927 | 0 | 49 | 1006.5 | 38 | 3853 | 509.22 | 356 | 873 | 0 | 0 | 38.5 | 37
13:00 | 3881 | 1955 | 927 | 0 | 50 | 1030 | 38 | 3915 | 438.62 | 356 | 912 | 0 | 0 | 46 | 37
13:30 | 3805.5 | 1927.75 | 927 | 0 | 50 | 1074 | 39 | 3948 | 454.615 | 338 | 922 | 0 | 0 | 53 | 34.5
14:00 | 3730 | 1900.5 | 927 | 0 | 50 | 1118 | 40 | 3981 | 470.61 | 320 | 932 | 0 | 0 | 60 | 32
14:30 | 3785.5 | 1942.5 | 927 | 0 | 50 | 1122.725 | 40 | 3990.5 | 398.705 | 320 | 888 | 0 | 0 | 49 | 37.5
15:00 | 3841 | 1984.5 | 927 | 0 | 50 | 1127.45 | 40 | 4000 | 326.8 | 320 | 844 | 0 | 0 | 38 | 43
15:30 | 3809.5 | 1969 | 927 | 0 | 50 | 1148.675 | 40 | 4040.5 | 289.645 | 320 | 906.5 | 0 | 0 | 22.5 | 57.5
16:00 | 3778 | 1953.5 | 927 | 0 | 50 | 1169.9 | 40 | 4081 | 252.49 | 320 | 969 | 0 | 0 | 7 | 72
16:30 | 3705 | 1959.5 | 926.5 | 0 | 53 | 1169.41 | 40 | 4082 | 191.715 | 328.5 | 990 | 0 | 0 | 12 | 62.5
17:00 | 3632 | 1965.5 | 926 | 0 | 56 | 1168.92 | 40 | 4083 | 130.94 | 337 | 1011 | 0 | 0 | 17 | 53
17:30 | 3573 | 1938 | 926 | 0 | 55 | 1168.075 | 40 | 4020 | 82.065 | 366.5 | 1053.5 | 0 | 0 | 12.5 | 51.5
18:00 | 3514 | 1910.5 | 926 | 0 | 54 | 1167.23 | 40 | 3957 | 33.19 | 396 | 1096 | 0 | 0 | 8 | 50
18:30 | 3637 | 1941.5 | 902.5 | 0 | 58 | 1240.815 | 40 | 4281 | 16.595 | 438 | 1275 | 0 | 0 | 6.5 | 48.5
19:00 | 3760 | 1972.5 | 879 | 0 | 62 | 1314.4 | 40 | 4605 | 0 | 480 | 1454 | 0 | 0 | 5 | 47
19:30 | 3645 | 1948.5 | 880 | 0 | 42 | 1456.93 | 40 | 4997 | 0 | 475 | 1722 | 0 | 0 | 9 | 63
20:00 | 3657 | 1954.5 | 880 | 0 | 42 | 1452.38 | 40 | 4841 | 0 | 493 | 1608 | 0 | 0 | 14 | 66
20:30 | 3684.5 | 1942.5 | 901.5 | 0 | 42 | 1453.65 | 39.5 | 4931 | 0 | 485 | 1527 | 0 | 0 | 9.5 | 67
21:00 | 3712 | 1930.5 | 923 | 0 | 42 | 1454.92 | 39 | 5021 | 0 | 477 | 1446 | 0 | 0 | 5 | 68
21:30 | 3702.5 | 1946 | 903.5 | 0 | 41 | 1458.98 | 38 | 5046 | 0 | 488.5 | 1397.5 | 0 | 0 | 12.5 | 73
22:00 | 3693 | 1961.5 | 884 | 0 | 40 | 1463.04 | 37 | 5071 | 0 | 500 | 1349 | 0 | 0 | 20 | 78
22:30 | 3654.5 | 1953.75 | 881.5 | 0 | 41 | 1458.15 | 37 | 5022 | 0 | 495.5 | 1351.5 | 0 | 0 | 17 | 108
23:00 | 3616 | 1946 | 879 | 0 | 42 | 1453.26 | 37 | 4973 | 0 | 491 | 1354 | 0 | 0 | 14 | 138
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 22-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 05:00 | 367 | 23:00 | Payra | 416 | 05:00 | 407 | 22:00
Ashuganj | 394 | 5:00 | 384 | 23:00 | Rahanpur | 413 | 05:00 | 387 | 21:00
Bhulta | 393 | 05:00 | 363 | 15:00 | Rampal | 403 | 05:00 | 385 | 22:00
Bibiana | 393 | 05:00 | 384 | 21:00
BIPTC | 405 | 04:00 | 393 | 23:00
Bogura | 405 | 05:00 | 373 | 19:30
Gopalganj | 397 | 06:00 | 378 | 21:00
Kaliakoir | 375 | 05:00 | 358 | 19:00
Madunaghat | 394 | 06:00 | 385 | 22:00
Meghnaghat | 388 | 05:00 | 373 | 21:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 05:00 | 212 | 15:00 | Keranigonj | 221 | 05:00 | 211 | 15:00
AKSML | 229 | 05:00 | 223 | 01:00 | Khulna(S) | 233 | 05:00 | 214 | 21:00
Aminbazar | 224 | 05:00 | 214 | 14:00 | Madunaghat | 231 | 06:00 | 226 | 00:00
Ashuganj | 229 | 05:00 | 215 | 21:00 | Madunaghat-400 | 232 | 06:00 | 227 | 00:00
Ashuganj-400 | 220 | 5:00 | 216 | 23:00 | Maniknagar | 216 | 04:00 | 210 | 12:00
Baghabari | 235 | 04:00 | 222 | 19:00 | Meghnaghat | 228 | 05:00 | 220 | 00:00
Barapukuria | 227 | 04:00 | 213 | 19:30 | Meghnaghat-400 | 223 | 06:00 | 215 | 15:00
Barapukuria-230 | 226 | 4:00 | 215 | 18:00 | Mirsorai | 225 | 06:00 | 218 | 16:00
Barishal | 237 | 07:00 | 226 | 21:00 | Rajshahi | 235 | 00:00 | 220 | 19:30
Bheramara | 234 | 00:00 | 222 | 13:00 | Rampal | 232 | 05:00 | 215 | 22:00
Bhulta | 228 | 05:00 | 209 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 07:00 | 218 | 19:30 | Rampura | 227 | 06:00 | 205 | 19:00
BIPTC | 237 | 01:00 | 222 | 13:00 | Shikalbaha | 228 | 06:00 | 223 | 00:00
Bogura | 234 | 05:00 | 215 | 21:00 | Shyampur | 221 | 06:00 | 212 | 15:00
Bogura-400 | 233 | 00:00 | 215 | 21:00 | Siddhirganj | 219 | 06:00 | 213 | 15:00
Borhanuddin | 241 | 06:00 | 233 | 22:00 | Sirajgonj | 240 | 05:00 | 229 | 19:30
BSRM | 226 | 07:00 | 217 | 22:00 | Sreepur | 228 | 05:00 | 215 | 21:00
Cumilla(N) | 221 | 06:00 | 210 | 22:00 | Tongi | 218 | 04:00 | 206 | 18:30
Faridpur | 234 | 06:00 | 220 | 21:00
Fenchuganj | 227 | 10:00 | 221 | 01:00
Ghorashal | 235 | 06:00 | 220 | 00:00
Ghorashal-230 | 226 | 05:00 | 208 | 19:00
Gopalganj | 235 | 05:00 | 223 | 21:00
GPH | 228 | 06:00 | 222 | 00:00
Haripur | 219 | 05:00 | 212 | 15:00
Hasnabad | 221 | 03:00 | 212 | 12:00
Hathazari | 230 | 04:00 | 225 | 00:00
Ishurdi | 236 | 00:00 | 223 | 19:30
Jhenaidah | 233 | 05:00 | 214 | 19:30
Kaliakoir | 230 | 05:00 | 216 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 05:00 | 125 | 15:00 | Madartek | 139 | 05:00 | 124 | 19:00
Agargaon | 134 | 05:00 | 127 | 13:00 | Madunaghat | 132 | 20:00 | 120 | 10:00
Agrabad | 130 | 05:00 | 126 | 23:00 | Magura | 136 | 01:00 | 120 | 21:00
AKS | 129 | 08:00 | 126 | 00:00 | Mahasthangarh | 138 | 00:00 | 122 | 21:00
Aminbazar | 130 | 05:00 | 124 | 10:00 | Manikganj | 127 | 05:00 | 121 | 16:00
Amnura | 137 | 00:00 | 123 | 22:00 | Maniknagar | 131 | 04:00 | 125 | 15:00
Ashuganj | 137 | 06:00 | 130 | 19:00 | Matarbari | 124 | 04:00 | 108 | 00:00
Bagerhat | 134 | 06:00 | 116 | 19:30 | Matuail | 127 | 04:00 | 123 | 16:00
Bajitpur | 132 | 06:00 | 121 | 19:00 | Millgate | 153 | 21:00 | 123 | 19:00
Bakulia | 131 | 05:00 | 128 | 00:00 | Mirpur | 129 | 05:00 | 123 | 10:00
Banani | 139 | 05:00 | 124 | 17:00 | Mirzapur | 134 | 07:00 | 125 | 19:00
Bangabhaban | 131 | 04:00 | 125 | 15:00 | Mithapukur | 134 | 00:00 | 120 | 21:00
Barapukuria | 135 | 00:00 | 122 | 19:30 | MI_Cement | 130 | 07:00 | 123 | 12:00
Barguna | 135 | 08:00 | 129 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 05:00 | 125 | 00:00 | Mogbazar | 138 | 07:00 | 125 | 15:00
Barishal-230 | 132 | 07:00 | 123 | 22:00 | Mongla | 135 | 06:00 | 117 | 22:00
Baroaulia | 132 | 00:00 | 128 | 10:00 | Motijheel | 131 | 04:00 | 125 | 15:00
Baroirhat | 124 | 07:00 | 118 | 22:00 | Muktagacha | 136 | 00:00 | 124 | 19:00
Bashundhara | 139 | 03:00 | 122 | 22:00 | Munshiganj | 127 | 04:00 | 121 | 11:00
BashundharaCement | 127 | 01:00 | 122 | 12:00 | Muradnagar | 124 | 05:00 | 117 | 22:00
Beanibazar | 132 | 05:00 | 125 | 19:30 | Mymensingh | 137 | 00:00 | 112 | 19:00
Benapole | 134 | 05:00 | 116 | 19:00 | Naogaon | 135 | 04:00 | 107 | 20:00
Bhaluka | 131 | 06:00 | 120 | 19:00 | Narail | 140 | 05:00 | 120 | 21:00
Bhandaria | 127 | 18:00 | 115 | 21:00 | Narinda | 131 | 4:00 | 125 | 15:00
Bhangura | 136 | 05:00 | 125 | 19:30 | Narshingdi | 126 | 07:00 | 116 | 00:00
Bheramara | 137 | 00:00 | 129 | 19:30 | Natore | 137 | 00:00 | 125 | 19:30
Bheramara(GK) | 137 | 00:00 | 129 | 14:00 | Nawabganj | 132 | 06:00 | 124 | 19:00
Bhulta | 120 | 04:00 | 114 | 15:00 | Netrakona | 128 | 05:00 | 111 | 19:00
Bog-Sherpur | 137 | 00:00 | 122 | 21:00 | New | 137 | 06:00 | 124 | 19:00
Bogura | 139 | 05:00 | 126 | 21:00 | Niamatpur | 137 | 05:00 | 127 | 21:00
Bogura-230 | 140 | 00:00 | 125 | 21:00 | Noapara | 137 | 04:00 | 120 | 21:00
Brahmanbaria | 127 | 07:00 | 119 | 19:00 | Pabna | 137 | 00:00 | 125 | 19:30
Cantonment | 135 | 05:00 | 126 | 15:00 | Palashbari | 135 | 00:00 | 117 | 21:00
Chandina | 126 | 05:00 | 120 | 22:00 | Panchagarh | 135 | 05:00 | 118 | 15:00
Chandpur | 129 | 18:30 | 119 | 00:00 | Patuakhali | 135 | 07:00 | 130 | 23:00
Chandraghona | 131 | 07:00 | 127 | 10:00 | Payra | 136 | 06:00 | 133 | 19:00
Chapai | 135 | 05:00 | 124 | 22:00 | PHP | 123 | 08:00 | 117 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 128 | 06:00 | 123 | 15:00 | Postogola | 132 | 05:00 | 126 | 10:00
Chauddagram | 123 | 18:00 | 116 | 00:00 | Purbachal | 139 | 02:00 | 124 | 16:00
Chhatak | 131 | 02:00 | 122 | 23:00 | Purbasadipur | 131 | 04:00 | 115 | 13:00
Chowmuhani | 120 | 18:30 | 110 | 00:00 | Rahanpur | 138 | 04:00 | 128 | 21:00
Chuadanga | 138 | 06:00 | 119 | 22:00 | Rahanpur-400 | 138 | 00:00 | 128 | 22:00
Coxsbazar | 120 | 15:00 | 110 | 00:00 | Rahim | 128 | 05:00 | 123 | 12:00
Cumilla(N) | 129 | 19:00 | 120 | 21:00 | Rajbari | 136 | 05:00 | 125 | 21:00
Cumilla(S) | 132 | 02:00 | 119 | 00:00 | Rajendrapur | 133 | 06:00 | 117 | 21:00
Daudkandi | 122 | 04:00 | 116 | 22:00 | Rajshahi | 137 | 00:00 | 126 | 19:00
Dhaka | 139 | 07:00 | 125 | 16:00 | Rajshahi-230 | 137 | 00:00 | 117 | 23:00
Dhamrai | 135 | 04:00 | 126 | 15:00 | Ramganj | 120 | 09:00 | 110 | 02:00
Dhanmondi | 140 | 05:00 | 125 | 19:00 | Rampur | 131 | 06:00 | 126 | 10:00
Dohazari | 128 | 18:00 | 121 | 00:00 | Rampura | 140 | 06:00 | 124 | 19:00
Faridpur | 136 | 05:00 | 127 | 21:00 | Rangamati | 130 | 06:00 | 126 | 00:00
Fatullah | 129 | 05:00 | 123 | 12:00 | Rangpur | 132 | 00:00 | 117 | 21:00
Fenchuganj | 135 | 08:00 | 131 | 22:00 | Ruppur | 138 | 03:00 | 129 | 22:00
Feni | 124 | 09:00 | 115 | 22:00 | Saidpur | 130 | 04:00 | 117 | 19:30
Ghatail | 132 | 00:00 | 121 | 19:00 | Satkhira | 136 | 06:00 | 116 | 19:00
Ghorashal | 135 | 05:00 | 126 | 19:00 | Satmasjid | 134 | 05:00 | 126 | 13:00
Goalpara | 139 | 05:00 | 124 | 22:00 | Savar | 128 | 06:00 | 122 | 10:00
Gollamari | 138 | 05:00 | 125 | 19:00 | SevenRings | 136 | 06:00 | 126 | 19:00
Gopalganj | 136 | 05:00 | 124 | 22:00 | ShahCement | 128 | 06:00 | 123 | 15:00
Gopalganj-400 | 137 | 06:00 | 128 | 22:00 | Shahjadpur | 135 | 00:00 | 130 | 21:00
Gulshan | 140 | 05:00 | 125 | 17:00 | Shahjibazar | 131 | 06:00 | 122 | 19:30
Halishahar | 132 | 05:00 | 126 | 10:00 | Shahmirpur | 131 | 09:00 | 128 | 00:00
Haripur | 128 | 05:00 | 123 | 12:00 | Shariatpur | 135 | 06:00 | 124 | 22:00
HaripurSBU | 127 | 05:00 | 123 | 12:00 | Sherpur | 140 | 00:00 | 125 | 19:00
Hasnabad | 131 | 07:00 | 125 | 15:00 | Shikalbaha | 121 | 06:00 | 116 | 00:00
Hathazari | 135 | 19:00 | 130 | 00:00 | Shikalbaha-230 | 132 | 06:00 | 128 | 00:00
Ishurdi | 139 | 00:00 | 130 | 19:30 | Shitalakhya | 130 | 07:00 | 123 | 12:00
Jaldhaka | 129 | 05:00 | 114 | 19:30 | Sholosohor | 131 | 18:00 | 126 | 00:00
Jamalpur | 140 | 00:00 | 128 | 19:00 | Shyampur | 127 | 01:00 | 125 | 00:00
Jashore | 135 | 06:00 | 117 | 21:00 | Shyampur-230 | 128 | 05:00 | 123 | 12:00
Jhenaidah | 139 | 05:00 | 117 | 19:00 | Siddhirganj | 127 | 04:00 | 123 | 15:00
Jhenaidah-230 | 139 | 05:00 | 124 | 19:00 | Sirajganj | 135 | 00:00 | 121 | 21:00
Joydebpur | 135 | 04:00 | 125 | 00:00 | Sonargaon | 127 | 03:00 | 120 | 17:00
Joypurhat | 133 | 06:00 | 106 | 21:00 | Sreemongol | 131 | 05:00 | 123 | 19:30
Juldah | 130 | 07:00 | 128 | 00:00 | Sreepur | 133 | 05:00 | 124 | 19:00
Kabirpur | 134 | 07:00 | 121 | 19:00 | Srinagar | 132 | 05:00 | 124 | 19:00
Kachua | 125 | 18:00 | 117 | 00:00 | SSM | 134 | 00:00 | 130 | 01:00
Kaliakoir | 137 | 04:00 | 129 | 16:00 | Sunamganj | 130 | 03:00 | 122 | 19:30
Kallyanpur | 129 | 07:00 | 124 | 10:00 | Sylhet | 132 | 03:00 | 127 | 19:30
Kalurghat | 130 | 05:00 | 127 | 00:00 | Sylhet-132 | 132 | 06:00 | 128 | 19:00
Kamrangirchar | 133 | 05:00 | 123 | 14:00 | Tangail | 132 | 00:00 | 121 | 19:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 135 | 05:00 | 119 | 14:00
Kasba | 124 | 05:00 | 117 | 21:00 | TK | 130 | 18:00 | 126 | 21:00
Kazla | 131 | 03:00 | 125 | 13:00 | Tongi | 134 | 04:00 | 126 | 15:00
Keranigonj | 133 | 05:00 | 125 | 15:00 | Ullahpara | 136 | 00:00 | 124 | 19:00
Khagrachori | 130 | 18:00 | 125 | 00:00 | Ullon | 140 | 05:00 | 125 | 15:00
Khulna | 137 | 05:00 | 122 | 19:00 | Uttara | 130 | 06:00 | 122 | 12:00
Khulna(S) | 139 | 05:00 | 125 | 19:00 | UttaraNew | 131 | 01:00 | 123 | 10:00
Khulshi | 130 | 20:00 | 126 | 00:00 | Zigatola | 132 | 05:00 | 124 | 18:30
Kishoreganj | 130 | 06:00 | 116 | 19:00
Kodda | 131 | 02:00 | 119 | 15:00
KSRM | 132 | 20:00 | 127 | 17:00
Kulaura | 135 | 08:00 | 129 | 23:00
Kurigram | 130 | 03:00 | 115 | 19:00
Kushtia | 135 | 03:00 | 123 | 19:00
Lalbag | 132 | 05:00 | 124 | 19:00
Lalmonirhat | 131 | 00:00 | 117 | 22:00
Madanganj | 127 | 07:00 | 122 | 12:00
Madaripur | 135 | 06:00 | 126 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division