## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 25-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-05-2025 | during | 25-05-2025 | during | 25-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 190 | 190 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 339 | 316 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 340 | 450 | 450 | 300 | 300 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 250 | 300 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 240 | 267 | 335 | 335 | 250 | 250 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 16 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 19 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 47 | 144 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 32 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.5 | 0 | 33 | 33 | 17.5 | 17.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 15 | 15 | 22 | 22 | 17 | 17 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 16 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 112 | 112 | 135 | 135 | 135 | 135 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 69 | 90 | 90 | 68 | 68 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 126 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 280 | 280 | -
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 450 | 583 | 583 | 420 | 420 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 142 | 142 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 2349.5 | 2752 | 5237.1 | 5229.1 | 3472.12 | 3472.12
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 100 | 100 | 150 | 150 | 150 | 150 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 6 | 0 | 10 | 0 | 10 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 33 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 36 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 2 | 81 | 72 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 34 | 34 | 34 | 34 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 75 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 8 | 2 | 22 | 2 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 35 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 0.85 | 0 | 0.85 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 60 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 0 | 10 | 12 | 10 | 12 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 568 | 571 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2015 | 2294 | 3346.57 | 3357.72 | 3330.57 | 3357.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 183 | 192 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 348 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 34 | 46.7 | 46.7 | 31 | 31 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 30 | 55 | 55 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 167 | 167 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 20 | 62 | 150 | 150 | 130 | 130 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 39 | 47 | 47 | 47 | 47
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 85 | 85 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 51 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 36 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 70 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 57 | 9 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 60 | 92 | 115 | 115 | 93 | 93 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 40 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1400 | 1560.2 | 2434 | 2394 | 2174.55 | 2134.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 24-05-2025 | during | 25-05-2025 | during | 25-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 0 | 0 | 0 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 121 | 170 | 200 | 200 | 160 | 160 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 104 | 115 | 115 | 102 | 102 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 48.95 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 251.95 | 303 | 597 | 549 | 376.5 | 328.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 0 | 30 | 0 | 0 | 0 | 0 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 38 | 37 | 40 | 40 | 40 | 40 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 152 | 134 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 20 | 20 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 80 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 172 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 12 | 10 | 25 | 25 | 12 | 12 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 315 | 339 | 385 | 385 | 385 | 385 | -
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1431 | 1460 | 1575 | 1575 | 1512 | 1512
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 910 | 910 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 165 | 142 | 410 | 410 | 187 | 187 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 78.53 | 0 | 65 | 0 | 65 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 791 | 1166 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1944.53 | 2253 | 3579.2 | 3514.2 | 3341.2 | 3276.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 298 | 308 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 7 | 10 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 90 | 110 | 130 | 130 | 120 | 120 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 920 | 1114 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 110 | 130 | 220 | 220 | 110 | 120 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.03 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1575.03 | 1979 | 2172 | 2171 | 2052 | 2061
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 172 | 169 | 214 | 214 | 214 | 214
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 163 | 156 | 220 | 220 | 220 | 220
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 360 | 414 | 413.79 | 413.79 | 372.41 | 372.41 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 33 | 97 | 97 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 100 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.9 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1107 | 1449 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 61.4 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 96 | 0 | 95 | 0 | 95 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1965.3 | 2343 | 3189.72 | 3027.87 | 3147.34 | 2985.49
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 154 | 158 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 49 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.4 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 21 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 162 | 0 | 143.29 | 0 | 143.29 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 389.4 | 372 | 635.89 | 462 | 585.89 | 412
System Total |  |  |  |  | 28886.2 | 27110.055 | 13321.71 | 15316.2 | 22766.48 | 22279.89 | 19992.17 | 19539.58
Forecast Scenario (25-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15190 |  | 0 |  | 15190
|  |  |  | 1:00 | 15050 |  | 0 |  | 15050
|  |  |  | 2:00 | 14801 |  | 0 |  | 14801
|  |  |  | 3:00 | 14351 |  | 0 |  | 14351
|  |  |  | 4:00 | 13950 |  | 0 |  | 13950
|  |  |  | 5:00 | 13701 |  | 0 |  | 13701
|  |  |  | 6:00 | 12802 |  | 0 |  | 12802
|  |  |  | 7:00 | 12503 |  | 0 |  | 12503
|  |  |  | 8:00 | 12352 |  | 0 |  | 12352
|  |  |  | 9:00 | 12504 |  | 0 |  | 12504
|  |  |  | 10:00 | 13125 |  | 0 |  | 13125
|  |  |  | 11:00 | 13572 |  | 0 |  | 13572
|  |  |  | 12:00 | 13953 |  | 0 |  | 13953
|  |  |  | 13:00 | 14386 |  | 0 |  | 14386
|  |  |  | 14:00 | 14824 |  | 0 |  | 14824
|  |  |  | 15:00 | 14702 |  | 0 |  | 14702
|  |  |  | 16:00 | 14034 |  | 0 |  | 14034
|  |  |  | 17:00 | 13600 |  | 0 |  | 13600
|  |  |  | 18:00 | 13650 |  | 0 |  | 13650
|  |  |  | 18:30 | 14200 |  | 0 |  | 14200
|  |  |  | 19:00 | 14800 |  | 0 |  | 14800
|  |  |  | 19:30 | 15050 |  | 0 |  | 15050
|  |  |  | 20:00 | 15100 |  | 0 |  | 15100
|  |  |  | 21:00 | 15200 |  | 0 |  | 15200
|  |  |  | 22:00 | 14700 |  | 0 |  | 14700
|  |  |  | 23:00 | 14300 |  | 0 |  | 14300
Probable Maximum Temperature: |  |  | 33.60°C
Probable Maximum Demand at Day Peak: |  |  | 13953.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15200.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13544.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 322.932 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:36 hrs on 25-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 24-05-2025 | [28 empty] | Date: | 24-05-2025 | [28 empty] | Date: | 24-05-2025 | [28 empty] | Date: | 24-05-2025 | [28 empty] | Date: | 24-05-2025 | [16 empty] | Date: | 24-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [16 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 17 | 17 | 102 | 112 | 0 | 0 | 17 | 0 | 0 | 32 | 300 | 279 | 500 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 34 | 39 | 0 | 36 | 0 | 0 | 37 | 0 | 34 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 8 | 0 | 355 | 340 | 53 | 183 | 27 | 90 | 81 | 98 | 10 | 14 | 114 | 42 | 8 | 0 | 40 | 310 | 320 | 350 | 0 | 39 | 0 | 150 | 8 | 0 | 82 | 22 | 0 | 18 | 169 | 35 | 96 | 150 | 0 | 0 | 0 | 12 | 7525.5 | 681 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 67 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 121 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 51 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 110 | 110 | 0 | 316 | 1244 | 0 | 6639 | 14164.5 | 76.97
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 17 | 17 | 83 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 290 | 500 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 34 | 16 | 0 | 0 | 0 | 0 | 37 | 0 | 34 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1178 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 39 | 216 | 27 | 90 | 80 | 38 | 9 | 14 | 114 | 40 | 8 | 0 | 40 | 300 | 320 | 353 | 0 | 39 | 0 | 148 | 8 | 0 | 82 | 22 | 0 | 18 | 169 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7035.5 | 854 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 72 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 118 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 158 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 110 | 110 | 0 | 261 | 1150 | 0 | 6412 | 13447.5 | 76.97
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 17 | 17 | 81 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 302 | 500 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 42 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 8 | 0 | 352 | 340 | 30 | 215 | 27 | 91 | 80 | 36 | 9 | 14 | 114 | 40 | 14 | 0 | 40 | 290 | 320 | 386 | 0 | 39 | 0 | 136 | 8 | 0 | 82 | 22 | 0 | 18 | 169 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 6974.5 | 927 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 990 | 70 | 1224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 118 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 154 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 90 | 110 | 0 | 215 | 1100 | 0 | 6001 | 12975.5 | 76.97
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 17 | 17 | 75 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 288 | 500 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 34 | 485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 8 | 0 | 355 | 340 | 30 | 216 | 27 | 90 | 80 | 36 | 9 | 14 | 114 | 38 | 25 | 0 | 40 | 305 | 320 | 355 | 0 | 39 | 0 | 130 | 6 | 0 | 82 | 22 | 0 | 18 | 169 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 6924.5 | 927 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 53 | 1199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 118 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 157 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 100 | 110 | 0 | 215 | 1100 | 0 | 5902 | 12826.5 | 76.97
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 17 | 17 | 69 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 287 | 500 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 142 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 11 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 30 | 216 | 27 | 90 | 80 | 35 | 9 | 14 | 114 | 38 | 25 | 0 | 40 | 300 | 320 | 359 | 0 | 39 | 0 | 130 | 6 | 0 | 82 | 22 | 0 | 18 | 170 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 6891.5 | 927 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 17 | 1038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 119 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 160 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 100 | 110 | 0 | 219 | 1100 | 0 | 5703 | 12594.5 | 76.97
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 17 | 17 | 70 | 48 | 0 | 0 | 0 | 0 | 0 | 16 | 300 | 284 | 500 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 125 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 42 | 452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1002 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 30 | 218 | 27 | 91 | 80 | 35 | 9 | 14 | 114 | 36 | 25 | 0 | 16 | 305 | 320 | 350 | 0 | 39 | 0 | 130 | 6 | 0 | 82 | 22 | 0 | 18 | 171 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 6734.5 | 928 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 908 | 17 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 137 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 162 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 100 | 110 | 0 | 219 | 1100 | 0 | 5687 | 12421.5 | 76.97
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 17 | 69 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 313 | 500 | 0 | 0 | 0 | 250 | 0 | 0 | 2 | 125 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 42 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 1 | 51 | 0 | 8 | 0 | 300 | 340 | 30 | 204 | 27 | 90 | 80 | 36 | 10 | 14 | 114 | 26 | 25 | 0 | 0 | 310 | 320 | 324 | 0 | 39 | 0 | 139 | 6 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 48 | 96 | 0 | 0 | 1.02 | 12 | 6557.52 | 927 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.87 | 770 | 0 | 898 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1.23 | 180 | 0 | 144 | 0 | 0 | 0 | 414 | 0 | 0.08 | 0 | 156 | 50 | 0 | 1 | 0 | 0 | 0 | 0.3 | 8 | 0.04 | 0 | 200 | 10 | 100 | 110 | 0 | 222 | 1020 | 0 | 5414.52 | 11972.04 | 76.97
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 17 | 71 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 240 | 583 | 0 | 0 | 0 | 240 | 0 | 0 | 6 | 142 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 32 | 368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 4 | 51 | 0 | 8 | 0 | 300 | 340 | 30 | 199 | 27 | 90 | 80 | 36 | 30 | 14 | 114 | 32 | 25 | 4 | 0 | 310 | 320 | 336 | 0 | 39 | 0 | 133 | 6 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 75 | 115 | 0 | 0 | 9.1 | 12 | 6616.6 | 927 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.74 | 758 | 0 | 872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 7.72 | 180 | 0 | 157 | 0 | 0 | 0 | 414 | 0 | 0.77 | 0 | 155 | 50 | 0 | 2 | 0 | 0 | 0 | 1.3 | 42 | 0.08 | 0 | 200 | 9 | 100 | 110 | 0 | 224 | 1000 | 0 | 5424.61 | 12041.21 | 76.97
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 88 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 240 | 583 | 0 | 0 | 0 | 240 | 0 | 0 | 11 | 142 | 16.5 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 6 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025 | 10 | 51 | 0 | 8 | 0 | 346 | 340 | 30 | 210 | 27 | 50 | 80 | 35 | 57 | 14 | 70 | 30 | 0 | 18 | 0 | 320 | 320 | 356 | 0 | 39 | 0 | 140 | 6 | 0 | 82 | 30 | 0 | 18 | 172 | 0 | 77 | 115 | 0 | 1 | 33.61 | 12 | 6717.11 | 863 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.75 | 760 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 18.74 | 180 | 0 | 162 | 0 | 0 | 0 | 414 | 0 | 1.31 | 0 | 155 | 51 | 0 | 6 | 0 | 0 | 0 | 1.8 | 76 | 0.14 | 0 | 200 | 8 | 120 | 110 | 0 | 230 | 1001 | 0 | 5432.74 | 12149.85 | 76.97
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 17 | 94 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 240 | 583 | 0 | 0 | 0 | 240 | 0 | 0 | 6 | 142 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 2 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 12 | 51 | 0 | 8 | 0 | 352 | 340 | 30 | 196 | 27 | 50 | 80 | 35 | 58 | 14 | 70 | 28 | 0 | 32 | 0 | 300 | 320 | 381 | 0 | 38 | 0 | 151 | 0 | 0 | 79 | 30 | 0 | 18 | 172 | 0 | 77 | 115 | 0 | 1 | 24.47 | 12 | 6761.47 | 863 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.19 | 758 | 0 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 26.12 | 180 | 0 | 163 | 0 | 0 | 0 | 370 | 0 | 2.35 | 0 | 160 | 51 | 0 | 12 | 0 | 0 | 0 | 2.9 | 100 | 0.26 | 0 | 200 | 9 | 120 | 110 | 0 | 300 | 1091 | 0 | 5617.82 | 12379.29 | 76.97
10:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 17 | 94 | 48 | 0 | 0 | 0 | 35 | 0 | 0 | 300 | 250 | 583 | 0 | 0 | 0 | 240 | 0 | 0 | 26 | 142 | 13.5 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 39 | 0 | 2 | 367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 15 | 51 | 0 | 8 | 0 | 345 | 340 | 30 | 210 | 27 | 50 | 80 | 34 | 57 | 14 | 70 | 32 | 0 | 21 | 0 | 295 | 320 | 379 | 0 | 38 | 0 | 134 | 12 | 0 | 78 | 30 | 0 | 18 | 172 | 0 | 66 | 115 | 0 | 2 | 26.32 | 12 | 6982.82 | 911 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.93 | 763 | 0 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 55.52 | 180 | 0 | 169 | 0 | 0 | 0 | 320 | 0 | 4.63 | 0 | 160 | 50 | 0 | 14 | 0 | 0 | 0 | 2.6 | 101 | 0.25 | 0 | 155 | 9 | 120 | 110 | 0 | 300 | 1010 | 0 | 5612.93 | 12595.75 | 76.97
11:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 0.3 | 17 | 104 | 48 | 0 | 0 | 2 | 90 | 0 | 0 | 300 | 250 | 583 | 0 | 0 | 0 | 240 | 0 | 0 | 19 | 142 | 13.5 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 12 | 0 | 3 | 38 | 0 | 2 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 11 | 51 | 1 | 8 | 0 | 300 | 300 | 30 | 202 | 27 | 50 | 80 | 35 | 57 | 14 | 70 | 32 | 0 | 42 | 0 | 300 | 320 | 360 | 0 | 38 | 0 | 151 | 12 | 0 | 79 | 28 | 0 | 18 | 172 | 0 | 67 | 117 | 0 | 3 | 41.87 | 12 | 7087.67 | 910 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.53 | 758 | 0 | 1063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 61.23 | 176 | 0 | 165 | 0 | 0 | 0 | 414 | 0 | 5.33 | 0 | 133 | 50 | 0 | 20 | 0 | 0 | 0 | 2 | 189 | 0.01 | 0 | 150 | 7 | 100 | 110 | 0 | 300 | 910 | 0 | 5895.1 | 12982.77 | 76.97
12:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 339 | 0 | 0 | 19 | 17 | 112 | 47 | 0 | 0 | 32 | 126 | 0 | 0 | 300 | 250 | 583 | 0 | 0 | 0 | 240 | 0 | 0 | 35 | 142 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 2 | 0 | 75 | 0 | 2 | 36 | 0 | 2 | 568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 6 | 51 | 20 | 8 | 0 | 348 | 340 | 30 | 183 | 29 | 60 | 80 | 34 | 57 | 14 | 70 | 36 | 0 | 40 | 0 | 305 | 320 | 315 | 0 | 38 | 0 | 152 | 12 | 0 | 79 | 20 | 0 | 18 | 172 | 0 | 67 | 121 | 0 | 3 | 48.95 | 12 | 7447.45 | 910 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.53 | 791 | 0 | 1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 61.4 | 172 | 0 | 163 | 0 | 0 | 0 | 360 | 0 | 5.9 | 0 | 154 | 50 | 0 | 21 | 0 | 0 | 0 | 2.4 | 162 | 0.03 | 0 | 150 | 7 | 90 | 110 | 0 | 298 | 920 | 0 | 5874.26 | 13321.71 | 76.98
13:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 17 | 112 | 47 | 15 | 0 | 35 | 162 | 0 | 16 | 300 | 250 | 583 | 0 | 35 | 0 | 240 | 0 | 0 | 35 | 160 | 15.5 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 16 | 0 | 75 | 0 | 3 | 36 | 0 | 6 | 569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1175 | 8 | 51 | 55 | 8 | 0 | 341 | 340 | 30 | 188 | 26 | 72 | 75 | 35 | 58 | 8 | 70 | 40 | 0 | 42 | 12 | 300 | 320 | 316 | 0 | 38 | 0 | 137 | 0 | 0 | 81 | 28 | 0 | 18 | 171 | 1 | 67 | 110 | 0 | 1 | 47.91 | 12 | 7586.41 | 910 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.55 | 859 | 0 | 1182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 21.69 | 169 | 0 | 161 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 50 | 0 | 14 | 0 | 0 | 0 | 4.1 | 160 | 0.09 | 0 | 150 | 7 | 120 | 110 | 0 | 300 | 924 | 0 | 6063.43 | 13649.84 | 76.98
14:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 54 | 17 | 112 | 47 | 15 | 0 | 35 | 162 | 0 | 48 | 300 | 250 | 583 | 0 | 35 | 0 | 240 | 0 | 0 | 32 | 160 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 22 | 0 | 88 | 0 | 2 | 36 | 0 | 3 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1102 | 6 | 51 | 97 | 8 | 0 | 332 | 335 | 30 | 207 | 26 | 72 | 70 | 43 | 58 | 8 | 114 | 40 | 0 | 38 | 31 | 305 | 320 | 390 | 0 | 37 | 0 | 146 | 0 | 0 | 81 | 28 | 0 | 18 | 172 | 48 | 67 | 121 | 0 | 3 | 43.74 | 11 | 7656.74 | 911 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.08 | 940 | 0 | 1150.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 10.4 | 171 | 0 | 158 | 0 | 0 | 0 | 350 | 0 | 0.93 | 0 | 160 | 50 | 0 | 22 | 0 | 0 | 0 | 4.3 | 182 | 0.43 | 0 | 180 | 7 | 100 | 110 | 0 | 300 | 862 | 0 | 5945.73 | 13602.47 | 76.98
15:00 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 54 | 17 | 112 | 47 | 15 | 0 | 35 | 162 | 0 | 64 | 300 | 250 | 583 | 0 | 35 | 0 | 240 | 0 | 0 | 20 | 160 | 15.3 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 26 | 0 | 75 | 8 | 2 | 38 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 4 | 51 | 104 | 8 | 0 | 336 | 340 | 30 | 205 | 24 | 74 | 70 | 52 | 58 | 0 | 114 | 40 | 0 | 25 | 37 | 305 | 320 | 372 | 0 | 37 | 0 | 155 | 0 | 0 | 79 | 25 | 0 | 18 | 172 | 52.5 | 67 | 121 | 0 | 0 | 27.11 | 11 | 7749.91 | 910 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.46 | 931 | 0 | 1224.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 12.03 | 172 | 0 | 155 | 0 | 0 | 0 | 350 | 0 | 0.88 | 0 | 162 | 50 | 30 | 10 | 0 | 0 | 0 | 2.7 | 81 | 0.3 | 0 | 200 | 7 | 100 | 110 | 0 | 299 | 907 | 0 | 5950.82 | 13700.73 | 76.98
16:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 54 | 17 | 112 | 47 | 20 | 0 | 35 | 162 | 0 | 64 | 300 | 287 | 520 | 0 | 35 | 0 | 280 | 0 | 0 | 14 | 160 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 0 | 44 | 0 | 75 | 24 | 1 | 39 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 3 | 51 | 70 | 8 | 0 | 343 | 325 | 30 | 199 | 27 | 73 | 70 | 51 | 50 | 0 | 114 | 38 | 0 | 12 | 38 | 300 | 320 | 353 | 0 | 37 | 0 | 152 | 8 | 0 | 81 | 25 | 0 | 18 | 173 | 54 | 67 | 122 | 0 | 1 | 34.99 | 11 | 7651.99 | 911 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.32 | 962 | 0 | 1208.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 13.28 | 170 | 0 | 154 | 0 | 0 | 0 | 300 | 0 | 1.22 | 0 | 161 | 50 | 35 | 22 | 0 | 0 | 0 | 1.4 | 58 | 0.15 | 0 | 200 | 7 | 100 | 110 | 0 | 298 | 947 | 0 | 5920.99 | 13572.98 | 76.98
17:00 | 0 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 54 | 17 | 112 | 47 | 60 | 0 | 35 | 162 | 0 | 67 | 300 | 272 | 450 | 0 | 35 | 0 | 259 | 0 | 0 | 7 | 120 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 70 | 0 | 100 | 24 | 0 | 40 | 0 | 2 | 472 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1053 | 1 | 51 | 70 | 8 | 0 | 320 | 325 | 30 | 182 | 33 | 74 | 70 | 51 | 16 | 10 | 114 | 38 | 0 | 9 | 31 | 300 | 320 | 339 | 0 | 37 | 0 | 148 | 8 | 0 | 81 | 28 | 0 | 18 | 172 | 54.5 | 67 | 122 | 0 | 0 | 3.75 | 11 | 7381.25 | 910 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.93 | 959 | 0 | 1213.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 5.85 | 150 | 0 | 155 | 0 | 0 | 0 | 300 | 0 | 0.73 | 0 | 161 | 50 | 35 | 7 | 0 | 0 | 0 | 1.3 | 8 | 0.1 | 0 | 184 | 7 | 90 | 110 | 0 | 298 | 938 | 0 | 5759.87 | 13141.12 | 76.98
18:00 | 0 | 53 | 24 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 112 | 47 | 60 | 0 | 35 | 90 | 0 | 52 | 300 | 308 | 450 | 0 | 35 | 0 | 290 | 0 | 0 | 1 | 90 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 78 | 0 | 100 | 24 | 0 | 40 | 0 | 3 | 453 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 1005 | 0 | 51 | 50 | 8 | 0 | 300 | 325 | 30 | 204 | 33 | 87 | 70 | 52 | 8 | 14 | 88 | 36 | 0 | 3 | 39 | 305 | 320 | 380 | 0 | 37 | 0 | 132 | 8 | 0 | 82 | 30 | 0 | 18 | 172 | 37 | 77 | 124 | 0 | 0 | 0.19 | 1 | 7320.19 | 910 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.46 | 915 | 17 | 1171.83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0.05 | 140 | 0 | 140 | 0 | 0 | 0 | 300 | 0 | 0.06 | 0 | 158 | 50 | 35 | 1 | 16 | 0 | 0 | 0.4 | 5 | 0.06 | 0 | 170 | 7 | 100 | 110 | 0 | 246 | 901 | 0 | 5543.86 | 12864.05 | 76.98
19:00 | 16 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 54 | 17 | 112 | 95 | 132 | 10 | 35 | 120 | 0 | 50 | 340 | 300 | 450 | 0 | 35 | 0 | 314 | 0 | 0 | 0 | 90 | 15 | 15 | 0 | 0 | 0 | 0 | 1 | 100 | 0 | 34 | 78 | 0 | 100 | 60 | 0 | 40 | 0 | 6 | 540 | 0 | 0 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 1175 | 0 | 51 | 50 | 8 | 0 | 335 | 340 | 30 | 210 | 33 | 74 | 80 | 51 | 9 | 14 | 114 | 44 | 16 | 0 | 39 | 310 | 320 | 388 | 20 | 37 | 0 | 139 | 10 | 0 | 83 | 20 | 0 | 18 | 172 | 17 | 55 | 131 | 0 | 0 | 0 | 6 | 8033 | 862 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1037 | 35 | 1390.64 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 22 | 0 | 156 | 0 | 161 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 157 | 50 | 70 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 10 | 120 | 110 | 0 | 250 | 987 | 0 | 6356.64 | 14389.64 | 76.98
19:30 | 16 | 53 | 16 | 0 | 0 | 0 | 0 | 0 | 344.26 | 0 | 0 | 54 | 17 | 112 | 95 | 168 | 15 | 35 | 162 | 0 | 50 | 340 | 304 | 480 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 125 | 15 | 15 | 0 | 0 | 0 | 0 | 25 | 100 | 0 | 34 | 78 | 0 | 100 | 90 | 0 | 40 | 0 | 2 | 563 | 0 | 0 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 8 | 0 | 343 | 340 | 30 | 208 | 33 | 92 | 80 | 51 | 9 | 14 | 114 | 44 | 43 | 0 | 39 | 310 | 320 | 375 | 20 | 37 | 0 | 145 | 10 | 0 | 83 | 20 | 0 | 18 | 173 | 17 | 60 | 167 | 0 | 0 | 0 | 12 | 8363.26 | 862 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 35 | 1474.17 | 0 | 0 | 0 | 34 | 0 | 33 | 0 | 0 | 0 | 0 | 22 | 0 | 170 | 0 | 162 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 155 | 50 | 112 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 110 | 0 | 277 | 1096 | 0 | 6773.17 | 15136.43
20:00 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 17 | 112 | 110 | 195 | 15 | 35 | 162 | 0 | 51 | 340 | 285 | 480 | 0 | 35 | 0 | 261 | 0 | 0 | 0 | 125 | 15 | 15 | 0 | 0 | 0 | 0 | 28 | 100 | 0 | 34 | 78 | 0 | 100 | 100 | 0 | 40 | 0 | 6 | 571 | 0 | 0 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 8 | 0 | 354 | 340 | 30 | 183 | 33 | 87 | 80 | 51 | 9 | 14 | 114 | 40 | 52.2 | 0 | 39 | 305 | 320 | 339 | 20 | 37 | 0 | 153 | 10 | 0 | 80 | 25 | 0 | 18 | 172 | 17 | 104 | 169 | 0 | 0 | 0 | 12 | 8378.2 | 861 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1153 | 35 | 1449.25 | 0 | 0 | 0 | 50 | 0 | 33 | 0 | 0 | 0 | 0 | 22 | 0 | 170 | 0 | 162 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 155 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 110 | 0 | 307 | 1098 | 0 | 6827.25 | 15205.45 | 76.98
21:00 | 16 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 54 | 17 | 112 | 144 | 195 | 15 | 35 | 162 | 0 | 69 | 340 | 300 | 450 | 0 | 35 | 0 | 267 | 0 | 0 | 0 | 142 | 0 | 15 | 0 | 0 | 0 | 0 | 35 | 100 | 0 | 34 | 81 | 0 | 100 | 60 | 0 | 40 | 0 | 8 | 571 | 0 | 0 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 62 | 8 | 0 | 354 | 340 | 30 | 192 | 34 | 92 | 80 | 51 | 9 | 14 | 114 | 38 | 52.2 | 0 | 39 | 300 | 320 | 339 | 30 | 37 | 0 | 134 | 10 | 0 | 80 | 20 | 0 | 18 | 172 | 17 | 104 | 170 | 0 | 0 | 0 | 12 | 8369.2 | 910 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1166 | 35 | 1449 | 0 | 0 | 0 | 100 | 0 | 33 | 0 | 0 | 0 | 0 | 22 | 0 | 169 | 0 | 156 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 158 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 130 | 0 | 308 | 1114 | 0 | 6947 | 15316.2 | 76.98
22:00 | 0 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 54 | 17 | 112 | 144 | 95 | 0 | 35 | 162 | 0 | 51 | 340 | 295 | 450 | 0 | 35 | 0 | 276 | 0 | 0 | 0 | 90 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 34 | 80 | 0 | 100 | 60 | 0 | 40 | 0 | 18 | 570 | 0 | 0 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 1227 | 0 | 51 | 80 | 8 | 0 | 354 | 340 | 30 | 187 | 34 | 93 | 80 | 51 | 9 | 14 | 114 | 44 | 52.2 | 0 | 31 | 310 | 320 | 339 | 30 | 27 | 0 | 129 | 10 | 0 | 80 | 20 | 0 | 18 | 172 | 17 | 105 | 171 | 0 | 0 | 0 | 12 | 8155.2 | 910 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 35 | 1462 | 0 | 0 | 0 | 70 | 0 | 33 | 0 | 0 | 0 | 0 | 15 | 0 | 170 | 0 | 156 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 160 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 112 | 210 | 0 | 306 | 1112 | 0 | 7029.2 | 15184.4 | 76.98
23:00 | 0 | 45 | 8 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 54 | 17 | 112 | 48 | 95 | 0 | 35 | 162 | 0 | 51 | 320 | 310 | 420 | 0 | 35 | 0 | 286 | 0 | 0 | 0 | 90 | 7 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 34 | 39 | 0 | 100 | 60 | 0 | 38 | 0 | 23 | 571 | 0 | 0 | 33 | 8 | 0 | 0 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 8 | 0 | 351 | 340 | 30 | 202 | 33 | 93 | 75 | 51 | 8 | 14 | 114 | 46 | 52.2 | 0 | 31 | 310 | 320 | 386 | 29 | 0 | 0 | 131 | 10 | 0 | 80 | 20 | 0 | 18 | 172 | 17 | 105 | 171 | 0 | 0 | 0 | 12 | 8023.2 | 910 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1236 | 35 | 1441 | 0 | 0 | 0 | 70 | 0 | 33 | 0 | 0 | 0 | 0 | 15 | 0 | 170 | 0 | 156 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 160 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 306 | 1113 | 0 | 7030 | 15053.2 | 76.98
Total KWH | 48816 | 780480 | 394080 | 0 | 0 | 0 | 0 | 0 | 7956000 | 0 | 0 | 786600 | 432720 | 2370096 | 1476480 | 980553 | 46015 | 477627 | 1991520 | 0 | 746880 | 7626000 | 6713658 | 12425455 | 0 | 428078 | 0 | 6195366 | 0 | 0 | 207185 | 3265200 | 307200 | 370800 | 0 | 0 | 0 | 0 | 71040 | 2500000 | 88800 | 355150 | 620960 | 0 | 1204800 | 444480 | 22777 | 935220 | 0 | 392640 | 11665454.55 | 0 | 0 | 182880 | 61432.2 | 0 | 77992 | 0 | 0 | 0 | 27087270 | 89775 | 1182632 | 976872 | 217455 | 0 | 8486200 | 8150000 | 736800 | 4894000 | 705744 | 1924800 | 1840490 | 1087200 | 676200 | 277350 | 2501160 | 892800 | 419098 | 286455 | 581904 | 7398500 | 7669800 | 8905000 | 142000 | 823200 | 0 | 3524645 | 180720 | 0 | 1924800 | 595448 | 0 | 432000 | 3541720 | 452880 | 1688400 | 2930400 | 0 | 11600 | 337910 | 275760 | 178499422.75 | 21757090 | 3872736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 558000 | 22647280 | 475200 | 28267926 | 0 | 0 | 0 | 382848 | 0 | 176416 | 0 | 0 | 0 | 671210 | 90680 | 280504 | 4183909 | 0 | 3812400 | 0 | 0 | 0 | 9046109 | 0 | 21360 | 0 | 3864000 | 1134109 | 849677 | 148139 | 357763 | 0 | 0 | 27611.28 | 1226160 | 2038 | 0 | 5411000 | 216086 | 2545000 | 2897690 | 0 | 6799999 | 25458909.09 | 0 | 147181849.37 | 325681272.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 24-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13321.71 | MW | 12:00 Hr. | Energy Generated |  |  | 325.6813 |  | MKWHr.
| Day Peak Demand |  |  | 13354.11 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.165 |  | MKWHr.
| Evening Peak Generation |  |  | 15316.2 | MW | 21:00 Hr. | Energy Demand |  |  | 327.8463 |  | MKWHr.
| Evening Peak Demand |  |  | 15400.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32 |  | °C
| Minimum Generation of the Day |  |  | 11972.04 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 983.73 |  | MMCFD
| Maximum Generation of the Day |  |  | 15316.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.4293 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 41.5945 | 0 | 14.2251 | 0 | 0 | 0.20719 | 0 | 0 | 56.0268 | Gas | 132.7675 | Gas | 477952791.34
| Chattogram Zone |  |  | 2.9706 | 38.7527 | 2.9407 | 0 | 0.93522 | 0.11255 | 0 | 0.0888 | 45.8007 | Coal | 104.068 | Coal | 673521805.6103
| Cumilla Zone |  |  | 26.4907 | 0 | 8.1672 | 0 | 0 | 0.28646 | 0.8928 | 0 | 35.8372 | HFO | 33.0131 | HFO | 614498657.384
| Mymensingh Zone |  |  | 0 | 0 | 5.3474 | 0 | 0 | 0.34951 | 0 | 0 | 5.697 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 35.1378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.1378 | Hydro | 0.93522 | Hydro | 93522
| Khulna Zone |  |  | 3.8727 | 22.6473 | 0.4752 | 0 | 0 | 0.558 | 21.7571 | 0 | 49.3103 | Solar | 3.8907 | Solar | 64514380.4908
| Barishal Zone |  |  | 5.6588 | 37.6699 | 0 | 0 | 0 | 0.002038 | 0 | 0 | 43.3307 | Import | 50.9178 | Import | 262005367.68
| Rajshahi Zone |  |  | 17.0424 | 0 | 0.64994 | 0 | 0 | 0.97307 | 28.2679 | 0 | 46.9334 | Wind | 0.0888 | Wind | 1300032
| Rangpur Zone |  |  | 0 | 4.9981 | 1.2074 | 0 | 0 | 1.4019 | 0 | 0 | 7.6075
| Total |  |  | 132.7675 | 104.068 | 33.0131 | 0 | 0.93522 | 3.8907 | 50.9178 | 0.0888 | 325.6813
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 477952791.34 |  | Hydro | 93522
|  |  |  | Coal | 673521805.6103 |  | Solar | 64514380.4908
|  |  |  | HFO | 614498657.384 |  | Import | 262005367.68
|  |  |  | HSD | 0 |  | Wind | 1300032
[5 empty] | Total: | 209,38,86,556 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.7571 | Peak Hr Flow | 910.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44173509.17 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 28.2679 | Peak Hr Flow | 1449.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 714 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8928 | Peak Hr Flow | 38.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 998 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 50.9178 | Peak Hr Flow | 2397.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 50 |  | 5570
|  |  |  | Chattogram |  | 0 |  | 1493
|  |  |  | Cumilla |  | 30 |  | 1319
|  |  |  | Mymensingh |  | 0 |  | 1141
|  |  |  | Sylhet |  | 0 |  | 627
|  |  |  | Khulna |  | 0 |  | 1840
|  |  |  | Barishal |  | 0 |  | 469
|  |  |  | Rajshahi |  | 0 |  | 1390
|  |  |  | Rangpur |  | 0 |  | 914
|  |  |  | Total |  | 80 |  | 14763
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:16 | Kodda 132/33kV S/S Tr-3 (426T) HT is restored.
|  | 08:18 | Kodda 132/33kV S/S Tr-3 (426T) LT is restored.
|  | 09:20 | Khulshi-Madunaghat 132kV Ckt-2 is restored.
| 10:00 | 13:37 | BIPTC S/S 20DF22 Forced S/D
| 10:26 | 10:30 | Sylhet 132/33kV S/S T2 LT Scheduled S/D Due to for t-2 and t-4 parallel | [7 empty] | 30.0MW load
interrup.
|  | 10:26 | Sreepur 230/132/33kV S/S 132 kV BUS-1 is restored.
| 10:32 | 11:42 | Bheramara(GK) 132/33kV S/S TR-1 LT Scheduled S/D Due to 132/33 kv, 25/41 Tr-01 & Tr-02 | [7 empty] | 15.0MW load
|  |  | ,33 kv bus cupler red hot removing work . | [7 empty] | interrup.
| 10:33 | 11:43 | Bheramara(GK) 132/33kV S/S TR-2 LT Scheduled S/D Due to 132/33 kv, 25/41 Tr-01 & Tr-02 | [7 empty] | 15.0MW load
|  |  | ,33 kv bus cupler red hot removing work . | [7 empty] | interrup.
| 10:34 | 11:41 | Bheramara(GK) 132/33kV S/S TR-2 HT Scheduled S/D Due to 132/33 kv, 25/41 Tr-01 & Tr-02 | [7 empty] | 15.0MW load
|  |  | ,33 kv bus cupler red hot removing work . | [7 empty] | interrup.
| 10:34 | 11:41 | Bheramara(GK) 132/33kV S/S TR-1 HT Scheduled S/D Due to 132/33 kv, 25/41 Tr-01 & Tr-02 | [7 empty] | 15.0MW load
|  |  | ,33 kv bus cupler red hot removing work . | [7 empty] | interrup.
| 12:00 |  | Day Peak Gen. 13321 MW
| 13:00 | 13:24 | Gopalganj 400/132kV S/S 132kV Bus-02 Scheduled S/D
|  | 13:37 | BIPTC S/S 20DF22 is restored.
| 14:48 | 18:17 | GPH 230/33kV S/S Transformer -2 (D07) HT Forced S/D Due to Oil leakage checking.
| 15:19 | 17:31 | Benapole 132/33kV S/S Transformer-2(416T) LT Scheduled S/D Due to 33 KV feeder | [7 empty] | 30.0MW load
|  |  | maintenance work of pbs | [7 empty] | interrup.
| 15:20 | 17:30 | Benapole 132/33kV S/S Transformer-2(416T) HT Scheduled S/D Due to 33 KV feeder | [7 empty] | 30.0MW load
|  |  | maintenance work of pbs | [7 empty] | interrup.
| 15:30 | 19:30 | Chauddagram-Feni 132 kV Ckt-2 Forced S/D from Chauddagram 132/33kV end Due to Emergency
Maintenance in Feni Grid.
|  | 16:32 | Baghabari-Shahjadpur 132 kV Ckt-2 is restored.
|  | 17:17 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
|  | 17:17 | Chowmuhani-Ramganj 132 kV Ckt-1 is restored.
|  | 17:18 | Chowmuhani-Ramganj 132 kV Ckt-2 is restored.
|  | 18:22 | Sylhet (South) S/S Trafo-2 LT is restored.
|  | 18:24 | Sylhet (South) S/S Trafo-2 HT is restored.
| 03:58 |  | Kodda-Rajendrapur 132kV Ckt-1 Forced S/D from Rajendrapur 132/33kV end.
| 06:00 |  | Minimum Generation: 12551 MW.
| 06:22 | 07:41 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 HT Scheduled S/D Due to maintenance
| 06:22 | 07:41 | Kaliakoir 400/230/132kV S/S 400/230kV TR2 LT Scheduled S/D Due to Maintenance
| 06:40 |  | Dhamrai 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Redhot maintenance
| 06:40 |  | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Redhot maintenance
| 06:51 |  | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to
CVT R phase Replacement
| 06:54 |  | Barishal 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to To remove high temperature
problem (nut bolt tightening)
| 06:55 |  | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Bucholz checking
| 06:55 |  | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to For Bucholz checking
| 06:55 |  | Barishal 132/33kV S/S T-2 (415T) LT Scheduled S/D Due to To remove high temperature
problem (nut bolt tightening)
| 07:34 |  | Hasnabad-Shyampur 230kV Ckt-1 Scheduled S/D from Hasnabad 230/132kV end Due to
Maintenance work due to temperature rise.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 24-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 316 | 7956000 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 340 | 7626000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6713658 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 15 | 46015 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 267 | 6195366 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 48816 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 786600 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 1476480 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 477627 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 428078 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 0 | 307200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 15 | 370800 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 394080 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 980553 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 2370096 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 780480 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 69 | 746880 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1991520 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 207185 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 450 | 12425455 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 3265200 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2752 | 56026809
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 100 | 2500000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 61432.2 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 89775 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 33 | 182880 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 935220 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 0 | 77992 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 81 | 620960 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 355150 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1204800 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 8 | 392640 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 35 | 71040 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 22777 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 444480 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27087270 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 88800 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 571 | 11665454.55 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2294 | 45800670.75
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 192 | 4894000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8486200 | Machine Problem
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8150000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 705744 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 736800 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 217455 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1182632 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 62 | 976872 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 581904 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1840490 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 51 | 1087200 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 892800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 419098 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 277350 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2501160 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 676200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 92 | 1924800 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 286455 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1560.2 | 35837160
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 2930400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 104 | 1688400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 337910 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 275760 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 452880 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 303 | 5696950
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 30 | 142000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 37 | 823200 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 134 | 3524645 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 595448 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1924800 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 172 | 3541720 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 10 | 180720 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7398500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 339 | 8905000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7669800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1460 | 35137833
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 910 | 21757090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 142 | 3872736 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 475200 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 558000 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1166 | 22647280 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2253 | 49310306
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 308 | 6799999 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 10 | 216086 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2545000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1114 | 25458909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 130 | 2897690 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5411000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2038 | -
Barishal Area Total |  |  |  |  | 2236 | 1979 | 43330722.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Engine Problem
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 169 | 4183909 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 156 | 3812400 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 9046109 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 90680 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 33 | 176416 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 100 | 382848 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 21360 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1449 | 28267926 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 280504 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 671210 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2343 | 46933362
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1134109 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3864000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 357763 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 27611.28 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 849677 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 148139 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1226160 | -
Rangpur Area Total |  |  |  |  | 950 | 372 | 7607459.28
Eastern Grid Total |  |  |  |  | 16771.895 | 8369.2 | 178499422.75
Western Grid Total |  |  |  |  | 10338.16 | 6947 | 147181849.37
National Grid Total |  |  |  |  | 27110.055 | 15316.2 | 325681272.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 24-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10069.4 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4613 | MW
i) Dhaka area |  |  | 5519.57 |  | MW | i) Khulna area |  |  |  | 1840 | MW
ii) Chattogram area |  |  | 1493 |  | MW | ii) Barishal area |  |  |  | 469.4 | MW
iii) Cumilla area |  |  | 1288.83 |  | MW | iii) Rajshahi area |  |  |  | 1389.6 | MW
iv) Mymensingh area |  |  | 1141 |  | MW | iv) Rangpur area |  |  |  | 914 | MW
v) Sylhet area |  |  | 627 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14682.4 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 79 | 19:30 | 133 | Patuakhali | 80 | 00:00
2 | AKSML | 119 | 11:00 | 68 | Jaldhaka | 82 | 19:30 | 134 | Payra | 32 | 21:00
3 | Aftabnagar | 38 | 12:00 | 69 | Jamalpur | 120 | 00:00 | 135 | Postogola | 60 | 13:00
4 | Agargaon | 138 | 13:00 | 70 | Jashore | 140 | 13:00 | 136 | Purbachal | 22 | 21:00
5 | Agrabad | 90 | 19:00 | 71 | Jhenaidah | 131 | 19:30 | 137 | Purbasadipur | 134 | 19:30
6 | Amnura | 34 | 21:00 | 72 | Joydebpur | 169 | 16:00 | 138 | Rahanpur | 24 | 21:00
7 | Ashuganj | 97 | 01:00 | 73 | Joypurhat | 61 | 20:00 | 139 | Rahim | 57 | 17:00
8 | BSRM | 165 | 06:00 | 74 | Juldah | 17 | 16:00 | 140 | Rajbari | 85 | 19:30
9 | Bagerhat | 92 | 00:00 | 75 | KSRM | 27 | 13:00 | 141 | Rajendrapur | 146 | 20:00
10 | Bajitpur | 52 | 22:00 | 76 | Kabirpur | 263 | 19:30 | 142 | Rajshahi | 109 | 21:00
11 | Bakulia | 106 | 20:00 | 77 | Kachua | 91 | 22:00 | 143 | Rajshahi-230 | 79 | 13:00
12 | Banani | 42 | 12:00 | 78 | Kallyanpur | 105 | 19:00 | 144 | Ramganj | 102 | 05:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kalurghat | 26 | 16:00 | 145 | Rampur | 40 | 23:00
14 | Barapukuria | 65 | 20:00 | 80 | Kamrangirchar | 70 | 13:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 147 | 19:00
16 | Barishal | 110 | 19:00 | 82 | Kasba | 38 | 22:00 | 148 | Ruppur | 5 | 22:00
17 | Barishal-230 | 100 | 00:00 | 83 | Kazla | 107 | 19:30 | 149 | SSM | 6 | 23:00
18 | Baroaulia | 58 | 20:00 | 84 | Keranigonj | 99 | 19:30 | 150 | Saidpur | 110 | 20:00
19 | Baroirhat | 59 | 21:00 | 85 | Khagrachori | 34 | 21:00 | 151 | Satkhira | 140 | 20:00
20 | Bashundhara | 204 | 13:00 | 86 | Khulna | 63 | 22:00 | 152 | Satmasjid | 110 | 14:00
21 | BashundharaCement | 15 | 14:00 | 87 | Khulshi | 180 | 12:00 | 153 | Savar | 228 | 15:00
22 | Beanibazar | 78 | 22:00 | 88 | Kishoreganj | 142 | 21:00 | 154 | SevenRings | 5 | 23:00
23 | Benapole | 69 | 19:30 | 89 | Kodda | 311 | 14:00 | 155 | ShahCement | 29 | 08:00
24 | Bhaluka | 166 | 15:00 | 90 | Kulaura | 50 | 19:30 | 156 | Shahjadpur | 83 | 21:00
25 | Bhandaria | 53 | 01:00 | 91 | Kurigram | 60 | 20:00 | 157 | Shahjibazar | 123 | 21:00
26 | Bhangura | 36 | 19:00 | 92 | Kushtia | 156 | 20:00 | 158 | Shahmirpur | 50 | 18:00
27 | Bheramara(GK) | 69 | 21:00 | 93 | Lalbag | 56 | 18:30 | 159 | Shariatpur | 86 | 00:00
28 | Bhulta | 212 | 01:00 | 94 | Lalmonirhat | 64 | 19:00 | 160 | Sherpur | 146 | 21:00
29 | Bog-Sherpur | 58 | 00:00 | 95 | MI_Cement | 14 | 20:00 | 161 | Shikalbaha | 22 | 19:00
30 | Bogura | 169 | 19:30 | 96 | Madanganj | 48 | 21:00 | 162 | Shitalakhya | 90 | 13:00
31 | Borhanuddin | 87 | 23:00 | 97 | Madaripur | 110 | 00:00 | 163 | Sholosohor | 44 | 13:00
32 | Brahmanbaria | 117 | 05:00 | 98 | Madartek | 90 | 23:00 | 164 | Shyampur | 176 | 13:00
33 | Cantonment | 154 | 13:00 | 99 | Madunaghat | 50 | 19:30 | 165 | Siddhirganj | 126 | 12:00
34 | Chandina | 22 | 21:00 | 100 | Magura | 66 | 19:30 | 166 | Sirajganj | 96 | 18:30
35 | Chandpur | 72 | 23:00 | 101 | Mahasthangarh | 74 | 00:00 | 167 | Sonargaon | 133 | 23:00
36 | Chandraghona | 36 | 20:00 | 102 | Manikganj | 133 | 21:00 | 168 | Sreemongol | 80 | 20:00
37 | Chapai | 64 | 13:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 101 | 22:00
38 | Charsaidpur | 44 | 15:00 | 104 | Matarbari | 50 | 19:00 | 170 | Srinagar | 49 | 22:00
39 | Chauddagram | 73 | 00:00 | 105 | Matuail | 68 | 12:00 | 171 | Sunamganj | 63 | 22:00
40 | Chhatak | 39 | 23:00 | 106 | Millgate | 110 | 15:00 | 172 | Sylhet | 46 | 00:00
41 | Chowmuhani | 200 | 18:30 | 107 | Mirpur | 124 | 12:00 | 173 | Sylhet-132 | 136 | 10:00
42 | Chuadanga | 113 | 20:00 | 108 | Mirsorai | 11 | 12:00 | 174 | TK | 33 | 19:00
43 | Coxsbazar | 132 | 21:00 | 109 | Mirzapur | 48 | 22:00 | 175 | Tangail | 180 | 20:00
44 | Cumilla(N) | 150 | 23:00 | 110 | Mithapukur | 62 | 19:30 | 176 | Thakurgaon | 110 | 20:00
45 | Cumilla(S) | 176 | 18:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 137 | 18:30
46 | Daudkandi | 155 | 20:00 | 112 | Mogbazar | 157 | 14:00 | 178 | Ullahpara | 38 | 19:30
47 | Dhaka | 70 | 13:00 | 113 | Mongla | 42 | 19:00 | 179 | Ullon | 41 | 21:00
48 | Dhamrai | 136 | 18:30 | 114 | Motijheel | 42 | 12:00 | 180 | Uttara | 87 | 16:00
49 | Dhanmondi | 168 | 13:00 | 115 | Muktagacha | 33 | 00:00 | 181 | UttaraNew | 64 | 22:00
50 | Dohazari | 98 | 23:00 | 116 | Munshiganj | 118 | 23:00 | 182 | Zigatola | 76 | 15:00
51 | Faridpur | 168 | 20:00 | 117 | Muradnagar | 30 | 22:00
52 | Fatullah | 103 | 16:00 | 118 | Mymensingh | 193 | 00:00
53 | Fenchuganj | 45 | 18:30 | 119 | Naogaon | 124 | 21:00
54 | Feni | 124 | 21:00 | 120 | Narail | 58 | 22:00
55 | GPH | 95 | 08:00 | 121 | Narinda | 84 | 13:00
56 | Ghatail | 74 | 00:00 | 122 | Narshingdi | 155 | 19:00
57 | Ghorashal | 18 | 19:00 | 123 | Natore | 149 | 20:00
58 | Ghorashal-230 | 101 | 21:00 | 124 | Nawabganj | 59 | 22:00
59 | Goalpara | 42 | 00:00 | 125 | Netrakona | 122 | 02:00
60 | Gollamari | 100 | 00:00 | 126 | New | 91 | 16:00
61 | Gopalganj | 104 | 21:00 | 127 | Niamatpur | 62 | 22:00
62 | Gulshan | 124 | 12:00 | 128 | Noapara | 48 | 20:00
63 | Halishahar | 73 | 16:00 | 129 | PHP | 8 | 19:30
64 | HaripurSBU | 164 | 09:00 | 130 | Pabna | 129 | 21:00
65 | Hasnabad | 73 | 12:00 | 131 | Palashbari | 108 | 19:30
66 | Hathazari | 84 | 19:30 | 132 | Panchagarh | 63 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 24-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14164.5 | 119 |  | 14288.86
1:00 | 13447.5 | 238 |  | 13696.21
2:00 | 12975.5 | 196 |  | 13180.5
3:00 | 12826.5 | 185 |  | 13019.5
4:00 | 12594.5 | 159 |  | 12760.5
5:00 | 12421.5 | 123 |  | 12550.5
6:00 | 11972.04 | 105 |  | 12082.04
7:00 | 12041.21 | 97 |  | 12142.21
8:00 | 12149.85 | 52 |  | 12203.85
9:00 | 12379.29 | 32 |  | 12412.29
10:00 | 12595.75 | 36 |  | 12633.75
11:00 | 12982.77 | 29 |  | 13012.77
12:00 | 13321.71 | 31 |  | 13354.11
13:00 | 13649.84 | 32 |  | 13682.84
14:00 | 13602.47 | 34 |  | 13638.47
15:00 | 13700.73 | 51 |  | 13754.03
16:00 | 13572.98 | 53 |  | 13627.98
17:00 | 13141.12 | 71 |  | 13215.12
18:00 | 12864.05 | 46 |  | 12912.05
19:00 | 14389.64 | 68 |  | 14460.64
19:30 | 15136.43 | 85 |  | 15225.43
20:00 | 15205.45 | 91 |  | 15300.45
21:00 | 15316.2 | 80 |  | 15400.2
22:00 | 15184.4 | 87 |  | 15275.4
23:00 | 15053.2 | 150 |  | 15210.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 24-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7525.5 | 6639 | 14164.5 | DAILY GENERATION CURVE
00:30 | 7280.5 | 6525.5 | 13806
01:00 | 7035.5 | 6412 | 13447.5 | 24-05-2025
01:30 | 7005 | 6206.5 | 13211.5
02:00 | 6974.5 | 6001 | 12975.5
02:30 | 6949.5 | 5951.5 | 12901
03:00 | 6924.5 | 5902 | 12826.5
03:30 | 6908 | 5802.5 | 12710.5
04:00 | 6891.5 | 5703 | 12594.5
04:30 | 6813 | 5695 | 12508
05:00 | 6734.5 | 5687 | 12421.5
05:30 | 6646.01 | 5550.76 | 12196.77
06:00 | 6557.52 | 5414.52 | 11972.04
06:30 | 6587.06 | 5419.565 | 12006.625
07:00 | 6616.6 | 5424.61 | 12041.21
07:30 | 6666.855 | 5428.675 | 12095.53
08:00 | 6717.11 | 5432.74 | 12149.85
08:30 | 6739.29 | 5525.28 | 12264.57
09:00 | 6761.47 | 5617.82 | 12379.29
09:30 | 6872.145 | 5615.375 | 12487.52
10:00 | 6982.82 | 5612.93 | 12595.75
10:30 | 7035.245 | 5754.015 | 12789.26
11:00 | 7087.67 | 5895.1 | 12982.77
11:30 | 7267.56 | 5884.68 | 13152.24
12:00 | 7447.45 | 5874.26 | 13321.71
12:30 | 7516.93 | 5968.845 | 13485.775
13:00 | 7586.41 | 6063.43 | 13649.84
13:30 | 7621.575 | 6004.58 | 13626.155
14:00 | 7656.74 | 5945.73 | 13602.47
14:30 | 7703.325 | 5948.275 | 13651.6
15:00 | 7749.91 | 5950.82 | 13700.73
15:30 | 7700.95 | 5935.905 | 13636.855
16:00 | 7651.99 | 5920.99 | 13572.98
16:30 | 7516.62 | 5840.43 | 13357.05
17:00 | 7381.25 | 5759.87 | 13141.12
17:30 | 7350.72 | 5651.865 | 13002.585
18:00 | 7320.19 | 5543.86 | 12864.05
18:30 | 7676.595 | 5950.25 | 13626.845
19:00 | 8033 | 6356.64 | 14389.64
19:30 | 8363.26 | 6773.17 | 15136.43
20:00 | 8378.2 | 6827.25 | 15205.45
20:30 | 8373.7 | 6887.125 | 15260.825 |  | Executive Engineer
21:00 | 8369.2 | 6947 | 15316.2 |  | Network Operation Division
21:30 | 8262.2 | 6988.1 | 15250.3
22:00 | 8155.2 | 7029.2 | 15184.4
22:30 | 8089.2 | 7029.6 | 15118.8
23:00 | 8023.2 | 7030 | 15053.2

## En-Curve
QF-LDC-12
Date | 24-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3566 | 1944.5 | 681 | 0 | 42 | 1450 | 37 | 4980 | 0 | 409 | 1050 | 0 | 0 | 5 | 119 | DAILY ENERGY CURVE
00:30 | 3541.5 | 1936.5 | 767.5 | 0 | 41 | 1439 | 37 | 4820.5 | 0 | 357 | 861 | 0 | 0 | 5 | 178.5 | 24-05-2025
01:00 | 3517 | 1928.5 | 854 | 0 | 40 | 1428 | 37 | 4661 | 0 | 305 | 672 | 0 | 0 | 5 | 238
01:30 | 3524 | 1923 | 890.5 | 0 | 40 | 1326 | 37.5 | 4512 | 0 | 297 | 655 | 0 | 0 | 6.5 | 217 | Energy Generated | 325.6813 |  | MKWHr
02:00 | 3531 | 1917.5 | 927 | 0 | 40 | 1224 | 38 | 4363 | 0 | 289 | 638 | 0 | 0 | 8 | 196 | Energy not Served | 2.165 |  | MKWHr
02:30 | 3524 | 1910 | 927 | 0 | 39 | 1211.5 | 38.5 | 4322.5 | 0 | 289 | 631.5 | 0 | 0 | 8 | 190.5 | Total Energy Requirement | 327.8463 |  | MKWHr
03:00 | 3517 | 1902.5 | 927 | 0 | 38 | 1199 | 39 | 4282 | 0 | 289 | 625 | 0 | 0 | 8 | 185
03:30 | 3518 | 1903.5 | 927 | 0 | 38 | 1118.5 | 39.5 | 4264 | 0 | 289 | 603.5 | 0 | 0 | 9.5 | 172
04:00 | 3519 | 1904.5 | 927 | 0 | 38 | 1038 | 40 | 4246 | 0 | 289 | 582 | 0 | 0 | 11 | 159
04:30 | 3525.5 | 1906 | 927.5 | 0 | 37 | 1020.5 | 40 | 4194.5 | 0 | 268.5 | 574.5 | 0 | 0 | 14 | 141
05:00 | 3532 | 1907.5 | 928 | 0 | 36 | 1003 | 40 | 4143 | 0 | 248 | 567 | 0 | 0 | 17 | 123
05:30 | 3547.5 | 1928.5 | 927.5 | 0 | 31 | 950.5 | 40 | 3967.5 | 15.77 | 223 | 550.5 | 0 | 0 | 15 | 114
06:00 | 3563 | 1949.5 | 927 | 0 | 26 | 898 | 40 | 3792 | 31.54 | 198 | 534 | 0 | 0 | 13 | 105
06:30 | 3560 | 1937.5 | 927 | 0 | 29 | 885 | 40 | 3778.5 | 72.625 | 206.5 | 559.5 | 0 | 0 | 11 | 101
07:00 | 3557 | 1925.5 | 927 | 0 | 32 | 872 | 40 | 3765 | 113.71 | 215 | 585 | 0 | 0 | 9 | 97
07:30 | 3616 | 1928.5 | 895 | 0 | 31 | 848 | 40 | 3780 | 180.53 | 215 | 553 | 0 | 0 | 8.5 | 74.5
08:00 | 3675 | 1931.5 | 863 | 0 | 30 | 824 | 40 | 3795 | 247.35 | 215 | 521 | 0 | 0 | 8 | 52
08:30 | 3653.5 | 1912.75 | 863 | 0 | 29 | 823.5 | 40 | 3888.5 | 284.32 | 241 | 524.5 | 0 | 0 | 4.5 | 42
09:00 | 3632 | 1894 | 863 | 0 | 28 | 823 | 40 | 3982 | 321.29 | 267 | 528 | 0 | 0 | 1 | 32
09:30 | 3610 | 1899.25 | 887 | 0 | 30 | 843.5 | 39.5 | 4005.5 | 366.27 | 267 | 539 | 0 | 0 | 0.5 | 34
10:00 | 3588 | 1904.5 | 911 | 0 | 32 | 864 | 39 | 4029 | 411.25 | 267 | 550 | 0 | 0 | 0 | 36
10:30 | 3563 | 1915 | 910.5 | 0 | 32 | 963.5 | 38.5 | 4002.5 | 505.11 | 267 | 592.15 | 0 | 0 | 0 | 32.5
11:00 | 3538 | 1925.5 | 910 | 0 | 32 | 1063 | 38 | 3976 | 598.97 | 267 | 634.3 | 0 | 0 | 0 | 29
11:30 | 3515 | 1929.5 | 910 | 0 | 34 | 1085 | 37 | 4065.5 | 580.59 | 267.5 | 728.15 | 0 | 0 | 0 | 30
12:00 | 3492 | 1933.5 | 910 | 0 | 36 | 1107 | 36 | 4155 | 562.21 | 268 | 822 | 0 | 0 | 0 | 31
12:30 | 3523 | 1917.5 | 910 | 0 | 38 | 1144.5 | 36 | 4172 | 543.275 | 290 | 911.5 | 0 | 0 | 0 | 31.5
13:00 | 3554 | 1901.5 | 910 | 0 | 40 | 1182 | 36 | 4189 | 524.34 | 312 | 1001 | 0 | 0 | 0 | 32
13:30 | 3544.5 | 1906.75 | 910.5 | 0 | 40 | 1166.295 | 36 | 4119 | 497.11 | 307 | 1099 | 0 | 0 | 0 | 33
14:00 | 3535 | 1912 | 911 | 0 | 40 | 1150.59 | 36 | 4049 | 469.88 | 302 | 1197 | 0 | 0 | 0 | 34
14:30 | 3532 | 1911.15 | 910.5 | 0 | 40 | 1187.52 | 37 | 4124 | 373.68 | 307 | 1228.75 | 0 | 0 | 0 | 42.5
15:00 | 3529 | 1910.3 | 910 | 0 | 40 | 1224.45 | 38 | 4199 | 277.48 | 312 | 1260.5 | 0 | 0 | 0 | 51
15:30 | 3493.5 | 1898.15 | 910.5 | 0 | 39 | 1216.535 | 38.5 | 4212 | 254.42 | 321 | 1252.75 | 0 | 0 | 0.5 | 52
16:00 | 3458 | 1886 | 911 | 0 | 38 | 1208.62 | 39 | 4225 | 231.36 | 330 | 1245 | 0 | 0 | 1 | 53
16:30 | 3403.5 | 1846.5 | 910.5 | 0 | 38 | 1211.29 | 39.5 | 4170 | 154.51 | 319.5 | 1263.25 | 0 | 0 | 0.5 | 62
17:00 | 3349 | 1807 | 910 | 0 | 38 | 1213.96 | 40 | 4115 | 77.66 | 309 | 1281.5 | 0 | 0 | 0 | 71
17:30 | 3395 | 1822.5 | 910 | 0 | 37 | 1192.895 | 40 | 4006.5 | 48.44 | 320 | 1230.25 | 0 | 0 | 0 | 58.5
18:00 | 3441 | 1838 | 910 | 0 | 36 | 1171.83 | 40 | 3898 | 19.22 | 331 | 1179 | 0 | 0 | 0 | 46
18:30 | 3600.5 | 1864.5 | 886 | 0 | 40 | 1281.235 | 40 | 4186 | 9.61 | 395.5 | 1323.5 | 0 | 0 | 0 | 57
19:00 | 3760 | 1891 | 862 | 0 | 44 | 1390.64 | 40 | 4474 | 0 | 460 | 1468 | 0 | 0 | 0 | 68
19:30 | 3724.26 | 1928 | 862 | 0 | 44 | 1474.17 | 40 | 4784 | 0 | 495 | 1785 | 0 | 0 | 0 | 85
20:00 | 3633 | 1913 | 861 | 0 | 40 | 1449.25 | 40 | 4865 | 0 | 509 | 1895.2 | 0 | 0 | 0 | 91
20:30 | 3621.5 | 1896.5 | 885.5 | 0 | 39 | 1449.125 | 40 | 4881.5 | 0 | 536 | 1911.7 | 0 | 0 | 0 | 85.5
21:00 | 3610 | 1880 | 910 | 0 | 38 | 1449 | 40 | 4898 | 0 | 563 | 1928.2 | 0 | 0 | 0 | 80
21:30 | 3585.5 | 1925.5 | 910 | 0 | 41 | 1455.5 | 40 | 4932.1 | 0 | 529 | 1831.7 | 0 | 0 | 0 | 83.5
22:00 | 3561 | 1971 | 910 | 0 | 44 | 1462 | 40 | 4966.2 | 0 | 495 | 1735.2 | 0 | 0 | 0 | 87
22:30 | 3587.5 | 1965.5 | 910 | 0 | 45 | 1451.5 | 39 | 4966.6 | 0 | 419 | 1734.7 | 0 | 0 | 0 | 118.5
23:00 | 3614 | 1960 | 910 | 0 | 46 | 1441 | 38 | 4967 | 0 | 343 | 1734.2 | 0 | 0 | 0 | 150
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 24-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 06:00 | 346 | 01:00 | Payra | 415 | 06:00 | 408 | 00:00
Ashuganj | 392 | 6:00 | 364 | 11:00 | Rahanpur | 408 | 08:00 | 391 | 19:30
Bhulta | 385 | 06:00 | 361 | 11:00 | Rampal | 401 | 06:00 | 386 | 23:00
Bibiana | 391 | 06:00 | 384 | 23:00
BIPTC | 404 | 08:00 | 393 | 22:00
Bogura | 398 | 09:00 | 378 | 19:30
Gopalganj | 396 | 07:00 | 380 | 23:00
Kaliakoir | 374 | 07:00 | 360 | 23:00
Madunaghat | 399 | 18:00 | 385 | 00:00
Meghnaghat | 389 | 07:00 | 374 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 226 | 05:00 | 214 | 15:00 | Keranigonj | 222 | 07:00 | 211 | 16:00
AKSML | 231 | 07:00 | 222 | 01:00 | Khulna(S) | 229 | 10:00 | 215 | 23:00
Aminbazar | 224 | 06:00 | 212 | 05:00 | Madunaghat | 233 | 07:00 | 225 | 00:00
Ashuganj | 225 | 06:00 | 217 | 12:00 | Madunaghat-400 | 233 | 08:00 | 226 | 01:00
Ashuganj-400 | 222 | 6:00 | 216 | 11:00 | Maniknagar | 220 | 06:00 | 210 | 16:00
Baghabari | 233 | 07:00 | 223 | 15:00 | Meghnaghat | 230 | 07:00 | 220 | 11:00
Barapukuria | 222 | 03:00 | 215 | 19:00 | Meghnaghat-400 | 224 | 07:00 | 216 | 15:00
Barapukuria-230 | 220 | 4:00 | 210 | 19:00 | Mirsorai | 229 | 07:00 | 219 | 00:00
Barishal | 237 | 07:00 | 226 | 23:00 | Rajshahi | 234 | 08:00 | 221 | 19:00
Bheramara | 233 | 08:00 | 222 | 19:00 | Rampal | 229 | 07:00 | 217 | 21:00
Bhulta | 223 | 06:00 | 207 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 222 | 01:00 | 216 | 23:00 | Rampura | 223 | 07:00 | 204 | 12:00
BIPTC | 236 | 09:00 | 221 | 19:00 | Shikalbaha | 230 | 07:00 | 222 | 00:00
Bogura | 229 | 06:00 | 219 | 01:00 | Shyampur | 222 | 07:00 | 212 | 16:00
Bogura-400 | 229 | 09:00 | 219 | 19:30 | Siddhirganj | 222 | 07:00 | 214 | 16:00
Borhanuddin | 240 | 05:00 | 233 | 00:00 | Sirajgonj | 240 | 13:00 | 230 | 01:00
BSRM | 229 | 07:00 | 219 | 01:00 | Sreepur | 226 | 06:00 | 217 | 12:00
Cumilla(N) | 223 | 07:00 | 212 | 19:00 | Tongi | 223 | 05:00 | 206 | 11:00
Faridpur | 232 | 06:00 | 221 | 22:00
Fenchuganj | 224 | 09:00 | 218 | 01:00
Ghorashal | 230 | 00:00 | 215 | 12:00
Ghorashal-230 | 223 | 07:00 | 209 | 12:00
Gopalganj | 260 | 13:00 | 224 | 22:00
GPH | 230 | 07:00 | 222 | 01:00
Haripur | 221 | 06:00 | 213 | 15:00
Hasnabad | 221 | 07:00 | 212 | 16:00
Hathazari | 230 | 05:00 | 225 | 23:00
Ishurdi | 235 | 08:00 | 223 | 19:00
Jhenaidah | 229 | 09:00 | 215 | 23:00
Kaliakoir | 228 | 06:00 | 218 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 137 | 05:00 | 124 | 11:00 | Madartek | 136 | 06:00 | 124 | 12:00
Agargaon | 134 | 04:00 | 126 | 15:00 | Madunaghat | 132 | 17:00 | 126 | 00:00
Agrabad | 132 | 07:00 | 127 | 00:00 | Magura | 133 | 09:00 | 122 | 19:00
AKS | 129 | 06:00 | 126 | 00:00 | Mahasthangarh | 132 | 07:00 | 126 | 01:00
Aminbazar | 130 | 06:00 | 125 | 15:00 | Manikganj | 130 | 21:00 | 117 | 23:00
Amnura | 135 | 08:00 | 122 | 23:00 | Maniknagar | 133 | 05:00 | 125 | 16:00
Ashuganj | 135 | 07:00 | 127 | 18:30 | Matarbari | 120 | 09:00 | 109 | 22:00
Bagerhat | 132 | 10:00 | 117 | 23:00 | Matuail | 129 | 06:00 | 123 | 16:00
Bajitpur | 127 | 06:00 | 119 | 12:00 | Millgate | 133 | 04:00 | 123 | 11:00
Bakulia | 131 | 04:00 | 126 | 15:00 | Mirpur | 130 | 07:00 | 123 | 15:00
Banani | 137 | 06:00 | 122 | 12:00 | Mirzapur | 134 | 18:30 | 127 | 23:00
Bangabhaban | 133 | 05:00 | 125 | 12:00 | Mithapukur | 129 | 05:00 | 124 | 19:00
Barapukuria | 132 | 08:00 | 123 | 19:00 | MI_Cement | 129 | 06:00 | 123.2 | 16:00
Barguna | 135 | 17:00 | 130 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 08:00 | 123 | 23:00 | Mogbazar | 137 | 05:00 | 125 | 11:00
Barishal-230 | 131 | 05:00 | 123 | 23:00 | Mongla | 132 | 09:00 | 119 | 22:00
Baroaulia | 133 | 06:00 | 128 | 11:00 | Motijheel | 133 | 07:00 | 125 | 12:00
Baroirhat | 126 | 05:00 | 118 | 19:00 | Muktagacha | 136 | 18:30 | 125 | 01:00
Bashundhara | 138 | 07:00 | 121 | 16:00 | Munshiganj | 129 | 07:00 | 123 | 00:00
BashundharaCement | 128 | 05:00 | 122 | 16:00 | Muradnagar | 126 | 07:00 | 118 | 19:30
Beanibazar | 128 | 08:00 | 122 | 00:00 | Mymensingh | 137 | 18:30 | 112 | 00:00
Benapole | 132 | 09:00 | 112 | 00:00 | Naogaon | 130 | 05:00 | 124 | 01:00
Bhaluka | 130 | 06:00 | 120 | 19:00 | Narail | 134 | 09:00 | 121 | 19:00
Bhandaria | 130 | 06:00 | 115 | 00:00 | Narinda | 133 | 5:00 | 125 | 16:00
Bhangura | 132 | 05:00 | 126 | 19:00 | Narshingdi | 123 | 06:00 | 110 | 19:00
Bheramara | 136 | 06:00 | 130 | 23:00 | Natore | 135 | 09:00 | 127 | 19:30
Bheramara(GK) | 137 | 09:00 | 130 | 19:00 | Nawabganj | 132 | 04:00 | 125 | 15:00
Bhulta | 122 | 05:00 | 117 | 16:00 | Netrakona | 125 | 18:30 | 110 | 00:00
Bog-Sherpur | 133 | 06:00 | 127 | 01:00 | New | 133 | 06:00 | 124 | 11:00
Bogura | 135 | 05:00 | 131 | 00:00 | Niamatpur | 135 | 08:00 | 128 | 19:30
Bogura-230 | 136 | 09:00 | 129 | 01:00 | Noapara | 134 | 09:00 | 115 | 00:00
Brahmanbaria | 124 | 07:00 | 117 | 19:00 | Pabna | 134 | 07:00 | 127 | 19:00
Cantonment | 135 | 07:00 | 126 | 15:00 | Palashbari | 128 | 05:00 | 122 | 19:00
Chandina | 130 | 07:00 | 120 | 23:00 | Panchagarh | 134 | 18:30 | 118 | 02:00
Chandpur | 128 | 07:00 | 115 | 01:00 | Patuakhali | 134 | 07:00 | 130 | 00:00
Chandraghona | 132 | 07:00 | 127 | 00:00 | Payra | 136 | 05:00 | 133 | 00:00
Chapai | 132 | 04:00 | 124 | 22:00 | PHP | 130 | 07:00 | 114 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 05:00 | 123 | 16:00 | Postogola | 131 | 05:00 | 126 | 15:00
Chauddagram | 129 | 07:00 | 116 | 19:00 | Purbachal | 137 | 04:00 | 123 | 12:00
Chhatak | 126 | 06:00 | 119 | 00:00 | Purbasadipur | 131 | 22:00 | 116 | 11:00
Chowmuhani | 128 | 07:00 | 107 | 19:30 | Rahanpur | 136 | 06:00 | 130 | 19:30
Chuadanga | 131 | 09:00 | 118 | 23:00 | Rahanpur-400 | 136 | 05:00 | 130 | 19:30
Coxsbazar | 121 | 10:00 | 110 | 21:00 | Rahim | 129 | 07:00 | 123 | 14:00
Cumilla(N) | 130 | 07:00 | 120 | 19:30 | Rajbari | 134 | 06:00 | 125 | 23:00
Cumilla(S) | 133 | 04:00 | 118 | 18:30 | Rajendrapur | 131 | 07:00 | 115 | 12:00
Daudkandi | 123 | 07:00 | 116 | 19:30 | Rajshahi | 135 | 08:00 | 128 | 19:00
Dhaka | 137 | 06:00 | 123 | 12:00 | Rajshahi-230 | 135 | 08:00 | 119 | 23:00
Dhamrai | 133 | 06:00 | 127 | 15:00 | Ramganj | 127 | 07:00 | 109 | 02:00
Dhanmondi | 138 | 07:00 | 124 | 12:00 | Rampur | 131 | 05:00 | 127 | 00:00
Dohazari | 128 | 10:00 | 123 | 00:00 | Rampura | 137 | 07:00 | 123 | 12:00
Faridpur | 135 | 05:00 | 128 | 23:00 | Rangamati | 131 | 07:00 | 126 | 00:00
Fatullah | 130 | 06:00 | 124 | 16:00 | Rangpur | 128 | 03:00 | 121 | 19:00
Fenchuganj | 134 | 18:30 | 128 | 01:00 | Ruppur | 137 | 04:00 | 130 | 19:00
Feni | 130 | 07:00 | 118 | 02:00 | Saidpur | 130 | 23:00 | 119 | 19:30
Ghatail | 135 | 18:30 | 124 | 19:30 | Satkhira | 132 | 09:00 | 117 | 23:00
Ghorashal | 133 | 04:00 | 126 | 12:00 | Satmasjid | 135 | 07:00 | 126 | 16:00
Goalpara | 137 | 09:00 | 125 | 23:00 | Savar | 128 | 05:00 | 118 | 04:00
Gollamari | 136 | 05:00 | 126 | 19:00 | SevenRings | 133 | 07:00 | 125 | 12:00
Gopalganj | 134 | 05:00 | 125 | 23:00 | ShahCement | 129 | 05:00 | 123 | 16:00
Gopalganj-400 | 136 | 06:00 | 129 | 23:00 | Shahjadpur | 136 | 04:00 | 131 | 17:00
Gulshan | 137 | 07:00 | 123 | 12:00 | Shahjibazar | 127 | 18:00 | 120 | 19:30
Halishahar | 132 | 18:00 | 126 | 12:00 | Shahmirpur | 132 | 17:00 | 127 | 01:00
Haripur | 129 | 06:00 | 124 | 11:00 | Shariatpur | 134 | 09:00 | 125 | 22:00
HaripurSBU | 128 | 04:00 | 124 | 11:00 | Sherpur | 139 | 16:00 | 126 | 01:00
Hasnabad | 132 | 03:00 | 126 | 15:00 | Shikalbaha | 123 | 07:00 | 117 | 00:00
Hathazari | 134 | 05:00 | 129 | 23:00 | Shikalbaha-230 | 133 | 07:00 | 129 | 00:00
Ishurdi | 138 | 08:00 | 131 | 01:00 | Shitalakhya | 129 | 06:00 | 123 | 16:00
Jaldhaka | 128 | 02:00 | 120 | 11:00 | Sholosohor | 135 | 07:00 | 127 | 00:00
Jamalpur | 140 | 12:00 | 128 | 01:00 | Shyampur | 127 | 01:00 | 122 | 16:00
Jashore | 129 | 08:00 | 115 | 00:00 | Shyampur-230 | 130 | 07:00 | 123 | 16:00
Jhenaidah | 135 | 07:00 | 120 | 19:00 | Siddhirganj | 129 | 03:00 | 124 | 10:00
Jhenaidah-230 | 135 | 09:00 | 125 | 01:00 | Sirajganj | 132 | 08:00 | 125 | 19:00
Joydebpur | 131 | 05:00 | 119 | 16:00 | Sonargaon | 127 | 05:00 | 121 | 12:00
Joypurhat | 129 | 05:00 | 121 | 19:00 | Sreemongol | 128 | 07:00 | 121 | 22:00
Juldah | 133 | 20:00 | 128 | 00:00 | Sreepur | 132 | 06:00 | 125 | 11:00
Kabirpur | 134 | 04:00 | 120 | 15:00 | Srinagar | 133 | 05:00 | 125 | 15:00
Kachua | 127 | 07:00 | 114 | 01:00 | SSM | 138 | 05:00 | 122 | 10:00
Kaliakoir | 138 | 07:00 | 129 | 15:00 | Sunamganj | 125 | 07:00 | 118 | 00:00
Kallyanpur | 131 | 05:00 | 124 | 14:00 | Sylhet | 130 | 08:00 | 124 | 00:00
Kalurghat | 131 | 18:00 | 127 | 00:00 | Sylhet-132 | 129 | 05:00 | 125 | 23:00
Kamrangirchar | 133 | 06:00 | 125 | 12:00 | Tangail | 132 | 18:30 | 123 | 01:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 134 | 23:00 | 117 | 02:00
Kasba | 126 | 07:00 | 117 | 19:30 | TK | 130 | 07:00 | 120 | 06:00
Kazla | 133 | 07:00 | 125 | 12:00 | Tongi | 134 | 07:00 | 126 | 11:00
Keranigonj | 133 | 05:00 | 125 | 16:00 | Ullahpara | 133 | 08:00 | 127 | 01:00
Khagrachori | 130 | 07:00 | 125 | 01:00 | Ullon | 137 | 07:00 | 123 | 12:00
Khulna | 134 | 02:00 | 123 | 23:00 | Uttara | 130 | 06:00 | 123 | 15:00
Khulna(S) | 136 | 05:00 | 125 | 23:00 | UttaraNew | 130 | 06:00 | 123 | 15:00
Khulshi | 130 | 07:00 | 125 | 01:00 | Zigatola | 134 | 07:00 | 125 | 16:00
Kishoreganj | 129 | 18:30 | 117 | 15:00
Kodda | 134 | 09:00 | 118 | 15:00
KSRM | 134 | 07:00 | 127 | 15:00
Kulaura | 132 | 08:00 | 127 | 22:00
Kurigram | 129 | 09:00 | 120 | 19:00
Kushtia | 135 | 10:00 | 125 | 19:00
Lalbag | 133 | 07:00 | 125 | 12:00
Lalmonirhat | 128 | 09:00 | 120 | 19:00
Madanganj | 128 | 05:00 | 122 | 16:00
Madaripur | 135 | 08:00 | 127 | 22:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division