## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 26-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-05-2025 | during | 26-05-2025 | during | 26-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 351 | 329 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 300 | 450 | 450 | 340 | 340 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 286 | 283 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 25 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 266 | 335 | 335 | 301.5 | 301.5 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 90 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 46 | 145 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 15.5 | 33 | 33 | 17.5 | 17.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 16 | 17 | 22 | 22 | 17 | 17 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 17 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 260 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 92 | 112 | 135 | 135 | 135 | 135 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 52 | 105 | 105 | 52 | 52 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 50 | 57 | 90 | 90 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 19 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 250 | 250 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 2333 | 2692.5 | 5249.9 | 5308.9 | 3267.88 | 3326.88
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 100 | 0 | 150 | 150 | 100 | 100 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 1 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 11 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 35 | 50 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 39 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 31 | 184 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 48 | 48 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 34 | 34 | 34 | 34 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 3 | 2 | 2 | 10 | 2 | 10 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 2.11 | 0 | 2.11 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 53 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 0 | 1 | 0 | 1 | 0 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 533 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2152 | 2411 | 3501.83 | 3513.72 | 3459.83 | 3463.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 187 | 182 | 221.43 | 221.43 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 346 | 354 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 330 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 24 | 29 | 46.7 | 46.7 | 34 | 34 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 30 | 55 | 55 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 16 | 195 | 195 | 16 | 16 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 108 | 128 | 150 | 150 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 31 | 47 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 80 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 170 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 40 | 46 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 14 | 14 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 28 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 75 | 94 | 115 | 115 | 93 | 93 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 78 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1702 | 1786 | 2434.43 | 2394.43 | 2040.55 | 2000.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 25-05-2025 | during | 26-05-2025 | during | 26-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 3 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 120 | 170 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 96 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 43.56 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 35 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 279.56 | 313 | 601.1 | 549 | 393.6 | 341.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 10 | 38 | 37 | 37 | 30 | 30 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 145 | 142 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 22 | 18 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 22 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 171 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 13 | 8 | 25 | 25 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 324 | 350 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1393 | 1369 | 1572 | 1572 | 1475 | 1475
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 920 | 871 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 44 | 44 | 44 | 44 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 129 | 96 | 410 | 410 | 187 | 187 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 29.58 | 0 | 78 | 0 | 78 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 838 | 1134 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1916.58 | 2118 | 3592.2 | 3514.2 | 3354.2 | 3276.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 221 | 299 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 7 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 115 | 130 | 130 | 113 | 113 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1111 | 1200 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1829 | 2152 | 2172 | 2171 | 2115 | 2114
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 13 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 165 | 140 | 214 | 214 | 182 | 182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 124 | 220 | 220 | 169 | 169 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 370 | 413.79 | 413.79 | 413.79 | 413.79 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 15 | 22 | 22 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 41 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 55 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 20 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.01 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1217.26 | 1442.54 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 48.94 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 121 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 2111.21 | 2220.54 | 3186.72 | 3019.87 | 3103.72 | 2936.87
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 0 | 0 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 158 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 63 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.3 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 70 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 25 | 0 | 25 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 145 | 0 | 161.21 | 0 | 161.21 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 408.3 | 341 | 653.81 | 462 | 603.81 | 412
System Total |  |  |  |  | 28886.2 | 27110.055 | 14124.65 | 15403.04 | 22963.99 | 22505.12 | 19813.59 | 19346.72
Forecast Scenario (26-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14950 |  | 0 |  | 14950
|  |  |  | 1:00 | 14680 |  | 0 |  | 14680
|  |  |  | 2:00 | 14170 |  | 0 |  | 14170
|  |  |  | 3:00 | 13910 |  | 0 |  | 13910
|  |  |  | 4:00 | 13640 |  | 0 |  | 13640
|  |  |  | 5:00 | 13400 |  | 0 |  | 13400
|  |  |  | 6:00 | 12840 |  | 0 |  | 12840
|  |  |  | 7:00 | 12960 |  | 0 |  | 12960
|  |  |  | 8:00 | 12940 |  | 0 |  | 12940
|  |  |  | 9:00 | 13512 |  | 0 |  | 13512
|  |  |  | 10:00 | 13640 |  | 0 |  | 13640
|  |  |  | 11:00 | 13870 |  | 0 |  | 13870
|  |  |  | 12:00 | 14310 |  | 0 |  | 14310
|  |  |  | 13:00 | 14480 |  | 0 |  | 14480
|  |  |  | 14:00 | 14260 |  | 0 |  | 14260
|  |  |  | 15:00 | 14280 |  | 0 |  | 14280
|  |  |  | 16:00 | 13880 |  | 0 |  | 13880
|  |  |  | 17:00 | 13760 |  | 0 |  | 13760
|  |  |  | 18:00 | 13400 |  | 0 |  | 13400
|  |  |  | 18:30 | 13900 |  | 0 |  | 13900
|  |  |  | 19:00 | 14950 |  | 0 |  | 14950
|  |  |  | 19:30 | 15500 |  | 0 |  | 15500
|  |  |  | 20:00 | 15120 |  | 0 |  | 15120
|  |  |  | 21:00 | 15230 |  | 0 |  | 15230
|  |  |  | 22:00 | 15100 |  | 0 |  | 15100
|  |  |  | 23:00 | 15000 |  | 0 |  | 15000
Probable Maximum Temperature: |  |  | 31.30°C
Probable Maximum Demand at Day Peak: |  |  | 14310.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15500.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 338.282 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:27 hrs on 26-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 25-05-2025 | [28 empty] | Date: | 25-05-2025 | [28 empty] | Date: | 25-05-2025 | [28 empty] | Date: | 25-05-2025 | [28 empty] | Date: | 25-05-2025 | [16 empty] | Date: | 25-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [16 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 54 | 17 | 110 | 48 | 95 | 0 | 35 | 126 | 0 | 51 | 320 | 308 | 370 | 0 | 35 | 0 | 272 | 0 | 0 | 0 | 90 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 6 | 34 | 39 | 0 | 100 | 24 | 0 | 36 | 0 | 24 | 575 | 0 | 0 | 25 | 8 | 0 | 51 | 0 | 0 | 0 | 1224 | 0 | 43 | 30 | 8 | 0 | 350 | 340 | 30 | 201 | 33 | 93 | 75 | 110 | 9 | 14 | 114 | 46 | 52.2 | 0 | 31 | 305 | 320 | 374 | 29 | 0 | 0 | 132 | 10 | 0 | 83 | 22 | 0 | 18 | 172 | 17 | 105 | 162 | 0 | 0 | 0 | 12 | 7912.2 | 910 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1186 | 35 | 1454 | 0 | 0 | 0 | 35 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 156 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 161 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 120 | 220 | 0 | 306 | 1112 | 0 | 6837 | 14749.2 | 76.98
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 41 | 17 | 108 | 47 | 0 | 0 | 35 | 90 | 0 | 34 | 320 | 298 | 370 | 0 | 17 | 0 | 260 | 0 | 0 | 0 | 17 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 4 | 34 | 38 | 0 | 100 | 24 | 0 | 36 | 0 | 24 | 575 | 0 | 0 | 19 | 8 | 0 | 51 | 0 | 0 | 0 | 1224 | 0 | 43 | 30 | 8 | 0 | 357 | 340 | 30 | 182 | 33 | 93 | 75 | 200 | 9 | 14 | 114 | 48 | 52.2 | 0 | 31 | 300 | 320 | 349 | 29 | 0 | 0 | 145 | 10 | 0 | 83 | 22 | 0 | 18 | 172 | 17 | 48 | 96 | 0 | 0 | 0 | 8 | 7548.2 | 919 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1160 | 35 | 1456 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 156 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 120 | 220 | 0 | 306 | 1110 | 0 | 6831 | 14379.2 | 76.98
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 29 | 17 | 105 | 47 | 0 | 0 | 35 | 17 | 0 | 34 | 320 | 304 | 370 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 5 | 34 | 15 | 0 | 70 | 0 | 0 | 37 | 0 | 29 | 576 | 0 | 0 | 0 | 8 | 0 | 51 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 30 | 195 | 34 | 93 | 80 | 200 | 9 | 14 | 114 | 46 | 52.2 | 0 | 31 | 300 | 320 | 364 | 29 | 0 | 0 | 148 | 10 | 0 | 83 | 22 | 0 | 18 | 172 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7380.2 | 919 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1159 | 17 | 1363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 149 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 156 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 120 | 220 | 0 | 306 | 1110 | 0 | 6495 | 13875.2 | 76.98
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 321 | 0 | 0 | 17 | 17 | 106 | 47 | 0 | 0 | 35 | 17 | 0 | 16 | 320 | 304 | 370 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 17 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 8 | 17 | 15 | 0 | 50 | 0 | 0 | 38 | 0 | 31 | 571 | 0 | 0 | 0 | 8 | 0 | 51 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 8 | 0 | 353 | 340 | 30 | 194 | 34 | 93 | 80 | 200 | 9 | 14 | 114 | 44 | 52.2 | 0 | 31 | 300 | 320 | 376 | 29 | 0 | 0 | 150 | 10 | 0 | 83 | 22 | 0 | 18 | 172 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7213.2 | 920 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1143 | 17 | 1322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 136 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 110 | 220 | 0 | 307 | 1110 | 0 | 6418 | 13631.2 | 76.98
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 17 | 17 | 104 | 48 | 0 | 0 | 35 | 17 | 0 | 16 | 320 | 301 | 370 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 17 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 9 | 17 | 15 | 0 | 50 | 0 | 0 | 39 | 0 | 32 | 497 | 0 | 0 | 0 | 8 | 0 | 51 | 0 | 0 | 0 | 1103 | 0 | 51 | 0 | 8 | 0 | 355 | 340 | 30 | 195 | 34 | 93 | 90 | 200 | 9 | 14 | 114 | 44 | 52.2 | 0 | 31 | 305 | 320 | 375 | 28 | 0 | 0 | 150 | 10 | 0 | 83 | 28 | 0 | 18 | 172 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7160.2 | 919 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1045 | 17 | 1239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 124 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 120 | 220 | 0 | 309 | 1110 | 0 | 6203 | 13363.2 | 76.98
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 17 | 17 | 0 | 48 | 0 | 0 | 35 | 17 | 0 | 16 | 320 | 297 | 370 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 17 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 100 | 12 | 17 | 15 | 0 | 50 | 0 | 0 | 40 | 0 | 32 | 456 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 1102 | 0 | 51 | 0 | 8 | 0 | 356 | 340 | 30 | 186 | 34 | 92 | 90 | 200 | 9 | 14 | 114 | 44 | 52.2 | 0 | 31 | 305 | 320 | 350 | 28 | 0 | 0 | 152 | 10 | 0 | 83 | 28 | 0 | 18 | 172 | 0 | 48 | 96 | 0 | 0 | 0 | 12 | 6964.2 | 920 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 17 | 1217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 129 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 166 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 110 | 220 | 0 | 306 | 1110 | 0 | 6145 | 13109.2 | 76.98
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 17 | 17 | 0 | 48 | 0 | 0 | 0 | 17 | 0 | 0 | 320 | 311 | 370 | 0 | 0 | 0 | 315 | 0 | 0 | 1 | 17 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 15 | 0 | 50 | 0 | 0 | 40 | 0 | 32 | 455 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 1005 | 1 | 51 | 0 | 8 | 0 | 300 | 280 | 30 | 209 | 34 | 68 | 80 | 200 | 8 | 14 | 114 | 42 | 34 | 6 | 32 | 290 | 320 | 397 | 28 | 0 | 0 | 136 | 10 | 0 | 83 | 28 | 0 | 18 | 172 | 0 | 48 | 96 | 0 | 0 | 2.01 | 12 | 6739.01 | 919 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.07 | 932 | 0 | 1222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2 | 166 | 0 | 145 | 0 | 0 | 0 | 350 | 0 | 0.2 | 0 | 165 | 51 | 0 | 1 | 0 | 0 | 0 | 0.3 | 17 | 0.15 | 0 | 150 | 9 | 120 | 180 | 0 | 220 | 1000 | 0 | 5812.72 | 12551.73 | 76.98
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 0 | 48 | 0 | 0 | 0 | 17 | 0 | 0 | 320 | 302 | 300 | 0 | 0 | 0 | 323 | 0 | 0 | 8 | 17 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 50 | 0 | 1 | 40 | 0 | 36 | 403 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 1031 | 9 | 51 | 0 | 8 | 0 | 352 | 335 | 30 | 192 | 34 | 68 | 80 | 200 | 9 | 14 | 114 | 40 | 16 | 27 | 32 | 295 | 320 | 360 | 28 | 0 | 0 | 152 | 10 | 0 | 83 | 28 | 0 | 18 | 172 | 3 | 68 | 125 | 0 | 0 | 7.32 | 12 | 6826.32 | 917 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 862 | 0 | 1233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 11.22 | 166 | 0 | 157 | 0 | 0 | 0 | 414 | 0 | 1.03 | 0 | 165 | 50 | 0 | 6 | 0 | 0 | 0 | 0.8 | 42 | 0.61 | 0 | 150 | 8 | 120 | 180 | 0 | 224 | 1000 | 0 | 5895.66 | 12721.98 | 76.98
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 0 | 17 | 17 | 36 | 48 | 0 | 0 | 17 | 17 | 0 | 0 | 320 | 308 | 300 | 0 | 0 | 0 | 320 | 0 | 0 | 16 | 17 | 12 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 50 | 0 | 2 | 40 | 0 | 7 | 402 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1030 | 0 | 51 | 0 | 8 | 0 | 350 | 340 | 30 | 195 | 34 | 68 | 80 | 170 | 9 | 14 | 114 | 34 | 8 | 36 | 32 | 305 | 320 | 335 | 28 | 0 | 0 | 136 | 10 | 0 | 83 | 30 | 0 | 18 | 172 | 17 | 67 | 125 | 0 | 1 | 24.18 | 11 | 6823.18 | 872 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.06 | 851 | 0 | 1213.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 17.81 | 166 | 0 | 160 | 0 | 0 | 0 | 350 | 0 | 2.72 | 0 | 167 | 50 | 0 | 8 | 0 | 0 | 0 | 1.8 | 120 | 0.58 | 0 | 150 | 7 | 120 | 180 | 0 | 222 | 1046 | 0 | 5910.96 | 12734.14 | 76.98
09:00 | 0 | 52 | 12 | 0 | 0 | 0 | 0 | 0 | 396 | 0 | 0 | 17 | 17 | 74 | 48 | 0 | 0 | 35 | 72 | 0 | 0 | 320 | 301 | 300 | 0 | 0 | 0 | 317 | 0 | 0 | 16 | 52 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 100 | 2 | 2 | 40 | 0 | 2 | 451 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 1055 | 0 | 51 | 0 | 8 | 0 | 346 | 335 | 30 | 199 | 33 | 72 | 80 | 170 | 9 | 14 | 114 | 36 | 8 | 50 | 32 | 310 | 320 | 387 | 27 | 0 | 0 | 138 | 10 | 0 | 80 | 25 | 0 | 18 | 173 | 17 | 67 | 125 | 0 | 2 | 43.1 | 12 | 7199.1 | 872 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.25 | 854 | 0 | 1217.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 28.38 | 166 | 0 | 155 | 0 | 0 | 0 | 414 | 0 | 2.42 | 0 | 168 | 50 | 35 | 14 | 0 | 0 | 0 | 1 | 146 | 0.17 | 0 | 150 | 7 | 120 | 220 | 0 | 222 | 1043 | 0 | 6111.08 | 13310.18 | 76.98
10:00 | 8 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 27 | 17 | 77 | 48 | 120 | 2 | 35 | 162 | 0 | 20 | 320 | 269 | 250 | 0 | 35 | 0 | 266 | 0 | 0 | 18 | 52 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 88 | 50 | 3 | 40 | 0 | 2 | 450 | 0 | 0 | 3 | 0 | 0 | 31 | 0 | 0 | 0 | 1100 | 0 | 43 | 13 | 16 | 0 | 348 | 335 | 30 | 205 | 21 | 76 | 75 | 170 | 9 | 14 | 114 | 36 | 8 | 34 | 32 | 310 | 320 | 336 | 27 | 0 | 0 | 151 | 3 | 0 | 80 | 25 | 0 | 16 | 172 | 17 | 67 | 122 | 0 | 2 | 50.06 | 12 | 7353.06 | 919 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.83 | 759 | 0 | 1218.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 37 | 166 | 0 | 150 | 0 | 0 | 0 | 414 | 0 | 3.47 | 0 | 165 | 50 | 35 | 17 | 0 | 0 | 0 | 1.7 | 157 | 0.38 | 0 | 150 | 7 | 110 | 220 | 0 | 221 | 1065 | 0 | 6126.78 | 13479.84 | 76.98
11:00 | 16 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 78 | 46 | 145 | 25 | 35 | 162 | 0 | 31 | 320 | 289 | 250 | 0 | 35 | 0 | 280 | 0 | 0 | 16 | 52 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 0 | 15 | 0 | 88 | 50 | 4 | 39 | 0 | 2 | 400 | 0 | 0 | 23 | 0 | 0 | 31 | 0 | 0 | 0 | 1150 | 16 | 43 | 75 | 16 | 0 | 340 | 300 | 30 | 198 | 21 | 74 | 75 | 170 | 8 | 14 | 114 | 38 | 8 | 61 | 31 | 305 | 320 | 311 | 27 | 0 | 0 | 136 | 13 | 0 | 78 | 22 | 0 | 16 | 172 | 20 | 67 | 120 | 0 | 3 | 50.43 | 11 | 7504.43 | 919 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.68 | 763 | 0 | 1219.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 64.95 | 166 | 0 | 141 | 0 | 0 | 0 | 414 | 0 | 4.96 | 0 | 162 | 50 | 35 | 12 | 0 | 0 | 0 | 1.8 | 142 | 0.28 | 0 | 150 | 7 | 120 | 220 | 0 | 221 | 1102 | 0 | 6195.18 | 13699.61 | 76.98
12:00 | 16 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 54 | 17 | 92 | 46 | 145 | 25 | 35 | 162 | 0 | 50 | 320 | 286 | 250 | 0 | 35 | 0 | 270 | 0 | 0 | 19 | 52 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 0 | 16 | 0 | 100 | 50 | 3 | 39 | 0 | 3 | 533 | 0 | 0 | 35 | 0 | 0 | 31 | 0 | 0 | 0 | 1224 | 11 | 43 | 108 | 16 | 0 | 346 | 340 | 30 | 187 | 24 | 75 | 70 | 170 | 8 | 14 | 114 | 40 | 8 | 78 | 31 | 310 | 320 | 324 | 10 | 0 | 0 | 145 | 13 | 0 | 78 | 22 | 0 | 0 | 171 | 35 | 67 | 120 | 0 | 3 | 43.56 | 11 | 7859.56 | 920 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.58 | 838 | 0 | 1217.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 48.94 | 165 | 0 | 140 | 0 | 0 | 0 | 414 | 0 | 5.01 | 0 | 160 | 50 | 35 | 16 | 0 | 0 | 0 | 2.3 | 145 | 0 | 0 | 150 | 7 | 120 | 220 | 0 | 221 | 1111 | 0 | 6265.09 | 14124.65 | 76.98
13:00 | 16 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 54 | 17 | 94 | 46 | 145 | 25 | 35 | 162 | 0 | 50 | 320 | 288 | 250 | 0 | 35 | 0 | 270 | 0 | 0 | 30 | 52 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 24 | 17 | 16 | 0 | 100 | 50 | 1 | 35 | 0 | 2 | 570 | 0 | 0 | 44 | 0 | 0 | 41 | 0 | 0 | 0 | 1224 | 11 | 43 | 118 | 16 | 0 | 343 | 340 | 30 | 187 | 25 | 79 | 70 | 169 | 9 | 14 | 114 | 46 | 8 | 54 | 34 | 315 | 320 | 325 | 12 | 0 | 0 | 150 | 0 | 0 | 80 | 22 | 0 | 0 | 171 | 35 | 66 | 120 | 0 | 2 | 41.64 | 11 | 7942.64 | 919 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.42 | 946 | 0 | 1256.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16.38 | 153 | 0 | 137 | 0 | 0 | 0 | 414 | 0 | 1.48 | 0 | 158 | 50 | 35 | 22 | 0 | 0 | 0 | 3.2 | 169 | 0 | 0 | 150 | 7 | 110 | 220 | 0 | 224 | 1109 | 0 | 6325.38 | 14268.02 | 76.98
14:00 | 16 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 54 | 17 | 94 | 46 | 145 | 25 | 35 | 162 | 0 | 50 | 320 | 290 | 250 | 0 | 35 | 0 | 275 | 0 | 0 | 2 | 52 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 27 | 34 | 16 | 0 | 100 | 50 | 1 | 35 | 0 | 2 | 570 | 0 | 0 | 8 | 0 | 0 | 41 | 0 | 0 | 0 | 1224 | 14 | 43 | 105 | 16 | 0 | 300 | 335 | 30 | 186 | 27 | 94 | 70 | 183 | 12 | 14 | 114 | 46 | 8 | 41 | 39 | 310 | 320 | 315 | 10 | 0 | 0 | 135 | 0 | 0 | 79 | 25 | 0 | 0 | 170 | 35 | 66 | 119 | 0 | 1 | 17.23 | 11 | 7766.23 | 920 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.37 | 963 | 0 | 1259.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 29.62 | 153 | 0 | 131 | 0 | 0 | 0 | 414 | 0 | 1.9 | 0 | 158 | 51 | 35 | 27 | 0 | 0 | 0 | 2.9 | 128 | 0.17 | 0 | 150 | 7 | 90 | 220 | 0 | 224 | 1110 | 0 | 6288.49 | 14054.72 | 76.98
15:00 | 16 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 54 | 17 | 94 | 46 | 145 | 25 | 35 | 162 | 0 | 50 | 320 | 313 | 250 | 0 | 35 | 0 | 268 | 0 | 0 | 3 | 52 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 13 | 34 | 16 | 0 | 100 | 50 | 2 | 37 | 0 | 2 | 570 | 0 | 0 | 40 | 0 | 0 | 59 | 0 | 0 | 0 | 1224 | 0 | 43 | 105 | 16 | 0 | 300 | 340 | 30 | 183 | 27 | 94 | 70 | 200 | 9 | 14 | 114 | 48 | 8 | 55 | 39 | 305 | 320 | 350 | 10 | 0 | 0 | 130 | 0 | 0 | 22 | 20 | 0 | 0 | 170 | 35 | 66 | 109 | 0 | 1 | 12.8 | 11 | 7785.8 | 918 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.99 | 962 | 0 | 1262.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 52.66 | 152 | 0 | 127 | 0 | 0 | 0 | 414 | 0 | 4.15 | 0 | 157 | 50 | 35 | 24 | 0 | 0 | 0 | 2.7 | 130 | 0.11 | 0 | 150 | 8 | 96 | 220 | 0 | 222 | 1110 | 0 | 6268.71 | 14054.51 | 76.98
16:00 | 16 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 54 | 17 | 108 | 46 | 60 | 25 | 35 | 162 | 0 | 50 | 320 | 304 | 250 | 0 | 35 | 0 | 295 | 0 | 0 | 4 | 52 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 100 | 7 | 34 | 16 | 0 | 100 | 12 | 3 | 38 | 0 | 2 | 575 | 0 | 0 | 46 | 0 | 0 | 103 | 0 | 0 | 0 | 1224 | 7 | 43 | 80 | 16 | 0 | 300 | 340 | 30 | 202 | 28 | 94 | 70 | 200 | 8 | 14 | 114 | 46 | 8 | 23 | 46 | 310 | 320 | 350 | 10 | 0 | 0 | 143 | 0 | 0 | 22 | 20 | 0 | 0 | 169 | 25 | 67 | 112 | 0 | 0 | 0.97 | 11 | 7746.97 | 919 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1 | 959 | 0 | 1142.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 18.4 | 144 | 0 | 125 | 0 | 0 | 0 | 350 | 0 | 2.66 | 0 | 156 | 50 | 35 | 22 | 0 | 0 | 0 | 2.4 | 131 | 0.2 | 0 | 150 | 8 | 100 | 180 | 0 | 221 | 1110 | 0 | 5946.82 | 13693.79 | 76.98
17:00 | 24 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 54 | 17 | 112 | 46 | 60 | 25 | 35 | 162 | 0 | 50 | 320 | 298 | 250 | 0 | 35 | 0 | 297 | 0 | 0 | 4 | 70 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 80 | 2 | 34 | 16 | 0 | 100 | 12 | 0 | 38 | 0 | 2 | 502 | 0 | 0 | 48 | 0 | 0 | 171 | 0 | 0 | 0 | 1224 | 4 | 51 | 50 | 16 | 0 | 320 | 340 | 30 | 208 | 28 | 94 | 70 | 200 | 9 | 14 | 114 | 40 | 8 | 10 | 39 | 310 | 320 | 378 | 38 | 0 | 0 | 144 | 0 | 0 | 22 | 20 | 0 | 0 | 170 | 29 | 68 | 114 | 0 | 0 | 1.03 | 11 | 7789.03 | 920 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.98 | 957 | 0 | 1134.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 10.77 | 144 | 0 | 123 | 0 | 0 | 0 | 380 | 0 | 1.08 | 0 | 162 | 48 | 35 | 4 | 0 | 0 | 0 | 1.3 | 28 | 0.15 | 0 | 150 | 7 | 100 | 220 | 0 | 221 | 1110 | 0 | 5865.32 | 13654.35 | 76.98
18:00 | 50 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 54 | 17 | 112 | 47 | 60 | 25 | 35 | 162 | 0 | 50 | 300 | 300 | 250 | 0 | 35 | 0 | 290 | 0 | 0 | 1 | 125 | 15.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34 | 16 | 0 | 100 | 12 | 0 | 40 | 0 | 2 | 452 | 0 | 0 | 49 | 0 | 0 | 184 | 0 | 0 | 0 | 1113 | 0 | 51 | 50 | 16 | 0 | 300 | 300 | 30 | 203 | 28 | 94 | 70 | 200 | 25 | 14 | 114 | 40 | 8 | 3 | 46 | 305 | 320 | 370 | 38 | 0 | 0 | 146 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 35 | 65 | 123 | 0 | 0 | 0 | 12 | 7612.5 | 919 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.28 | 936 | 5 | 1136.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1.98 | 140 | 0 | 123 | 0 | 0 | 0 | 350 | 0 | 0.19 | 0 | 157 | 50 | 35 | 1 | 0 | 0 | 0 | 0.5 | 2 | 0.04 | 0 | 164 | 7 | 120 | 220 | 0 | 228 | 1000 | 0 | 5672.44 | 13284.94 | 76.98
19:00 | 90 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 397 | 0 | 0 | 54 | 17 | 112 | 120 | 130 | 25 | 35 | 162 | 0 | 54 | 300 | 301 | 250 | 0 | 35 | 0 | 308 | 0 | 0 | 0 | 150 | 15.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 100 | 56 | 0 | 40 | 0 | 5 | 575 | 17 | 0 | 50 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 16 | 0 | 342 | 325 | 30 | 213 | 29 | 94 | 75 | 200 | 26 | 14 | 114 | 48 | 16 | 0 | 47 | 305 | 320 | 352 | 38 | 0 | 0 | 146 | 8 | 0 | 22 | 20 | 0 | 0 | 171 | 35 | 97 | 152 | 0 | 0 | 0 | 12 | 8348.5 | 872 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 17 | 1447.52 | 0 | 0 | 0 | 12 | 0 | 40 | 0 | 12 | 0 | 0 | 15 | 0 | 141 | 0 | 125 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 159 | 50 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 125 | 220 | 0 | 299 | 1030 | 0 | 6506.52 | 14855.02 | 76.97
19:30 | 90 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 35 | 17 | 112 | 145 | 260 | 55 | 35 | 162 | 0 | 57 | 300 | 283 | 250 | 0 | 35 | 0 | 266 | 0 | 0 | 0 | 160 | 15.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 48 | 0 | 100 | 100 | 0 | 40 | 0 | 2 | 575 | 53 | 0 | 50 | 1 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 128 | 16 | 0 | 354 | 330 | 30 | 182 | 29 | 94 | 80 | 200 | 28 | 14 | 114 | 46 | 43 | 0 | 47 | 300 | 320 | 350 | 38 | 0 | 0 | 142 | 8 | 0 | 22 | 18 | 0 | 0 | 171 | 35 | 96 | 170 | 0 | 0 | 0 | 12 | 8571.5 | 871 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1134 | 17 | 1442.54 | 0 | 0 | 0 | 55 | 0 | 41 | 20 | 13 | 0 | 0 | 15 | 0 | 140 | 0 | 124 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 158 | 50 | 70 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 115 | 220 | 0 | 299 | 1200 | 0 | 6831.54 | 15403.04 | 76.97
20:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 36 | 17 | 112 | 144 | 145 | 15 | 35 | 162 | 0 | 55 | 300 | 275 | 250 | 0 | 35 | 0 | 267 | 0 | 0 | 0 | 125 | 15.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 48 | 0 | 100 | 48 | 0 | 40 | 0 | 5 | 575 | 17 | 0 | 50 | 5 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 16 | 0 | 320 | 330 | 30 | 218 | 30 | 94 | 80 | 200 | 29 | 11 | 114 | 46 | 52.2 | 0 | 47 | 300 | 320 | 350 | 38 | 0 | 0 | 134 | 8 | 0 | 22 | 20 | 0 | 0 | 172 | 35 | 87 | 171 | 0 | 0 | 0 | 12 | 8142.7 | 871 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224 | 17 | 1448.42 | 0 | 32 | 0 | 50 | 0 | 41 | 30 | 25 | 0 | 0 | 22 | 0 | 140 | 0 | 125 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 157 | 50 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 180 | 0 | 298 | 1210 | 0 | 6878.42 | 15021.12 | 76.97
21:00 | 0 | 52 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 46 | 17 | 112 | 144 | 45 | 0 | 35 | 156 | 0 | 66 | 300 | 285 | 250 | 0 | 35 | 0 | 270 | 0 | 0 | 0 | 108 | 15.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 60 | 12 | 0 | 40 | 0 | 18 | 575 | 17 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 50 | 16 | 0 | 354 | 330 | 30 | 217 | 30 | 94 | 80 | 200 | 28 | 11 | 114 | 46 | 52.2 | 0 | 47 | 300 | 320 | 351 | 39 | 0 | 0 | 138 | 0 | 0 | 22 | 20 | 0 | 0 | 172 | 35 | 106 | 171 | 0 | 0 | 0 | 12 | 8014.7 | 918 | 89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 17 | 1461.89 | 0 | 50 | 0 | 35 | 0 | 41 | 0 | 32 | 0 | 0 | 15 | 0 | 140 | 0 | 125 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 159 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 299 | 1244 | 0 | 7118.89 | 15133.59 | 76.97
22:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 112 | 144 | 45 | 0 | 35 | 144 | 0 | 16 | 300 | 298 | 250 | 0 | 35 | 0 | 286 | 0 | 0 | 0 | 90 | 15.7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 60 | 12 | 0 | 40 | 0 | 22 | 555 | 17 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 351 | 330 | 30 | 215 | 30 | 94 | 80 | 200 | 29 | 11 | 114 | 48 | 52.2 | 0 | 47 | 295 | 320 | 386 | 39 | 0 | 0 | 141 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 35 | 106 | 172 | 0 | 0 | 0 | 12 | 7937.9 | 919 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1460.64 | 0 | 0 | 0 | 45 | 0 | 42 | 0 | 0 | 0 | 0 | 15 | 0 | 140 | 0 | 126 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 159 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 298 | 1215 | 0 | 7023.84 | 14961.74 | 76.97
23:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 112 | 112 | 45 | 0 | 35 | 162 | 0 | 16 | 300 | 303 | 250 | 0 | 35 | 0 | 308 | 0 | 0 | 0 | 90 | 15.7 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 70 | 24 | 0 | 40 | 0 | 20 | 571 | 17 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 348 | 335 | 30 | 215 | 30 | 94 | 80 | 200 | 28 | 14 | 114 | 46 | 52.2 | 0 | 46 | 305 | 320 | 392 | 39 | 0 | 0 | 141 | 0 | 0 | 22 | 18 | 0 | 0 | 171 | 35 | 105 | 172 | 0 | 0 | 0 | 12 | 8001.9 | 919 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1461.73 | 0 | 0 | 0 | 72 | 0 | 42 | 0 | 0 | 0 | 0 | 15 | 0 | 139 | 0 | 125 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 157 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 300 | 1244 | 0 | 7078.93 | 15080.83 | 76.97
Total KWH | 265824 | 839040 | 424320 | 0 | 0 | 0 | 0 | 0 | 8726400 | 0 | 0 | 849600 | 432720 | 2118816 | 1552320 | 1588004 | 269651 | 779741 | 2695680 | 0 | 754560 | 7724500 | 7190720 | 7039091 | 0 | 550232 | 0 | 6976948 | 0 | 0 | 110078 | 1410000 | 343800 | 393480 | 0 | 0 | 0 | 0 | 0 | 1800000 | 127680 | 511359 | 460272 | 0 | 1956480 | 510720 | 21582 | 924180 | 0 | 329760 | 12421818.18 | 100364 | 0 | 527040 | 59076.9 | 0 | 2079611 | 0 | 0 | 0 | 27878179 | 70605 | 1144244 | 1142472 | 351273 | 0 | 8429000 | 8066000 | 730080 | 4859000 | 711864 | 2105280 | 1834970 | 4630080 | 341040 | 303680 | 2764500 | 1041600 | 685229 | 494709 | 880736 | 7390500 | 7667400 | 8999000 | 450000 | 0 | 0 | 3439964 | 151320 | 0 | 1411200 | 550176 | 0 | 226000 | 4532830 | 613080 | 1678800 | 2966400 | 0 | 13000 | 304250 | 284880 | 184008809.08 | 22041454 | 2904192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 474480 | 24145450 | 220800 | 31054884 | 0 | 48025 | 0 | 394272 | 0 | 238400 | 38976 | 56485 | 0 | 541590 | 75783 | 354000 | 3757364 | 0 | 3484782 | 0 | 0 | 0 | 9618181 | 0 | 29880 | 0 | 3922000 | 1134109 | 1183263 | 166804 | 280560 | 0 | 0 | 24712.32 | 1306080 | 2997 | 0 | 4604000 | 221625 | 2745000 | 5268240 | 0 | 6254545 | 27335272.73 | 0 | 153928206.05 | 337937015.13

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 25-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14124.65 | MW | 12:00 Hr. | Energy Generated |  |  | 337.937 |  | MKWHr.
| Day Peak Demand |  |  | 14312.75 | MW | 12:00 Hr. | Energy Unserverd |  |  | 4.526 |  | MKWHr.
| Evening Peak Generation |  |  | 15403.04 | MW | 19:30 Hr. | Energy Demand |  |  | 342.463 |  | MKWHr.
| Evening Peak Demand |  |  | 15501.04 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.1 |  | °C
| Minimum Generation of the Day |  |  | 12551.73 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 942.68 |  | MMCFD
| Maximum Generation of the Day |  |  | 15403.04 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.6651 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.3949 | 0 | 14.5305 | 0 | 0 | 0.11008 | 0 | 0 | 53.0355 | Gas | 131.8522 | Gas | 471463779.65
| Chattogram Zone |  |  | 4.2094 | 40.3 | 4.1253 | 0 | 0.92418 | 0.092187 | 0 | 0.12768 | 49.7787 | Coal | 107.6954 | Coal | 703645149.0491
| Cumilla Zone |  |  | 26.4301 | 0 | 12.5493 | 0 | 0 | 0.49471 | 1.0416 | 0 | 40.5158 | HFO | 39.2849 | HFO | 728096095.998
| Mymensingh Zone |  |  | 0 | 0 | 5.5432 | 0 | 0 | 0.31725 | 0 | 0 | 5.8604 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8184 | Hydro | 0.92418 | Hydro | 92418
| Khulna Zone |  |  | 2.9042 | 24.1455 | 0.2208 | 0 | 0 | 0.47448 | 22.0415 | 0 | 49.7864 | Solar | 3.9148 | Solar | 63601063.0852
| Barishal Zone |  |  | 8.2349 | 38.1938 | 0 | 0 | 0 | 0.002997 | 0 | 0 | 46.4317 | Import | 54.1379 | Import | 283618985.64
| Rajshahi Zone |  |  | 16.8603 | 0 | 0.85194 | 0 | 0 | 0.92547 | 31.0549 | 0 | 49.6926 | Wind | 0.12768 | Wind | 1869235.2
| Rangpur Zone |  |  | 0 | 5.0561 | 1.4638 | 0 | 0 | 1.4976 | 0 | 0 | 8.0175
| Total |  |  | 131.8522 | 107.6954 | 39.2849 | 0 | 0.92418 | 3.9148 | 54.1379 | 0.12768 | 337.937
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 471463779.65 |  | Hydro | 92418
|  |  |  | Coal | 703645149.0491 |  | Solar | 63601063.0852
|  |  |  | HFO | 728096095.998 |  | Import | 283618985.64
|  |  |  | HSD | 0 |  | Wind | 1869235.2
[5 empty] | Total: | 225,23,86,726 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0415 | Peak Hr Flow | 871.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35035000 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 31.0549 | Peak Hr Flow | 1442.54 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 762 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 1.0416 | Peak Hr Flow | 46.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1030 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 54.1379 | Peak Hr Flow | 2359.54 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 44 |  | 5774
|  |  |  | Chattogram |  | 0 |  | 1527
|  |  |  | Cumilla |  | 10 |  | 1472
|  |  |  | Mymensingh |  | 25 |  | 1100
|  |  |  | Sylhet |  | 15 |  | 543
|  |  |  | Khulna |  | 0 |  | 1779
|  |  |  | Barishal |  | 0 |  | 473
|  |  |  | Rajshahi |  | 0 |  | 1431
|  |  |  | Rangpur |  | 0 |  | 870
|  |  |  | Total |  | 94 |  | 14969
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:20 | Barishal 132/33kV S/S T-2 (415T) HT is restored.
|  | 08:21 | Barishal 132/33kV S/S T-2 (415T) LT is restored.
| 08:25 | 13:30 | Rajshahi-Rajshahi(New) 132kV Ckt-1 Scheduled S/D from Rajshahi 132/33kV end Due to For
maintenance work at Rajshahi 230 Kv S/S. and from Rajshahi 230/132/33kV end Due to
Maintenance Work.
|  | 08:27 | Dhamrai 132/33kV S/S Transformer-2 HT is restored.
|  | 08:28 | Dhamrai 132/33kV S/S Transformer-2 LT is restored.
| 08:31 | 09:25 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 LT Scheduled S/D Due to maintenance
| 08:31 | 09:24 | Kaliakoir 400/230/132kV S/S 400/230kV TR1 HT Scheduled S/D Due to maintenance
| 09:23 |  | Madunaghat 132/33kV S/S TR-1(507T) HT Scheduled S/D Due to Painting work.
| 09:24 | 12:33 | Ishwardi-Natore 132kV Ckt-2 Scheduled S/D from Ishurdi 132/33kV end.
|  | 09:45 | Savar 132/33kV S/S T-3 HT is restored.
|  | 09:45 | Savar 132/33kV S/S T-3 LT is restored.
|  | 09:55 | Cumilla(N)-Daudkandi 132 kV Ckt-1 is restored.
| 09:59 | 10:10 | Ullon-Dhanmondi ckt-1 switched off because of switching of 920 No. CB at Ullon side. As a | [7 empty] | 55MW load interrup.
result, Dhanmondi-DU ckt was tripped showing overcurrent relay.
| 09:59 | 10:18 | Ullon-Rampura ckt-1 by DPDC as Isolator of Ullon was found in flashing condition. | [7 empty] | 32MW load interrup.
Transformer T-1 and T-2 was also forced shutdown for this switching.
| 10:10 |  | Transformer T-2 and T-3 of Dhanmondi grid S/S was switched on.
| 10:18 |  | Transformer T-1 and T-2 of Ullon was switched on.
| 10:30 | 11:08 | Palashbari 132/33kV S/S TR2-404T LT Forced S/D Due to Red hot maintenance
| 10:31 | 11:05 | Palashbari 132/33kV S/S TR2-404T HT Forced S/D Due to Red hot maintenance
| 10:33 | 11:18 | Borhanuddin 230/33kV S/S Tr-Load HT Tripped showing Buchholz relays. | [7 empty] | 52.0MW load interrup.
| 10:43 | 17:57 | Rampura-Ullon-2 132kV Ckt-1 Scheduled S/D from Rampura 230/132kV end Due to Shutdown from NLDC
|  | 11:54 | Hasnabad-Shyampur 230kV Ckt-1 is restored.
| 11:57 | 16:51 | Hasnabad 230/132kV S/S AUTO TR-3 HT Scheduled S/D Due to High Temp Maintenance
| 11:57 | 16:52 | Hasnabad 230/132kV S/S AUTO TR-3 LT Scheduled S/D Due to High Temp Maintenance
| 12:00 |  | Day peak generation 14122 MW.
|  | 12:05 | Mirsorai 230/33kV S/S 150 MW Power Station -02 is restored.
|  | 12:34 | Kodda-Rajendrapur 132kV Ckt-1 is restored.
| 12:35 |  | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Feni 132/33kV end Due to 54 no tower
R(Phase) Jumper maintenance
| 14:08 | 00:26 | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D Due to None
| 17:06 | 19:51 | Savar 132/33kV S/S T-3 HT Scheduled S/D Due to Buchholz maintenance
| 17:07 | 19:52 | Savar 132/33kV S/S T-3 LT Scheduled S/D Due to Buchholz maintenance
| 17:58 |  | Rampura-Ullon-2 132kV Ckt-1 Tripped from Rampura 230/132kV end showing Switch on to
Fault relays Due to R-ph LA burned/burst at the time of the restoring shutdown event.
| 19:30 |  | Evening Peak Gen.15403 MW
| 05:05 |  | Rampura 230/132kV S/S Capacitor Bank- 2 Scheduled S/D Due to high voltage
| 05:05 |  | Rampura 230/132kV S/S Capacitor Bank- 1 Scheduled S/D Due to high voltage
| 06:11 |  | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna (C) end Due to Due to
replace defective loop for reduce temperature. and from Khulna(S) 230/132kVend.
| 07:15 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to GT | [7 empty] | 20.0MW load
|  |  | -4 33kV BUS section PBS side redhot maintenance | [7 empty] | interrup.
| 07:15 |  | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT Scheduled S/D Due to GT | [7 empty] | 20.0MW load
|  |  | -4 33kV BUS section PBS side redhot maintenance | [7 empty] | interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 25-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 329 | 8726400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7724500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 283 | 7190720 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 269651 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 266 | 6976948 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 265824 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 849600 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 1552320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 779741 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 550232 | Liquid fuel shortage
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15.5 | 343800 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 393480 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 17 | 424320 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 260 | 1588004 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 2118816 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 839040 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 57 | 754560 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2695680 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 110078 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432720 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | -
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 250 | 7039091 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1410000 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2692.5 | 53035525
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 1800000 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 1 | 59076.9 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 70605 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 527040 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 924180 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 184 | 2079611 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 0 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 48 | 460272 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 511359 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1956480 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 329760 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 21582 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 0 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 510720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 53 | 100364 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 27878179 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 0 | 127680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 12421818.18 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2411 | 49778727.08
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 182 | 4859000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 354 | 8429000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 8066000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 29 | 711864 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 30 | 730080 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 351273 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1144244 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 128 | 1142472 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 880736 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1834970 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4630080 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 46 | 1041600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 685229 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 303680 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2764500 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 341040 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 2105280 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 494709 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1786 | 40515757
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 13000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 170 | 2966400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1678800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 304250 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 284880 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 613080 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 313 | 5860410
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 38 | 450000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 142 | 3439964 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 18 | 550176 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 22 | 1411200 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 4532830 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 226000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 8 | 151320 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7390500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8999000 | -
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7667400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1369 | 34818390
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 871 | 22041454 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 96 | 2904192 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 220800 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 474480 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1134 | 24145450 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2118 | 49786376
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 299 | 6254545 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 221625 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 115 | 2745000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 27335272.73 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5268240 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4604000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2997 | -
Barishal Area Total |  |  |  |  | 2236 | 2152 | 46431679.73
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 48025 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 13 | 56485 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3757364 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 124 | 3484782 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 370 | 9618181 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 15 | 75783 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 41 | 238400 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 55 | 394272 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 20 | 38976 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 29880 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1442.54 | 31054884 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 354000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 541590 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2220.54 | 49692622
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1134109 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 158 | 3922000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 63 | 280560 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 24712.32 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 70 | 1183263 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 166804 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1306080 | -
Rangpur Area Total |  |  |  |  | 950 | 341 | 8017528.32
Eastern Grid Total |  |  |  |  | 16771.895 | 8571.5 | 184008809.08
Western Grid Total |  |  |  |  | 10338.16 | 6831.54 | 153928206.05
National Grid Total |  |  |  |  | 27110.055 | 15403.04 | 337937015.13
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 25-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10322.72 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4552.8 | MW
i) Dhaka area |  |  | 5730.49 |  | MW | i) Khulna area |  |  |  | 1779 | MW
ii) Chattogram area |  |  | 1527 |  | MW | ii) Barishal area |  |  |  | 473 | MW
iii) Cumilla area |  |  | 1462.23 |  | MW | iii) Rajshahi area |  |  |  | 1430.8 | MW
iv) Mymensingh area |  |  | 1075 |  | MW | iv) Rangpur area |  |  |  | 870 | MW
v) Sylhet area |  |  | 528 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14875.52 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 82 | 19:30 | 133 | Patuakhali | 82 | 23:00
2 | AKSML | 110 | 08:00 | 68 | Jaldhaka | 78 | 00:00 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 40 | 13:00 | 69 | Jamalpur | 112 | 23:00 | 135 | Postogola | 61 | 13:00
4 | Agargaon | 138 | 13:00 | 70 | Jashore | 146 | 19:00 | 136 | Purbachal | 23 | 23:00
5 | Agrabad | 98 | 19:30 | 71 | Jhenaidah | 124 | 00:00 | 137 | Purbasadipur | 126 | 00:00
6 | Amnura | 34 | 19:30 | 72 | Joydebpur | 163 | 10:00 | 138 | Rahanpur | 27 | 21:00
7 | Ashuganj | 102 | 00:00 | 73 | Joypurhat | 55 | 00:00 | 139 | Rahim | 46 | 03:00
8 | BSRM | 200 | 18:00 | 74 | Juldah | 18 | 15:00 | 140 | Rajbari | 82 | 00:00
9 | Bagerhat | 86 | 19:30 | 75 | KSRM | 27 | 06:00 | 141 | Rajendrapur | 151 | 19:30
10 | Bajitpur | 56 | 21:00 | 76 | Kabirpur | 282 | 11:00 | 142 | Rajshahi | 109 | 19:30
11 | Bakulia | 96 | 10:00 | 77 | Kachua | 98 | 19:00 | 143 | Rajshahi-230 | 76 | 14:00
12 | Banani | 46 | 13:00 | 78 | Kallyanpur | 120 | 19:30 | 144 | Ramganj | 116 | 22:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 44 | 16:00 | 145 | Rampur | 41 | 19:00
14 | Barapukuria | 66 | 01:00 | 80 | Kamrangirchar | 70 | 18:30 | 146 | Rangamati | 17 | 19:00
15 | Barguna | 22 | 19:30 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 155 | 19:30
16 | Barishal | 122 | 13:00 | 82 | Kasba | 38 | 22:00 | 148 | Ruppur | 8 | 10:00
17 | Barishal-230 | 106 | 22:00 | 83 | Kazla | 102 | 23:00 | 149 | SSM | 5 | 00:00
18 | Baroaulia | 69 | 14:00 | 84 | Keranigonj | 99 | 19:30 | 150 | Saidpur | 105 | 19:30
19 | Baroirhat | 66 | 19:30 | 85 | Khagrachori | 32 | 19:00 | 151 | Satkhira | 139 | 19:30
20 | Bashundhara | 210 | 13:00 | 86 | Khulna | 68 | 13:00 | 152 | Satmasjid | 110 | 13:00
21 | BashundharaCement | 15 | 11:00 | 87 | Khulshi | 183 | 17:00 | 153 | Savar | 230 | 17:00
22 | Beanibazar | 76 | 19:00 | 88 | Kishoreganj | 147 | 21:00 | 154 | SevenRings | 18 | 23:00
23 | Benapole | 68 | 19:00 | 89 | Kodda | 289 | 10:00 | 155 | ShahCement | 35 | 18:00
24 | Bhaluka | 154 | 22:00 | 90 | Kulaura | 48 | 00:00 | 156 | Shahjadpur | 88 | 20:00
25 | Bhandaria | 55 | 22:00 | 91 | Kurigram | 65 | 19:30 | 157 | Shahjibazar | 122 | 00:00
26 | Bhangura | 37 | 19:30 | 92 | Kushtia | 159 | 20:00 | 158 | Shahmirpur | 59 | 02:00
27 | Bheramara(GK) | 65 | 00:00 | 93 | Lalbag | 58 | 19:30 | 159 | Shariatpur | 90 | 22:00
28 | Bhulta | 237 | 17:00 | 94 | Lalmonirhat | 64 | 20:00 | 160 | Sherpur | 144 | 00:00
29 | Bog-Sherpur | 62 | 19:30 | 95 | MI_Cement | 14 | 11:00 | 161 | Shikalbaha | 28 | 18:00
30 | Bogura | 165 | 19:30 | 96 | Madanganj | 48 | 23:00 | 162 | Shitalakhya | 93 | 12:00
31 | Borhanuddin | 88 | 19:00 | 97 | Madaripur | 111 | 22:00 | 163 | Sholosohor | 51 | 15:00
32 | Brahmanbaria | 111 | 05:00 | 98 | Madartek | 94 | 23:00 | 164 | Shyampur | 192 | 11:00
33 | Cantonment | 158 | 13:00 | 99 | Madunaghat | 54 | 18:30 | 165 | Siddhirganj | 127 | 12:00
34 | Chandina | 23 | 19:30 | 100 | Magura | 62 | 00:00 | 166 | Sirajganj | 120 | 21:00
35 | Chandpur | 78 | 00:00 | 101 | Mahasthangarh | 72 | 23:00 | 167 | Sonargaon | 128 | 00:00
36 | Chandraghona | 36 | 18:30 | 102 | Manikganj | 141 | 20:00 | 168 | Sreemongol | 80 | 00:00
37 | Chapai | 68 | 21:00 | 103 | Maniknagar | 88 | 12:00 | 169 | Sreepur | 110 | 10:00
38 | Charsaidpur | 45 | 10:00 | 104 | Matarbari | 51 | 19:30 | 170 | Srinagar | 49 | 22:00
39 | Chauddagram | 79 | 22:00 | 105 | Matuail | 70 | 15:00 | 171 | Sunamganj | 61 | 00:00
40 | Chhatak | 43 | 19:30 | 106 | Millgate | 108 | 11:00 | 172 | Sylhet | 51 | 19:00
41 | Chowmuhani | 232 | 19:30 | 107 | Mirpur | 131 | 23:00 | 173 | Sylhet-132 | 128 | 12:00
42 | Chuadanga | 109 | 00:00 | 108 | Mirsorai | 12 | 12:00 | 174 | TK | 34 | 19:00
43 | Coxsbazar | 131 | 22:00 | 109 | Mirzapur | 50 | 19:00 | 175 | Tangail | 197 | 20:00
44 | Cumilla(N) | 158 | 19:00 | 110 | Mithapukur | 64 | 19:30 | 176 | Thakurgaon | 99 | 21:00
45 | Cumilla(S) | 192 | 15:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 141 | 11:00
46 | Daudkandi | 153 | 19:30 | 112 | Mogbazar | 161 | 13:00 | 178 | Ullahpara | 40 | 19:00
47 | Dhaka | 74 | 13:00 | 113 | Mongla | 41 | 09:00 | 179 | Ullon | 42 | 21:00
48 | Dhamrai | 140 | 19:30 | 114 | Motijheel | 44 | 13:00 | 180 | Uttara | 89 | 13:00
49 | Dhanmondi | 170 | 13:00 | 115 | Muktagacha | 30 | 21:00 | 181 | UttaraNew | 66 | 23:00
50 | Dohazari | 101 | 21:00 | 116 | Munshiganj | 126 | 19:00 | 182 | Zigatola | 78 | 13:00
51 | Faridpur | 162 | 19:30 | 117 | Muradnagar | 30 | 19:00
52 | Fatullah | 108 | 12:00 | 118 | Mymensingh | 192 | 20:00
53 | Fenchuganj | 47 | 19:00 | 119 | Naogaon | 123 | 21:00
54 | Feni | 125 | 19:30 | 120 | Narail | 59 | 19:30
55 | GPH | 94 | 03:00 | 121 | Narinda | 86 | 13:00
56 | Ghatail | 78 | 19:00 | 122 | Narshingdi | 166 | 06:00
57 | Ghorashal | 18 | 00:00 | 123 | Natore | 151 | 22:00
58 | Ghorashal-230 | 102 | 23:00 | 124 | Nawabganj | 59 | 22:00
59 | Goalpara | 36 | 23:00 | 125 | Netrakona | 115 | 22:00
60 | Gollamari | 104 | 23:00 | 126 | New | 93 | 15:00
61 | Gopalganj | 105 | 23:00 | 127 | Niamatpur | 60 | 00:00
62 | Gulshan | 134 | 13:00 | 128 | Noapara | 52 | 20:00
63 | Halishahar | 87 | 19:00 | 129 | PHP | 5 | 15:00
64 | HaripurSBU | 178 | 16:00 | 130 | Pabna | 127 | 21:00
65 | Hasnabad | 75 | 12:00 | 131 | Palashbari | 92 | 00:00
66 | Hathazari | 88 | 19:30 | 132 | Panchagarh | 59 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 25-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14749.2 | 192 |  | 14949.84
1:00 | 14379.2 | 297 |  | 14689.2
2:00 | 13875.2 | 282 |  | 14170.2
3:00 | 13631.2 | 276 |  | 13919.2
4:00 | 13363.2 | 274 |  | 13649.2
5:00 | 13109.2 | 278 |  | 13400.2
6:00 | 12551.73 | 276 |  | 12840.15
7:00 | 12721.98 | 236 |  | 12968.6
8:00 | 12734.14 | 201 |  | 12944.19
9:00 | 13310.18 | 193 |  | 13511.87
10:00 | 13479.84 | 156 |  | 13642.84
11:00 | 13699.61 | 167 |  | 13874.13
12:00 | 14124.65 | 180 |  | 14312.75
13:00 | 14268.02 | 205 |  | 14482.25
14:00 | 14054.72 | 200 |  | 14263.72
15:00 | 14054.51 | 219 |  | 14283.51
16:00 | 13693.79 | 180 |  | 13881.79
17:00 | 13654.35 | 103 |  | 13762.35
18:00 | 13284.94 | 113 |  | 13402.94
19:00 | 14855.02 | 92 |  | 14951.02
19:30 | 15403.04 | 94 |  | 15501.04
20:00 | 15021.12 | 96 |  | 15121.12
21:00 | 15133.59 | 98 |  | 15235.59
22:00 | 14961.74 | 96 |  | 15061.74
23:00 | 15080.83 | 116 |  | 15201.83
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 25-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7912.2 | 6837 | 14749.2 | DAILY GENERATION CURVE
00:30 | 7730.2 | 6834 | 14564.2
01:00 | 7548.2 | 6831 | 14379.2 | 25-05-2025
01:30 | 7464.2 | 6663 | 14127.2
02:00 | 7380.2 | 6495 | 13875.2
02:30 | 7296.7 | 6456.5 | 13753.2
03:00 | 7213.2 | 6418 | 13631.2
03:30 | 7186.7 | 6310.5 | 13497.2
04:00 | 7160.2 | 6203 | 13363.2
04:30 | 7062.2 | 6174 | 13236.2
05:00 | 6964.2 | 6145 | 13109.2
05:30 | 6851.605 | 5978.86 | 12830.465
06:00 | 6739.01 | 5812.72 | 12551.73
06:30 | 6782.665 | 5854.19 | 12636.855
07:00 | 6826.32 | 5895.66 | 12721.98
07:30 | 6824.75 | 5903.31 | 12728.06
08:00 | 6823.18 | 5910.96 | 12734.14
08:30 | 7011.14 | 6011.02 | 13022.16
09:00 | 7199.1 | 6111.08 | 13310.18
09:30 | 7276.08 | 6118.93 | 13395.01
10:00 | 7353.06 | 6126.78 | 13479.84
10:30 | 7428.745 | 6160.98 | 13589.725
11:00 | 7504.43 | 6195.18 | 13699.61
11:30 | 7681.995 | 6230.135 | 13912.13
12:00 | 7859.56 | 6265.09 | 14124.65
12:30 | 7901.1 | 6295.235 | 14196.335
13:00 | 7942.64 | 6325.38 | 14268.02
13:30 | 7854.435 | 6306.935 | 14161.37
14:00 | 7766.23 | 6288.49 | 14054.72
14:30 | 7776.015 | 6278.6 | 14054.615
15:00 | 7785.8 | 6268.71 | 14054.51
15:30 | 7766.385 | 6107.765 | 13874.15
16:00 | 7746.97 | 5946.82 | 13693.79
16:30 | 7768 | 5906.07 | 13674.07
17:00 | 7789.03 | 5865.32 | 13654.35
17:30 | 7700.765 | 5768.88 | 13469.645
18:00 | 7612.5 | 5672.44 | 13284.94
18:30 | 7980.5 | 6089.48 | 14069.98
19:00 | 8348.5 | 6506.52 | 14855.02
19:30 | 8571.5 | 6831.54 | 15403.04
20:00 | 8142.7 | 6878.42 | 15021.12
20:30 | 8078.7 | 6998.655 | 15077.355 |  | Executive Engineer
21:00 | 8014.7 | 7118.89 | 15133.59 |  | Network Operation Division
21:30 | 7976.3 | 7071.365 | 15047.665
22:00 | 7937.9 | 7023.84 | 14961.74
22:30 | 7969.9 | 7051.385 | 15021.285
23:00 | 8001.9 | 7078.93 | 15080.83

## En-Curve
QF-LDC-12
Date | 25-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3640 | 1908 | 910 | 0 | 46 | 1454 | 36 | 4814 | 0 | 317 | 1618.2 | 0 | 0 | 6 | 192 | DAILY ENERGY CURVE
00:30 | 3640 | 1906.5 | 914.5 | 0 | 47 | 1455 | 36 | 4799.5 | 0 | 254.5 | 1506.2 | 0 | 0 | 5 | 244.5 | 25-05-2025
01:00 | 3640 | 1905 | 919 | 0 | 48 | 1456 | 36 | 4785 | 0 | 192 | 1394.2 | 0 | 0 | 4 | 297
01:30 | 3654.5 | 1916.5 | 919 | 0 | 47 | 1409.5 | 36.5 | 4758 | 0 | 180.5 | 1201.2 | 0 | 0 | 4.5 | 289.5 | Energy Generated | 337.937 |  | MKWHr
02:00 | 3669 | 1928 | 919 | 0 | 46 | 1363 | 37 | 4731 | 0 | 169 | 1008.2 | 0 | 0 | 5 | 282 | Energy not Served | 4.526 |  | MKWHr
02:30 | 3667.5 | 1929.5 | 919.5 | 0 | 45 | 1342.5 | 37.5 | 4661 | 0 | 160.5 | 983.7 | 0 | 0 | 6.5 | 279 | Total Energy Requirement | 342.463 |  | MKWHr
03:00 | 3666 | 1931 | 920 | 0 | 44 | 1322 | 38 | 4591 | 0 | 152 | 959.2 | 0 | 0 | 8 | 276
03:30 | 3670.5 | 1933 | 919.5 | 0 | 44 | 1280.5 | 38.5 | 4509.5 | 0 | 152.5 | 940.7 | 0 | 0 | 8.5 | 275
04:00 | 3675 | 1935 | 919 | 0 | 44 | 1239 | 39 | 4428 | 0 | 153 | 922.2 | 0 | 0 | 9 | 274
04:30 | 3662 | 1933.5 | 919.5 | 0 | 44 | 1228 | 39.5 | 4389 | 0 | 153 | 857.2 | 0 | 0 | 10.5 | 276
05:00 | 3649 | 1932 | 920 | 0 | 44 | 1217 | 40 | 4350 | 0 | 153 | 792.2 | 0 | 0 | 12 | 278
05:30 | 3629 | 1903.5 | 919.5 | 0 | 43 | 1219.5 | 40 | 4164 | 20.865 | 145 | 736.6 | 0 | 0 | 9.5 | 277
06:00 | 3609 | 1875 | 919 | 0 | 42 | 1222 | 40 | 3978 | 41.73 | 137 | 681 | 0 | 0 | 7 | 276
06:30 | 3697 | 1847.5 | 918 | 0 | 41 | 1227.5 | 40 | 3931.5 | 95.355 | 137 | 698.5 | 0 | 0 | 3.5 | 256
07:00 | 3785 | 1820 | 917 | 0 | 40 | 1233 | 40 | 3885 | 148.98 | 137 | 716 | 0 | 0 | 0 | 236
07:30 | 3741 | 1804 | 894.5 | 0 | 37 | 1223.495 | 40 | 3901.5 | 220.065 | 137 | 729.5 | 0 | 0 | 0 | 218.5
08:00 | 3697 | 1788 | 872 | 0 | 34 | 1213.99 | 40 | 3918 | 291.15 | 137 | 743 | 0 | 0 | 0 | 201
08:30 | 3739 | 1805.5 | 872 | 0 | 35 | 1215.925 | 40 | 3955.5 | 340.735 | 174 | 844.5 | 0 | 0 | 0 | 197
09:00 | 3781 | 1823 | 872 | 0 | 36 | 1217.86 | 40 | 3993 | 390.32 | 211 | 946 | 0 | 0 | 0 | 193
09:30 | 3691.5 | 1785 | 895.5 | 0 | 36 | 1218.13 | 40 | 3976.5 | 418.38 | 217.5 | 1116.5 | 0 | 0 | 0 | 174.5
10:00 | 3602 | 1747 | 919 | 0 | 36 | 1218.4 | 40 | 3960 | 446.44 | 224 | 1287 | 0 | 0 | 0 | 156
10:30 | 3564 | 1750 | 919 | 0 | 37 | 1218.955 | 39.5 | 3979 | 485.27 | 222.5 | 1374 | 0 | 0 | 0.5 | 161.5
11:00 | 3526 | 1753 | 919 | 0 | 38 | 1219.51 | 39 | 3998 | 524.1 | 221 | 1461 | 0 | 0 | 1 | 167
11:30 | 3530 | 1759.5 | 919.5 | 0 | 39 | 1218.385 | 39 | 4142.5 | 524.745 | 221.5 | 1514 | 0 | 0 | 4 | 173.5
12:00 | 3534 | 1766 | 920 | 0 | 40 | 1217.26 | 39 | 4287 | 525.39 | 222 | 1567 | 0 | 0 | 7 | 180
12:30 | 3516 | 1766 | 919.5 | 0 | 43 | 1237.08 | 37 | 4359 | 492.255 | 232 | 1579 | 0 | 0 | 15.5 | 192.5
13:00 | 3498 | 1766 | 919 | 0 | 46 | 1256.9 | 35 | 4431 | 459.12 | 242 | 1591 | 0 | 0 | 24 | 205
13:30 | 3453 | 1749 | 919.5 | 0 | 46 | 1258.215 | 35 | 4440.5 | 417.155 | 235.5 | 1582 | 0 | 0 | 25.5 | 202.5
14:00 | 3408 | 1732 | 920 | 0 | 46 | 1259.53 | 35 | 4450 | 375.19 | 229 | 1573 | 0 | 0 | 27 | 200
14:30 | 3415 | 1717 | 919 | 0 | 47 | 1260.815 | 36 | 4447.5 | 372.3 | 229 | 1591 | 0 | 0 | 20 | 209.5
15:00 | 3422 | 1702 | 918 | 0 | 48 | 1262.1 | 37 | 4445 | 369.41 | 229 | 1609 | 0 | 0 | 13 | 219
15:30 | 3441 | 1688 | 918.5 | 0 | 47 | 1202.08 | 37.5 | 4445 | 311.07 | 232.5 | 1541.5 | 0 | 0 | 10 | 199.5
16:00 | 3460 | 1674 | 919 | 0 | 46 | 1142.06 | 38 | 4445 | 252.73 | 236 | 1474 | 0 | 0 | 7 | 180
16:30 | 3539.5 | 1695 | 919.5 | 0 | 43 | 1138.05 | 38 | 4409.5 | 175.52 | 241.5 | 1470 | 0 | 0 | 4.5 | 141.5
17:00 | 3619 | 1716 | 920 | 0 | 40 | 1134.04 | 38 | 4374 | 98.31 | 247 | 1466 | 0 | 0 | 2 | 103
17:30 | 3537.5 | 1705.75 | 919.5 | 0 | 40 | 1135.245 | 39 | 4237 | 59.65 | 296 | 1496.5 | 0 | 0 | 3.5 | 108
18:00 | 3456 | 1695.5 | 919 | 0 | 40 | 1136.45 | 40 | 4100 | 20.99 | 345 | 1527 | 0 | 0 | 5 | 113
18:30 | 3564.5 | 1703.5 | 895.5 | 0 | 44 | 1291.985 | 40 | 4378 | 10.495 | 428 | 1711.5 | 0 | 0 | 2.5 | 102.5
19:00 | 3673 | 1711.5 | 872 | 0 | 48 | 1447.52 | 40 | 4656 | 0 | 511 | 1896 | 0 | 0 | 0 | 92
19:30 | 3496 | 1681.5 | 871 | 0 | 46 | 1442.54 | 40 | 4947 | 0 | 572 | 2307 | 0 | 0 | 0 | 94
20:00 | 3481 | 1625.5 | 871 | 0 | 46 | 1448.42 | 40 | 5045 | 0 | 587 | 1877.2 | 0 | 0 | 0 | 96
20:30 | 3568.5 | 1655 | 894.5 | 0 | 46 | 1455.155 | 40 | 5062.5 | 0 | 575.5 | 1780.2 | 0 | 0 | 0 | 97
21:00 | 3656 | 1684.5 | 918 | 0 | 46 | 1461.89 | 40 | 5080 | 0 | 564 | 1683.2 | 0 | 0 | 0 | 98
21:30 | 3675.5 | 1692.1 | 918.5 | 0 | 47 | 1461.265 | 40 | 5061.1 | 0 | 527.5 | 1624.7 | 0 | 0 | 0 | 97
22:00 | 3695 | 1699.7 | 919 | 0 | 48 | 1460.64 | 40 | 5042.2 | 0 | 491 | 1566.2 | 0 | 0 | 0 | 96
22:30 | 3708.5 | 1707.7 | 919 | 0 | 47 | 1461.185 | 40 | 5064.7 | 0 | 474.5 | 1598.7 | 0 | 0 | 0 | 106
23:00 | 3722 | 1715.7 | 919 | 0 | 46 | 1461.73 | 40 | 5087.2 | 0 | 458 | 1631.2 | 0 | 0 | 0 | 116
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 25-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 379 | 06:00 | 363 | 20:00 | Payra | 412 | 06:00 | 405 | 23:00
Ashuganj | 392 | 6:00 | 380 | 21:00 | Rahanpur | 404 | 16:00 | 390 | 21:00
Bhulta | 380 | 04:00 | 363 | 11:00 | Rampal | 399 | 06:00 | 381 | 23:00
Bibiana | 391 | 07:00 | 383 | 18:30
BIPTC | 405 | 08:00 | 394 | 21:00
Bogura | 393 | 16:00 | 378 | 21:00
Gopalganj | 393 | 07:00 | 375 | 23:00
Kaliakoir | 373 | 07:00 | 360 | 00:00
Madunaghat | 392 | 07:00 | 383 | 22:00
Meghnaghat | 383 | 06:00 | 368 | 23:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 220 | 06:00 | 211 | 21:00 | Keranigonj | 218 | 06:00 | 209 | 21:00
AKSML | 228 | 06:00 | 220 | 22:00 | Khulna(S) | 229 | 08:00 | 214 | 19:30
Aminbazar | 221 | 04:00 | 211 | 21:00 | Madunaghat | 230 | 06:00 | 223 | 22:00
Ashuganj | 223 | 18:00 | 215 | 17:00 | Madunaghat-400 | 231 | 07:00 | 225 | 22:00
Ashuganj-400 | 220 | 6:00 | 210 | 21:00 | Maniknagar | 216 | 06:00 | 209 | 23:00
Baghabari | 230 | 06:00 | 221 | 22:00 | Meghnaghat | 222 | 07:00 | 218 | 21:00
Barapukuria | 221 | 16:00 | 213 | 20:00 | Meghnaghat-400 | 220 | 05:00 | 213 | 23:00
Barapukuria-230 | 220 | 15:00 | 210 | 20:00 | Mirsorai | 225 | 07:00 | 216 | 23:00
Barishal | 235 | 07:00 | 225 | 22:00 | Rajshahi | 234 | 08:00 | 221 | 19:30
Bheramara | 234 | 08:00 | 222 | 19:30 | Rampal | 228 | 09:00 | 214 | 22:00
Bhulta | 220 | 04:00 | 209 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 223 | 05:00 | 216 | 23:00 | Rampura | 218 | 04:00 | 205 | 12:00
BIPTC | 236 | 08:00 | 221 | 19:30 | Shikalbaha | 229 | 07:00 | 221 | 18:30
Bogura | 226 | 16:00 | 218 | 21:00 | Shyampur | 218 | 06:00 | 210 | 23:00
Bogura-400 | 227 | 16:00 | 219 | 00:00 | Siddhirganj | 217 | 08:00 | 212 | 23:00
Borhanuddin | 240 | 07:00 | 232 | 23:00 | Sirajgonj | 234 | 08:00 | 229 | 21:00
BSRM | 224 | 06:00 | 217 | 23:00 | Sreepur | 224 | 18:00 | 214 | 22:00
Cumilla(N) | 218 | 06:00 | 210 | 23:00 | Tongi | 217 | 17:00 | 207 | 18:30
Faridpur | 230 | 06:00 | 217 | 22:00
Fenchuganj | 224 | 07:00 | 217 | 18:00
Ghorashal | 220 | 01:00 | 215 | 00:00
Ghorashal-230 | 220 | 04:00 | 209 | 22:00
Gopalganj | 232 | 07:00 | 221 | 23:00
GPH | 227 | 06:00 | 220 | 23:00
Haripur | 218 | 07:00 | 211 | 23:00
Hasnabad | 218 | 05:00 | 210 | 21:00
Hathazari | 230 | 06:00 | 221 | 22:00
Ishurdi | 235 | 08:00 | 223 | 19:30
Jhenaidah | 229 | 08:00 | 213 | 19:30
Kaliakoir | 225 | 06:00 | 217 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 134 | 04:00 | 124 | 12:00 | Madartek | 133 | 04:00 | 122 | 12:00
Agargaon | 133 | 06:00 | 126 | 11:00 | Madunaghat | 132 | 18:00 | 126 | 18:30
Agrabad | 130 | 05:00 | 126 | 21:00 | Magura | 133 | 05:00 | 121 | 23:00
AKS | 129 | 06:00 | 124 | 20:00 | Mahasthangarh | 132 | 16:00 | 126 | 20:00
Aminbazar | 129 | 04:00 | 123 | 19:00 | Manikganj | 130 | 07:00 | 117 | 00:00
Amnura | 135 | 08:00 | 124 | 00:00 | Maniknagar | 130 | 03:00 | 125 | 12:00
Ashuganj | 134 | 18:00 | 129 | 00:00 | Matarbari | 118 | 15:00 | 108 | 22:00
Bagerhat | 131 | 09:00 | 116 | 22:00 | Matuail | 126 | 05:00 | 122 | 16:00
Bajitpur | 127 | 18:00 | 119 | 21:00 | Millgate | 129 | 03:00 | 123 | 09:00
Bakulia | 130 | 07:00 | 126 | 22:00 | Mirpur | 130 | 05:00 | 121 | 18:30
Banani | 134 | 03:00 | 123 | 12:00 | Mirzapur | 132 | 06:00 | 126 | 23:00
Bangabhaban | 131 | 06:00 | 125 | 12:00 | Mithapukur | 131 | 16:00 | 122 | 20:00
Barapukuria | 134 | 17:00 | 124 | 20:00 | MI_Cement | 127 | 04:00 | 123 | 13:00
Barguna | 134 | 08:00 | 128 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 07:00 | 122 | 23:00 | Mogbazar | 136 | 04:00 | 125 | 12:00
Barishal-230 | 131 | 07:00 | 122 | 23:00 | Mongla | 132 | 18:00 | 118 | 22:00
Baroaulia | 133 | 03:00 | 129 | 09:00 | Motijheel | 131 | 06:00 | 125 | 12:00
Baroirhat | 125 | 06:00 | 118 | 22:00 | Muktagacha | 134 | 09:00 | 126 | 06:00
Bashundhara | 133 | 03:00 | 123 | 09:00 | Munshiganj | 127 | 18:00 | 120 | 23:00
BashundharaCement | 126 | 05:00 | 122 | 09:00 | Muradnagar | 123 | 06:00 | 117 | 23:00
Beanibazar | 130 | 21:00 | 122 | 00:00 | Mymensingh | 136 | 14:00 | 111 | 21:00
Benapole | 131 | 10:00 | 117 | 22:00 | Naogaon | 131 | 16:00 | 124 | 00:00
Bhaluka | 131 | 18:00 | 119 | 12:00 | Narail | 135 | 10:00 | 121 | 19:30
Bhandaria | 126 | 08:00 | 113 | 22:00 | Narinda | 130 | 3:00 | 125 | 12:00
Bhangura | 131 | 05:00 | 126 | 20:00 | Narshingdi | 129 | 18:00 | 110 | 12:00
Bheramara | 136 | 10:00 | 128 | 19:30 | Natore | 134 | 08:00 | 126 | 22:00
Bheramara(GK) | 136 | 12:00 | 127 | 19:30 | Nawabganj | 131 | 04:00 | 122 | 23:00
Bhulta | 120 | 07:00 | 116 | 09:00 | Netrakona | 124 | 18:00 | 106 | 22:00
Bog-Sherpur | 132 | 08:00 | 126 | 21:00 | New | 131 | 03:00 | 124 | 09:00
Bogura | 135 | 15:00 | 129 | 21:00 | Niamatpur | 134 | 16:00 | 128 | 00:00
Bogura-230 | 134 | 08:00 | 129 | 21:00 | Noapara | 134 | 10:00 | 121 | 19:30
Brahmanbaria | 120 | 05:00 | 116 | 23:00 | Pabna | 134 | 10:00 | 126 | 19:30
Cantonment | 133 | 05:00 | 125 | 13:00 | Palashbari | 130 | 16:00 | 122 | 00:00
Chandina | 126 | 06:00 | 120 | 22:00 | Panchagarh | 136 | 19:00 | 120 | 04:00
Chandpur | 128 | 05:00 | 121 | 22:00 | Patuakhali | 134 | 06:00 | 130 | 22:00
Chandraghona | 131 | 07:00 | 126 | 18:30 | Payra | 136 | 07:00 | 132 | 22:00
Chapai | 131 | 16:00 | 123 | 01:00 | PHP | 125 | 07:00 | 116 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 18:00 | 122 | 23:00 | Postogola | 129 | 04:00 | 124 | 13:00
Chauddagram | 123 | 05:00 | 115 | 23:00 | Purbachal | 133 | 02:00 | 123 | 12:00
Chhatak | 128 | 21:00 | 119 | 19:00 | Purbasadipur | 132 | 19:00 | 117 | 20:00
Chowmuhani | 117 | 10:00 | 110 | 01:00 | Rahanpur | 135 | 16:00 | 130 | 00:00
Chuadanga | 132 | 14:00 | 119 | 00:00 | Rahanpur-400 | 135 | 16:00 | 130 | 20:00
Coxsbazar | 118 | 08:00 | 108 | 22:00 | Rahim | 126 | 04:00 | 123 | 09:00
Cumilla(N) | 126 | 05:00 | 120 | 22:00 | Rajbari | 133 | 06:00 | 124 | 23:00
Cumilla(S) | 133 | 03:00 | 119 | 19:00 | Rajendrapur | 128 | 18:30 | 117 | 01:00
Daudkandi | 121 | 18:00 | 116 | 22:00 | Rajshahi | 134 | 06:00 | 127 | 22:00
Dhaka | 134 | 06:00 | 125 | 11:00 | Rajshahi-230 | 135 | 08:00 | 119 | 21:00
Dhamrai | 131 | 06:00 | 126 | 09:00 | Ramganj | 120 | 05:00 | 113 | 19:30
Dhanmondi | 135 | 05:00 | 123 | 12:00 | Rampur | 130 | 06:00 | 127 | 13:00
Dohazari | 126 | 17:00 | 121 | 21:00 | Rampura | 134 | 04:00 | 124 | 11:00
Faridpur | 135 | 07:00 | 126 | 22:00 | Rangamati | 128 | 03:00 | 125 | 21:00
Fatullah | 128 | 05:00 | 123 | 23:00 | Rangpur | 130 | 16:00 | 117 | 20:00
Fenchuganj | 132 | 06:00 | 128 | 16:00 | Ruppur | 137 | 07:00 | 130 | 19:30
Feni | 123 | 06:00 | 115 | 19:00 | Saidpur | 131 | 18:00 | 120 | 06:00
Ghatail | 131 | 19:30 | 122 | 01:00 | Satkhira | 133 | 10:00 | 117 | 19:30
Ghorashal | 130 | 04:00 | 126 | 17:00 | Satmasjid | 132 | 06:00 | 125 | 12:00
Goalpara | 136 | 08:00 | 124 | 22:00 | Savar | 128 | 06:00 | 121 | 23:00
Gollamari | 137 | 09:00 | 125 | 22:00 | SevenRings | 132 | 04:00 | 124 | 21:00
Gopalganj | 134 | 10:00 | 123 | 23:00 | ShahCement | 127 | 18:00 | 122 | 23:00
Gopalganj-400 | 135 | 07:00 | 128 | 22:00 | Shahjadpur | 135 | 01:00 | 130 | 20:00
Gulshan | 133 | 03:00 | 124 | 12:00 | Shahjibazar | 124 | 07:00 | 118 | 17:00
Halishahar | 131 | 05:00 | 126 | 22:00 | Shahmirpur | 132 | 19:30 | 128 | 21:00
Haripur | 126 | 04:00 | 123 | 09:00 | Shariatpur | 132 | 08:00 | 123 | 23:00
HaripurSBU | 126 | 05:00 | 123 | 08:00 | Sherpur | 138 | 14:00 | 124 | 01:00
Hasnabad | 129 | 04:00 | 124 | 12:00 | Shikalbaha | 121 | 04:00 | 118 | 00:00
Hathazari | 134 | 10:00 | 127 | 22:00 | Shikalbaha-230 | 132 | 06:00 | 120 | 18:30
Ishurdi | 138 | 08:00 | 130 | 19:30 | Shitalakhya | 127 | 04:00 | 123 | 13:00
Jaldhaka | 131 | 18:30 | 117 | 20:00 | Sholosohor | 131 | 08:00 | 125 | 22:00
Jamalpur | 139 | 14:00 | 127 | 01:00 | Shyampur | 126 | 18:00 | 122 | 21:00
Jashore | 130 | 08:00 | 118 | 00:00 | Shyampur-230 | 128 | 06:00 | 123 | 12:00
Jhenaidah | 135 | 07:00 | 116 | 19:30 | Siddhirganj | 127 | 04:00 | 123 | 22:00
Jhenaidah-230 | 135 | 08:00 | 124 | 19:30 | Sirajganj | 131 | 07:00 | 124 | 21:00
Joydebpur | 125 | 18:00 | 119 | 21:00 | Sonargaon | 125 | 18:00 | 120 | 22:00
Joypurhat | 130 | 16:00 | 121 | 00:00 | Sreemongol | 126 | 08:00 | 120 | 17:00
Juldah | 132 | 03:00 | 128 | 20:00 | Sreepur | 132 | 18:00 | 123 | 22:00
Kabirpur | 133 | 19:30 | 120 | 09:00 | Srinagar | 130 | 05:00 | 123 | 00:00
Kachua | 129 | 08:00 | 118 | 21:00 | SSM | 136 | 07:00 | 132 | 00:00
Kaliakoir | 137 | 07:00 | 129 | 09:00 | Sunamganj | 125 | 21:00 | 118 | 19:00
Kallyanpur | 130 | 04:00 | 122 | 23:00 | Sylhet | 129 | 21:00 | 122 | 19:00
Kalurghat | 130 | 05:00 | 125 | 23:00 | Sylhet-132 | 129 | 06:00 | 125 | 15:00
Kamrangirchar | 130 | 05:00 | 123 | 19:00 | Tangail | 130 | 09:00 | 124 | 01:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 135 | 19:00 | 117 | 04:00
Kasba | 123 | 06:00 | 117 | 23:00 | TK | 129 | 04:00 | 125 | 22:00
Kazla | 130 | 06:00 | 124 | 13:00 | Tongi | 131 | 04:00 | 126 | 07:00
Keranigonj | 130 | 05:00 | 123 | 23:00 | Ullahpara | 133 | 03:00 | 125 | 22:00
Khagrachori | 129 | 06:00 | 123 | 21:00 | Ullon | 134 | 18:00 | 125 | 10:00
Khulna | 134 | 08:00 | 122 | 00:00 | Uttara | 128 | 05:00 | 120 | 23:00
Khulna(S) | 137 | 10:00 | 125 | 19:30 | UttaraNew | 130 | 05:00 | 121 | 20:00
Khulshi | 129 | 03:00 | 125 | 22:00 | Zigatola | 131 | 06:00 | 123 | 21:00
Kishoreganj | 128 | 18:00 | 116 | 22:00
Kodda | 132 | 07:00 | 118 | 19:00
KSRM | 133 | 18:00 | 126 | 22:00
Kulaura | 131 | 08:00 | 127 | 00:00
Kurigram | 129 | 16:00 | 115 | 20:00
Kushtia | 132 | 10:00 | 121 | 19:30
Lalbag | 130 | 06:00 | 122 | 23:00
Lalmonirhat | 128 | 16:00 | 117 | 20:00
Madanganj | 126 | 05:00 | 122 | 09:00
Madaripur | 134 | 08:00 | 127 | 21:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division