## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 26-05-2025 | [28 empty] | Date: | 26-05-2025 | [28 empty] | Date: | 26-05-2025 | [28 empty] | Date: | 26-05-2025 | [28 empty] | Date: | 26-05-2025 | [16 empty] | Date: | 26-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [16 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 0 | 17 | 17 | 112 | 79 | 45 | 0 | 35 | 162 | 0 | 16 | 300 | 290 | 250 | 0 | 35 | 0 | 283 | 0 | 0 | 0 | 90 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 100 | 36 | 0 | 38 | 0 | 26 | 572 | 17 | 0 | 19 | 0 | 0 | 183 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 355 | 340 | 30 | 216 | 30 | 94 | 80 | 200 | 15 | 14 | 114 | 48 | 52.2 | 0 | 46 | 300 | 320 | 355 | 39 | 0 | 0 | 140 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 35 | 105 | 162 | 0 | 0 | 0 | 12 | 7910.2 | 920 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1457.36 | 0 | 0 | 0 | 103 | 0 | 42 | 0 | 0 | 0 | 0 | 15 | 0 | 136 | 0 | 124 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 116 | 220 | 0 | 300 | 1244 | 0 | 7099.56 | 15009.76 | 76.97
01:00 | 0 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 0 | 17 | 17 | 112 | 63 | 45 | 0 | 35 | 126 | 0 | 16 | 300 | 286 | 250 | 0 | 35 | 0 | 268 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 34 | 24 | 0 | 100 | 36 | 0 | 37 | 0 | 26 | 568 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 354 | 330 | 30 | 217 | 30 | 94 | 80 | 200 | 9 | 14 | 114 | 44 | 52.2 | 0 | 46 | 280 | 320 | 349 | 39 | 0 | 0 | 129 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7552.2 | 919 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1457.46 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 126 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 156 | 50 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 298 | 1244 | 0 | 6906.66 | 14458.86 | 76.96
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 112 | 63 | 0 | 0 | 35 | 126 | 0 | 16 | 300 | 290 | 250 | 0 | 35 | 0 | 285 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 34 | 24 | 0 | 100 | 36 | 0 | 36 | 0 | 26 | 503 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 354 | 335 | 30 | 216 | 30 | 77 | 80 | 200 | 9 | 14 | 114 | 42 | 52.2 | 0 | 46 | 285 | 320 | 354 | 38 | 0 | 0 | 131 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7352.2 | 927 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1206 | 17 | 1360.05 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 126 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 157 | 50 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 116 | 220 | 0 | 300 | 1170 | 0 | 6653.05 | 14005.25 | 76.96
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 17 | 17 | 112 | 48 | 0 | 0 | 35 | 126 | 0 | 16 | 300 | 285 | 250 | 0 | 35 | 0 | 285 | 0 | 0 | 0 | 17 | 16.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 100 | 24 | 0 | 36 | 0 | 26 | 501 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 354 | 335 | 30 | 218 | 30 | 74 | 80 | 200 | 9 | 14 | 114 | 42 | 52.2 | 0 | 47 | 285 | 320 | 369 | 38 | 0 | 0 | 131 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7331.7 | 927 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 1320.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 126 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 157 | 49 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 120 | 220 | 0 | 300 | 1170 | 0 | 6416.11 | 13747.81 | 76.96
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 17 | 17 | 112 | 48 | 0 | 0 | 35 | 90 | 0 | 16 | 300 | 305 | 250 | 0 | 35 | 0 | 300 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 100 | 24 | 0 | 38 | 0 | 26 | 502 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 300 | 335 | 30 | 216 | 30 | 75 | 80 | 200 | 9 | 14 | 114 | 40 | 52.2 | 0 | 47 | 290 | 320 | 400 | 38 | 0 | 0 | 137 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7326.2 | 927 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 1214.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 156 | 47 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 10 | 120 | 180 | 0 | 301 | 1060 | 0 | 6089.12 | 13415.32 | 76.95
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 17 | 17 | 102 | 48 | 0 | 0 | 35 | 72 | 0 | 16 | 300 | 272 | 250 | 0 | 35 | 0 | 265 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 100 | 24 | 0 | 40 | 0 | 26 | 505 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 12 | 16 | 0 | 300 | 330 | 30 | 219 | 28 | 74 | 80 | 200 | 9 | 14 | 114 | 40 | 52.2 | 0 | 47 | 285 | 320 | 350 | 38 | 0 | 0 | 134 | 0 | 0 | 22 | 20 | 0 | 0 | 173 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 7168.2 | 927 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1060 | 0 | 1211.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 126 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 155 | 46 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 10 | 120 | 180 | 0 | 272 | 1050 | 0 | 6034.79 | 13202.99 | 76.95
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 17 | 95 | 48 | 0 | 0 | 35 | 35 | 0 | 16 | 300 | 295 | 300 | 0 | 35 | 0 | 300 | 0 | 0 | 2 | 17 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 0 | 60 | 24 | 0 | 40 | 0 | 25 | 505 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1110 | 1 | 51 | 12 | 16 | 0 | 300 | 330 | 30 | 216 | 28 | 75 | 80 | 200 | 8 | 14 | 114 | 38 | 25 | 5 | 47 | 290 | 320 | 388 | 38 | 0 | 0 | 139 | 0 | 0 | 22 | 23 | 0 | 0 | 172 | 17 | 48 | 96 | 0 | 0 | 2.56 | 12 | 7115.56 | 453 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1062 | 34 | 1156.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 136 | 0 | 127 | 0 | 0 | 0 | 350 | 0 | 0.15 | 0 | 155 | 46 | 35 | 1 | 34 | 0 | 0 | 0.3 | 2 | 0.32 | 0 | 200 | 10 | 124 | 180 | 0 | 223 | 1050 | 0 | 5515.21 | 12630.77 | 76.95
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 17 | 17 | 95 | 48 | 0 | 0 | 35 | 35 | 0 | 16 | 300 | 285 | 300 | 0 | 35 | 0 | 275 | 0 | 0 | 12 | 17 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 8 | 0 | 60 | 0 | 1 | 40 | 0 | 17 | 508 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1110 | 4 | 51 | 12 | 16 | 0 | 300 | 335 | 30 | 216 | 28 | 74 | 80 | 155 | 9 | 14 | 114 | 36 | 8 | 18 | 16 | 290 | 320 | 376 | 38 | 0 | 0 | 136 | 0 | 0 | 22 | 23 | 0 | 0 | 171 | 17 | 67 | 125 | 0 | 1 | 5.12 | 12 | 7007.12 | 456 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 1107 | 34 | 1159.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.33 | 139 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 1.26 | 0 | 151 | 46 | 0 | 4 | 0 | 0 | 0 | 0.7 | 23 | 0.13 | 0 | 200 | 9 | 120 | 220 | 0 | 218 | 1085 | 0 | 5628.11 | 12635.23 | 76.94
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 17 | 95 | 48 | 0 | 0 | 35 | 35 | 0 | 16 | 300 | 287 | 300 | 0 | 17 | 0 | 275 | 0 | 0 | 7 | 17 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 8 | 0 | 36 | 0 | 3 | 40 | 0 | 2 | 502 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1105 | 12 | 51 | 12 | 16 | 0 | 300 | 335 | 30 | 215 | 28 | 74 | 80 | 120 | 9 | 14 | 114 | 34 | 8 | 33 | 16 | 290 | 320 | 381 | 38 | 0 | 0 | 130 | 0 | 0 | 22 | 23 | 0 | 0 | 172 | 17 | 67 | 124 | 0 | 1 | 28.82 | 12 | 6923.82 | 457 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 1110 | 17 | 1163.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 27.25 | 139 | 0 | 130 | 0 | 0 | 0 | 350 | 0 | 2.45 | 0 | 147 | 48 | 0 | 3 | 0 | 0 | 0 | 0.8 | 20 | 0.33 | 0 | 200 | 7 | 120 | 220 | 0 | 219 | 1090 | 0 | 5657.82 | 12581.64 | 76.94
09:00 | 0 | 34 | 13 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 17 | 17 | 95 | 143 | 0 | 0 | 35 | 35 | 0 | 16 | 300 | 281 | 300 | 0 | 17 | 0 | 266 | 0 | 0 | 5 | 52 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 8 | 0 | 36 | 0 | 3 | 40 | 0 | 2 | 505 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1108 | 14 | 51 | 12 | 16 | 0 | 300 | 335 | 30 | 216 | 17 | 74 | 80 | 120 | 9 | 14 | 114 | 36 | 8 | 58 | 16 | 300 | 320 | 350 | 38 | 0 | 0 | 133 | 0 | 0 | 22 | 20 | 0 | 0 | 172 | 17 | 67 | 125 | 0 | 1 | 36.97 | 11 | 7079.97 | 456 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 1109 | 17 | 1159.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 37.37 | 140 | 0 | 135 | 0 | 0 | 0 | 350 | 0 | 2.59 | 0 | 124 | 49 | 0 | 1 | 0 | 0 | 0 | 0.6 | 10 | 0.64 | 0 | 200 | 7 | 110 | 220 | 0 | 291 | 1080 | 0 | 5717.06 | 12797.03 | 76.94
10:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 17 | 105 | 110 | 0 | 0 | 35 | 80 | 0 | 0 | 300 | 287 | 300 | 0 | 0 | 0 | 286 | 0 | 0 | 18 | 52 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 24 | 0 | 4 | 40 | 0 | 2 | 501 | 0 | 0 | 19 | 0 | 0 | 184 | 0 | 0 | 0 | 1105 | 9 | 51 | 12 | 16 | 0 | 351 | 335 | 30 | 214 | 23 | 74 | 80 | 85 | 9 | 14 | 98 | 34 | 0 | 68 | 16 | 305 | 320 | 386 | 38 | 0 | 0 | 143 | 0 | 0 | 22 | 20 | 0 | 0 | 172 | 17 | 68 | 123 | 0 | 2 | 29.32 | 11 | 7116.32 | 456 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 1106 | 0 | 1265.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 28.33 | 142 | 0 | 139 | 0 | 0 | 0 | 414 | 0 | 3.93 | 0 | 162 | 48 | 0 | 3 | 0 | 0 | 0 | 2.3 | 45 | 0.38 | 0 | 200 | 7 | 110 | 220 | 0 | 307 | 1085 | 0 | 5956.28 | 13072.6 | 76.93
11:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 17 | 17 | 112 | 110 | 0 | 0 | 35 | 150 | 0 | 0 | 300 | 308 | 300 | 0 | 17 | 0 | 311 | 0 | 0 | 10 | 52 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 17 | 0 | 0 | 24 | 0 | 3 | 40 | 0 | 2 | 575 | 0 | 0 | 19 | 0 | 0 | 185 | 0 | 0 | 0 | 1224 | 13 | 51 | 18 | 16 | 0 | 338 | 335 | 30 | 212 | 24 | 69 | 80 | 82 | 9 | 14 | 113 | 38 | 0 | 71 | 16 | 305 | 320 | 390 | 38 | 0 | 0 | 154 | 0 | 0 | 22 | 18 | 0 | 0 | 172 | 17 | 67 | 123 | 0 | 2 | 36.53 | 11 | 7500.53 | 456 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 1085 | 0 | 1333.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 53.92 | 151 | 0 | 137 | 0 | 0 | 0 | 414 | 0 | 3.56 | 0 | 163 | 51 | 0 | 7 | 0 | 0 | 0 | 2.8 | 78 | 0.38 | 0 | 200 | 7 | 120 | 220 | 0 | 306 | 1090 | 0 | 6100.48 | 13601.01 | 76.93
12:00 | 0 | 34 | 25 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 39 | 17 | 109 | 110 | 72 | 0 | 35 | 162 | 0 | 28 | 300 | 287 | 300 | 0 | 17 | 0 | 288 | 0 | 0 | 15 | 52 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 17 | 0 | 0 | 88 | 35 | 3 | 38 | 0 | 2 | 575 | 0 | 0 | 21 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 17 | 51 | 58 | 16 | 0 | 346 | 335 | 30 | 212 | 30 | 65 | 70 | 135 | 8 | 6 | 98 | 38 | 8 | 70 | 39 | 300 | 320 | 368 | 38 | 0 | 0 | 153 | 0 | 0 | 22 | 18 | 0 | 0 | 172 | 17 | 67 | 121 | 0 | 2 | 50.68 | 11 | 7789.68 | 457 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 1100 | 0 | 1396.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 16.08 | 148 | 0 | 135 | 0 | 0 | 0 | 414 | 0 | 1.51 | 0 | 163 | 50 | 0 | 13 | 0 | 0 | 0 | 2.4 | 87 | 0.7 | 0 | 200 | 8 | 120 | 220 | 0 | 304 | 1093 | 0 | 6185.76 | 13975.44 | 76.93
13:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 54 | 17 | 112 | 95 | 145 | 7 | 35 | 162 | 0 | 50 | 300 | 267 | 300 | 0 | 17 | 0 | 267 | 0 | 0 | 16 | 52 | 15 | 17 | 0 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 0 | 0 | 88 | 50 | 3 | 36 | 13 | 11 | 575 | 0 | 0 | 38 | 0 | 13 | 185 | 0 | 0 | 0 | 1224 | 18 | 51 | 110 | 16 | 0 | 354 | 335 | 30 | 215 | 34 | 74 | 50 | 132 | 8 | 11 | 114 | 44 | 16 | 70 | 45 | 300 | 320 | 338 | 38 | 0 | 0 | 141 | 0 | 0 | 22 | 18 | 0 | 0 | 172 | 17 | 69 | 121 | 0 | 2 | 38.84 | 0 | 7965.84 | 456 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 1106 | 0 | 1441.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 16.63 | 145 | 0 | 134 | 0 | 0 | 0 | 350 | 0 | 1.32 | 0 | 163 | 50 | 0 | 4 | 0 | 0 | 0 | 4.1 | 107 | 0.82 | 0 | 200 | 8 | 110 | 220 | 0 | 306 | 1140 | 0 | 6184.21 | 14150.05 | 76.93
14:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 17 | 112 | 95 | 145 | 15 | 35 | 162 | 0 | 50 | 300 | 297 | 250 | 0 | 17 | 0 | 290 | 0 | 0 | 30 | 52 | 16 | 17 | 0 | 0 | 0 | 15 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 50 | 5 | 35 | 17 | 8 | 575 | 0 | 0 | 50 | 0 | 17 | 185 | 0 | 0 | 0 | 1167 | 12 | 51 | 98 | 16 | 0 | 340 | 305 | 30 | 181 | 34 | 90 | 70 | 151 | 8 | 11 | 114 | 44 | 16 | 37 | 44 | 295 | 320 | 364 | 38 | 0 | 0 | 145 | 0 | 0 | 22 | 18 | 0 | 0 | 172 | 17 | 68 | 121 | 0 | 1 | 35.42 | 2 | 7925.42 | 457 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 1058 | 0 | 1381.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 66.69 | 145 | 0 | 132 | 0 | 0 | 0 | 414 | 0 | 4.51 | 0 | 154 | 50 | 0 | 6 | 0 | 0 | 0 | 6.8 | 144 | 0.54 | 0 | 250 | 8 | 114 | 180 | 0 | 308 | 1040 | 0 | 6107.9 | 14033.32 | 76.92
15:00 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 0 | 112 | 47 | 95 | 15 | 35 | 162 | 0 | 52 | 300 | 299 | 250 | 0 | 0 | 0 | 285 | 0 | 0 | 6 | 52 | 16 | 17 | 0 | 0 | 0 | 15 | 0 | 0 | 5 | 0 | 0 | 0 | 100 | 12 | 4 | 35 | 17 | 2 | 520 | 0 | 0 | 50 | 0 | 17 | 185 | 0 | 0 | 0 | 1155 | 13 | 51 | 50 | 16 | 0 | 300 | 305 | 31 | 211 | 30 | 93 | 70 | 156 | 9 | 14 | 101 | 44 | 16 | 18 | 44 | 305 | 320 | 363 | 37 | 0 | 0 | 147 | 0 | 0 | 22 | 18 | 0 | 0 | 171 | 17 | 68 | 121 | 0 | 1 | 22.96 | 11 | 7585.96 | 928 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 1016 | 0 | 1357.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 15.71 | 141 | 0 | 127 | 0 | 0 | 0 | 300 | 0 | 2.04 | 0 | 155 | 50 | 0 | 13 | 0 | 0 | 0 | 3.8 | 49 | 0.36 | 0 | 200 | 8 | 120 | 180 | 0 | 305 | 1000 | 0 | 6198.28 | 13784.24 | 76.91
16:00 | 0 | 89 | 32 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 0 | 112 | 47 | 95 | 15 | 35 | 126 | 0 | 52 | 300 | 294 | 250 | 0 | 0 | 0 | 285 | 0 | 0 | 2 | 52 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 100 | 12 | 1 | 36 | 17 | 3 | 501 | 0 | 0 | 50 | 0 | 17 | 184 | 0 | 0 | 0 | 1106 | 10 | 51 | 50 | 16 | 0 | 300 | 300 | 42 | 216 | 22 | 94 | 50 | 152 | 8 | 6 | 114 | 40 | 16 | 16 | 45 | 305 | 320 | 360 | 37 | 0 | 0 | 131 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 68 | 121 | 0 | 1 | 11.4 | 11 | 7401.4 | 928 | 136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 989 | 0 | 1366.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 18.51 | 141 | 0 | 124 | 0 | 0 | 0 | 300 | 0 | 1.31 | 0 | 154 | 50 | 0 | 17 | 0 | 0 | 0 | 2.9 | 55 | 0.17 | 0 | 150 | 10 | 120 | 180 | 0 | 307 | 1000 | 0 | 6098.65 | 13500.05 | 76.91
17:00 | 0 | 90 | 32 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 17 | 15 | 112 | 47 | 95 | 15 | 35 | 126 | 0 | 52 | 300 | 277 | 250 | 0 | 0 | 0 | 267 | 0 | 0 | 3 | 70 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 12 | 0 | 0 | 100 | 12 | 0 | 38 | 17 | 5 | 502 | 0 | 0 | 50 | 2 | 17 | 184 | 0 | 0 | 0 | 1105 | 3 | 51 | 50 | 16 | 0 | 300 | 300 | 49 | 182 | 26 | 94 | 70 | 151 | 9 | 12 | 114 | 40 | 16 | 9 | 45 | 310 | 320 | 339 | 38 | 0 | 0 | 133 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 68 | 121 | 0 | 0 | 4.79 | 11 | 7380.79 | 927 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.37 | 960 | 0 | 1371.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 9.67 | 141 | 0 | 125 | 0 | 0 | 0 | 300 | 0 | 0.88 | 0 | 156 | 50 | 0 | 5 | 0 | 0 | 0 | 1.3 | 63 | 0.08 | 0 | 150 | 6 | 110 | 180 | 0 | 307 | 1000 | 0 | 6030.03 | 13410.82 | 76.9
18:00 | 0 | 105 | 32 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 17 | 112 | 47 | 95 | 15 | 35 | 126 | 0 | 52 | 300 | 302 | 250 | 0 | 0 | 0 | 281 | 0 | 0 | 1 | 160 | 16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 17 | 0 | 0 | 100 | 12 | 0 | 39 | 17 | 6 | 454 | 0 | 0 | 50 | 8 | 17 | 184 | 0 | 0 | 0 | 1002 | 0 | 51 | 50 | 16 | 0 | 280 | 290 | 50 | 195 | 31 | 93 | 70 | 149 | 25 | 14 | 114 | 36 | 16 | 2 | 45 | 300 | 320 | 305 | 38 | 0 | 0 | 133 | 0 | 0 | 22 | 25 | 0 | 0 | 171 | 17 | 103 | 122 | 0 | 0 | 2.59 | 12 | 7373.59 | 928 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.72 | 906 | 0 | 1314.61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.66 | 140 | 0 | 129 | 0 | 0 | 0 | 250 | 0 | 0.3 | 0 | 156 | 50 | 0 | 3 | 0 | 0 | 0 | 0.5 | 11 | 0.03 | 0 | 150 | 8 | 100 | 180 | 0 | 307 | 900 | 0 | 5681.82 | 13055.41 | 76.9
19:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 26 | 17 | 100 | 146 | 95 | 15 | 35 | 151 | 0 | 69 | 300 | 306 | 250 | 0 | 35 | 0 | 294 | 0 | 0 | 0 | 160 | 16 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 34 | 33 | 0 | 88 | 12 | 0 | 40 | 17 | 2 | 575 | 17 | 0 | 50 | 8 | 17 | 184 | 0 | 0 | 0 | 1202 | 0 | 51 | 88 | 16 | 0 | 340 | 300 | 50 | 200 | 31 | 94 | 70 | 152 | 27 | 14 | 114 | 46 | 43 | 0 | 47 | 305 | 320 | 346 | 38 | 0 | 0 | 135 | 0 | 0 | 22 | 22 | 0 | 0 | 171 | 35 | 96 | 176 | 0 | 0 | 0 | 12 | 8178 | 881 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1014 | 15 | 1438.52 | 0 | 0 | 0 | 6 | 0 | 50 | 0 | 15 | 0 | 0 | 22 | 0 | 141 | 0 | 132 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 156 | 49 | 111 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 11 | 120 | 220 | 0 | 307 | 960 | 0 | 6437.52 | 14615.52 | 76.89
19:30 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 54 | 17 | 95 | 145 | 20 | 15 | 35 | 141 | 0 | 69 | 300 | 288 | 250 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 160 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 34 | 40 | 0 | 88 | 50 | 0 | 40 | 17 | 8 | 576 | 17 | 0 | 36 | 8 | 17 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 130 | 16 | 0 | 354 | 300 | 50 | 181 | 29 | 94 | 70 | 185 | 38 | 14 | 114 | 42 | 43 | 0 | 47 | 300 | 320 | 317 | 38 | 0 | 0 | 149 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 35 | 96 | 176 | 0 | 0 | 0 | 12 | 8093 | 881 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1130 | 17 | 1444.15 | 0 | 0 | 0 | 55 | 0 | 50 | 0 | 29 | 0 | 0 | 22 | 0 | 140 | 0 | 132 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 156 | 49 | 114 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 306 | 1200 | 0 | 6874.15 | 14967.15
20:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 54 | 17 | 95 | 145 | 0 | 0 | 35 | 141 | 0 | 33 | 300 | 304 | 250 | 0 | 17 | 0 | 290 | 0 | 0 | 0 | 142 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 34 | 40 | 0 | 60 | 50 | 0 | 40 | 17 | 2 | 575 | 17 | 0 | 19 | 0 | 17 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 16 | 0 | 350 | 330 | 50 | 197 | 29 | 93 | 70 | 167 | 38 | 14 | 114 | 40 | 52.2 | 0 | 47 | 300 | 320 | 366 | 39 | 0 | 0 | 149 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 35 | 96 | 177 | 0 | 0 | 0 | 12 | 8056.2 | 881 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 17 | 1449.74 | 0 | 15 | 0 | 50 | 0 | 50 | 0 | 32 | 0 | 0 | 22 | 0 | 140 | 0 | 133 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 155 | 49 | 114 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 306 | 1210 | 0 | 6900.74 | 14956.94 | 76.89
21:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 53 | 17 | 112 | 145 | 0 | 0 | 35 | 143 | 0 | 33 | 300 | 280 | 250 | 0 | 17 | 0 | 275 | 0 | 0 | 0 | 142 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 40 | 0 | 60 | 12 | 0 | 40 | 17 | 15 | 575 | 0 | 0 | 0 | 0 | 17 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 16 | 0 | 352 | 330 | 51 | 188 | 35 | 110 | 80 | 200 | 38 | 12 | 114 | 42 | 52.2 | 0 | 47 | 305 | 320 | 341 | 39 | 0 | 0 | 150 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 96 | 177 | 0 | 0 | 0 | 12 | 8012.2 | 928 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 17 | 1442 | 0 | 25 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 0 | 140 | 0 | 135 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 155 | 49 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 11 | 120 | 220 | 0 | 307 | 1244 | 0 | 7004 | 15016.2 | 76.88
22:00 | 0 | 105 | 34 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 32 | 17 | 112 | 145 | 0 | 0 | 17 | 119 | 0 | 33 | 300 | 299 | 300 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 90 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 34 | 8 | 0 | 60 | 0 | 0 | 40 | 17 | 27 | 575 | 0 | 0 | 0 | 0 | 17 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 16 | 0 | 354 | 330 | 52 | 195 | 34 | 115 | 80 | 136 | 38 | 6 | 88 | 32 | 8 | 0 | 0 | 305 | 320 | 349 | 39 | 0 | 0 | 149 | 0 | 0 | 22 | 20 | 0 | 0 | 171 | 17 | 96 | 179 | 0 | 0 | 0 | 12 | 7762 | 832 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1127 | 17 | 1457 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 133 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 50 | 75 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 120 | 220 | 0 | 307 | 1244 | 0 | 6771 | 14533 | 76.88
23:00 | 0 | 105 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 17 | 17 | 111 | 112 | 0 | 0 | 17 | 112 | 0 | 32 | 300 | 296 | 300 | 0 | 17 | 0 | 284 | 0 | 0 | 0 | 90 | 16.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 34 | 0 | 0 | 50 | 0 | 0 | 40 | 17 | 32 | 570 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 16 | 0 | 354 | 330 | 52 | 187 | 34 | 98 | 80 | 136 | 39 | 12 | 88 | 34 | 8 | 0 | 0 | 300 | 320 | 322 | 39 | 0 | 0 | 148 | 0 | 0 | 52 | 0 | 0 | 0 | 171 | 17 | 96 | 180 | 0 | 0 | 0 | 4 | 7618.5 | 881 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1194 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 131 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 159 | 50 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 218 | 1244 | 0 | 6779 | 14397.5 | 76.87
Total KWH | 0 | 1417920 | 542880 | 0 | 0 | 0 | 0 | 0 | 8629200 | 0 | 0 | 667440 | 409680 | 2595168 | 2027520 | 953455 | 110812 | 838759 | 2754720 | 0 | 682560 | 7564500 | 7061585 | 6538591 | 0 | 477872 | 0 | 6870521 | 0 | 0 | 147109 | 1518000 | 384000 | 380880 | 0 | 0 | 0 | 55200 | 0 | 0 | 219840 | 581206 | 278003 | 0 | 1800960 | 497280 | 26660 | 912660 | 191527 | 337920 | 12814545.46 | 38473 | 0 | 635520 | 24183 | 213272 | 4292040 | 0 | 0 | 0 | 28063634 | 126765 | 1235660 | 1206036 | 434909.09 | 0 | 8232500 | 7960000 | 903840 | 5053000 | 700488 | 2051520 | 1775860 | 3777600 | 375480 | 280750 | 2601480 | 916800 | 592637 | 478818 | 817152 | 7247000 | 7675800 | 8944000 | 905000 | 0 | 0 | 3362809 | 0 | 0 | 575040 | 441408 | 0 | 0 | 3537240 | 472680 | 1695600 | 3076800 | 0 | 11450 | 324590 | 256320 | 181603127.55 | 14767272 | 2874816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 633600 | 26210910 | 204960 | 32172008 | 0 | 48701 | 0 | 326112 | 0 | 237680 | 0 | 57712 | 0 | 326930 | 75460 | 303000 | 3410273 | 0 | 3331027 | 0 | 0 | 0 | 8663054 | 0 | 26640 | 0 | 3828000 | 1134109 | 915866 | 76586 | 454588 | 0 | 0 | 26864.76 | 612720 | 4449 | 0 | 5629000 | 213672 | 2772000 | 5214640 | 0 | 6702533 | 26965818.18 | 0 | 148221000.94 | 329824128.49

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 27-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-05-2025 | during | 27-05-2025 | during | 27-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 381 | 346 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 320 | 320 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 287 | 280 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 288 | 275 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 39 | 53 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 110 | 145 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 55 | 55 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 16 | 33 | 33 | 16.5 | 16.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 17 | 17 | 22 | 22 | 17 | 17 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 34 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 72 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 109 | 112 | 135 | 135 | 115 | 115 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 34 | 105 | 105 | 105 | 105 | 105 | -
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 28 | 33 | 104 | 104 | 65 | 65 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 162 | 143 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 15 | 0 | 30 | 0 | 30 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 300 | 250 | 583 | 583 | 370 | 370 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 52 | 142 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 2304 | 2320 | 5274.1 | 5338.1 | 3137.58 | 3201.58
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 17 | 0 | 17 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 21 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 38 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 184 | 184 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 48 | 72 | 72 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 17 | 34 | 34 | 34 | 34 | 34 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 60 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 15 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 90 | 90 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 3 | 0 | 2.76 | 0 | 2.76 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 17 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 35 | 12 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 7 | 6 | 1 | 40 | 1 | 40 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 575 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2211 | 2224 | 3355.48 | 3405.72 | 3361.48 | 3387.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 212 | 188 | 221.43 | 221.43 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 346 | 352 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 330 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 30 | 35 | 46.7 | 46.7 | 34 | 34 | -
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 30 | 51 | 55 | 55 | 30 | 30 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 16 | 195 | 195 | 16 | 16 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 58 | 80 | 150 | 150 | 145 | 145 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 39 | 47 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 70 | 80 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 135 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 42 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 12 | 17.75 | 17.75 | 14 | 14 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 38 | 113 | 113 | 28 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 65 | 110 | 115 | 115 | 92 | 92 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 70 | 0 | 40 | 0 | 40 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1615 | 1798.2 | 2434.43 | 2394.43 | 2011.55 | 1971.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 26-05-2025 | during | 27-05-2025 | during | 27-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 121 | 177 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 67 | 96 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 50.68 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 17 | 54.5 | 54.5 | 17 | 17 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 268.68 | 302 | 601.1 | 549 | 356.1 | 304
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 38 | 39 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 30 | 30 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 150 | 163 | 163 | 163 | 163 | -
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 18 | 20 | 30 | 30 | 30 | 30 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 22 | 22 | 83 | 83 | 83 | 83 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 172 | 171 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 13 | 13 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 368 | 341 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1391 | 1368 | 1601 | 1601 | 1497 | 1497
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 457 | 928 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 95 | 142 | 410 | 410 | 153 | 153 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 90 | 90 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 104 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1100 | 1126 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1756 | 2213 | 3582.2 | 3512.2 | 3310.2 | 3240.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 304 | 307 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 8 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 120 | 130 | 130 | 130 | 130 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1093 | 1244 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 258 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.7 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1945.7 | 2160 | 2172 | 2171 | 2172 | 2171
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 25 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | -
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 148 | 140 | 214 | 214 | 172 | 172 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 135 | 135 | 220 | 220 | 160 | 160 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 371 | 371 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 22 | 22 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 50 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 50 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.51 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1396.07 | 1442 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 16.08 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 58 | 0 | 75 | 0 | 75 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 2168.66 | 2278 | 3161.72 | 3019.87 | 3016.93 | 2875.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 49 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 163 | 155 | 160 | 160 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 2.4 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 13 | 0 | 18 | 0 | 18 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 87 | 0 | 179.12 | 0 | 179.12 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 315.4 | 353 | 674.72 | 472 | 674.72 | 472
System Total |  |  |  |  | 28886.2 | 27110.055 | 13975.44 | 15016.2 | 22856.75 | 22463.32 | 19537.56 | 19120.13
Forecast Scenario (27-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14950 |  | 0 |  | 14950
|  |  |  | 1:00 | 14680 |  | 0 |  | 14680
|  |  |  | 2:00 | 14170 |  | 0 |  | 14170
|  |  |  | 3:00 | 13910 |  | 0 |  | 13910
|  |  |  | 4:00 | 13640 |  | 0 |  | 13640
|  |  |  | 5:00 | 13400 |  | 0 |  | 13400
|  |  |  | 6:00 | 12840 |  | 0 |  | 12840
|  |  |  | 7:00 | 12960 |  | 0 |  | 12960
|  |  |  | 8:00 | 12940 |  | 0 |  | 12940
|  |  |  | 9:00 | 13510 |  | 0 |  | 13510
|  |  |  | 10:00 | 13640 |  | 0 |  | 13140
|  |  |  | 11:00 | 13870 |  | 0 |  | 13370
|  |  |  | 12:00 | 14310 |  | 0 |  | 13810
|  |  |  | 13:00 | 14480 |  | 0 |  | 13980
|  |  |  | 14:00 | 14260 |  | 0 |  | 13760
|  |  |  | 15:00 | 14280 |  | 0 |  | 13780
|  |  |  | 16:00 | 13880 |  | 0 |  | 13380
|  |  |  | 17:00 | 13760 |  | 0 |  | 13260
|  |  |  | 18:00 | 13400 |  | 0 |  | 12900
|  |  |  | 18:30 | 14000 |  | 0 |  | 13500
|  |  |  | 19:00 | 14950 |  | 0 |  | 14450
|  |  |  | 19:30 | 15500 |  | 0 |  | 15000
|  |  |  | 20:00 | 15120 |  | 0 |  | 14620
|  |  |  | 21:00 | 15230 |  | 0 |  | 14730
|  |  |  | 22:00 | 15060 |  | 0 |  | 14560
|  |  |  | 23:00 | 15200 |  | 0 |  | 14700
Probable Maximum Temperature: |  |  | 32.10°C
Probable Maximum Demand at Day Peak: |  |  | 13810.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15000.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15500.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 338.44 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:58 hrs on 27-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 26-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13975.44 | MW | 12:00 Hr. | Energy Generated |  |  | 329.8241 |  | MKWHr.
| Day Peak Demand |  |  | 14082.44 | MW | 12:00 Hr. | Energy Unserverd |  |  | 3.819 |  | MKWHr.
| Evening Peak Generation |  |  | 15016.2 | MW | 21:00 Hr. | Energy Demand |  |  | 333.6431 |  | MKWHr.
| Evening Peak Demand |  |  | 15130.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.4 |  | °C
| Minimum Generation of the Day |  |  | 12581.64 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 914.53 |  | MMCFD
| Maximum Generation of the Day |  |  | 15016.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.7233 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.4293 | 0 | 14.9968 | 0 | 0 | 0.14711 | 0 | 0 | 52.5732 | Gas | 127.804 | Gas | 450958424.2053
| Chattogram Zone |  |  | 4.63 | 40.8782 | 4.3156 | 0 | 0.91266 | 0.15343 | 0 | 0.21984 | 51.1097 | Coal | 111.3485 | Coal | 727077216.5106
| Cumilla Zone |  |  | 26.577 | 0 | 11.4219 | 0 | 0 | 0.47882 | 0.9168 | 0 | 39.3945 | HFO | 38.5568 | HFO | 714764963.19
| Mymensingh Zone |  |  | 0 | 0 | 5.5014 | 0 | 0 | 0.33604 | 0 | 0 | 5.8374 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.6883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.6883 | Hydro | 0.91266 | Hydro | 91266
| Khulna Zone |  |  | 2.8748 | 26.2109 | 0.20496 | 0 | 0 | 0.6336 | 14.7673 | 0 | 44.6916 | Solar | 3.1262 | Solar | 49947479.3436
| Barishal Zone |  |  | 8.2003 | 39.2974 | 0 | 0 | 0 | 0.004449 | 0 | 0 | 47.5021 | Import | 47.8561 | Import | 271452289.6
| Rajshahi Zone |  |  | 15.4044 | 0 | 0.74567 | 0 | 0 | 0.65657 | 32.172 | 0 | 48.9786 | Wind | 0.21984 | Wind | 3218457.6
| Rangpur Zone |  |  | 0 | 4.9621 | 1.3705 | 0 | 0 | 0.71617 | 0 | 0 | 7.0487
| Total |  |  | 127.804 | 111.3485 | 38.5568 | 0 | 0.91266 | 3.1262 | 47.8561 | 0.21984 | 329.8241
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 450958424.2053 |  | Hydro | 91266
|  |  |  | Coal | 727077216.5106 |  | Solar | 49947479.3436
|  |  |  | HFO | 714764963.19 |  | Import | 271452289.6
|  |  |  | HSD | 0 |  | Wind | 3218457.6
[5 empty] | Total: | 221,75,10,096 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 14.7673 | Peak Hr Flow | 928.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 47190545.52 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 32.172 | Peak Hr Flow | 1442.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 712 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9168 | Peak Hr Flow | 42.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 922 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 47.8561 | Peak Hr Flow | 2412.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 45 |  | 5567
|  |  |  | Chattogram |  | 0 |  | 1267
|  |  |  | Cumilla |  | 25 |  | 1215
|  |  |  | Mymensingh |  | 19 |  | 1238
|  |  |  | Sylhet |  | 20 |  | 621
|  |  |  | Khulna |  | 0 |  | 1721
|  |  |  | Barishal |  | 0 |  | 502
|  |  |  | Rajshahi |  | 0 |  | 1451
|  |  |  | Rangpur |  | 0 |  | 918
|  |  |  | Total |  | 109 |  | 14500
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:25 | 09:37 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to 33kv. shahapur pdb feeder B-phase Bus | [7 empty] | 10.0MW load
|  |  | connector clamp maintenance work. | [7 empty] | interrup.
| 08:25 | 09:37 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to 33kv shahapur pdb feeder B-phase Bus | [7 empty] | 10.0MW load
|  |  | connector clamp maintenance work. | [7 empty] | interrup.
| 08:36 | 09:50 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to Bus section DS maintenance by | [7 empty] | 14.0MW load
|  |  | BPDB | [7 empty] | interrup.
|  | 08:45 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) HT is restored.
|  | 08:45 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT is restored.
| 09:30 | 12:26 | Tongi 230/132/33kV S/S 230 kV Bus-2 Project Work S/D
| 09:37 | 09:49 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to Bus section DS Maintenance by | [7 empty] | 14.0MW load
|  |  | BPDB | [7 empty] | interrup.
|  | 09:44 | Khulna(C )-Khulna (S) 132kV Ckt-2 is restored.
|  | 09:44 | Khulna(C )-Khulna (S) 132kV Ckt-2 is restored.
| 10:50 | 01:39 | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
| 10:53 | 13:02 | Barguna 132/33kV S/S Transformer-2 LT Scheduled S/D Due to To remove oil level alarm in
main tank of T2-Transformer.
| 10:53 | 13:01 | Barguna 132/33kV S/S Transformer-2 HT Scheduled S/D Due to To remove oil level alarm in
main tank of T2-Transformer.
| 11:04 | 11:50 | Mymensingh RPCL-Tangail 132kV Ckt-2 Forced S/D from Ghatail 132/33kV end.
|  | 11:58 | Rampura-Ullon-2 132kV Ckt-1 is restored.
| 12:00 |  | Day peak generation 13973 MW
| 12:25 | 12:53 | Cox'sbazar-Dohazari 132 kV Ckt-1 Tripped from Dohazari 132/33kV end showing Distance | [7 empty] | 38.0MW load
|  |  | Relay Lockout Relay relays. and from Coxsbazar 132/33kV end showing QUADRAMHO SHPM-101 | [7 empty] | interrup. Dohazari
|  |  | relays Due to Phase B,C & Zone-2 fault | [7 empty] | 132/33kV end
| 12:49 | 13:01 | Tangail 132/33kV S/S Tr-2 LT Tripped showing REF615 relays Due to Due to new feeder trial | [7 empty] | 46.0MW load
|  |  | BPDB. | [7 empty] | interrup.
| 12:49 | 13:01 | Tangail 132/33kV S/S Tr-1 LT Tripped showing REF615 relays Due to Due to new feeder trial | [7 empty] | 46.0MW load
|  |  | BPDB. | [7 empty] | interrup.
| 12:51 | 13:35 | Aminbazar-Keraniganj 230kV Ckt-2 Tripped from Keranigonj 230/132/33kV end showing 86.2
Trip Relay Operated relays.
|  | 13:31 | Moghbazar-Rampura 132kV Ckt-2 is restored.
| 15:07 | 16:59 | Borhanuddin 230/33kV S/S Tr-Load HT Forced S/D Due to PDB Tx operation | [7 empty] | 60.0MW load
interrup.
| 15:10 | 17:05 | Borhanuddin 230/33kV S/S Tr-Load LT Forced S/D Due to PDB Tx operation | [7 empty] | 60.0MW load
interrup.
|  | 18:39 | Bheramara P/S-Ishurdi 132 kV Ckt-1 is restored.
| 18:40 | 19:39 | Hathazari-Kaptai 132kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing Main relays
Due to trip outside heavily rain
|  | 18:40 | Bheramara P/S-Ishurdi 132 kV Ckt-2 is restored.
| 20:57 | 21:24 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Tripped showing N/A relays Due to 132kV
CB Trip - PBS Auxiliary Transformer Fault
| 20:57 | 21:24 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Tripped showing P-632 (Dffifrential
Relay) relays Due to REF Trip (P-632) PBS Auxiliary Transformer Fault
| 20:57 | 22:59 | Joypurhat 132/33kV S/S Transformer T-3 (427 T) LT Tripped showing Relay- P122 relays Due | [7 empty] | 15.0MW load
|  |  | to 50/51 (Over corrent) PBS Auxiliary Transformer Fault | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation: 15016 MW.
| 21:18 | 21:38 | Cumilla(S) 132/33kV S/S TR-3 LT Tripped showing 1.RET650 2.REF615 relays Due to 33 KV | [7 empty] | 30.0MW load
|  |  | Nangolkot REB feeder fault. | [7 empty] | interrup.
| 21:25 | 00:32 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) LT Scheduled S/D
| 21:25 | 00:07 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT Scheduled S/D Due to 132 kV Circuit
Breaker closing Problem
| 02:11 |  | Sirajganj Unit-1 tripped.
| 02:11 |  | Sirajgonj 225MW CCPP Unit-1 Tripped with remarks:- GT
| 02:26 |  | Bogura 230/132kV S/S T-02 LT Tripped showing REL505C1 (No alarm) relays.
| 02:26 |  | Bogura 230/132kV S/S T-02 HT Tripped showing RET316 relays Due to Bukhholz/oil
temperature trip
| 02:42 | 03:41 | Sylhet 132/33kV S/S T2 LT Tripped showing LV O/C A B C Phase E/F General Trip relays Due
to IC-2 Burst
| 02:42 |  | Sylhet 132/33kV S/S T4 LT Tripped showing General TRip 20/51 relays Due to IC-2 CB Burst
| 02:42 | 03:41 | Sylhet 132/33kV S/S T2 HT Tripped showing LV O/c General TRip 87 relays Due to IC-2 CB | [7 empty] | 15.0MW load
|  |  | Burst | [7 empty] | interrup.
| 02:45 |  | Sylhet CCPP 225 MW tripped.
| 03:52 |  | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to work of 33kv bus
| 04:55 | 05:17 | Mirzapur 132/33kV S/S Transformer-01(E05) LT Tripped showing SIEMENS ( 7UT61) SIEMENS ( | [7 empty] | 35.0MW load
|  |  | 7SJ85) relays Due to 33 kv Square PBS feeder fault | [7 empty] | interrup.
| 06:00 |  | Min. Gen. 12346 MW
| 06:37 |  | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Bajitpur 132/33kV end. and from
Ashuganj 230/132/33kV end Due to Re-routing of 3 nos tower
| 06:45 |  | Sirajganj Unit-1 GT was sync.
| 06:45 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 07:05 |  | Natore 132/33kV S/S TR-2 (415 T) HT Scheduled S/D
| 07:05 |  | Natore 132/33kV S/S TR-1 (405 T) HT Scheduled S/D
| 07:05 |  | Natore 132/33kV S/S TR-2 (415 T) LT Scheduled S/D
| 07:05 |  | Natore 132/33kV S/S TR-1 (405 T) LT Scheduled S/D
| 07:40 |  | Khulna (S)-Satkhira 132kV Ckt-2 Scheduled S/D from Satkhira 132/33kV end Due to
Maintenance work for Khulna south grid and from Khulna(S) 230/132kVend.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 26-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 346 | 8629200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7564500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 280 | 7061585 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 110812 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 275 | 6870521 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 53 | 667440 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 2027520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 838759 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 477872 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16 | 384000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 17 | 380880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 34 | 542880 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 953455 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 2595168 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1417920 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 33 | 682560 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 143 | 2754720 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 147109 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 409680 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 250 | 6538591 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 142 | 1518000 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2320 | 52573172
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 24183 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 126765 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 635520 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 912660 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 184 | 4292040 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 213272 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 40 | 278003 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 581206 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 60 | 1800960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 15 | 337920 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26660 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 55200 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 191527 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 497280 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 38473 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28063634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 6 | 219840 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 12814545.46 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2224 | 51109688.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 188 | 5053000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 352 | 8232500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 330 | 7960000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 35 | 700488 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 51 | 903840 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 434909.09 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1235660 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 80 | 1206036 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 817152 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1775860 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 3777600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 42 | 916800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 592637 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 12 | 280750 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2601480 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 38 | 375480 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 110 | 2051520 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 478818 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1798.2 | 39394530.09
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 11450 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 177 | 3076800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 96 | 1695600 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 324590 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 256320 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 472680 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 302 | 5837440
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 39 | 905000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 150 | 3362809 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 441408 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 22 | 575040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 171 | 3537240 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7247000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 341 | 8944000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7675800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1368 | 32688297
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 928 | 14767272 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 142 | 2874816 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 204960 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 633600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1126 | 26210910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2213 | 44691558
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 307 | 6702533 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 213672 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 2772000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26965818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5214640 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 258 | 5629000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4449 | -
Barishal Area Total |  |  |  |  | 2236 | 2160 | 47502112.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 25 | 48701 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 57712 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 140 | 3410273 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 135 | 3331027 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8663054 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 75460 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 237680 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 326112 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 26640 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1442 | 32172008 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 303000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 326930 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2278 | 48978597
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 49 | 1134109 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3828000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 454588 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 26864.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 915866 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 76586 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 612720 | -
Rangpur Area Total |  |  |  |  | 950 | 353 | 7048733.76
Eastern Grid Total |  |  |  |  | 16771.895 | 8012.2 | 181603127.55
Western Grid Total |  |  |  |  | 10338.16 | 7004 | 148221000.94
National Grid Total |  |  |  |  | 27110.055 | 15016.2 | 329824128.49
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 26-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9799.23 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4591.8 | MW
i) Dhaka area |  |  | 5522.45 |  | MW | i) Khulna area |  |  |  | 1721 | MW
ii) Chattogram area |  |  | 1267 |  | MW | ii) Barishal area |  |  |  | 502 | MW
iii) Cumilla area |  |  | 1189.78 |  | MW | iii) Rajshahi area |  |  |  | 1450.8 | MW
iv) Mymensingh area |  |  | 1219 |  | MW | iv) Rangpur area |  |  |  | 918 | MW
v) Sylhet area |  |  | 601 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14391.03 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | 67 | Ishurdi | 79 | 19:30 | 133 | Patuakhali | 81.2 | 23:00
2 | AKSML | 128 | 04:00 | 68 | Jaldhaka | 76 | 19:30 | 134 | Payra | 34 | 22:00
3 | Aftabnagar | 42 | 13:00 | 69 | Jamalpur | 134 | 20:00 | 135 | Postogola | 61 | 13:00
4 | Agargaon | 139 | 13:00 | 70 | Jashore | 138 | 20:00 | 136 | Purbachal | 22 | 00:00
5 | Agrabad | 94 | 12:00 | 71 | Jhenaidah | 122 | 20:00 | 137 | Purbasadipur | 127 | 19:30
6 | Amnura | 34 | 20:00 | 72 | Joydebpur | 156 | 15:00 | 138 | Rahanpur | 26 | 23:00
7 | Ashuganj | 101 | 00:00 | 73 | Joypurhat | 56 | 20:00 | 139 | Rahim | 52 | 18:00
8 | BSRM | 193 | 19:00 | 74 | Juldah | 16 | 00:00 | 140 | Rajbari | 80 | 22:00
9 | Bagerhat | 89 | 22:00 | 75 | KSRM | 27 | 06:00 | 141 | Rajendrapur | 148 | 19:30
10 | Bajitpur | 53 | 00:00 | 76 | Kabirpur | 283 | 12:00 | 142 | Rajshahi | 128 | 21:00
11 | Bakulia | 98 | 21:00 | 77 | Kachua | 102 | 21:00 | 143 | Rajshahi-230 | 73 | 01:00
12 | Banani | 42.8 | 13:00 | 78 | Kallyanpur | 120 | 00:00 | 144 | Ramganj | 114 | 21:00
13 | Bangabhaban | 18 | 10:00 | 79 | Kalurghat | 44 | 15:00 | 145 | Rampur | 41 | 00:00
14 | Barapukuria | 68 | 19:30 | 80 | Kamrangirchar | 70.1 | 18:00 | 146 | Rangamati | 16 | 13:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 153 | 20:00
16 | Barishal | 117 | 19:30 | 82 | Kasba | 37 | 21:00 | 148 | Ruppur | 7.2 | 16:00
17 | Barishal-230 | 110 | 21:00 | 83 | Kazla | 108 | 13:00 | 149 | SSM | 4 | 03:00
18 | Baroaulia | 71 | 14:00 | 84 | Keranigonj | 98 | 13:00 | 150 | Saidpur | 110 | 19:30
19 | Baroirhat | 63 | 00:00 | 85 | Khagrachori | 28 | 13:00 | 151 | Satkhira | 139 | 19:00
20 | Bashundhara | 209 | 13:00 | 86 | Khulna | 71 | 13:00 | 152 | Satmasjid | 113 | 13:00
21 | BashundharaCement | 7 | 01:00 | 87 | Khulshi | 182 | 16:00 | 153 | Savar | 240 | 12:00
22 | Beanibazar | 82 | 21:00 | 88 | Kishoreganj | 143 | 23:00 | 154 | SevenRings | 19.54 | 13:00
23 | Benapole | 64 | 21:00 | 89 | Kodda | 308 | 22:00 | 155 | ShahCement | 35 | 06:00
24 | Bhaluka | 159 | 19:00 | 90 | Kulaura | 57 | 20:00 | 156 | Shahjadpur | 91 | 21:00
25 | Bhandaria | 57 | 22:00 | 91 | Kurigram | 62 | 19:30 | 157 | Shahjibazar | 110 | 18:30
26 | Bhangura | 36 | 20:00 | 92 | Kushtia | 160 | 20:00 | 158 | Shahmirpur | 55 | 01:00
27 | Bheramara(GK) | 60 | 00:00 | 93 | Lalbag | 58 | 18:00 | 159 | Shariatpur | 85 | 21:00
28 | Bhulta | 238 | 12:00 | 94 | Lalmonirhat | 63 | 19:30 | 160 | Sherpur | 156 | 19:00
29 | Bog-Sherpur | 66 | 19:30 | 95 | MI_Cement | 14.1 | 13:00 | 161 | Shikalbaha | 28 | 01:00
30 | Bogura | 172 | 21:00 | 96 | Madanganj | 48 | 16:00 | 162 | Shitalakhya | 91.4 | 13:00
31 | Borhanuddin | 93 | 21:00 | 97 | Madaripur | 105 | 00:00 | 163 | Sholosohor | 48 | 15:00
32 | Brahmanbaria | 112 | 13:00 | 98 | Madartek | 113.19 | 00:00 | 164 | Shyampur | 164 | 00:00
33 | Cantonment | 160 | 13:00 | 99 | Madunaghat | 52 | 15:00 | 165 | Siddhirganj | 127 | 13:00
34 | Chandina | 22.4 | 00:00 | 100 | Magura | 62 | 19:30 | 166 | Sirajganj | 116 | 20:00
35 | Chandpur | 74 | 21:00 | 101 | Mahasthangarh | 84 | 19:30 | 167 | Sonargaon | 127 | 14:00
36 | Chandraghona | 33 | 00:00 | 102 | Manikganj | 141 | 21:00 | 168 | Sreemongol | 79 | 23:00
37 | Chapai | 66 | 22:00 | 103 | Maniknagar | 92 | 13:00 | 169 | Sreepur | 110 | 16:00
38 | Charsaidpur | 46 | 17:00 | 104 | Matarbari | 48 | 01:00 | 170 | Srinagar | 45.76 | 00:00
39 | Chauddagram | 76 | 19:00 | 105 | Matuail | 70 | 12:00 | 171 | Sunamganj | 60 | 19:00
40 | Chhatak | 36 | 19:30 | 106 | Millgate | 108 | 12:00 | 172 | Sylhet | 51 | 23:00
41 | Chowmuhani | 223 | 19:00 | 107 | Mirpur | 129 | 15:00 | 173 | Sylhet-132 | 130 | 19:00
42 | Chuadanga | 108 | 19:00 | 108 | Mirsorai | 12 | 15:00 | 174 | TK | 32.8 | 04:00
43 | Coxsbazar | 139 | 13:00 | 109 | Mirzapur | 48 | 21:00 | 175 | Tangail | 186 | 19:30
44 | Cumilla(N) | 150 | 21:00 | 110 | Mithapukur | 67 | 19:30 | 176 | Thakurgaon | 99 | 19:30
45 | Cumilla(S) | 190 | 15:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 140 | 10:00
46 | Daudkandi | 145 | 02:00 | 112 | Mogbazar | 165.4 | 13:00 | 178 | Ullahpara | 40 | 19:30
47 | Dhaka | 72 | 12:00 | 113 | Mongla | 34 | 19:00 | 179 | Ullon | 42 | 00:00
48 | Dhamrai | 140 | 08:00 | 114 | Motijheel | 44 | 13:00 | 180 | Uttara | 91 | 15:00
49 | Dhanmondi | 168.7 | 13:00 | 115 | Muktagacha | 36 | 20:00 | 181 | UttaraNew | 65 | 00:00
50 | Dohazari | 96 | 00:00 | 116 | Munshiganj | 113 | 00:00 | 182 | Zigatola | 78 | 15:00
51 | Faridpur | 160 | 00:00 | 117 | Muradnagar | 30 | 19:30
52 | Fatullah | 109 | 12:00 | 118 | Mymensingh | 206 | 19:30
53 | Fenchuganj | 46 | 22:00 | 119 | Naogaon | 128 | 21:00
54 | Feni | 131 | 20:00 | 120 | Narail | 59 | 21:00
55 | GPH | 94 | 11:00 | 121 | Narinda | 90 | 13:00
56 | Ghatail | 78 | 23:00 | 122 | Narshingdi | 165 | 20:00
57 | Ghorashal | 17 | 14:00 | 123 | Natore | 148 | 00:00
58 | Ghorashal-230 | 103 | 01:00 | 124 | Nawabganj | 56.4 | 22:00
59 | Goalpara | 36 | 00:00 | 125 | Netrakona | 121 | 18:30
60 | Gollamari | 104 | 00:00 | 126 | New | 94.2 | 15:00
61 | Gopalganj | 102.2 | 19:30 | 127 | Niamatpur | 63 | 21:00
62 | Gulshan | 138 | 13:00 | 128 | Noapara | 49 | 19:30
63 | Halishahar | 82 | 09:00 | 129 | PHP | 5 | 02:00
64 | HaripurSBU | 180 | 12:00 | 130 | Pabna | 118 | 00:00
65 | Hasnabad | 79 | 13:00 | 131 | Palashbari | 102 | 21:00
66 | Hathazari | 85 | 00:00 | 132 | Panchagarh | 58 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 26-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15009.76 | 182 |  | 15199.95
1:00 | 14458.86 | 327 |  | 14800.86
2:00 | 14005.25 | 282 |  | 14300.25
3:00 | 13747.81 | 242 |  | 14000.81
4:00 | 13415.32 | 224 |  | 13649.32
5:00 | 13202.99 | 208 |  | 13419.99
6:00 | 12630.77 | 183 |  | 12821.77
7:00 | 12635.23 | 207 |  | 12851.23
8:00 | 12581.64 | 164 |  | 12752.64
9:00 | 12797.03 | 150 |  | 12954.03
10:00 | 13072.6 | 124 |  | 13202.6
11:00 | 13601.01 | 98 |  | 13703.01
12:00 | 13975.44 | 102 |  | 14082.44
13:00 | 14150.05 | 108 |  | 14263.05
14:00 | 14033.32 | 162 |  | 14202.32
15:00 | 13784.24 | 180 |  | 13972.24
16:00 | 13500.05 | 175 |  | 13682.93
17:00 | 13410.82 | 98 |  | 13512.82
18:00 | 13055.41 | 46 |  | 13103.48
19:00 | 14615.52 | 81 |  | 14700.52
19:30 | 14967.15 | 89 |  | 15060.16
20:00 | 14956.94 | 90 |  | 15050.94
21:00 | 15016.2 | 109 |  | 15130.2
22:00 | 14533 | 131 |  | 14670
23:00 | 14397.5 | 146 |  | 14550.5
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 26-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7910.2 | 7099.56 | 15009.76 | DAILY GENERATION CURVE
00:30 | 7731.2 | 7003.11 | 14734.31
01:00 | 7552.2 | 6906.66 | 14458.86 | 26-05-2025
01:30 | 7452.2 | 6779.855 | 14232.055
02:00 | 7352.2 | 6653.05 | 14005.25
02:30 | 7341.95 | 6534.58 | 13876.53
03:00 | 7331.7 | 6416.11 | 13747.81
03:30 | 7328.95 | 6252.615 | 13581.565
04:00 | 7326.2 | 6089.12 | 13415.32
04:30 | 7247.2 | 6061.955 | 13309.155
05:00 | 7168.2 | 6034.79 | 13202.99
05:30 | 7141.88 | 5775 | 12916.88
06:00 | 7115.56 | 5515.21 | 12630.77
06:30 | 7061.34 | 5571.66 | 12633
07:00 | 7007.12 | 5628.11 | 12635.23
07:30 | 6965.47 | 5642.965 | 12608.435
08:00 | 6923.82 | 5657.82 | 12581.64
08:30 | 7001.895 | 5687.44 | 12689.335
09:00 | 7079.97 | 5717.06 | 12797.03
09:30 | 7098.145 | 5836.67 | 12934.815
10:00 | 7116.32 | 5956.28 | 13072.6
10:30 | 7308.425 | 6028.38 | 13336.805
11:00 | 7500.53 | 6100.48 | 13601.01
11:30 | 7645.105 | 6143.12 | 13788.225
12:00 | 7789.68 | 6185.76 | 13975.44
12:30 | 7877.76 | 6184.985 | 14062.745
13:00 | 7965.84 | 6184.21 | 14150.05
13:30 | 7945.63 | 6146.055 | 14091.685
14:00 | 7925.42 | 6107.9 | 14033.32
14:30 | 7755.69 | 6153.09 | 13908.78
15:00 | 7585.96 | 6198.28 | 13784.24
15:30 | 7493.68 | 6148.465 | 13642.145
16:00 | 7401.4 | 6098.65 | 13500.05
16:30 | 7391.095 | 6064.34 | 13455.435
17:00 | 7380.79 | 6030.03 | 13410.82
17:30 | 7377.19 | 5855.925 | 13233.115
18:00 | 7373.59 | 5681.82 | 13055.41
18:30 | 7775.795 | 6059.67 | 13835.465
19:00 | 8178 | 6437.52 | 14615.52
19:30 | 8093 | 6874.15 | 14967.15
20:00 | 8056.2 | 6900.74 | 14956.94
20:30 | 8034.2 | 6952.37 | 14986.57 |  | Executive Engineer
21:00 | 8012.2 | 7004 | 15016.2 |  | Network Operation Division
21:30 | 7887.1 | 6887.5 | 14774.6
22:00 | 7762 | 6771 | 14533
22:30 | 7690.25 | 6775 | 14465.25
23:00 | 7618.5 | 6779 | 14397.5

## En-Curve
QF-LDC-12
Date | 26-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3664 | 1703 | 920 | 0 | 48 | 1457.36 | 38 | 5091.2 | 0 | 407 | 1681.2 | 0 | 0 | 0 | 182 | DAILY ENERGY CURVE
00:30 | 3623.5 | 1685 | 919.5 | 0 | 46 | 1457.41 | 37.5 | 5086.2 | 0 | 321.5 | 1542.2 | 0 | 0 | 15.5 | 254.5 | 26-05-2025
01:00 | 3583 | 1667 | 919 | 0 | 44 | 1457.46 | 37 | 5081.2 | 0 | 236 | 1403.2 | 0 | 0 | 31 | 327
01:30 | 3573.5 | 1672.5 | 923 | 0 | 43 | 1408.755 | 36.5 | 4980.6 | 0 | 222.5 | 1354.7 | 0 | 0 | 17 | 304.5 | Energy Generated | 329.8241 |  | MKWHr
02:00 | 3564 | 1678 | 927 | 0 | 42 | 1360.05 | 36 | 4880 | 0 | 209 | 1306.2 | 0 | 0 | 3 | 282 | Energy not Served | 3.819 |  | MKWHr
02:30 | 3551.5 | 1675.75 | 927 | 0 | 42 | 1340.08 | 36 | 4845.5 | 0 | 202 | 1255.2 | 0 | 0 | 1.5 | 262 | Total Energy Requirement | 333.6431 |  | MKWHr
03:00 | 3539 | 1673.5 | 927 | 0 | 42 | 1320.11 | 36 | 4811 | 0 | 195 | 1204.2 | 0 | 0 | 0 | 242
03:30 | 3533.5 | 1668.75 | 927 | 0 | 41 | 1267.115 | 37 | 4725.5 | 0 | 195 | 1186.7 | 0 | 0 | 0 | 233
04:00 | 3528 | 1664 | 927 | 0 | 40 | 1214.12 | 38 | 4640 | 0 | 195 | 1169.2 | 0 | 0 | 0 | 224
04:30 | 3495 | 1643.5 | 927 | 0 | 40 | 1212.955 | 39 | 4602 | 0 | 195 | 1154.7 | 0 | 0 | 0 | 216
05:00 | 3462 | 1623 | 927 | 0 | 40 | 1211.79 | 40 | 4564 | 0 | 195 | 1140.2 | 0 | 0 | 0 | 208
05:30 | 3535 | 1664 | 690 | 0 | 39 | 1184.335 | 40 | 4457.5 | 10.445 | 195 | 1101.6 | 0 | 0 | 0 | 195.5
06:00 | 3608 | 1705 | 453 | 0 | 38 | 1156.88 | 40 | 4351 | 20.89 | 195 | 1063 | 0 | 0 | 0 | 183
06:30 | 3593 | 1713.5 | 454.5 | 0 | 37 | 1158.285 | 40 | 4388 | 67.715 | 171.5 | 1009.5 | 0 | 0 | 0 | 195
07:00 | 3578 | 1722 | 456 | 0 | 36 | 1159.69 | 40 | 4425 | 114.54 | 148 | 956 | 0 | 0 | 0 | 207
07:30 | 3569 | 1711.5 | 456.5 | 0 | 35 | 1161.84 | 40 | 4423 | 155.095 | 148 | 908.5 | 0 | 0 | 0 | 185.5
08:00 | 3560 | 1701 | 457 | 0 | 34 | 1163.99 | 40 | 4421 | 195.65 | 148 | 861 | 0 | 0 | 0 | 164
08:30 | 3534 | 1704.5 | 456.5 | 0 | 35 | 1161.925 | 40 | 4443.5 | 228.91 | 224 | 861 | 0 | 0 | 0 | 157
09:00 | 3508 | 1708 | 456 | 0 | 36 | 1159.86 | 40 | 4466 | 262.17 | 300 | 861 | 0 | 0 | 0 | 150
09:30 | 3594 | 1718.5 | 456 | 0 | 35 | 1212.6 | 40 | 4490 | 284.215 | 277 | 827.5 | 0 | 0 | 0 | 137
10:00 | 3680 | 1729 | 456 | 0 | 34 | 1265.34 | 40 | 4514 | 306.26 | 254 | 794 | 0 | 0 | 0 | 124
10:30 | 3704.5 | 1745 | 456 | 0 | 36 | 1299.58 | 40 | 4604 | 349.225 | 254 | 847 | 0 | 0 | 1.5 | 111
11:00 | 3729 | 1761 | 456 | 0 | 38 | 1333.82 | 40 | 4694 | 392.19 | 254 | 900 | 0 | 0 | 3 | 98
11:30 | 3701.5 | 1744.5 | 456.5 | 0 | 38 | 1364.945 | 39 | 4701.5 | 416.28 | 265.5 | 1055.5 | 0 | 0 | 5 | 100
12:00 | 3674 | 1728 | 457 | 0 | 38 | 1396.07 | 38 | 4709 | 440.37 | 277 | 1211 | 0 | 0 | 7 | 102
12:30 | 3580 | 1718.5 | 456.5 | 0 | 41 | 1418.705 | 37 | 4736.5 | 428.54 | 294.5 | 1344 | 0 | 0 | 7.5 | 105
13:00 | 3486 | 1709 | 456 | 0 | 44 | 1441.34 | 36 | 4764 | 416.71 | 312 | 1477 | 0 | 0 | 8 | 108
13:30 | 3519 | 1677.5 | 456.5 | 0 | 44 | 1411.35 | 35.5 | 4683 | 436.835 | 311.5 | 1509 | 0 | 0 | 7.5 | 135
14:00 | 3552 | 1646 | 457 | 0 | 44 | 1381.36 | 35 | 4602 | 456.96 | 311 | 1541 | 0 | 0 | 7 | 162
14:30 | 3513 | 1652 | 692.5 | 0 | 44 | 1369.365 | 35 | 4501.5 | 348.915 | 287 | 1459.5 | 0 | 0 | 6 | 171
15:00 | 3474 | 1658 | 928 | 0 | 44 | 1357.37 | 35 | 4401 | 240.87 | 263 | 1378 | 0 | 0 | 5 | 180
15:30 | 3450.5 | 1650.5 | 928 | 0 | 42 | 1362.065 | 35.5 | 4329 | 212.58 | 264 | 1347.5 | 0 | 0 | 20.5 | 177.5
16:00 | 3427 | 1643 | 928 | 0 | 40 | 1366.76 | 36 | 4257 | 184.29 | 265 | 1317 | 0 | 0 | 36 | 175
16:30 | 3401 | 1643.5 | 927.5 | 0 | 40 | 1369.245 | 37 | 4243.5 | 154.69 | 280.5 | 1316.5 | 0 | 0 | 42 | 136.5
17:00 | 3375 | 1644 | 927 | 0 | 40 | 1371.73 | 38 | 4230 | 125.09 | 296 | 1316 | 0 | 0 | 48 | 98
17:30 | 3336.5 | 1651 | 927.5 | 0 | 38 | 1343.17 | 38.5 | 4077.5 | 76.445 | 351 | 1345 | 0 | 0 | 48.5 | 72
18:00 | 3298 | 1658 | 928 | 0 | 36 | 1314.61 | 39 | 3925 | 27.8 | 406 | 1374 | 0 | 0 | 49 | 46
18:30 | 3415.5 | 1684 | 904.5 | 0 | 41 | 1376.565 | 39.5 | 4233 | 13.9 | 526 | 1572.5 | 0 | 0 | 29 | 63.5
19:00 | 3533 | 1710 | 881 | 0 | 46 | 1438.52 | 40 | 4541 | 0 | 646 | 1771 | 0 | 0 | 9 | 81
19:30 | 3420 | 1695 | 881 | 0 | 42 | 1444.15 | 40 | 4948 | 0 | 666 | 1828 | 0 | 0 | 3 | 89
20:00 | 3560 | 1705 | 881 | 0 | 40 | 1449.74 | 40 | 4950 | 0 | 666 | 1651.2 | 0 | 0 | 14 | 90
20:30 | 3596 | 1710.5 | 904.5 | 0 | 41 | 1445.87 | 40 | 4944 | 0 | 655 | 1639.7 | 0 | 0 | 10 | 99.5
21:00 | 3632 | 1716 | 928 | 0 | 42 | 1442 | 40 | 4938 | 0 | 644 | 1628.2 | 0 | 0 | 6 | 109
21:30 | 3638.5 | 1748 | 880 | 0 | 37 | 1449.5 | 40 | 4937.5 | 0 | 555 | 1482.1 | 0 | 0 | 7 | 120
22:00 | 3645 | 1780 | 832 | 0 | 32 | 1457 | 40 | 4937 | 0 | 466 | 1336 | 0 | 0 | 8 | 131
22:30 | 3595 | 1801.75 | 856.5 | 0 | 33 | 1453 | 40 | 4951.5 | 0 | 441 | 1288 | 0 | 0 | 5.5 | 138.5
23:00 | 3545 | 1823.5 | 881 | 0 | 34 | 1449 | 40 | 4966 | 0 | 416 | 1240 | 0 | 0 | 3 | 146
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 26-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 378 | 05:00 | 365 | 00:00 | Payra | 413 | 16:00 | 406 | 00:00
Ashuganj | 389 | 18:00 | 361 | 11:24 | Rahanpur | 403 | 04:00 | 390 | 21:00
Bhulta | 383 | 18:00 | 357 | 11:00 | Rampal | 400 | 17:00 | 383 | 00:00
Bibiana | 390 | 18:30 | 382 | 11:00
BIPTC | 408 | 06:00 | 394 | 01:00
Bogura | 393 | 06:00 | 375 | 22:00
Gopalganj | 392 | 18:00 | 377 | 00:00
Kaliakoir | 371 | 18:00 | 355 | 11:00
Madunaghat | 391 | 06:00 | 381 | 12:00
Meghnaghat | 381 | 06:00 | 368 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 221 | 05:00 | 210 | 11:00 | Keranigonj | 218 | 05:00 | 208 | 11:00
AKSML | 235 | 09:00 | 215 | 11:00 | Khulna(S) | 228 | 18:00 | 215 | 00:00
Aminbazar | 220 | 05:00 | 212 | 00:00 | Madunaghat | 232 | 19:30 | 221 | 11:00
Ashuganj | 226 | 18:00 | 213 | 11:00 | Madunaghat-400 | 231 | 06:00 | 222 | 12:00
Ashuganj-400 | 226 | 18:00 | 213 | 11:00 | Maniknagar | 216 | 03:00 | 207 | 12:00
Baghabari | 231 | 04:00 | 221 | 20:00 | Meghnaghat | 224 | 18:30 | 218 | 11:00
Barapukuria | 221 | 05:00 | 213 | 19:30 | Meghnaghat-400 | 220 | 05:00 | 213 | 11:00
Barapukuria-230 | 221 | 05:00 | 213 | 19:30 | Mirsorai | 224 | 07:00 | 211 | 12:00
Barishal | 234 | 06:00 | 226 | 00:00 | Rajshahi | 234 | 05:00 | 221 | 21:00
Bheramara | 234 | 05:00 | 222 | 20:00 | Rampal | 228 | 17:00 | 215 | 00:00
Bhulta | 222 | 04:00 | 205 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 222 | 05:00 | 216 | 11:00 | Rampura | 223 | 05:00 | 203 | 11:00
BIPTC | 237 | 05:00 | 222 | 19:30 | Shikalbaha | 230 | 17:00 | 220 | 11:00
Bogura | 227 | 05:00 | 216 | 22:00 | Shyampur | 218 | 05:00 | 209 | 11:00
Bogura-400 | 227 | 05:00 | 217 | 22:00 | Siddhirganj | 219 | 03:00 | 21 | 00:00
Borhanuddin | 240 | 17:00 | 232 | 00:00 | Sirajgonj | 234 | 04:00 | 229 | 20:00
BSRM | 225 | 06:00 | 212 | 11:00 | Sreepur | 224 | 18:00 | 213 | 11:00
Cumilla(N) | 218 | 06:00 | 210 | 11:00 | Tongi | 217 | 17:00 | 202 | 10:00
Faridpur | 230 | 18:00 | 21 | 00:00
Fenchuganj | 223 | 06:00 | 218 | 01:00
Ghorashal | 220 | 00:00 | 210 | 12:00
Ghorashal-230 | 222 | 05:00 | 205 | 11:00
Gopalganj | 232 | 06:00 | 222 | 00:00
GPH | 228 | 18:00 | 215 | 11:00
Haripur | 218 | 05:00 | 210 | 10:00
Hasnabad | 218 | 05:00 | 210 | 11:00
Hathazari | 230 | 04:00 | 219 | 11:00
Ishurdi | 235 | 05:00 | 223 | 21:00
Jhenaidah | 229 | 05:00 | 216 | 00:00
Kaliakoir | 227 | 18:00 | 215 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 136 | 03:00 | 122 | 12:00 | Madartek | 137 | 05:00 | 122 | 12:00
Agargaon | 133 | 05:00 | 124 | 12:00 | Madunaghat | 132 | 05:00 | 124 | 11:00
Agrabad | 132 | 18:30 | 124 | 10:00 | Magura | 134 | 18:00 | 123 | 00:00
AKS | 131 | 19:30 | 124 | 11:00 | Mahasthangarh | 133 | 05:00 | 124 | 19:30
Aminbazar | 129 | 05:00 | 123 | 10:00 | Manikganj | 130 | 07:00 | 118 | 11:00
Amnura | 136 | 18:30 | 125 | 00:00 | Maniknagar | 130 | 05:00 | 123 | 11:00
Ashuganj | 135 | 18:00 | 128 | 12:00 | Matarbari | 129 | 18:00 | 109 | 00:00
Bagerhat | 130 | 09:00 | 116 | 23:00 | Matuail | 126 | 02:00 | 121 | 12:00
Bajitpur | 129 | 18:00 | 120 | 09:00 | Millgate | 131 | 18:30 | 120 | 11:00
Bakulia | 133 | 18:00 | 125 | 11:00 | Mirpur | 128 | 04:00 | 122 | 00:00
Banani | 138 | 05:00 | 123 | 11:00 | Mirzapur | 132 | 13:00 | 126 | 11:00
Bangabhaban | 130 | 04:00 | 123 | 11:00 | Mithapukur | 132 | 06:00 | 119 | 19:30
Barapukuria | 134 | 05:00 | 124 | 19:30 | MI_Cement | 127 | 04:00 | 121.7 | 11:00
Barguna | 135 | 09:00 | 129 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 18:00 | 122 | 00:00 | Mogbazar | 137 | 04:00 | 124 | 12:00
Barishal-230 | 130 | 07:00 | 123 | 00:00 | Mongla | 131 | 08:00 | 119 | 00:00
Baroaulia | 133 | 19:00 | 126 | 11:00 | Motijheel | 130 | 04:00 | 123 | 11:00
Baroirhat | 129 | 21:00 | 116 | 12:00 | Muktagacha | 135 | 07:00 | 125 | 21:00
Bashundhara | 138 | 05:00 | 120 | 11:00 | Munshiganj | 126 | 07:00 | 121 | 00:00
BashundharaCement | 127 | 08:00 | 120 | 11:00 | Muradnagar | 124 | 18:00 | 117 | 00:00
Beanibazar | 127 | 06:00 | 121 | 19:00 | Mymensingh | 135 | 08:00 | 110 | 19:30
Benapole | 131 | 18:30 | 117 | 00:00 | Naogaon | 131 | 05:00 | 122 | 22:00
Bhaluka | 132 | 18:00 | 119 | 12:00 | Narail | 133 | 05:00 | 122 | 00:00
Bhandaria | 125 | 09:00 | 114 | 00:00 | Narinda | 130 | 05:00 | 123 | 11:00
Bhangura | 133 | 05:00 | 125 | 20:00 | Narshingdi | 132 | 18:00 | 109 | 10:00
Bheramara | 136 | 05:00 | 128 | 00:00 | Natore | 133 | 05:00 | 126 | 21:00
Bheramara(GK) | 135 | 06:00 | 127 | 00:00 | Nawabganj | 130 | 04:00 | 123 | 00:00
Bhulta | 121 | 06:00 | 115 | 10:00 | Netrakona | 124 | 18:00 | 108 | 20:00
Bog-Sherpur | 133 | 05:00 | 125 | 20:00 | New | 132 | 18:00 | 121 | 11:00
Bogura | 135 | 04:00 | 128 | 20:00 | Niamatpur | 134 | 08:00 | 128 | 19:30
Bogura-230 | 135 | 05:00 | 127 | 22:00 | Noapara | 133 | 18:00 | 121 | 07:00
Brahmanbaria | 122 | 18:00 | 114 | 13:00 | Pabna | 133 | 05:00 | 126 | 19:30
Cantonment | 132 | 04:00 | 124 | 11:00 | Palashbari | 130 | 04:00 | 118 | 19:30
Chandina | 127 | 22:00 | 118 | 11:00 | Panchagarh | 136 | 19:00 | 121 | 07:00
Chandpur | 131 | 21:00 | 119 | 11:00 | Patuakhali | 134 | 07:00 | 130 | 00:00
Chandraghona | 132 | 19:30 | 124 | 11:00 | Payra | 135 | 08:00 | 132 | 00:00
Chapai | 132 | 05:00 | 125 | 00:00 | PHP | 129 | 21:00 | 115 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 127 | 05:00 | 122 | 11:00 | Postogola | 130 | 05:00 | 124 | 12:00
Chauddagram | 128 | 21:00 | 115 | 11:00 | Purbachal | 138 | 04:00 | 122 | 11:00
Chhatak | 126 | 04:00 | 119 | 19:30 | Purbasadipur | 132 | 18:30 | 123 | 03:00
Chowmuhani | 125 | 21:00 | 110 | 11:00 | Rahanpur | 135 | 09:00 | 130 | 00:00
Chuadanga | 132 | 05:00 | 120 | 19:30 | Rahanpur-400 | 135 | 09:00 | 130 | 00:00
Coxsbazar | 127 | 18:00 | 109 | 23:00 | Rahim | 126 | 06:00 | 123 | 13:00
Cumilla(N) | 126 | 18:00 | 120 | 00:00 | Rajbari | 133 | 18:00 | 125 | 00:00
Cumilla(S) | 132 | 00:00 | 116 | 11:00 | Rajendrapur | 131 | 18:00 | 116 | 12:00
Daudkandi | 123 | 16:00 | 115 | 11:00 | Rajshahi | 134 | 05:00 | 127 | 21:00
Dhaka | 137 | 03:00 | 124 | 11:00 | Rajshahi-230 | 135 | 05:00 | 120 | 00:00
Dhamrai | 132 | 18:00 | 125 | 10:00 | Ramganj | 126 | 21:00 | 112 | 11:00
Dhanmondi | 136 | 18:00 | 122.5 | 11:00 | Rampur | 132 | 06:00 | 124 | 12:00
Dohazari | 132 | 18:00 | 121 | 00:00 | Rampura | 138 | 05:00 | 123 | 11:00
Faridpur | 134 | 07:00 | 126 | 00:00 | Rangamati | 131 | 06:00 | 123 | 11:00
Fatullah | 128 | 06:00 | 122 | 11:00 | Rangpur | 127 | 09:00 | 116 | 19:30
Fenchuganj | 132 | 00:00 | 129 | 01:00 | Ruppur | 136 | 05:00 | 130 | 19:30
Feni | 128 | 21:00 | 114 | 12:00 | Saidpur | 130 | 09:00 | 123 | 19:30
Ghatail | 134 | 13:00 | 122 | 20:00 | Satkhira | 131 | 18:00 | 118 | 20:00
Ghorashal | 133 | 17:00 | 124 | 12:00 | Satmasjid | 132 | 05:00 | 124 | 11:00
Goalpara | 136 | 18:00 | 124 | 00:00 | Savar | 129 | 17:00 | 121 | 09:00
Gollamari | 136 | 18:00 | 125 | 00:00 | SevenRings | 133 | 18:00 | 122 | 11:00
Gopalganj | 133 | 16:00 | 124 | 00:00 | ShahCement | 127 | 05:00 | 122 | 11:00
Gopalganj-400 | 135 | 18:00 | 128 | 00:00 | Shahjadpur | 136 | 04:00 | 130 | 19:00
Gulshan | 135 | 02:00 | 123 | 11:00 | Shahjibazar | 123 | 23:00 | 117 | 12:00
Halishahar | 133 | 05:00 | 124 | 11:00 | Shahmirpur | 134 | 19:30 | 126 | 11:00
Haripur | 127 | 05:00 | 122 | 10:00 | Shariatpur | 133 | 18:00 | 124 | 00:00
HaripurSBU | 127 | 04:00 | 122 | 11:00 | Sherpur | 139 | 09:00 | 127 | 20:00
Hasnabad | 130 | 03:00 | 124 | 12:00 | Shikalbaha | 123 | 18:00 | 117 | 23:00
Hathazari | 134 | 04:00 | 128 | 00:00 | Shikalbaha-230 | 134 | 17:00 | 126 | 11:00
Ishurdi | 138 | 05:00 | 130 | 19:30 | Shitalakhya | 127 | 04:00 | 121.7 | 11:00
Jaldhaka | 127 | 04:00 | 122 | 19:30 | Sholosohor | 132 | 18:00 | 123 | 11:00
Jamalpur | 141 | 00:00 | 130 | 01:00 | Shyampur | 127 | 08:00 | 122 | 00:00
Jashore | 133 | 18:00 | 119 | 00:00 | Shyampur-230 | 127 | 05:00 | 122 | 00:00
Jhenaidah | 134 | 05:00 | 38 | 08:00 | Siddhirganj | 127 | 04:00 | 122 | 11:00
Jhenaidah-230 | 135 | 05:00 | 125 | 00:00 | Sirajganj | 130 | 05:00 | 123 | 19:30
Joydebpur | 133 | 18:00 | 116 | 10:00 | Sonargaon | 126 | 18:00 | 119 | 11:00
Joypurhat | 130 | 09:00 | 121 | 20:00 | Sreemongol | 124 | 07:00 | 121 | 00:00
Juldah | 134 | 18:00 | 124 | 11:00 | Sreepur | 132 | 18:00 | 122 | 12:00
Kabirpur | 135 | 18:30 | 117 | 11:00 | Srinagar | 130 | 04:00 | 123 | 00:00
Kachua | 129 | 22:00 | 116 | 12:00 | SSM | 138 | 19:00 | 130 | 11:00
Kaliakoir | 137 | 18:00 | 127 | 11:00 | Sunamganj | 124 | 06:00 | 117 | 19:30
Kallyanpur | 130 | 04:00 | 122 | 00:00 | Sylhet | 128 | 07:00 | 123 | 19:00
Kalurghat | 131 | 05:00 | 124 | 11:00 | Sylhet-132 | 128 | 04:00 | 124 | 19:30
Kamrangirchar | 130 | 07:00 | 122 | 12:00 | Tangail | 132 | 13:00 | 122 | 19:30
Kaptai | 134 | 5:00 | 128 | 11:00 | Thakurgaon | 135 | 19:00 | 119 | 07:00
Kasba | 124 | 18:00 | 117 | 11:00 | TK | 131 | 18:00 | 124 | 11:00
Kazla | 130 | 05:00 | 123 | 12:00 | Tongi | 133 | 17:00 | 122 | 10:00
Keranigonj | 131 | 06:00 | 123 | 11:00 | Ullahpara | 133 | 05:00 | 125 | 20:00
Khagrachori | 132 | 19:30 | 122 | 11:00 | Ullon | 136 | 04:00 | 124 | 11:00
Khulna | 134 | 18:00 | 122 | 00:00 | Uttara | 129 | 06:00 | 121 | 00:00
Khulna(S) | 136 | 18:00 | 126 | 00:00 | UttaraNew | 129 | 18:00 | 122 | 00:00
Khulshi | 132 | 19:30 | 70 | 20:00 | Zigatola | 130 | 08:00 | 123 | 12:00
Kishoreganj | 129 | 18:00 | 117 | 19:30
Kodda | 134 | 18:00 | 116 | 12:00
KSRM | 133 | 18:00 | 124 | 11:00
Kulaura | 130 | 06:00 | 126 | 20:00
Kurigram | 130 | 05:00 | 115 | 19:30
Kushtia | 132 | 05:00 | 122 | 00:00
Lalbag | 130 | 05:00 | 122 | 12:00
Lalmonirhat | 129 | 05:00 | 115 | 19:30
Madanganj | 127 | 08:00 | 120 | 11:00
Madaripur | 134 | 18:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division