## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 28-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-05-2025 | during | 28-05-2025 | during | 28-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 352 | 361 | 400.75 | 400.75 | 381 | 381 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 330 | 450 | 450 | 300 | 300 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 295 | 288 | 335 | 335 | 301 | 301 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 282 | 335 | 335 | 311 | 311 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 90 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 43 | 51 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 46 | 139 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16.5 | 16.8 | 33 | 33 | 17.5 | 17.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 17 | 18 | 22 | 22 | 17 | 17 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 25 | 24 | 52.19 | 52.19 | 33 | 33 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 145 | 265 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 94 | 117 | 135 | 135 | 115 | 115 | -
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 70 | 88 | 88 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 15 | 68 | 104 | 104 | 52 | 52 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 122 | 152 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 24 | 0 | 32 | 0 | 32 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 16 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 300 | 250 | 583 | 583 | 250 | 250 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 2403.5 | 2805.8 | 5243.9 | 5243.9 | 2872.83 | 2872.83
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 16 | 25.5 | 25.5 | 8 | 8 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 17 | 0 | 20 | 0 | 20 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 37 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 184 | 184 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 90 | 105 | 105 | 90 | 90 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 64 | 56 | 78 | 56 | 78 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 34 | 34 | 34 | 34 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 0 | 0 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 21 | 108 | 108 | 90 | 90 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 4 | 0 | 2.78 | 0 | 2.78 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 135 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 54 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 110 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 88 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 110 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1226 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 10 | 57 | 57 | 57 | 57 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 571 | 570 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2176 | 3085 | 3417.5 | 3416.72 | 3372 | 3386.22
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 194 | 210 | 221.43 | 221.43 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 344 | 343 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 330 | 335 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 29 | 31 | 46.7 | 46.7 | 30 | 30 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 49 | 55 | 55 | 54 | 54 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 16 | 16 | 195 | 195 | 195 | 195 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 62 | 108 | 150 | 150 | 140 | 140 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 46 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 80 | 163 | 163 | 80 | 80 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 126 | 170 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 38 | 44 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 3 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 14 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 38 | 38 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 71 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 63 | 0 | 70 | 0 | 70 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1584 | 1807.2 | 2454.43 | 2384.43 | 2249.55 | 2179.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 27-05-2025 | during | 28-05-2025 | during | 28-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 123 | 184 | 200 | 200 | 170 | 170 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 64 | 81 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 52.76 | 0 | 48 | 0 | 48 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 35 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 268.76 | 312 | 599.1 | 549 | 391.6 | 341.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 38 | 37 | 36 | 36 | 34 | 34 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | GT#3 is not on FGMO Mode due to problem of Flame
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 149 | 149 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 25 | 25 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 65 | 80 | 83 | 83 | 60 | 60 | Allocation limit by Titas, instructed by DS(Gen)
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 100 | 100 | 100 | 173 | 173 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 365 | 338 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 207 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1342 | 1211 | 1501 | 1501 | 1423 | 1423
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 929 | 782 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 197 | 144 | 410 | 410 | 180 | 180 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 105 | 105 | 34 | 34 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 33.58 | 0 | 80 | 0 | 80 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1015 | 1228 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2174.58 | 2171 | 3592.2 | 3512.2 | 3291.2 | 3211.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 214 | 296 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 9 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 110 | 130 | 130 | 118 | 118 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1035 | 1155 | 1244 | 1244 | 1244 | 1244 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 0 | 0 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.96 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1798.96 | 2099 | 2172 | 2171 | 2010 | 2009
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 151 | 144 | 214 | 214 | 166 | 166 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 129 | 220 | 220 | 162 | 162 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 300 | 414 | 413.79 | 413.79 | 371 | 371 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 22 | 22 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 33 | 52.2 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 95 | 97 | 97 | 97 | 97 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.47 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1159 | 959.29 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 63.93 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 85 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1924.4 | 2115.29 | 3186.72 | 3019.87 | 2985.73 | 2818.88
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 48 | 50 | 50 | 50 | 49 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 160 | 164 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 90 | 113 | 113 | 50 | 50 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.4 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 203 | 0 | 200 | 0 | 200 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 475.4 | 417 | 697.6 | 462 | 644.6 | 408
System Total |  |  |  |  | 28886.2 | 27110.055 | 14147.6 | 16023.29 | 22864.45 | 22260.12 | 19240.51 | 18650.18
Forecast Scenario (28-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15200 |  | 0 |  | 15200
|  |  |  | 1:00 | 14700 |  | 0 |  | 14700
|  |  |  | 2:00 | 14300 |  | 0 |  | 14300
|  |  |  | 3:00 | 13800 |  | 0 |  | 13800
|  |  |  | 4:00 | 13550 |  | 0 |  | 13550
|  |  |  | 5:00 | 13200 |  | 0 |  | 13200
|  |  |  | 6:00 | 12700 |  | 0 |  | 12700
|  |  |  | 7:00 | 12600 |  | 0 |  | 12600
|  |  |  | 8:00 | 12540 |  | 0 |  | 12540
|  |  |  | 9:00 | 12880 |  | 0 |  | 12880
|  |  |  | 10:00 | 13310 |  | 0 |  | 13310
|  |  |  | 11:00 | 13650 |  | 0 |  | 13650
|  |  |  | 12:00 | 14230 |  | 0 |  | 14230
|  |  |  | 13:00 | 14560 |  | 0 |  | 14560
|  |  |  | 14:00 | 14760 |  | 0 |  | 14760
|  |  |  | 15:00 | 14970 |  | 0 |  | 14970
|  |  |  | 16:00 | 14920 |  | 0 |  | 14920
|  |  |  | 17:00 | 14540 |  | 0 |  | 14540
|  |  |  | 18:00 | 13990 |  | 0 |  | 13990
|  |  |  | 18:30 | 14500 |  | 0 |  | 14500
|  |  |  | 19:00 | 15000 |  | 0 |  | 15000
|  |  |  | 19:30 | 15620 |  | 0 |  | 15620
|  |  |  | 20:00 | 15690 |  | 0 |  | 15690
|  |  |  | 21:00 | 15830 |  | 0 |  | 15830
|  |  |  | 22:00 | 15800 |  | 0 |  | 15800
|  |  |  | 23:00 | 15600 |  | 0 |  | 15600
Probable Maximum Temperature: |  |  | 32.90°C
Probable Maximum Demand at Day Peak: |  |  | 14230.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15830.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15830.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 342.32 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 08:56 hrs on 28-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [7 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [7 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 27-05-2025 | [28 empty] | Date: | 27-05-2025 | [28 empty] | Date: | 27-05-2025 | [28 empty] | Date: | 27-05-2025 | [28 empty] | Date: | 27-05-2025 | [16 empty] | Date: | 27-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [28 empty] | Day: | Tuesday | [16 empty] | Day: | Tuesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Maona 33 MW PP(Summit) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 33.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 17 | 112 | 79 | 0 | 0 | 17 | 122 | 0 | 0 | 300 | 298 | 300 | 0 | 17 | 0 | 294 | 0 | 0 | 0 | 90 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34 | 0 | 0 | 12 | 0 | 0 | 40 | 0 | 32 | 570 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 10 | 16 | 0 | 354 | 330 | 52 | 201 | 34 | 93 | 80 | 136 | 13 | 15 | 88 | 40 | 8 | 0 | 0 | 305 | 320 | 334 | 35 | 0 | 0 | 142 | 0 | 0 | 62 | 0 | 0 | 0 | 170 | 0 | 87 | 153 | 0 | 0 | 0 | 1 | 7382 | 881 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 161 | 50 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 223 | 1244 | 0 | 6774.2 | 14156.2 | 76.87
01:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 17 | 17 | 113 | 48 | 0 | 0 | 17 | 90 | 0 | 0 | 300 | 281 | 300 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 17 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 34 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 30 | 568 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 16 | 0 | 340 | 335 | 52 | 182 | 35 | 94 | 80 | 136 | 9 | 15 | 88 | 36 | 8 | 0 | 0 | 305 | 320 | 300 | 35 | 0 | 0 | 131 | 0 | 0 | 62 | 0 | 0 | 0 | 171 | 2 | 48 | 96 | 0 | 0 | 0 | 9 | 6932 | 880 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 130 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 160 | 49 | 70 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 220 | 1244 | 0 | 6759.2 | 13691.2 | 76.86
02:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 17 | 113 | 48 | 0 | 0 | 17 | 80 | 0 | 0 | 300 | 293 | 300 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 17 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 32 | 547 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 16 | 0 | 320 | 335 | 52 | 187 | 35 | 93 | 80 | 136 | 9 | 15 | 88 | 40 | 0 | 0 | 0 | 300 | 320 | 299 | 38 | 0 | 0 | 131 | 0 | 0 | 62 | 0 | 0 | 0 | 171 | 13 | 48 | 96 | 0 | 0 | 0 | 12 | 6877.5 | 928 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1452 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 129 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 160 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 180 | 0 | 222 | 1100 | 0 | 6528.2 | 13405.7 | 76.85
03:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 0 | 17 | 113 | 48 | 0 | 0 | 17 | 56 | 0 | 0 | 300 | 299 | 300 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 17 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 32 | 500 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 16 | 0 | 352 | 330 | 52 | 211 | 35 | 93 | 80 | 136 | 9 | 15 | 88 | 38 | 0 | 0 | 0 | 300 | 320 | 355 | 38 | 0 | 0 | 145 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 6834.5 | 928 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1146 | 0 | 1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 160 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 124 | 180 | 0 | 221 | 1100 | 0 | 6210 | 13044.5 | 76.84
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 0 | 17 | 112 | 48 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 298 | 300 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 17 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 32 | 500 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 16 | 0 | 354 | 330 | 52 | 198 | 35 | 93 | 80 | 136 | 9 | 15 | 88 | 38 | 0 | 0 | 0 | 305 | 320 | 331 | 38 | 0 | 0 | 137 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 6723.5 | 928 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1113 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 162 | 49 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 180 | 0 | 221 | 1100 | 0 | 6179 | 12902.5 | 76.83
05:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 17 | 112 | 48 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 294 | 300 | 0 | 0 | 0 | 277 | 0 | 0 | 0 | 17 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 32 | 500 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 16 | 0 | 354 | 335 | 53 | 193 | 35 | 79 | 80 | 136 | 9 | 15 | 88 | 32 | 0 | 0 | 0 | 305 | 320 | 300 | 38 | 0 | 0 | 136 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 17 | 48 | 96 | 0 | 0 | 0 | 12 | 6651.5 | 928 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1013 | 0 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 150 | 48 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 120 | 180 | 0 | 217 | 1100 | 0 | 6055 | 12706.5 | 76.82
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 17 | 94 | 48 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 288 | 300 | 0 | 0 | 0 | 277 | 0 | 0 | 2 | 125 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 34 | 501 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1102 | 1 | 51 | 0 | 16 | 0 | 355 | 335 | 53 | 186 | 35 | 74 | 80 | 136 | 9 | 15 | 88 | 36 | 0 | 6 | 0 | 300 | 320 | 331 | 38 | 0 | 0 | 128 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 17 | 48 | 95 | 0 | 0 | 1.19 | 5 | 6608.69 | 928 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 922 | 0 | 1206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3.92 | 0 | 0 | 144 | 0 | 0 | 0 | 300 | 0 | 0.32 | 0 | 158 | 50 | 0 | 1 | 0 | 0 | 0 | 0.3 | 6 | 0.05 | 0 | 209 | 6 | 120 | 180 | 0 | 218 | 1040 | 0 | 5737.59 | 12346.28 | 76.81
07:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 17 | 94 | 48 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 296 | 300 | 0 | 0 | 0 | 283 | 0 | 0 | 9 | 125 | 17.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 33 | 501 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1111 | 3 | 51 | 0 | 16 | 0 | 354 | 330 | 53 | 195 | 35 | 51 | 80 | 99 | 9 | 15 | 74 | 32 | 0 | 17 | 0 | 305 | 320 | 312 | 38 | 0 | 0 | 132 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 68 | 123 | 0 | 0 | 8.4 | 12 | 6604.9 | 928 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.19 | 919 | 0 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 13.85 | 20 | 0 | 149 | 0 | 0 | 0 | 300 | 0 | 1.05 | 0 | 151 | 50 | 0 | 5 | 0 | 0 | 0 | 0.8 | 16 | 0.12 | 0 | 200 | 0 | 120 | 180 | 0 | 219 | 950 | 0 | 5755.01 | 12359.91 | 76.8
08:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 17 | 94 | 48 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 299 | 300 | 0 | 0 | 0 | 282 | 0 | 0 | 14 | 125 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 40 | 0 | 9 | 500 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1110 | 11 | 51 | 0 | 16 | 0 | 320 | 330 | 54 | 196 | 35 | 51 | 80 | 89 | 9 | 15 | 52 | 32 | 0 | 31 | 0 | 305 | 320 | 315 | 38 | 0 | 0 | 129 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 68 | 125 | 0 | 1 | 13.32 | 12 | 6531.32 | 881 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.45 | 914 | 0 | 1231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 31.09 | 40 | 0 | 156 | 0 | 0 | 0 | 300 | 0 | 2.66 | 0 | 154 | 51 | 0 | 12 | 0 | 0 | 0 | 1.9 | 64 | 0.34 | 0 | 200 | 5 | 100 | 180 | 0 | 220 | 941 | 0 | 5861.44 | 12392.76 | 76.79
09:00 | 0 | 70 | 13 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 17 | 94 | 48 | 0 | 0 | 35 | 0 | 0 | 0 | 300 | 300 | 300 | 0 | 0 | 0 | 284 | 0 | 0 | 26 | 125 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 4 | 500 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1110 | 15 | 51 | 0 | 16 | 0 | 350 | 330 | 54 | 200 | 35 | 51 | 80 | 97 | 9 | 15 | 52 | 28 | 0 | 49 | 0 | 310 | 320 | 390 | 38 | 0 | 0 | 139 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 68 | 124 | 0 | 2 | 20.32 | 12 | 6782.32 | 881 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.19 | 906 | 0 | 1228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 44.77 | 65 | 0 | 161 | 0 | 0 | 0 | 300 | 0 | 3.9 | 0 | 159 | 50 | 30 | 20 | 0 | 0 | 0 | 3.3 | 160 | 0.54 | 0 | 200 | 5 | 100 | 180 | 0 | 221 | 944 | 0 | 6004.7 | 12787.02 | 76.78
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 3 | 17 | 94 | 48 | 0 | 0 | 35 | 31 | 0 | 0 | 300 | 285 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 31 | 142 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 4 | 40 | 0 | 2 | 575 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 43 | 2 | 16 | 0 | 347 | 330 | 48 | 199 | 34 | 53 | 80 | 97 | 9 | 14 | 52 | 34 | 0 | 73 | 0 | 305 | 320 | 392 | 38 | 0 | 0 | 149 | 0 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 68 | 122 | 0 | 2 | 27.37 | 9 | 7058.37 | 929 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.76 | 906 | 0 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 54.63 | 66 | 0 | 162 | 0 | 0 | 0 | 300 | 0 | 4.8 | 0 | 159 | 50 | 35 | 20 | 0 | 0 | 0 | 4 | 190 | 0.27 | 0 | 200 | 5 | 120 | 220 | 0 | 219 | 982 | 0 | 6177.46 | 13235.83 | 76.78
11:00 | 8 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 367 | 0 | 0 | 17 | 0 | 94 | 46 | 30 | 1 | 35 | 47 | 0 | 2 | 300 | 310 | 300 | 0 | 17 | 0 | 284 | 0 | 0 | 31 | 160 | 16 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 75 | 0 | 4.8 | 40 | 3 | 2 | 570 | 0 | 0 | 0 | 0 | 6 | 184 | 0 | 0 | 0 | 1224 | 15 | 43 | 23 | 16 | 0 | 341 | 330 | 48 | 196 | 29 | 68 | 80 | 113 | 9 | 14 | 98 | 38 | 0 | 39 | 0 | 300 | 320 | 386 | 38 | 0 | 0 | 154 | 0 | 0 | 77 | 0 | 0 | 0 | 0 | 6 | 55 | 114 | 0 | 2 | 51.85 | 6 | 7296.65 | 929 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9 | 958 | 0 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 60.99 | 84 | 0 | 162 | 0 | 0 | 0 | 300 | 0 | 5.26 | 0 | 159 | 50 | 35 | 20 | 0 | 0 | 0 | 6.3 | 208 | 0.69 | 0 | 200 | 7 | 120 | 220 | 0 | 213 | 999 | 0 | 6296.14 | 13592.79 | 76.78
12:00 | 16 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 43 | 16 | 94 | 46 | 145 | 15 | 35 | 122 | 0 | 15 | 300 | 295 | 300 | 0 | 17 | 0 | 280 | 0 | 0 | 24 | 160 | 16.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 4 | 40 | 17 | 2 | 571 | 0 | 0 | 0 | 0 | 17 | 184 | 0 | 0 | 0 | 1224 | 17 | 43 | 62 | 16 | 0 | 344 | 330 | 48 | 194 | 29 | 71 | 80 | 126 | 9 | 14 | 114 | 38 | 3 | 63 | 0 | 305 | 320 | 365 | 38 | 0 | 0 | 149 | 0 | 0 | 65 | 0 | 0 | 0 | 100 | 17 | 64 | 123 | 0 | 2 | 52.76 | 10 | 7774.26 | 929 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.58 | 1015 | 0 | 1159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 63.93 | 151 | 0 | 160 | 0 | 0 | 0 | 300 | 0 | 5.47 | 0 | 160 | 50 | 35 | 20 | 0 | 0 | 0 | 7.4 | 203 | 0.96 | 0 | 200 | 9 | 120 | 220 | 0 | 214 | 1035 | 0 | 6373.34 | 14147.6 | 76.78
13:00 | 16 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 368 | 0 | 0 | 54 | 17 | 94 | 46 | 145 | 15 | 35 | 152 | 0 | 41 | 300 | 305 | 300 | 0 | 17 | 0 | 293 | 0 | 0 | 10 | 160 | 16.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 38 | 17 | 7 | 575 | 0 | 0 | 0 | 0 | 17 | 184 | 0 | 0 | 0 | 1224 | 0 | 43 | 95 | 16 | 0 | 337 | 330 | 48 | 206 | 29 | 93 | 80 | 156 | 9 | 12 | 114 | 42 | 16 | 63 | 23 | 310 | 320 | 383 | 37 | 0 | 0 | 150 | 0 | 0 | 61 | 0 | 0 | 0 | 100 | 17 | 64 | 120 | 0 | 2 | 48.92 | 11 | 7981.42 | 929 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.58 | 1052 | 0 | 966 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 64.49 | 166 | 0 | 152 | 0 | 0 | 0 | 414 | 0 | 5.01 | 0 | 158 | 50 | 50 | 20 | 24 | 0 | 0 | 4.2 | 195 | 0.89 | 0 | 200 | 10 | 120 | 220 | 0 | 219 | 1074 | 0 | 6465.17 | 14446.59 | 76.79
14:00 | 16 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 54 | 17 | 105 | 46 | 260 | 42 | 35 | 146 | 0 | 49 | 300 | 305 | 250 | 0 | 17 | 0 | 288 | 0 | 0 | 30 | 160 | 0 | 17 | 0 | 0 | 0 | 15 | 0 | 0 | 3 | 0 | 17 | 0 | 88 | 48 | 3 | 36 | 28 | 5 | 575 | 0 | 0 | 0 | 0 | 29 | 185 | 0 | 0 | 0 | 1224 | 16 | 43 | 92 | 16 | 0 | 300 | 300 | 47 | 196 | 25 | 94 | 80 | 155 | 9 | 11 | 100 | 44 | 25 | 59 | 43 | 305 | 320 | 386 | 37 | 0 | 0 | 140 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 17 | 63 | 120 | 0 | 2 | 49.55 | 2 | 8089.55 | 929 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.62 | 1116 | 0 | 974.84 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 54.07 | 161 | 0 | 139 | 0 | 0 | 0 | 350 | 0 | 5.07 | 0 | 160 | 49 | 52 | 20 | 34 | 0 | 0 | 6.4 | 187 | 0.51 | 0 | 200 | 10 | 118 | 180 | 0 | 217 | 1175 | 0 | 6548.51 | 14638.06 | 76.79
15:00 | 16 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 54 | 17 | 110 | 46 | 280 | 55 | 35 | 153 | 0 | 49 | 300 | 300 | 250 | 0 | 0 | 0 | 304 | 0 | 0 | 24 | 160 | 16.8 | 17 | 0 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 32 | 0 | 88 | 48 | 2 | 34 | 34 | 2 | 575 | 0 | 0 | 0 | 0 | 34 | 185 | 0 | 0 | 0 | 1224 | 1 | 43 | 83 | 16 | 0 | 329 | 335 | 43 | 203 | 26 | 94 | 80 | 165 | 8 | 11 | 114 | 46 | 25 | 52 | 43 | 305 | 320 | 370 | 37 | 0 | 0 | 141 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 17 | 64 | 118 | 0 | 2 | 39.77 | 4 | 8229.57 | 929 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.96 | 1114 | 0 | 971.2 | 0 | 0 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 45.89 | 159 | 0 | 138 | 0 | 0 | 0 | 414 | 0 | 1.52 | 0 | 160 | 50 | 52 | 19 | 34 | 0 | 0 | 5.2 | 149 | 0.35 | 0 | 200 | 10 | 120 | 180 | 0 | 228 | 1200 | 0 | 6571.12 | 14800.69 | 76.81
16:00 | 32 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 54 | 17 | 112 | 46 | 264 | 55 | 35 | 152 | 0 | 54 | 330 | 305 | 250 | 0 | 17 | 0 | 273 | 0 | 0 | 18 | 160 | 16.8 | 18 | 0 | 0 | 2 | 15 | 0 | 0 | 15 | 0 | 32 | 0 | 76 | 72 | 1 | 35 | 36 | 3 | 575 | 0 | 0 | 13 | 0 | 35 | 184 | 0 | 0 | 0 | 1224 | 4 | 43 | 83 | 16 | 0 | 329 | 335 | 40 | 190 | 26 | 89 | 80 | 170 | 9 | 11 | 114 | 42 | 25 | 0 | 43 | 305 | 320 | 360 | 37 | 0 | 0 | 148 | 0 | 0 | 60 | 0 | 0 | 0 | 95 | 17 | 53 | 118 | 0 | 1 | 27.59 | 10 | 8181.39 | 929 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.02 | 1231 | 0 | 967.07 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 29.46 | 146 | 0 | 135 | 0 | 0 | 0 | 414 | 0 | 2.83 | 0 | 165 | 47 | 52 | 17 | 65 | 0 | 0 | 4.6 | 87 | 0.3 | 0 | 170 | 10 | 110 | 220 | 0 | 218 | 1200 | 0 | 6577.28 | 14758.67 | 76.83
17:00 | 50 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 54 | 17 | 115 | 46 | 210 | 55 | 35 | 139 | 0 | 64 | 330 | 303 | 250 | 0 | 17 | 0 | 283 | 0 | 0 | 9 | 160 | 16.5 | 18 | 0 | 0 | 17 | 30 | 0 | 0 | 21 | 0 | 34 | 0 | 100 | 48 | 1 | 37 | 51 | 5 | 571 | 0 | 0 | 29 | 0 | 51 | 184 | 0 | 0 | 0 | 1224 | 1 | 43 | 85 | 16 | 0 | 333 | 335 | 40 | 185 | 26 | 90 | 80 | 170 | 9 | 11 | 114 | 44 | 25 | 0 | 43 | 300 | 207 | 353 | 37 | 0 | 0 | 149 | 0 | 0 | 60 | 0 | 0 | 0 | 95 | 17 | 63 | 118 | 0 | 1 | 12.86 | 11 | 8061.36 | 928 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.75 | 1222 | 0 | 973.99 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 11.66 | 143 | 0 | 134 | 0 | 0 | 0 | 414 | 0 | 1.17 | 0 | 167 | 48 | 52 | 8 | 70 | 0 | 0 | 1.9 | 76 | 0.21 | 0 | 150 | 9 | 120 | 220 | 0 | 223 | 1200 | 0 | 6479.68 | 14541.04 | 76.85
18:00 | 50 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 45 | 17 | 117 | 46 | 210 | 55 | 35 | 142 | 0 | 66 | 330 | 297 | 250 | 0 | 17 | 0 | 287 | 0 | 0 | 2 | 160 | 16.5 | 18 | 0 | 0 | 17 | 15 | 0 | 0 | 2 | 0 | 44 | 0 | 48 | 24 | 0 | 38 | 34 | 5 | 523 | 0 | 0 | 33 | 0 | 34 | 184 | 0 | 0 | 0 | 1150 | 0 | 43 | 85 | 16 | 0 | 300 | 335 | 44 | 198 | 30 | 91 | 80 | 170 | 17 | 11 | 114 | 40 | 25 | 0 | 43 | 300 | 193 | 298 | 37 | 0 | 0 | 140 | 0 | 0 | 60 | 0 | 0 | 0 | 97 | 18 | 80 | 178 | 0 | 0 | 1.67 | 11 | 7822.17 | 929 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.83 | 1161 | 0 | 957.11 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 3.67 | 143 | 0 | 131 | 0 | 0 | 0 | 320 | 0 | 0.32 | 0 | 168 | 50 | 115 | 0 | 70 | 0 | 0 | 1 | 19 | 0.03 | 0 | 150 | 9 | 100 | 180 | 0 | 295 | 1120 | 0 | 6170.96 | 13993.13 | 76.87
19:00 | 50 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 379 | 0 | 0 | 37 | 17 | 117 | 141 | 260 | 55 | 35 | 145 | 0 | 67 | 330 | 300 | 250 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 160 | 16.5 | 18 | 0 | 0 | 17 | 15 | 0 | 0 | 0 | 31 | 64 | 0 | 100 | 70 | 0 | 40 | 40 | 3 | 570 | 53 | 0 | 0 | 0 | 36 | 184 | 0 | 0 | 0 | 1224 | 0 | 43 | 92 | 16 | 0 | 335 | 335 | 44 | 205 | 30 | 111 | 80 | 170 | 26 | 14 | 114 | 48 | 44 | 0 | 36 | 300 | 193 | 375 | 37 | 0 | 0 | 134 | 0 | 0 | 60 | 0 | 0 | 0 | 100 | 37 | 80 | 183 | 0 | 0 | 0 | 12 | 8489.5 | 881 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1178 | 17 | 972.09 | 0 | 21 | 0 | 95 | 0 | 90 | 45 | 13 | 0 | 0 | 30 | 0 | 144 | 0 | 129 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 11 | 100 | 180 | 0 | 298 | 1120 | 0 | 6517.09 | 15006.59 | 76.89
19:30 | 74 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 381 | 0 | 0 | 54 | 17 | 117 | 140 | 260 | 55 | 35 | 155 | 0 | 67 | 330 | 303 | 250 | 0 | 17 | 0 | 306 | 0 | 0 | 0 | 160 | 16.8 | 18 | 0 | 0 | 51 | 80 | 0 | 0 | 3 | 42 | 64 | 17 | 100 | 88 | 0 | 40 | 40 | 11 | 571 | 108 | 0 | 20 | 1 | 85 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 105 | 16 | 0 | 334 | 335 | 44 | 208 | 30 | 115 | 80 | 170 | 28 | 14 | 114 | 48 | 52.2 | 0 | 36 | 300 | 207 | 385 | 37 | 0 | 0 | 148 | 0 | 0 | 79 | 0 | 0 | 0 | 100 | 54.5 | 80 | 175 | 0 | 0 | 0 | 12 | 8936.5 | 881 | 151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1157 | 17 | 958.76 | 0 | 48 | 0 | 113 | 0 | 95 | 108 | 20 | 8 | 0 | 30 | 0 | 143 | 0 | 129 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 50 | 115 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 291 | 11 | 110 | 180 | 0 | 299 | 1120 | 0 | 6685.76 | 15622.26
20:00 | 82 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 54 | 17 | 117 | 136 | 265 | 55 | 35 | 153 | 0 | 68 | 330 | 283 | 250 | 0 | 17 | 0 | 282 | 0 | 0 | 0 | 160 | 16.8 | 18 | 0 | 0 | 51 | 80 | 0 | 0 | 1 | 48 | 64 | 54 | 100 | 88 | 0 | 40 | 73 | 20 | 571 | 160 | 0 | 28 | 6 | 80 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 104 | 16 | 0 | 343 | 335 | 46 | 192 | 31 | 115 | 80 | 170 | 27 | 14 | 114 | 46 | 52.2 | 0 | 36 | 295 | 207 | 337 | 37 | 0 | 0 | 149 | 0 | 0 | 79 | 0 | 0 | 0 | 100 | 50 | 81 | 175 | 0 | 0 | 0 | 12 | 8964 | 881 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1158 | 17 | 958.66 | 0 | 48 | 0 | 113 | 0 | 95 | 108 | 24 | 17 | 0 | 30 | 0 | 143 | 0 | 129 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 49 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 100 | 180 | 0 | 296 | 1130 | 0 | 6725.66 | 15689.66 | 76.91
21:00 | 90 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 51 | 17 | 117 | 139 | 265 | 55 | 35 | 152 | 0 | 68 | 330 | 288 | 250 | 0 | 17 | 0 | 282 | 0 | 0 | 0 | 160 | 16.8 | 18 | 0 | 0 | 110 | 135 | 21 | 0 | 10 | 50 | 64 | 54 | 100 | 88 | 0 | 40 | 110 | 20 | 570 | 160 | 0 | 37 | 16 | 90 | 184 | 0 | 0 | 0 | 1226 | 0 | 51 | 108 | 16 | 0 | 343 | 335 | 49 | 210 | 31 | 115 | 80 | 170 | 29 | 14 | 114 | 44 | 52.2 | 0 | 46 | 300 | 207 | 338 | 37 | 0 | 0 | 149 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 35 | 81 | 184 | 0 | 0 | 0 | 12 | 9221 | 782 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 17 | 959.29 | 0 | 48 | 0 | 113 | 0 | 95 | 113 | 37 | 33 | 0 | 30 | 0 | 144 | 0 | 129 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 48 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 296 | 1155 | 0 | 6802.29 | 16023.29 | 76.93
22:00 | 90 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 17 | 120 | 139 | 145 | 55 | 35 | 138 | 0 | 68 | 330 | 285 | 250 | 0 | 17 | 0 | 272 | 0 | 0 | 0 | 52 | 16.8 | 18 | 0 | 0 | 114 | 150 | 50 | 0 | 51 | 50 | 64 | 54 | 100 | 88 | 0 | 40 | 110 | 15 | 575 | 160 | 0 | 0 | 16 | 90 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 115 | 16 | 0 | 349 | 335 | 49 | 214 | 30 | 115 | 80 | 170 | 29 | 14 | 114 | 48 | 52.2 | 0 | 46 | 305 | 207 | 326 | 39 | 0 | 0 | 146 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 35 | 81 | 177 | 0 | 0 | 0 | 12 | 9000 | 782 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238 | 30 | 967.71 | 0 | 47 | 0 | 113 | 5 | 95 | 113 | 37 | 43 | 0 | 30 | 0 | 143 | 0 | 129 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 165 | 50 | 115 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 110 | 220 | 0 | 297 | 1244 | 0 | 6872.71 | 15872.71 | 76.95
23:00 | 8 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 54 | 17 | 120 | 112 | 145 | 55 | 35 | 146 | 0 | 68 | 330 | 301 | 250 | 0 | 17 | 0 | 274 | 0 | 0 | 0 | 52 | 16.8 | 16 | 0 | 0 | 116 | 190 | 56 | 0 | 55 | 50 | 64 | 54 | 100 | 88 | 0 | 40 | 110 | 29 | 575 | 160 | 0 | 5 | 16 | 90 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 120 | 16 | 0 | 343 | 330 | 50 | 197 | 30 | 98 | 81 | 177 | 29 | 14 | 114 | 48 | 52.2 | 0 | 46 | 305 | 70 | 338 | 39 | 0 | 0 | 139 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 35 | 81 | 176 | 0 | 0 | 0 | 12 | 8817 | 782 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 36 | 1016.79 | 0 | 48 | 0 | 113 | 5 | 95 | 113 | 37 | 43 | 0 | 30 | 0 | 143 | 0 | 129 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 159 | 50 | 115 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 120 | 220 | 0 | 303 | 1244 | 0 | 6951.99 | 15768.99 | 76.97
Total KWH | 547488 | 1337280 | 437280 | 0 | 0 | 0 | 0 | 0 | 8672400 | 0 | 0 | 707400 | 428040 | 2629584 | 1582560 | 2762760 | 632958 | 713091 | 2236320 | 0 | 739200 | 7739500 | 7161949 | 6840862 | 0 | 232694 | 0 | 6928648 | 0 | 0 | 240672 | 2608800 | 380400 | 413280 | 0 | 0 | 562036 | 833018 | 192000 | 0 | 195360 | 487771 | 495024 | 252531 | 1248960 | 714240 | 26363 | 915780 | 800396 | 420480 | 13200000 | 757745 | 0 | 202560 | 73956.6 | 725964 | 4274047 | 0 | 0 | 0 | 28750906 | 60480 | 1081904 | 1279177 | 434909 | 0 | 8485000 | 8084000 | 1166880 | 4819000 | 762912 | 2113920 | 1914600 | 3513600 | 330120 | 314540 | 2327880 | 964800 | 439435 | 453309 | 462320 | 7365500 | 6667400 | 8694000 | 889000 | 0 | 0 | 3411736 | 0 | 0 | 1640640 | 0 | 0 | 0 | 1651900 | 460440 | 1514400 | 3060000 | 0 | 17050 | 348280 | 247440 | 186078875.6 | 21690182 | 4281120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 619920 | 26327280 | 165120 | 27176138 | 0 | 240409 | 0 | 1209408 | 16039 | 497728 | 572928 | 144914 | 162571 | 779250 | 148225 | 469496 | 2530300 | 0 | 3574964 | 0 | 0 | 0 | 8639636 | 0 | 40320 | 0 | 3943000 | 1114036 | 1400673 | 173721 | 854236 | 0 | 0 | 50031.6 | 1540800 | 4977 | 0 | 5847000 | 208179 | 2731000 | 5071850 | 0 | 5959284 | 27131636.36 | 0 | 155316371.96 | 341395247.56

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 27-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14147.6 | MW | 12:00 Hr. | Energy Generated |  |  | 341.3952 |  | MKWHr.
| Day Peak Demand |  |  | 14234.6 | MW | 12:00 Hr. | Energy Unserverd |  |  | 5.265 |  | MKWHr.
| Evening Peak Generation |  |  | 16023.29 | MW | 21:00 Hr. | Energy Demand |  |  | 346.6602 |  | MKWHr.
| Evening Peak Demand |  |  | 16420.29 | MW | 21:00 Hr. | Maximum Temperature |  |  | 35.6 |  | °C
| Minimum Generation of the Day |  |  | 12346.28 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 926.25 |  | MMCFD
| Maximum Generation of the Day |  |  | 16023.29 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.9906 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 38.137 | 0 | 17.5955 | 0 | 0 | 0.24067 | 0 | 0 | 55.9732 | Gas | 127.2525 | Gas | 451145969.84
| Chattogram Zone |  |  | 4.6945 | 41.9509 | 7.3462 | 0 | 0.91578 | 0.086843 | 0 | 0.19536 | 55.1896 | Coal | 112.2731 | Coal | 738224929.5412
| Cumilla Zone |  |  | 27.0637 | 0 | 10.4665 | 0 | 0 | 0.45331 | 0.9648 | 0 | 38.9483 | HFO | 46.1026 | HFO | 860666057.712
| Mymensingh Zone |  |  | 0 | 0 | 5.2823 | 0 | 0 | 0.36533 | 0 | 0 | 5.6476 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.3202 | Hydro | 0.91578 | Hydro | 91578
| Khulna Zone |  |  | 4.2811 | 26.3273 | 0.16512 | 0 | 0 | 0.61992 | 21.6902 | 0 | 53.0836 | Solar | 4.8247 | Solar | 78668941.416
| Barishal Zone |  |  | 8.011 | 38.9379 | 0 | 0 | 0 | 0.004977 | 0 | 0 | 46.9539 | Import | 49.8311 | Import | 254902544.8
| Rajshahi Zone |  |  | 14.7449 | 0 | 2.9922 | 0 | 0 | 1.2891 | 27.1761 | 0 | 46.2023 | Wind | 0.19536 | Wind | 2860070.4
| Rangpur Zone |  |  | 0 | 5.057 | 2.2549 | 0 | 0 | 1.7646 | 0 | 0 | 9.0765
| Total |  |  | 127.2525 | 112.2731 | 46.1026 | 0 | 0.91578 | 4.8247 | 49.8311 | 0.19536 | 341.3952
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 451145969.84 |  | Hydro | 91578
|  |  |  | Coal | 738224929.5412 |  | Solar | 78668941.416
|  |  |  | HFO | 860666057.712 |  | Import | 254902544.8
|  |  |  | HSD | 0 |  | Wind | 2860070.4
[5 empty] | Total: | 238,65,60,091 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 21.6902 | Peak Hr Flow | 782.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 45900563.72 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 27.1761 | Peak Hr Flow | 959.29 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 534 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.9648 | Peak Hr Flow | 44.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 1020 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 49.8311 | Peak Hr Flow | 1785.29 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 140 |  | 5993
|  |  |  | Chattogram |  | 0 |  | 1554
|  |  |  | Cumilla |  | 15 |  | 1345
|  |  |  | Mymensingh |  | 45 |  | 1266
|  |  |  | Sylhet |  | 15 |  | 630
|  |  |  | Khulna |  | 0 |  | 1933
|  |  |  | Barishal |  | 0 |  | 504
|  |  |  | Rajshahi |  | 0 |  | 1702
|  |  |  | Rangpur |  | 165 |  | 972
|  |  |  | Total |  | 380 |  | 15899
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:40 |  | Bogura 230/132kV S/S T-02 LT Forced S/D
| 08:40 | 21:12 | Bogura 230/132kV S/S T-02 HT Forced S/D
| 09:01 | 10:51 | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw Scheduled S/D Due to PPP 132 KV CT Oil Leakage
Maintenance work.
| 09:14 | 11:59 | Ishurdi 132/33kV S/S 132 kV Baghabari Line Scheduled S/D Due to 82 no tower loop jumper
connection
|  | 09:26 | Sylhet 132/33kV S/S T4 LT is restored.
|  | 09:26 | Sylhet 132/33kV S/S T4 HT is restored.
|  | 09:40 | Natore 132/33kV S/S TR-1 (405 T) HT is restored.
|  | 09:40 | Natore 132/33kV S/S TR-2 (415 T) HT is restored.
|  | 09:45 | Natore 132/33kV S/S TR-1 (405 T) LT is restored.
|  | 09:46 | Natore 132/33kV S/S TR-2 (415 T) LT is restored.
|  | 09:57 | Khulna (S)-Satkhira 132kV Ckt-2 is restored.
|  | 10:08 | Madunaghat 132/33kV S/S TR-1(507T) HT is restored.
| 10:08 | 13:42 | Khulna(S) 230/132kV S/S TR-2 LT Scheduled S/D
| 10:09 | 13:40 | Khulna(S) 230/132kV S/S TR-2 HT Scheduled S/D
| 10:21 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 11:15 | 12:49 | Khulna (C) S/S TR-1 425T LT Forced S/D Due to ৩৩ কেভি সাইডের কেবল মাটির মধ্যে ঢেকে রাখার
জন্য সাটডাউন নেয়া হয়।
| 11:16 | 12:48 | Khulna (C) S/S TR-1 425T HT Forced S/D Due to ৩৩ কেভি সাইডের কেবল মাটির মধ্যে ঢেকে রাখার
জন্য সাটডাউন নেয়া হয়।
| 11:25 | 11:36 | Brahmanbaria-Shahjibazar 132 kV Ckt-1 Tripped from Shahjibazar 132/33kV end showing
Distance relay relays Due to N/A
| 11:26 | 19:41 | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D Due to Busbar Integration
| 11:50 | 12:24 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to Multifunctional meter | [7 empty] | 50.0MW load
|  |  | changed. | [7 empty] | interrup.
| 12:00 |  | Day peak Generation is 14143 MW
| 12:05 | 16:00 | Rampur 230/132/33 S/S ATR-02 (716T) LT Scheduled S/D Due to GIS bay commission work of
TR-02 132kv bay.
| 12:05 | 16:00 | Rampur 230/132/33 S/S ATR-02 (716T) HT Scheduled S/D Due to GIS bay commission work of
TR-02 132kv bay.
|  | 12:11 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
| 14:01 | 15:19 | Cumilla(N)-Meghnaghat 230 kV Ckt-1 Tripped from Cumilla(N) 230/132/33kV end showing Main
-1 A phase to N Zone -01 Main -02 Distance protection A N Micom I>>,I>,I>,I>> A
Phase relays.
| 14:25 | 15:03 | Hasnabad 132/33kV S/S 33kv Reserve Bus Tripped showing O/C & E/F relays Due to 33kv | [7 empty] | 28.0MW load
|  |  | lalbagh-1 fault,PT explode | [7 empty] | interrup.
| 14:25 | 15:03 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT Tripped showing Over current & Earth Fault | [7 empty] | 28.0MW load
|  |  | relays Due to 33 Lalbagh-1 fault,trip by O/C & E/F and PT explode | [7 empty] | interrup.
| 15:27 | 16:54 | Mirsorai 230/33kV S/S TR-1, 718T HT Tripped showing Bus-ber Protection Relay relays Due | [7 empty] | 12.0MW load
|  |  | to DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS | [7 empty] | interrup.
Compartment by Contractor.
| 15:27 | 17:20 | Mirsorai 230/33kV S/S TR-2, 728T HT Tripped showing Bus-ber protection Relay relays Due | [7 empty] | 12.0MW load
|  |  | to DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS | [7 empty] | interrup.
Compartment by Contractor.
| 15:27 | 17:22 | BSRM-Mirsharai 230 kV Ckt-1 Tripped from Mirsorai 230/33kV end showing Bus-ber Protection | [7 empty] | 12.0MW load
|  |  | Relay relays Due to DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas | [7 empty] | interrup. Mirsorai
|  |  | from DS Compartment by Contractor. | [7 empty] | 230/33kV end
| 15:27 | 17:24 | Mirsorai 230/33kV S/S 150 MW Power Station -01 Tripped showing Bus-ber protection Relay | [7 empty] | 12.0MW load
|  |  | relays Due to DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from | [7 empty] | interrup.
DS Compartment by Contractor.
| 15:27 |  | Rajshahi-Rajshahi(New) 132kV Ckt-1 Tripped from Mirsorai 230/33kV end showing Bus-Bar | [7 empty] | 12.0MW load
|  |  | Protection Relay relays Due to DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to | [7 empty] | interrup. Mirsorai
|  |  | release gas from DS Compartment by Contractor. | [7 empty] | 230/33kV end
| 15:27 | 16:53 | Mirsorai 230/33kV S/S Bus-2 Tripped showing Bus-bar Protection Relay. relays Due to DS | [7 empty] | 12.0MW load
|  |  | (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from DS Compartment by | [7 empty] | interrup.
Contractor.
| 15:27 | 16:58 | Mirsorai 230/33kV S/S 150 MW Power Station -02 Tripped showing Bus-Bar Protection Relay | [7 empty] | 12.0MW load
|  |  | relays Due to DS (Q1) adjacent to Bus-1, Flashing of EGCB Feeder due to release gas from | [7 empty] | interrup.
DS Compartment by Contractor.
|  | 16:41 | Madunaghat 132/33kV S/S TR-1(507T) LT is restored.
| 16:44 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Tripped showing RET 521 relays Due
to AT GUARD AL
| 16:44 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Tripped showing RET 521 relays Due
to AT GUARD AL
| 16:54 |  | Bibiyana South 400 MW Tripped with remarks:- ST
| 17:00 |  | Bibiyana South 400 MW Synchronized with remarks:- False
| 17:00 |  | Bibiyana South 400 MW Synchronized with remarks:- gt
| 17:35 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Forced S/D Due to Emergency | [7 empty] | 22.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 17:35 |  | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Forced S/D Due to Emergency | [7 empty] | 22.0MW load
|  |  | maintenance. | [7 empty] | interrup.
| 18:41 | 19:54 | Aminbazar 400/230/132kV S/S Gopalganj-2 Tripped showing SEL -421 relays Due to Unknown
| 19:05 |  | Adani-Rahanpur ckt-2 is switched on from Rahanpur end but tripped immediately showing
Distance Zone-1 (B-phase to ground, 65 km)
| 21:00 |  | Evening peak generation 16022 MW
| 21:00 |  | Peak generation 16022MW
| 21:07 |  | Ishurdi 230/132kV S/S 230/132 kV T-03 LT Forced S/D Due to 230/132 x-former T-03 LT side
connector redhot.
| 01:30 | 03:04 | Hathazari 230/132/33kV S/S T-01 LT Forced S/D Due to redhot 33kv bus | [7 empty] | 30.0MW load
interrup.
| 01:30 | 03:04 | Hathazari 230/132/33kV S/S T-01 HT Forced S/D Due to redhot | [7 empty] | 30.0MW load
interrup.
| 06:15 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) LT Scheduled S/D Due to Due to PBD hotspot
maintenance
| 06:16 |  | Kishoreganj 132/33kV S/S Tr-1 (404T) HT Scheduled S/D Due to Due to PBD hotspot
maintenance
| 07:00 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to Red hot maintenance at 33 | [7 empty] | 25.0MW load
|  |  | kV Bus-section-1. | [7 empty] | interrup.
| 07:00 |  | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Forced S/D Due to Red hot maintenance at 33 | [7 empty] | 25.0MW load
|  |  | kV Bus-section-1. | [7 empty] | interrup.
| 07:00 |  | Minimum Generation: 13367 MW.
| 07:01 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT Forced S/D Due to Red hot maintenance at 33 | [7 empty] | 25.0MW load
|  |  | kV Bus-section-1. | [7 empty] | interrup.
| 07:02 |  | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT Forced S/D Due to Red hot maintenance at 33 | [7 empty] | 25.0MW load
|  |  | kV Bus-section-1. | [7 empty] | interrup.
| 07:04 |  | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to Redhot maintenance | [7 empty] | 47.0MW load
interrup.
| 07:04 |  | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to Redhot maintenance | [7 empty] | 47.0MW load
interrup.
| 07:06 |  | Kushtia 132/33kV S/S T-3 LT Forced S/D Due to T -3 A , 33 KV incomer Side U clamp a Red | [7 empty] | 50.0MW load
|  |  | Hot Maintenance work . | [7 empty] | interrup.
| 07:07 |  | Kushtia 132/33kV S/S T-3 HT Forced S/D Due to T -3 A , 33 KV incomer Side U clamp a Red | [7 empty] | 50.0MW load
|  |  | Hot Maintenance work . | [7 empty] | interrup.
| 07:22 |  | Khulna(S) 230/132kV S/S TR-1 LT Scheduled S/D
| 07:23 |  | Khulna(S) 230/132kV S/S TR-1 HT Scheduled S/D
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 27-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 361 | 8672400 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 7739500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 288 | 7161949 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 632958 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 282 | 6928648 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 90 | 547488 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 51 | 707400 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 139 | 1582560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 713091 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 232694 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 16.8 | 380400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 413280 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 437280 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 265 | 2762760 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 117 | 2629584 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1337280 | -
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 68 | 739200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 152 | 2236320 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 240672 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 428040 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 250 | 6840862 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 2608800 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2805.8 | 55973166
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 73956.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 60480 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 37 | 202560 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 915780 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 184 | 4274047 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 90 | 725964 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 64 | 495024 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 487771 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1248960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 420480 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 21 | 192000 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 26363 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 135 | 833018 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 54 | 252531 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 110 | 800396 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 714240 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 110 | 562036 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 757745 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1226 | 28750906 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 195360 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 570 | 13200000 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 3085 | 55189617.6
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 210 | 4819000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 343 | 8485000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 8084000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 31 | 762912 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1166880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 16 | 434909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1081904 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 108 | 1279177 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 46 | 462320 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 80 | 1914600 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 170 | 3513600 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 44 | 964800 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 439435 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 314540 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2327880 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 330120 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2113920 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 453309 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1807.2 | 38948306
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 17050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 184 | 3060000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 81 | 1514400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 348280 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 247440 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 35 | 460440 | Liquid fuel shortage
Mymensingh Area Total |  |  |  |  | 654.21 | 312 | 5647610
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 37 | 889000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 149 | 3411736 | -
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1640640 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 100 | 1651900 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7365500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 338 | 8694000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 207 | 6667400 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1211 | 30320176
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 782 | 21690182 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 144 | 4281120 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 165120 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 619920 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1228 | 26327280 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2171 | 53083622
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 296 | 5959284 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 208179 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2731000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1155 | 27131636.36 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5071850 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 5847000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 4977 | -
Barishal Area Total |  |  |  |  | 2236 | 2099 | 46953926.36
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 240409 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 16039 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 144914 | -
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 144 | 2530300 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 129 | 3574964 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8639636 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 148225 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 33 | 162571 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 497728 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1209408 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 572928 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 40320 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 959.29 | 27176138 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 469496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 779250 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2115.29 | 46202326
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 48 | 1114036 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 164 | 3943000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 90 | 854236 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 50031.6 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1400673 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 173721 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1540800 | -
Rangpur Area Total |  |  |  |  | 950 | 417 | 9076497.6
Eastern Grid Total |  |  |  |  | 16771.895 | 9221 | 186078875.6
Western Grid Total |  |  |  |  | 10338.16 | 6802.29 | 155316371.96
National Grid Total |  |  |  |  | 27110.055 | 16023.29 | 341395247.56
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 27-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10573.62 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4946.1 | MW
i) Dhaka area |  |  | 5853.12 |  | MW | i) Khulna area |  |  |  | 1933 | MW
ii) Chattogram area |  |  | 1554.5 |  | MW | ii) Barishal area |  |  |  | 504.5 | MW
iii) Cumilla area |  |  | 1330 |  | MW | iii) Rajshahi area |  |  |  | 1701.6 | MW
iv) Mymensingh area |  |  | 1221 |  | MW | iv) Rangpur area |  |  |  | 807 | MW
v) Sylhet area |  |  | 615 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 15519.72 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 15 | 13:00 | 67 | Ishurdi | 90 | 21:00 | 133 | Patuakhali | 88.5 | 22:00
2 | AKSML | 95.5 | 04:00 | 68 | Jaldhaka | 68 | 19:00 | 134 | Payra | 34 | 23:00
3 | Aftabnagar | 42 | 19:00 | 69 | Jamalpur | 125 | 19:30 | 135 | Postogola | 62 | 13:00
4 | Agargaon | 142 | 13:00 | 70 | Jashore | 152 | 20:00 | 136 | Purbachal | 24 | 23:00
5 | Agrabad | 82 | 17:00 | 71 | Jhenaidah | 140 | 20:00 | 137 | Purbasadipur | 114 | 15:00
6 | Amnura | 37 | 21:00 | 72 | Joydebpur | 151 | 19:00 | 138 | Rahanpur | 32 | 22:00
7 | Ashuganj | 116 | 20:00 | 73 | Joypurhat | 69 | 20:00 | 139 | Rahim | 47 | 09:00
8 | BSRM | 194 | 18:00 | 74 | Juldah | 15 | 00:00 | 140 | Rajbari | 90 | 23:00
9 | Bagerhat | 89 | 23:00 | 75 | KSRM | 22 | 19:00 | 141 | Rajendrapur | 148 | 22:00
10 | Bajitpur | 59 | 22:00 | 76 | Kabirpur | 276 | 18:00 | 142 | Rajshahi | 138 | 22:00
11 | Bakulia | 113 | 17:00 | 77 | Kachua | 114 | 21:00 | 143 | Rajshahi-230 | 78 | 23:00
12 | Banani | 42 | 14:00 | 78 | Kallyanpur | 114 | 21:00 | 144 | Ramganj | 126 | 19:00
13 | Bangabhaban | 17 | 10:00 | 79 | Kalurghat | 41 | 19:00 | 145 | Rampur | 43 | 23:00
14 | Barapukuria | 58 | 00:00 | 80 | Kamrangirchar | 67 | 12:00 | 146 | Rangamati | 18 | 19:30
15 | Barguna | 24 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 136 | 13:00
16 | Barishal | 121 | 19:00 | 82 | Kasba | 40 | 20:00 | 148 | Ruppur | 8.6 | 16:00
17 | Barishal-230 | 116 | 21:00 | 83 | Kazla | 104 | 20:00 | 149 | SSM | 15 | 23:00
18 | Baroaulia | 65 | 15:00 | 84 | Keranigonj | 105 | 23:00 | 150 | Saidpur | 105 | 15:00
19 | Baroirhat | 71 | 19:30 | 85 | Khagrachori | 30 | 13:00 | 151 | Satkhira | 140 | 19:30
20 | Bashundhara | 216 | 15:00 | 86 | Khulna | 71 | 13:00 | 152 | Satmasjid | 116 | 19:30
21 | BashundharaCement | 7 | 17:00 | 87 | Khulshi | 206 | 15:00 | 153 | Savar | 238 | 12:00
22 | Beanibazar | 87 | 22:00 | 88 | Kishoreganj | 150 | 20:00 | 154 | SevenRings | 21.84 | 13:00
23 | Benapole | 70 | 22:00 | 89 | Kodda | 319 | 20:00 | 155 | ShahCement | 35 | 00:00
24 | Bhaluka | 179 | 19:00 | 90 | Kulaura | 60 | 19:00 | 156 | Shahjadpur | 102 | 21:00
25 | Bhandaria | 57.4 | 22:00 | 91 | Kurigram | 54 | 18:30 | 157 | Shahjibazar | 109 | 15:00
26 | Bhangura | 42 | 19:30 | 92 | Kushtia | 172 | 21:00 | 158 | Shahmirpur | 59 | 16:00
27 | Bheramara(GK) | 70 | 21:00 | 93 | Lalbag | 58 | 13:00 | 159 | Shariatpur | 93 | 21:00
28 | Bhulta | 239 | 18:00 | 94 | Lalmonirhat | 52 | 18:30 | 160 | Sherpur | 136 | 22:00
29 | Bog-Sherpur | 72 | 20:00 | 95 | MI_Cement | 14.1 | 15:00 | 161 | Shikalbaha | 30 | 19:00
30 | Bogura | 191 | 21:00 | 96 | Madanganj | 48 | 13:00 | 162 | Shitalakhya | 94.3 | 16:00
31 | Borhanuddin | 88 | 01:00 | 97 | Madaripur | 130 | 22:00 | 163 | Sholosohor | 46 | 15:00
32 | Brahmanbaria | 115 | 21:00 | 98 | Madartek | 100.25 | 23:00 | 164 | Shyampur | 186 | 01:00
33 | Cantonment | 164 | 15:00 | 99 | Madunaghat | 60 | 21:00 | 165 | Siddhirganj | 130 | 22:00
34 | Chandina | 24.33 | 20:00 | 100 | Magura | 74 | 21:00 | 166 | Sirajganj | 132 | 21:00
35 | Chandpur | 74 | 21:00 | 101 | Mahasthangarh | 94 | 20:00 | 167 | Sonargaon | 123 | 17:00
36 | Chandraghona | 37 | 20:00 | 102 | Manikganj | 147 | 19:00 | 168 | Sreemongol | 88 | 22:00
37 | Chapai | 74 | 21:00 | 103 | Maniknagar | 92 | 15:00 | 169 | Sreepur | 116 | 15:00
38 | Charsaidpur | 47 | 12:00 | 104 | Matarbari | 53 | 20:00 | 170 | Srinagar | 53 | 22:00
39 | Chauddagram | 82 | 20:00 | 105 | Matuail | 72 | 16:00 | 171 | Sunamganj | 60 | 23:00
40 | Chhatak | 42 | 23:00 | 106 | Millgate | 113 | 15:00 | 172 | Sylhet | 53 | 19:30
41 | Chowmuhani | 221 | 22:00 | 107 | Mirpur | 132 | 19:00 | 173 | Sylhet-132 | 136 | 20:00
42 | Chuadanga | 118 | 22:00 | 108 | Mirsorai | 12 | 15:00 | 174 | TK | 35.6 | 22:00
43 | Coxsbazar | 136 | 18:30 | 109 | Mirzapur | 47 | 19:30 | 175 | Tangail | 184 | 21:00
44 | Cumilla(N) | 162 | 19:00 | 110 | Mithapukur | 82 | 20:00 | 176 | Thakurgaon | 94 | 19:30
45 | Cumilla(S) | 190 | 19:30 | 111 | Modern | N/A | N/A | 177 | Tongi | 145 | 18:30
46 | Daudkandi | 160 | 22:00 | 112 | Mogbazar | 166 | 15:00 | 178 | Ullahpara | 44 | 21:00
47 | Dhaka | 74 | 13:00 | 113 | Mongla | 38 | 12:00 | 179 | Ullon | 45 | 21:00
48 | Dhamrai | 138 | 22:00 | 114 | Motijheel | 44 | 13:00 | 180 | Uttara | 92 | 19:00
49 | Dhanmondi | 163 | 13:00 | 115 | Muktagacha | 33 | 22:00 | 181 | UttaraNew | 68 | 23:00
50 | Dohazari | 83 | 21:00 | 116 | Munshiganj | 128 | 23:00 | 182 | Zigatola | 78 | 14:00
51 | Faridpur | 175 | 19:30 | 117 | Muradnagar | 31 | 23:00
52 | Fatullah | 106 | 16:00 | 118 | Mymensingh | 210 | 19:00
53 | Fenchuganj | 47 | 19:30 | 119 | Naogaon | 147 | 21:00
54 | Feni | 128 | 19:30 | 120 | Narail | 62 | 22:00
55 | GPH | 99 | 19:00 | 121 | Narinda | 88 | 13:00
56 | Ghatail | 84 | 19:00 | 122 | Narshingdi | 188 | 23:00
57 | Ghorashal | 16 | 23:00 | 123 | Natore | 168 | 22:00
58 | Ghorashal-230 | 105 | 23:00 | 124 | Nawabganj | 66 | 22:00
59 | Goalpara | 38 | 22:00 | 125 | Netrakona | 129 | 20:00
60 | Gollamari | 108 | 19:30 | 126 | New | 93 | 15:00
61 | Gopalganj | 116 | 22:00 | 127 | Niamatpur | 74 | 23:00
62 | Gulshan | 136 | 15:00 | 128 | Noapara | 51 | 20:00
63 | Halishahar | 77.5 | 15:00 | 129 | PHP | 5 | 16:00
64 | HaripurSBU | 185 | 12:00 | 130 | Pabna | 135 | 19:30
65 | Hasnabad | 75 | 21:00 | 131 | Palashbari | 118 | 21:00
66 | Hathazari | 89 | 21:00 | 132 | Panchagarh | 48 | 00:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 27-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14156.2 | 233 |  | 14399.69
1:00 | 13691.2 | 295 |  | 13999.2
2:00 | 13405.7 | 282 |  | 13700.7
3:00 | 13044.5 | 244 |  | 13299.5
4:00 | 12902.5 | 237 |  | 13150.5
5:00 | 12706.5 | 223 |  | 12939.5
6:00 | 12346.28 | 197 |  | 12552.28
7:00 | 12359.91 | 156 |  | 12522.91
8:00 | 12392.76 | 143 |  | 12541.76
9:00 | 12787.02 | 96 |  | 12887.02
10:00 | 13235.83 | 74 |  | 13312.83
11:00 | 13592.79 | 59 |  | 13654.79
12:00 | 14147.6 | 83 |  | 14234.6
13:00 | 14446.59 | 112 |  | 14563.59
14:00 | 14638.06 | 119 |  | 14762.06
15:00 | 14800.69 | 166 |  | 14973.69
16:00 | 14758.67 | 158 |  | 14923.67
17:00 | 14541.04 | 176 |  | 14725.04
18:00 | 13993.13 | 124 |  | 14123.13
19:00 | 15006.59 | 329 |  | 15350.59
19:30 | 15622.26 | 430 |  | 16071.26
20:00 | 15689.66 | 413 |  | 16121.66
21:00 | 16023.29 | 380 |  | 16420.29
22:00 | 15872.71 | 457 |  | 16350.71
23:00 | 15768.99 | 509 |  | 16300.99
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 27-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7382 | 6774.2 | 14156.2 | DAILY GENERATION CURVE
00:30 | 7157 | 6766.7 | 13923.7
01:00 | 6932 | 6759.2 | 13691.2 | 27-05-2025
01:30 | 6904.75 | 6643.7 | 13548.45
02:00 | 6877.5 | 6528.2 | 13405.7
02:30 | 6856 | 6369.1 | 13225.1
03:00 | 6834.5 | 6210 | 13044.5
03:30 | 6779 | 6194.5 | 12973.5
04:00 | 6723.5 | 6179 | 12902.5
04:30 | 6687.5 | 6117 | 12804.5
05:00 | 6651.5 | 6055 | 12706.5
05:30 | 6630.095 | 5896.295 | 12526.39
06:00 | 6608.69 | 5737.59 | 12346.28
06:30 | 6606.795 | 5746.3 | 12353.095
07:00 | 6604.9 | 5755.01 | 12359.91
07:30 | 6568.11 | 5808.225 | 12376.335
08:00 | 6531.32 | 5861.44 | 12392.76
08:30 | 6656.82 | 5933.07 | 12589.89
09:00 | 6782.32 | 6004.7 | 12787.02
09:30 | 6920.345 | 6091.08 | 13011.425
10:00 | 7058.37 | 6177.46 | 13235.83
10:30 | 7177.51 | 6236.8 | 13414.31
11:00 | 7296.65 | 6296.14 | 13592.79
11:30 | 7535.455 | 6334.74 | 13870.195
12:00 | 7774.26 | 6373.34 | 14147.6
12:30 | 7877.84 | 6419.255 | 14297.095
13:00 | 7981.42 | 6465.17 | 14446.59
13:30 | 8035.485 | 6506.84 | 14542.325
14:00 | 8089.55 | 6548.51 | 14638.06
14:30 | 8159.56 | 6559.815 | 14719.375
15:00 | 8229.57 | 6571.12 | 14800.69
15:30 | 8205.48 | 6574.2 | 14779.68
16:00 | 8181.39 | 6577.28 | 14758.67
16:30 | 8121.375 | 6528.48 | 14649.855
17:00 | 8061.36 | 6479.68 | 14541.04
17:30 | 7941.765 | 6325.32 | 14267.085
18:00 | 7822.17 | 6170.96 | 13993.13
18:30 | 8155.835 | 6344.025 | 14499.86
19:00 | 8489.5 | 6517.09 | 15006.59
19:30 | 8936.5 | 6685.76 | 15622.26
20:00 | 8964 | 6725.66 | 15689.66
20:30 | 9092.5 | 6763.975 | 15856.475 |  | Executive Engineer
21:00 | 9221 | 6802.29 | 16023.29 |  | Network Operation Division
21:30 | 9110.5 | 6837.5 | 15948
22:00 | 9000 | 6872.71 | 15872.71
22:30 | 8908.5 | 6912.35 | 15820.85
23:00 | 8817 | 6951.99 | 15768.99

## En-Curve
QF-LDC-12
Date | 27-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3596 | 1836 | 881 | 0 | 40 | 1449 | 40 | 5013.2 | 0 | 289 | 1007 | 0 | 0 | 5 | 233 | DAILY ENERGY CURVE
00:30 | 3536.5 | 1821 | 880.5 | 0 | 38 | 1449 | 40 | 5009.7 | 0 | 215 | 927.5 | 0 | 0 | 6.5 | 264 | 27-05-2025
01:00 | 3477 | 1806 | 880 | 0 | 36 | 1449 | 40 | 5006.2 | 0 | 141 | 848 | 0 | 0 | 8 | 295
01:30 | 3452.5 | 1791.75 | 904 | 0 | 38 | 1450.5 | 39 | 4925.2 | 0 | 141 | 802.5 | 0 | 0 | 4 | 288.5 | Energy Generated | 341.3952 |  | MKWHr
02:00 | 3428 | 1777.5 | 928 | 0 | 40 | 1452 | 38 | 4844.2 | 0 | 141 | 757 | 0 | 0 | 0 | 282 | Energy not Served | 5.265 |  | MKWHr
02:30 | 3385 | 1787.5 | 928 | 0 | 39 | 1384 | 37.5 | 4776.1 | 0 | 141 | 747 | 0 | 0 | 0 | 263 | Total Energy Requirement | 346.6602 |  | MKWHr
03:00 | 3342 | 1797.5 | 928 | 0 | 38 | 1316 | 37 | 4708 | 0 | 141 | 737 | 0 | 0 | 0 | 244
03:30 | 3310.5 | 1801.5 | 928 | 0 | 38 | 1317 | 37 | 4692 | 0 | 141 | 708.5 | 0 | 0 | 0 | 240.5
04:00 | 3279 | 1805.5 | 928 | 0 | 38 | 1318 | 37 | 4676 | 0 | 141 | 680 | 0 | 0 | 0 | 237
04:30 | 3256 | 1798 | 928 | 0 | 35 | 1318 | 38 | 4617.5 | 0 | 141 | 673 | 0 | 0 | 0 | 230
05:00 | 3233 | 1790.5 | 928 | 0 | 32 | 1318 | 39 | 4559 | 0 | 141 | 666 | 0 | 0 | 0 | 223
05:30 | 3251 | 1787 | 928 | 0 | 34 | 1262 | 39.5 | 4379.5 | 17.39 | 195 | 633 | 0 | 0 | 0 | 210
06:00 | 3269 | 1783.5 | 928 | 0 | 36 | 1206 | 40 | 4200 | 34.78 | 249 | 600 | 0 | 0 | 0 | 197
06:30 | 3304.5 | 1788 | 928 | 0 | 34 | 1213 | 40 | 4150.5 | 76.095 | 237 | 582 | 0 | 0 | 0 | 176.5
07:00 | 3340 | 1792.5 | 928 | 0 | 32 | 1220 | 40 | 4101 | 117.41 | 225 | 564 | 0 | 0 | 0 | 156
07:30 | 3327 | 1783.25 | 904.5 | 0 | 32 | 1225.5 | 40 | 4095.5 | 199.585 | 220 | 549 | 0 | 0 | 0 | 149.5
08:00 | 3314 | 1774 | 881 | 0 | 32 | 1231 | 40 | 4090 | 281.76 | 215 | 534 | 0 | 0 | 0 | 143
08:30 | 3363.5 | 1780 | 881 | 0 | 30 | 1229.5 | 40 | 4090 | 378.89 | 235.5 | 561.5 | 0 | 0 | 0 | 119.5
09:00 | 3413 | 1786 | 881 | 0 | 28 | 1228 | 40 | 4090 | 476.02 | 256 | 589 | 0 | 0 | 0 | 96
09:30 | 3411 | 1791 | 905 | 0 | 31 | 1208 | 40 | 4202.5 | 526.425 | 270.5 | 626 | 0 | 0 | 0 | 85
10:00 | 3409 | 1796 | 929 | 0 | 34 | 1188 | 40 | 4315 | 576.83 | 285 | 663 | 0 | 0 | 0 | 74
10:30 | 3412.5 | 1810 | 929 | 0 | 36 | 1178 | 40 | 4344 | 608.81 | 293 | 762.5 | 0 | 0 | 0.5 | 66.5
11:00 | 3416 | 1824 | 929 | 0 | 38 | 1168 | 40 | 4373 | 640.79 | 301 | 862 | 0 | 0 | 1 | 59
11:30 | 3480 | 1811.75 | 929 | 0 | 38 | 1163.5 | 40 | 4421 | 611.445 | 301 | 1074 | 0 | 0 | 0.5 | 71
12:00 | 3544 | 1799.5 | 929 | 0 | 38 | 1159 | 40 | 4469 | 582.1 | 301 | 1286 | 0 | 0 | 0 | 83
12:30 | 3621 | 1807.5 | 929 | 0 | 40 | 1062.5 | 39 | 4510.5 | 590.095 | 312 | 1385.5 | 0 | 0 | 0 | 97.5
13:00 | 3698 | 1815.5 | 929 | 0 | 42 | 966 | 38 | 4552 | 598.09 | 323 | 1485 | 0 | 0 | 0 | 112
13:30 | 3602.5 | 1752.25 | 929 | 0 | 43 | 970.42 | 37 | 4634 | 589.655 | 341.5 | 1641.5 | 0 | 0 | 1.5 | 115.5
14:00 | 3507 | 1689 | 929 | 0 | 44 | 974.84 | 36 | 4716 | 581.22 | 360 | 1798 | 0 | 0 | 3 | 119
14:30 | 3585.5 | 1691.9 | 929 | 0 | 45 | 973.02 | 35 | 4733.5 | 515.955 | 367.5 | 1836.5 | 0 | 0 | 6.5 | 142.5
15:00 | 3664 | 1694.8 | 929 | 0 | 46 | 971.2 | 34 | 4751 | 450.69 | 375 | 1875 | 0 | 0 | 10 | 166
15:30 | 3607 | 1735.3 | 929 | 0 | 44 | 969.135 | 34.5 | 4790.5 | 365.745 | 375 | 1917 | 0 | 0 | 12.5 | 162
16:00 | 3550 | 1775.8 | 929 | 0 | 42 | 967.07 | 35 | 4830 | 280.8 | 375 | 1959 | 0 | 0 | 15 | 158
16:30 | 3483.5 | 1773.15 | 928.5 | 0 | 43 | 970.53 | 36 | 4817.5 | 223.675 | 367 | 1989 | 0 | 0 | 18 | 167
17:00 | 3417 | 1770.5 | 928 | 0 | 44 | 973.99 | 37 | 4805 | 166.55 | 359 | 2019 | 0 | 0 | 21 | 176
17:30 | 3331 | 1745 | 928.5 | 0 | 42 | 965.55 | 37.5 | 4711 | 101.035 | 373 | 2021 | 0 | 0 | 11.5 | 150
18:00 | 3245 | 1719.5 | 929 | 0 | 40 | 957.11 | 38 | 4617 | 35.52 | 387 | 2023 | 0 | 0 | 2 | 124
18:30 | 3367.5 | 1719.5 | 905 | 0 | 44 | 964.6 | 39 | 4725.5 | 17.76 | 533.5 | 2182.5 | 0 | 0 | 1 | 226.5
19:00 | 3490 | 1719.5 | 881 | 0 | 48 | 972.09 | 40 | 4834 | 0 | 680 | 2342 | 0 | 0 | 0 | 329
19:30 | 3534 | 1771.8 | 881 | 0 | 48 | 958.76 | 40 | 4874 | 0 | 729 | 2782.7 | 0 | 0 | 3 | 430
20:00 | 3429 | 1758.8 | 881 | 0 | 46 | 958.66 | 40 | 4897 | 0 | 735 | 2943.2 | 0 | 0 | 1 | 413
20:30 | 3439 | 1785.8 | 831.5 | 0 | 45 | 958.975 | 40 | 4945.5 | 0 | 749 | 3056.2 | 0 | 0 | 5.5 | 396.5
21:00 | 3449 | 1812.8 | 782 | 0 | 44 | 959.29 | 40 | 4994 | 0 | 763 | 3169.2 | 0 | 0 | 10 | 380
21:30 | 3396 | 1809.8 | 782 | 0 | 46 | 963.5 | 40 | 5047 | 0 | 711 | 3122.2 | 0 | 0 | 30.5 | 418.5
22:00 | 3343 | 1806.8 | 782 | 0 | 48 | 967.71 | 40 | 5100 | 0 | 659 | 3075.2 | 0 | 0 | 51 | 457
22:30 | 3279.5 | 1817.3 | 782 | 0 | 48 | 992.25 | 40 | 5098.1 | 0 | 637 | 3073.7 | 0 | 0 | 53 | 483
23:00 | 3216 | 1827.8 | 782 | 0 | 48 | 1016.79 | 40 | 5096.2 | 0 | 615 | 3072.2 | 0 | 0 | 55 | 509
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 27-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 380 | 06:00 | 364 | 19:30 | Payra | 413 | 06:00 | 406 | 00:00
Ashuganj | 395 | 5:00 | 363 | 12:00 | Rahanpur | 402 | 10:00 | 381 | 12:00
Bhulta | 388 | 05:00 | 360 | 15:00 | Rampal | 400 | 07:00 | 382 | 21:00
Bibiana | 389 | 05:00 | 379 | 11:00
BIPTC | 401 | 07:00 | 393 | 20:00
Bogura | 391 | 09:00 | 374 | 12:00
Gopalganj | 394 | 06:00 | 377 | 22:00
Kaliakoir | 371 | 06:00 | 357 | 10:00
Madunaghat | 398 | 21:00 | 382 | 11:00
Meghnaghat | 381 | 05:00 | 369 | 15:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 221 | 06:00 | 210 | 11:00 | Keranigonj | 219 | 06:00 | 208 | 11:00
AKSML | 232 | 20:00 | 219 | 11:00 | Khulna(S) | 229 | 06:00 | 210 | 22:00
Aminbazar | 220 | 05:00 | 212 | 10:00 | Madunaghat | 235 | 20:00 | 223 | 00:00
Ashuganj | 225 | 05:00 | 215 | 11:00 | Madunaghat-400 | 234 | 21:00 | 224 | 02:00
Ashuganj-400 | 225 | 05:00 | 215 | 11:00 | Maniknagar | 216 | 05:00 | 208 | 11:00
Baghabari | 231 | 05:00 | 222 | 11:00 | Meghnaghat | 226 | 06:00 | 218 | 10:00
Barapukuria | 222 | 09:00 | 214 | 02:00 | Meghnaghat-400 | 219 | 04:00 | 213 | 11:00
Barapukuria-230 | 222 | 09:00 | 214 | 02:00 | Mirsorai | 231 | 21:00 | 214 | 13:00
Barishal | 235 | 07:00 | 225 | 22:00 | Rajshahi | 234 | 06:00 | 221 | 12:00
Bheramara | 234 | 05:00 | 222 | 12:00 | Rampal | 228 | 06:00 | 212 | 21:00
Bhulta | 226 | 05:00 | 207 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 224 | 18:30 | 217 | 09:00 | Rampura | 226 | 05:00 | 205 | 15:00
BIPTC | 236 | 06:00 | 222 | 12:00 | Shikalbaha | 234 | 20:00 | 220 | 11:00
Bogura | 226 | 09:00 | 217 | 00:00 | Shyampur | 219 | 06:00 | 210 | 10:00
Bogura-400 | 226 | 09:00 | 217 | 00:00 | Siddhirganj | 218 | 05:00 | 211 | 12:00
Borhanuddin | 239 | 06:00 | 232 | 21:00 | Sirajgonj | 234 | 07:00 | 229 | 12:00
BSRM | 228 | 20:00 | 215 | 12:00 | Sreepur | 225 | 06:00 | 214 | 15:00
Cumilla(N) | 219 | 05:00 | 210 | 11:00 | Tongi | 217 | 04:00 | 206 | 11:00
Faridpur | 231 | 06:00 | 219 | 21:00
Fenchuganj | 224 | 06:00 | 215 | 14:00
Ghorashal | 220 | 00:00 | 212 | 11:00
Ghorashal-230 | 224 | 06:00 | 208 | 11:00
Gopalganj | 232 | 06:00 | 222 | 22:00
GPH | 230 | 20:00 | 218 | 12:00
Haripur | 218 | 06:00 | 210 | 11:00
Hasnabad | 218 | 06:00 | 209 | 11:00
Hathazari | 234 | 20:00 | 223 | 13:00
Ishurdi | 235 | 05:00 | 224 | 12:00
Jhenaidah | 230 | 06:00 | 212 | 21:00
Kaliakoir | 227 | 06:00 | 216 | 10:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 04:00 | 123 | 15:00 | Madartek | 139 | 05:00 | 124 | 15:00
Agargaon | 133 | 05:00 | 124 | 11:00 | Madunaghat | 135 | 19:00 | 125 | 01:00
Agrabad | 134 | 19:00 | 124 | 11:00 | Magura | 135 | 06:00 | 118 | 19:30
AKS | 132 | 19:00 | 124 | 00:00 | Mahasthangarh | 131 | 09:00 | 124 | 00:00
Aminbazar | 129 | 03:00 | 123 | 10:00 | Manikganj | 129 | 06:00 | 120 | 11:00
Amnura | 136 | 22:00 | 123 | 12:00 | Maniknagar | 131 | 06:00 | 123 | 11:00
Ashuganj | 134 | 05:00 | 130 | 00:00 | Matarbari | 127 | 19:00 | 108 | 12:00
Bagerhat | 130 | 06:00 | 114 | 21:00 | Matuail | 126.5 | 06:00 | 121 | 10:00
Bajitpur | 128 | 06:00 | 119 | 10:00 | Millgate | 133 | 04:00 | 122 | 11:00
Bakulia | 135 | 22:00 | 125 | 12:00 | Mirpur | 128 | 04:00 | 121 | 16:00
Banani | 139 | 04:00 | 123 | 15:00 | Mirzapur | 131 | 04:00 | 126 | 19:30
Bangabhaban | 131 | 06:00 | 123 | 12:00 | Mithapukur | 129 | 09:00 | 121 | 00:00
Barapukuria | 135 | 09:00 | 126 | 00:00 | MI_Cement | 128 | 20:00 | 122 | 10:00
Barguna | 133 | 06:00 | 128 | 21:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 07:00 | 121 | 22:00 | Mogbazar | 138 | 05:00 | 124 | 15:00
Barishal-230 | 131 | 07:00 | 122 | 22:00 | Mongla | 131 | 08:00 | 116 | 19:30
Baroaulia | 133 | 19:30 | 126 | 12:00 | Motijheel | 131 | 06:00 | 123 | 12:00
Baroirhat | 125 | 19:30 | 116 | 14:00 | Muktagacha | 134 | 09:00 | 125 | 01:00
Bashundhara | 139 | 04:00 | 122 | 11:00 | Munshiganj | 127 | 20:00 | 120 | 11:00
BashundharaCement | 127 | 20:00 | 121 | 10:00 | Muradnagar | 123 | 06:00 | 117 | 11:00
Beanibazar | 128 | 00:00 | 119 | 11:00 | Mymensingh | 135 | 09:00 | 109 | 21:00
Benapole | 131 | 07:00 | 114 | 21:00 | Naogaon | 129 | 06:00 | 121 | 00:00
Bhaluka | 131 | 06:00 | 119 | 15:00 | Narail | 136 | 06:00 | 118 | 21:00
Bhandaria | 125 | 09:00 | 112 | 22:00 | Narinda | 0 | 00:00 | N/A | N/A
Bhangura | 131 | 05:00 | 126 | 12:00 | Narshingdi | 130 | 01:00 | 109 | 14:00
Bheramara | 136 | 05:00 | 129 | 19:30 | Natore | 134 | 08:00 | 127 | 00:00
Bheramara(GK) | 137 | 07:00 | 129 | 15:00 | Nawabganj | 131 | 04:00 | 123 | 11:00
Bhulta | 120 | 05:00 | 116 | 11:00 | Netrakona | 124 | 06:00 | 108 | 21:00
Bog-Sherpur | 131 | 08:00 | 125 | 00:00 | New | 134 | 05:00 | 123 | 11:00
Bogura | 134 | 09:00 | 128 | 00:00 | Niamatpur | 133 | 06:00 | 126 | 12:00
Bogura-230 | 133 | 06:00 | 127 | 00:00 | Noapara | 135 | 05:00 | 118 | 21:00
Brahmanbaria | 123 | 05:00 | 115 | 15:00 | Pabna | 134 | 06:00 | 126 | 19:30
Cantonment | 133 | 06:00 | 123 | 15:00 | Palashbari | 127 | 09:00 | 119 | 00:00
Chandina | 125 | 06:00 | 119 | 11:00 | Panchagarh | 137 | 18:00 | 122 | 07:00
Chandpur | 128 | 19:00 | 119 | 11:00 | Patuakhali | 133 | 06:00 | 129 | 23:00
Chandraghona | 133 | 19:00 | 125 | 13:00 | Payra | 136 | 07:00 | 132 | 21:00
Chapai | 131 | 06:00 | 122 | 12:00 | PHP | 123 | 19:00 | 115 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 135 | 08:00 | 122 | 10:00 | Postogola | 130 | 06:00 | 124 | 10:00
Chauddagram | 122 | 19:00 | 115 | 14:00 | Purbachal | 140 | 04:00 | 122 | 15:00
Chhatak | 127 | 06:00 | 115 | 11:00 | Purbasadipur | 132 | 21:00 | 122 | 08:00
Chowmuhani | 121 | 19:00 | 109 | 14:00 | Rahanpur | 134 | 05:00 | 127 | 12:00
Chuadanga | 131 | 05:00 | 116 | 19:30 | Rahanpur-400 | 134 | 06:00 | 127 | 12:00
Coxsbazar | 125 | 19:00 | 108 | 12:00 | Rahim | 126 | 00:00 | 122 | 12:00
Cumilla(N) | 126 | 05:00 | 120 | 11:00 | Rajbari | 133 | 06:00 | 124 | 21:00
Cumilla(S) | 132 | 04:00 | 118 | 11:00 | Rajendrapur | 129 | 05:00 | 116 | 11:00
Daudkandi | 121 | 05:00 | 116 | 00:00 | Rajshahi | 135 | 06:00 | 127 | 12:00
Dhaka | 139 | 04:00 | 125 | 15:00 | Rajshahi-230 | 135 | 06:00 | 117 | 12:00
Dhamrai | 132 | 04:00 | 126 | 11:00 | Ramganj | 123 | 21:00 | 111 | 11:00
Dhanmondi | 139 | 05:00 | 124 | 15:00 | Rampur | 134 | 18:30 | 124 | 10:00
Dohazari | 134 | 19:00 | 121 | 12:00 | Rampura | 140 | 05:00 | 124 | 15:00
Faridpur | 135 | 06:00 | 126 | 23:00 | Rangamati | 132 | 19:00 | 124 | 13:00
Fatullah | 128 | 06:00 | 122 | 10:00 | Rangpur | 129 | 09:00 | 119 | 01:00
Fenchuganj | 133 | 06:00 | 128 | 19:00 | Ruppur | 137 | 07:00 | 130 | 00:00
Feni | 123 | 19:00 | 116 | 11:00 | Saidpur | 131 | 18:00 | 123 | 07:00
Ghatail | 131 | 07:00 | 124 | 16:00 | Satkhira | 130 | 05:00 | 113 | 21:00
Ghorashal | 133 | 05:00 | 125 | 09:00 | Satmasjid | 133 | 06:00 | 123 | 13:00
Goalpara | 136 | 06:00 | 122 | 19:30 | Savar | 128 | 20:00 | 121 | 10:00
Gollamari | 135 | 05:00 | 122 | 21:00 | SevenRings | 133 | 04:00 | 123 | 11:00
Gopalganj | 134 | 06:00 | 122 | 21:00 | ShahCement | 127 | 04:00 | 122 | 10:00
Gopalganj-400 | 135 | 06:00 | 128 | 21:00 | Shahjadpur | 135 | 03:00 | 130 | 00:00
Gulshan | 138 | 05:00 | 124 | 15:00 | Shahjibazar | 127 | 06:00 | 117 | 15:00
Halishahar | 135 | 19:00 | 123 | 12:00 | Shahmirpur | 135 | 19:00 | 126 | 00:00
Haripur | 127 | 06:00 | 122 | 10:00 | Shariatpur | 133 | 06:00 | 124 | 20:00
HaripurSBU | 127 | 20:00 | 122 | 10:00 | Sherpur | 137 | 23:00 | 125 | 02:00
Hasnabad | 130 | 03:00 | 124 | 10:00 | Shikalbaha | 124 | 18:30 | 115 | 01:00
Hathazari | 135 | 19:30 | 128 | 15:00 | Shikalbaha-230 | 137 | 19:00 | 126 | 11:00
Ishurdi | 138 | 06:00 | 130 | 19:30 | Shitalakhya | 128 | 20:00 | 122 | 10:00
Jaldhaka | 129 | 09:00 | 121 | 08:00 | Sholosohor | 133 | 23:00 | 124 | 12:00
Jamalpur | 140 | 23:00 | 125 | 02:00 | Shyampur | 127 | 19:00 | 122 | 10:00
Jashore | 133 | 06:00 | 115 | 19:30 | Shyampur-230 | 127 | 05:00 | 121 | 11:00
Jhenaidah | 136 | 06:00 | 118 | 19:30 | Siddhirganj | 127 | 06:00 | 122 | 11:00
Jhenaidah-230 | 136 | 06:00 | 122 | 19:30 | Sirajganj | 130 | 03:00 | 124 | 00:00
Joydebpur | 130 | 05:00 | 120 | 15:00 | Sonargaon | 125 | 20:00 | 119 | 11:00
Joypurhat | 129 | 09:00 | 120 | 00:00 | Sreemongol | 126 | 04:00 | 120 | 11:00
Juldah | 137 | 19:00 | 126 | 10:00 | Sreepur | 131 | 06:00 | 123 | 15:00
Kabirpur | 133 | 01:00 | 120 | 15:00 | Srinagar | 131 | 05:00 | 123 | 11:00
Kachua | 126 | 19:00 | 118 | 11:00 | SSM | 138 | 19:00 | 129 | 12:00
Kaliakoir | 136 | 05:00 | 129 | 12:00 | Sunamganj | 126 | 06:00 | 114 | 11:00
Kallyanpur | 129 | 01:00 | 123 | 09:00 | Sylhet | 128 | 00:00 | 119 | 11:00
Kalurghat | 132 | 20:00 | 125 | 00:00 | Sylhet-132 | 129 | 06:00 | 120 | 11:00
Kamrangirchar | 131 | 05:00 | 122 | 10:00 | Tangail | 129 | 05:00 | 122 | 19:30
Kaptai | 135 | 20:00 | 128 | 11:00 | Thakurgaon | 137 | 18:00 | 119 | 07:00
Kasba | 123 | 05:00 | 117 | 11:00 | TK | 132 | 19:00 | 125 | 00:00
Kazla | 130 | 05:00 | 122 | 13:00 | Tongi | 135 | 04:00 | 125 | 15:00
Keranigonj | 131 | 06:00 | 123 | 11:00 | Ullahpara | 132 | 05:00 | 126 | 00:00
Khagrachori | 131 | 19:00 | 123 | 10:00 | Ullon | 138 | 04:00 | 124 | 15:00
Khulna | 134 | 06:00 | 120 | 21:00 | Uttara | 135 | 4:00 | 121 | 10:00
Khulna(S) | 136 | 06:00 | 123 | 19:30 | UttaraNew | 128 | 05:00 | 121 | 10:00
Khulshi | 133 | 19:00 | 123 | 12:00 | Zigatola | 131 | 07:00 | 123 | 11:00
Kishoreganj | 128 | 06:00 | 117 | 21:00
Kodda | 131 | 04:00 | 119 | 11:00
KSRM | 135 | 19:00 | 125 | 11:00
Kulaura | 131 | 03:00 | 126 | 10:00
Kurigram | 130 | 09:00 | 118 | 00:00
Kushtia | 133 | 07:00 | 122 | 19:30
Lalbag | 130 | 05:00 | 122 | 12:00
Lalmonirhat | 129 | 09:00 | 120 | 00:00
Madanganj | 127 | 20:00 | 121 | 10:00
Madaripur | 134 | 06:00 | 126 | 19:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division