## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [6 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [6 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 28-05-2025 | [28 empty] | Date: | 28-05-2025 | [28 empty] | Date: | 28-05-2025 | [28 empty] | Date: | 28-05-2025 | [28 empty] | Date: | 28-05-2025 | [15 empty] | Date: | 28-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [28 empty] | Day: | Wednesday | [15 empty] | Day: | Wednesday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 8 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 54 | 17 | 125 | 79 | 145 | 55 | 35 | 162 | 52 | 330 | 305 | 250 | 0 | 17 | 0 | 300 | 0 | 0 | 0 | 52 | 17 | 17 | 0 | 0 | 116 | 230 | 63 | 0 | 19 | 50 | 55 | 54.36 | 100 | 88 | 0 | 40 | 110 | 30 | 575 | 160 | 0 | 32 | 17 | 90 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 117 | 16 | 0 | 343 | 335 | 50 | 212 | 30 | 93 | 81 | 200 | 13 | 14 | 114 | 42 | 52.2 | 0 | 46 | 310 | 15 | 386 | 40 | 0 | 0 | 153 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 35 | 27 | 112 | 0 | 0 | 0 | 12 | 8769.56 | 782 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 54 | 1017.51 | 0 | 48 | 0 | 113 | 16 | 95 | 113 | 30 | 43 | 0 | 30 | 0 | 143 | 0 | 129 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 160 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 120 | 220 | 0 | 302 | 1244 | 0 | 6981.71 | 15751.27 | 76.99
01:00 | 8 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 54 | 17 | 129 | 47 | 145 | 55 | 35 | 162 | 52 | 330 | 270 | 250 | 0 | 17 | 0 | 267 | 0 | 0 | 0 | 17 | 17 | 16 | 0 | 0 | 72 | 230 | 63 | 0 | 29 | 50 | 55 | 17 | 100 | 100 | 0 | 40 | 110 | 30 | 575 | 72 | 0 | 33 | 17 | 90 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 118 | 16 | 0 | 354 | 335 | 50 | 217 | 30 | 94 | 81 | 200 | 13 | 14 | 114 | 40 | 52.2 | 0 | 46 | 305 | 100 | 348 | 40 | 0 | 0 | 149 | 0 | 0 | 80 | 0 | 0 | 0 | 101 | 19 | 28 | 112 | 0 | 0 | 0 | 12 | 8469.2 | 923 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 70 | 1016.41 | 0 | 48 | 0 | 113 | 13 | 87 | 113 | 30 | 43 | 0 | 30 | 0 | 142 | 0 | 129 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 161 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 110 | 220 | 0 | 297 | 1244 | 0 | 7004.61 | 15473.81 | 77.02
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 54 | 17 | 129 | 47 | 45 | 15 | 35 | 162 | 52 | 330 | 290 | 250 | 0 | 17 | 0 | 290 | 0 | 0 | 0 | 17 | 18 | 16 | 0 | 0 | 17 | 230 | 0 | 0 | 31 | 34 | 55 | 0 | 100 | 100 | 0 | 40 | 51 | 30 | 575 | 0 | 0 | 33 | 8 | 51 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 108 | 8 | 0 | 353 | 330 | 51 | 215 | 30 | 93 | 86 | 200 | 9 | 14 | 114 | 38 | 52.2 | 0 | 46 | 295 | 208 | 342 | 40 | 0 | 0 | 135 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 17 | 28 | 112 | 0 | 0 | 0 | 12 | 8094.2 | 923 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 70 | 1023.01 | 0 | 48 | 0 | 113 | 10 | 0 | 35 | 30 | 0 | 0 | 30 | 0 | 142 | 0 | 136 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 163 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 100 | 220 | 0 | 299 | 1244 | 0 | 6749.21 | 14843.41 | 77.05
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 54 | 17 | 129 | 47 | 45 | 0 | 35 | 162 | 34 | 330 | 291 | 250 | 0 | 17 | 0 | 272 | 0 | 0 | 0 | 17 | 18 | 16 | 0 | 0 | 17 | 230 | 0 | 0 | 37 | 34 | 55 | 0 | 100 | 48 | 0 | 39 | 17 | 32 | 575 | 0 | 0 | 33 | 8 | 51 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 110 | 8 | 0 | 353 | 335 | 51 | 195 | 30 | 94 | 90 | 200 | 9 | 15 | 114 | 38 | 52.2 | 0 | 46 | 300 | 208 | 313 | 39 | 0 | 0 | 131 | 0 | 0 | 81 | 0 | 0 | 0 | 100 | 17 | 28 | 112 | 0 | 0 | 0 | 12 | 7926.2 | 923 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 34 | 1022.89 | 0 | 48 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 145 | 0 | 144 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 164 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 100 | 220 | 0 | 299 | 1244 | 0 | 6651.09 | 14577.29 | 77.08
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 54 | 17 | 129 | 47 | 45 | 0 | 35 | 162 | 34 | 330 | 299 | 250 | 0 | 17 | 0 | 293 | 0 | 0 | 0 | 17 | 18.5 | 16 | 0 | 0 | 17 | 30 | 0 | 0 | 46 | 25 | 55 | 0 | 90 | 24 | 0 | 38 | 17 | 32 | 575 | 0 | 0 | 19 | 8 | 17 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 112 | 8 | 0 | 352 | 335 | 52 | 199 | 30 | 93 | 90 | 200 | 9 | 15 | 114 | 38 | 52.2 | 0 | 46 | 300 | 208 | 321 | 39 | 0 | 0 | 131 | 0 | 0 | 81 | 0 | 0 | 0 | 100 | 17 | 28 | 112 | 0 | 0 | 0 | 12 | 7683.7 | 924 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 34 | 1023.02 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 150 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 163 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 100 | 220 | 0 | 300 | 1244 | 0 | 6584.22 | 14267.92 | 77.11
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 17 | 129 | 47 | 45 | 0 | 35 | 162 | 34 | 330 | 277 | 250 | 0 | 17 | 0 | 266 | 0 | 0 | 0 | 17 | 18.5 | 16 | 0 | 0 | 17 | 30 | 0 | 0 | 35 | 16 | 55 | 0 | 90 | 24 | 0 | 38 | 17 | 32 | 575 | 0 | 0 | 19 | 8 | 17 | 184 | 0 | 0 | 0 | 1224 | 0 | 51 | 112 | 8 | 0 | 340 | 335 | 51 | 182 | 30 | 92 | 90 | 200 | 9 | 15 | 114 | 36 | 52.2 | 0 | 46 | 305 | 208 | 300 | 39 | 0 | 0 | 135 | 0 | 0 | 81 | 0 | 0 | 0 | 100 | 17 | 28 | 112 | 0 | 0 | 0 | 12 | 7576.7 | 924 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 35 | 1016.98 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 151 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 132 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 11 | 100 | 180 | 0 | 296 | 1230 | 0 | 6448.18 | 14024.88 | 77.14
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 54 | 17 | 116 | 47 | 45 | 0 | 35 | 72 | 33 | 330 | 297 | 250 | 0 | 17 | 0 | 290 | 0 | 0 | 2 | 17 | 18.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 47 | 0 | 76 | 24 | 0 | 39 | 17 | 35 | 503 | 0 | 0 | 19 | 8 | 17 | 184 | 0 | 0 | 0 | 1150 | 0 | 51 | 60 | 8 | 0 | 330 | 335 | 52 | 200 | 30 | 93 | 90 | 155 | 9 | 14 | 114 | 36 | 52.2 | 0 | 16 | 300 | 208 | 321 | 39 | 0 | 0 | 136 | 0 | 0 | 81 | 0 | 0 | 0 | 100 | 17 | 28 | 111 | 0 | 0 | 1.99 | 12 | 7216.69 | 925 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.86 | 1167 | 0 | 1022.62 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.2 | 150 | 0 | 152 | 0 | 0 | 0 | 300 | 0 | 0.16 | 0 | 145 | 50 | 115 | 1 | 91 | 0 | 0 | 0.5 | 13 | 0.03 | 0 | 150 | 0 | 90 | 180 | 0 | 298 | 1120 | 0 | 6156.37 | 13373.06 | 77.17
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 54 | 17 | 104 | 47 | 45 | 0 | 35 | 72 | 16 | 330 | 289 | 250 | 0 | 17 | 0 | 267 | 0 | 0 | 11 | 17 | 18 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 16 | 47 | 0 | 76 | 24 | 0 | 40 | 17 | 32 | 505 | 0 | 0 | 19 | 8 | 17 | 184 | 0 | 0 | 0 | 1155 | 2 | 51 | 24 | 8 | 0 | 320 | 335 | 51 | 186 | 30 | 93 | 90 | 155 | 9 | 14 | 114 | 34 | 52.2 | 0 | 16 | 305 | 208 | 300 | 39 | 0 | 0 | 129 | 0 | 0 | 82 | 0 | 0 | 0 | 101 | 17 | 55 | 128 | 0 | 0 | 14.95 | 12 | 7138.15 | 924 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.55 | 1157 | 0 | 991.27 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 11.49 | 160 | 0 | 155 | 0 | 0 | 0 | 300 | 0 | 0.97 | 0 | 166 | 50 | 115 | 7 | 91 | 0 | 0 | 2.4 | 54 | 0.06 | 0 | 150 | 10 | 100 | 180 | 0 | 298 | 1100 | 0 | 6232.74 | 13370.89 | 77.2
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 29 | 17 | 103 | 47 | 30 | 0 | 35 | 35 | 16 | 330 | 289 | 250 | 0 | 17 | 0 | 290 | 0 | 0 | 9 | 17 | 16.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 16 | 15 | 0 | 36 | 12 | 1 | 40 | 0 | 7 | 505 | 0 | 0 | 19 | 8 | 0 | 184 | 0 | 0 | 0 | 1190 | 2 | 51 | 10 | 8 | 0 | 280 | 300 | 51 | 214 | 30 | 93 | 90 | 120 | 9 | 14 | 88 | 32 | 16 | 0 | 16 | 290 | 208 | 348 | 40 | 0 | 0 | 137 | 0 | 0 | 82 | 0 | 0 | 0 | 100 | 17 | 55 | 128 | 0 | 1 | 24.89 | 5 | 6853.39 | 878 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.75 | 1121 | 0 | 875.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 29.51 | 162 | 0 | 157 | 0 | 0 | 0 | 250 | 0 | 1.94 | 0 | 162 | 50 | 115 | 17 | 91 | 0 | 0 | 4.5 | 109 | 0.12 | 0 | 150 | 8 | 120 | 220 | 0 | 297 | 1045 | 0 | 6057.59 | 12910.98 | 77.23
09:00 | 0 | 70 | 15 | 0 | 0 | 0 | 0 | 0 | 369 | 0 | 0 | 17 | 17 | 103 | 47 | 30 | 0 | 35 | 35 | 16 | 330 | 296 | 250 | 0 | 17 | 0 | 300 | 0 | 0 | 29 | 17 | 16.5 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 16 | 0 | 36 | 12 | 1 | 40 | 0 | 2 | 502 | 0 | 0 | 19 | 8 | 0 | 184 | 0 | 0 | 0 | 1224 | 2 | 51 | 10 | 8 | 0 | 300 | 300 | 51 | 210 | 30 | 93 | 80 | 120 | 9 | 14 | 88 | 32 | 16 | 0 | 16 | 300 | 208 | 352 | 38 | 0 | 0 | 142 | 0 | 0 | 78 | 0 | 0 | 0 | 100 | 17 | 55 | 127 | 0 | 2 | 45.87 | 7 | 7021.37 | 877 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.79 | 1105 | 0 | 870.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 43.1 | 166 | 0 | 157 | 0 | 0 | 0 | 350 | 0 | 3.8 | 0 | 160 | 49 | 115 | 17 | 100 | 0 | 0 | 6.2 | 106 | 0.17 | 0 | 150 | 0 | 120 | 220 | 0 | 297 | 1042 | 0 | 6219.37 | 13240.74 | 77.26
10:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 17 | 17 | 103 | 47 | 97 | 0 | 35 | 72 | 16 | 330 | 289 | 250 | 0 | 17 | 0 | 270 | 0 | 0 | 20 | 17 | 16.5 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 16 | 16 | 0 | 36 | 12 | 1 | 40 | 0 | 5 | 503 | 0 | 0 | 19 | 8 | 0 | 184 | 0 | 0 | 0 | 1224 | 3 | 43 | 10 | 8 | 0 | 342 | 330 | 49 | 211 | 30 | 92 | 75 | 120 | 9 | 14 | 88 | 32 | 16 | 0 | 16 | 305 | 208 | 323 | 38 | 0 | 0 | 151 | 0 | 0 | 76 | 0 | 0 | 0 | 100 | 17 | 55 | 126 | 0 | 2 | 32.3 | 11 | 7131.8 | 924 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.45 | 1107 | 0 | 962.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 36.5 | 162 | 0 | 148 | 0 | 0 | 0 | 414 | 0 | 4.62 | 0 | 161 | 49 | 111 | 31 | 89 | 0 | 0 | 7.4 | 179 | 0.16 | 0 | 150 | 0 | 120 | 220 | 0 | 299 | 1045 | 0 | 6494.56 | 13626.36 | 77.29
11:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 17 | 17 | 114 | 47 | 278 | 0 | 35 | 105 | 16 | 330 | 305 | 250 | 0 | 17 | 0 | 303 | 0 | 0 | 17 | 45 | 15.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 16 | 16 | 0 | 36 | 12 | 4 | 40 | 0 | 2 | 575 | 0 | 0 | 19 | 8 | 0 | 186 | 0 | 0 | 0 | 1224 | 5 | 43 | 12 | 8 | 0 | 333 | 330 | 46 | 206 | 28 | 92 | 75 | 120 | 9 | 14 | 88 | 34 | 16 | 0 | 16 | 305 | 208 | 379 | 38 | 0 | 0 | 147 | 0 | 0 | 76 | 0 | 0 | 0 | 100 | 17 | 55 | 125 | 0 | 3 | 25.34 | 6 | 7554.94 | 924 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.74 | 1070 | 0 | 962.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 56.67 | 154 | 0 | 139 | 0 | 0 | 0 | 414 | 0 | 5.31 | 0 | 128 | 49 | 109 | 25 | 108 | 0 | 0 | 8 | 114 | 0.26 | 0 | 220 | 0 | 120 | 220 | 0 | 299 | 999 | 0 | 6392.03 | 13946.97 | 77.32
12:00 | 0 | 88 | 41 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 50 | 0 | 122 | 77 | 278 | 0 | 35 | 155 | 30 | 330 | 304 | 250 | 0 | 17 | 0 | 281 | 0 | 0 | 31 | 90 | 15.6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 16 | 16 | 0 | 63 | 34 | 2 | 40 | 0 | 2 | 575 | 26 | 0 | 19 | 12 | 0 | 185 | 0 | 0 | 0 | 1224 | 2 | 43 | 38 | 8 | 0 | 343 | 335 | 44 | 210 | 28 | 91 | 50 | 136 | 8 | 14 | 114 | 16 | 22 | 4 | 15 | 310 | 208 | 369 | 37 | 0 | 0 | 147 | 0 | 0 | 75 | 0 | 0 | 0 | 100 | 17 | 53 | 125 | 0 | 1 | 51.93 | 6 | 7845.53 | 924 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.88 | 1011 | 0 | 1007.42 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 84 | 0 | 35.35 | 151 | 0 | 134 | 0 | 0 | 0 | 414 | 0 | 3.11 | 0 | 130 | 48 | 109 | 36 | 113 | 0 | 0 | 8 | 160 | 0.27 | 0 | 250 | 0 | 120 | 220 | 0 | 297 | 1010 | 0 | 6478.03 | 14323.56 | 77.36
13:00 | 16 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 0 | 0 | 54 | 0 | 129 | 77 | 278 | 11 | 35 | 162 | 46 | 330 | 290 | 250 | 0 | 17 | 0 | 270 | 0 | 0 | 30 | 90 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 16 | 35 | 0 | 77 | 72 | 3 | 40 | 0 | 13 | 575 | 140 | 0 | 9 | 16 | 0 | 184 | 0 | 0 | 0 | 1224 | 0 | 43 | 92 | 8 | 0 | 340 | 335 | 43 | 209 | 29 | 76 | 30 | 173 | 9 | 14 | 114 | 30 | 52.2 | 39 | 28 | 300 | 208 | 304 | 37 | 0 | 0 | 142 | 0 | 0 | 75 | 0 | 0 | 0 | 100 | 17 | 53 | 116 | 0 | 2 | 48.04 | 6 | 8076.24 | 924 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.27 | 1008 | 0 | 1010.01 | 0 | 0 | 0 | 27 | 0 | 0 | 45 | 0 | 0 | 122 | 0 | 23.27 | 150 | 0 | 125 | 0 | 0 | 0 | 414 | 0 | 5.27 | 0 | 130 | 48 | 109 | 32 | 113 | 0 | 0 | 8 | 211 | 0.37 | 0 | 150 | 0 | 110 | 180 | 0 | 298 | 1102 | 0 | 6513.19 | 14589.43 | 77.4
14:00 | 16 | 88 | 40 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 47 | 0 | 129 | 77 | 278 | 45 | 35 | 162 | 50 | 330 | 284 | 250 | 0 | 17 | 0 | 268 | 0 | 0 | 10 | 90 | 15.6 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 16 | 60 | 0 | 76 | 100 | 2 | 38 | 0 | 3 | 506 | 160 | 0 | 18 | 16 | 0 | 184 | 0 | 0 | 0 | 1090 | 1 | 51 | 100 | 8 | 0 | 335 | 335 | 44 | 182 | 32 | 72 | 30 | 192 | 9 | 14 | 114 | 30 | 52.2 | 24 | 41 | 300 | 208 | 325 | 37 | 0 | 0 | 147 | 0 | 0 | 75 | 0 | 0 | 0 | 100 | 17 | 53 | 126 | 0 | 1 | 37.58 | 6 | 8003.38 | 923 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.82 | 954 | 0 | 1016 | 0 | 0 | 0 | 104 | 5 | 28 | 113 | 0 | 0 | 89 | 0 | 35.33 | 147 | 0 | 122 | 0 | 0 | 0 | 414 | 0 | 2.94 | 0 | 137 | 50 | 106 | 28 | 113 | 0 | 0 | 7.4 | 185 | 0.17 | 0 | 150 | 0 | 110 | 220 | 0 | 297 | 1050 | 0 | 6575.66 | 14579.04 | 77.44
15:00 | 16 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 51 | 0 | 129 | 77 | 278 | 55 | 35 | 162 | 50 | 300 | 287 | 250 | 0 | 17 | 0 | 275 | 0 | 0 | 17 | 90 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 16 | 60 | 0 | 88 | 100 | 2 | 37 | 0 | 3 | 503 | 160 | 0 | 0 | 16 | 0 | 184 | 0 | 0 | 0 | 1150 | 2 | 51 | 112 | 8 | 0 | 351 | 335 | 44 | 181 | 30 | 73 | 30 | 200 | 9 | 14 | 114 | 40 | 52.2 | 25 | 41 | 295 | 208 | 332 | 36 | 0 | 0 | 134 | 0 | 0 | 78 | 0 | 0 | 0 | 100 | 17 | 53 | 126 | 0 | 1 | 32.1 | 6 | 8086.3 | 924 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.21 | 1008 | 0 | 1013.44 | 0 | 0 | 0 | 113 | 5 | 50 | 113 | 0 | 0 | 47 | 0 | 20.1 | 143 | 0 | 122 | 0 | 0 | 0 | 414 | 0 | 1.63 | 0 | 160 | 50 | 107 | 24 | 113 | 0 | 0 | 6.2 | 161 | 0.14 | 0 | 150 | 0 | 120 | 220 | 0 | 298 | 1000 | 0 | 6548.72 | 14635.02 | 77.48
16:00 | 32 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 54 | 0 | 129 | 76 | 278 | 55 | 35 | 162 | 51 | 300 | 289 | 250 | 0 | 17 | 0 | 275 | 0 | 0 | 9 | 90 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 60 | 0 | 88 | 48 | 1 | 36 | 0 | 2 | 506 | 160 | 0 | 5 | 16 | 0 | 184 | 0 | 0 | 0 | 1100 | 1 | 51 | 50 | 8 | 0 | 347 | 300 | 49 | 208 | 30 | 83 | 30 | 200 | 9 | 5 | 114 | 36 | 52.2 | 14 | 41 | 300 | 208 | 330 | 38 | 0 | 0 | 130 | 0 | 0 | 81 | 0 | 0 | 0 | 102 | 17 | 53 | 126 | 0 | 1 | 17.97 | 6 | 7902.17 | 923 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.86 | 1008 | 0 | 1021.46 | 0 | 0 | 0 | 50 | 5 | 50 | 50 | 0 | 0 | 53 | 10 | 14.75 | 143 | 0 | 123 | 0 | 0 | 0 | 350 | 0 | 1.26 | 0 | 161 | 50 | 106 | 21 | 113 | 0 | 0 | 4.3 | 115 | 0.25 | 0 | 150 | 0 | 110 | 180 | 0 | 299 | 1000 | 0 | 6291.88 | 14194.05 | 77.52
17:00 | 50 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 34 | 5 | 129 | 76 | 278 | 55 | 35 | 126 | 51 | 300 | 291 | 250 | 0 | 17 | 0 | 281 | 0 | 0 | 3 | 90 | 13 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 16 | 69 | 0 | 48 | 24 | 0 | 35 | 0 | 7 | 450 | 53 | 0 | 15 | 16 | 0 | 184 | 0 | 0 | 0 | 1055 | 0 | 51 | 50 | 8 | 0 | 349 | 280 | 49 | 206 | 30 | 93 | 30 | 200 | 9 | 8 | 114 | 0 | 52.2 | 8 | 43 | 305 | 208 | 334 | 39 | 0 | 0 | 129 | 0 | 0 | 82 | 0 | 0 | 0 | 102 | 17 | 62 | 125 | 0 | 1 | 4.49 | 6 | 7568.69 | 923 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.72 | 915 | 0 | 1013.83 | 0 | 49 | 0 | 50 | 18 | 50 | 35 | 13 | 0 | 11 | 22 | 10.68 | 142 | 0 | 123 | 0 | 0 | 0 | 350 | 0 | 1.2 | 0 | 164 | 50 | 107 | 8 | 70 | 0 | 0 | 2.8 | 18 | 0.09 | 0 | 150 | 0 | 120 | 180 | 0 | 226 | 950 | 0 | 5909.32 | 13478.01 | 77.56
18:00 | 85 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 17 | 17 | 129 | 80 | 278 | 55 | 35 | 126 | 67 | 300 | 270 | 250 | 0 | 17 | 0 | 274 | 0 | 0 | 0 | 160 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 16 | 76 | 0 | 48 | 24 | 0 | 37 | 0 | 2 | 430 | 53 | 0 | 0 | 16 | 0 | 184 | 0 | 0 | 0 | 550 | 0 | 51 | 50 | 8 | 0 | 300 | 280 | 48 | 206 | 31 | 94 | 30 | 200 | 18 | 6 | 114 | 38 | 52.2 | 5 | 43 | 300 | 208 | 324 | 39 | 0 | 0 | 128 | 0 | 0 | 82 | 0 | 0 | 0 | 102 | 17 | 45 | 90 | 0 | 0 | 1.15 | 9 | 7037.35 | 923 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.89 | 914 | 0 | 1011.93 | 0 | 48 | 0 | 50 | 20 | 50 | 35 | 8 | 0 | 4 | 30 | 1.24 | 139 | 0 | 123 | 0 | 0 | 0 | 300 | 0 | 0.11 | 0 | 163 | 50 | 113 | 3 | 70 | 0 | 0 | 0.7 | 21 | 0.03 | 0 | 182 | 9 | 120 | 180 | 0 | 220 | 920 | 0 | 5834.9 | 12872.25 | 77.6
19:00 | 98 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 29 | 17 | 129 | 147 | 278 | 55 | 35 | 162 | 68 | 300 | 304 | 250 | 0 | 17 | 0 | 306 | 0 | 0 | 0 | 160 | 14.5 | 15 | 0 | 0 | 11 | 30 | 0 | 0 | 65 | 50 | 76 | 0 | 100 | 100 | 0 | 39 | 6 | 2 | 575 | 145 | 0 | 0 | 16 | 10 | 184 | 0 | 0 | 0 | 612 | 0 | 51 | 78 | 8 | 0 | 342 | 325 | 48 | 198 | 31 | 96 | 30 | 200 | 26 | 14 | 114 | 42 | 52.2 | 0 | 43 | 305 | 208 | 356 | 39 | 0 | 0 | 138 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 17 | 46 | 94 | 0 | 0 | 0 | 12 | 7990.7 | 876 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1150 | 17 | 1089.11 | 0 | 48 | 0 | 70 | 20 | 97 | 100 | 32 | 34 | 0 | 30 | 0 | 138 | 0 | 123 | 0 | 0 | 0 | 387 | 0 | 0 | 0 | 159 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 9 | 120 | 220 | 0 | 223 | 1000 | 10 | 6632.11 | 14622.81 | 77.64
19:30 | 98 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 17 | 129 | 147 | 278 | 55 | 35 | 162 | 68 | 300 | 283 | 250 | 0 | 17 | 0 | 285 | 0 | 0 | 0 | 160 | 14.5 | 15 | 0 | 0 | 17 | 65 | 0 | 0 | 64 | 50 | 76 | 0 | 100 | 100 | 0 | 39 | 21 | 2 | 575 | 160 | 0 | 0 | 16 | 68 | 184 | 0 | 0 | 0 | 612 | 0 | 51 | 120 | 8 | 0 | 354 | 335 | 48 | 189 | 31 | 96 | 30 | 200 | 28 | 14 | 114 | 40 | 52.2 | 0 | 43 | 300 | 208 | 332 | 39 | 0 | 0 | 150 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 54.5 | 82 | 160 | 0 | 0 | 0 | 12 | 8220.2 | 877 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 17 | 1123.96 | 0 | 48 | 0 | 113 | 20 | 97 | 113 | 37 | 43 | 0 | 30 | 0 | 136 | 0 | 123 | 0 | 0 | 0 | 385 | 0 | 0 | 0 | 156 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 10 | 110 | 220 | 0 | 300 | 1180 | 17 | 7049.16 | 15269.36 | 77.64
20:00 | 98 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 54 | 17 | 129 | 147 | 300 | 55 | 35 | 162 | 69 | 300 | 283 | 250 | 0 | 17 | 0 | 278 | 0 | 0 | 0 | 160 | 14 | 15 | 0 | 0 | 17 | 65 | 0 | 0 | 64 | 50 | 76 | 0 | 100 | 100 | 0 | 40 | 51 | 7 | 575 | 160 | 0 | 0 | 16 | 72 | 184 | 0 | 0 | 0 | 612 | 0 | 51 | 120 | 8 | 0 | 352 | 335 | 50 | 186 | 32 | 96 | 30 | 200 | 28 | 15 | 114 | 40 | 52.2 | 0 | 43 | 300 | 208 | 363 | 39 | 0 | 0 | 150 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 54.5 | 82 | 163 | 0 | 0 | 0 | 12 | 8325.7 | 878 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1180 | 17 | 1117.51 | 0 | 48 | 0 | 113 | 20 | 97 | 113 | 37 | 43 | 0 | 30 | 0 | 134 | 0 | 123 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 156 | 50 | 115 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 250 | 10 | 120 | 220 | 0 | 300 | 1224 | 17 | 6954.51 | 15280.21 | 77.68
21:00 | 40 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 54 | 17 | 129 | 147 | 300 | 55 | 35 | 162 | 68 | 300 | 264 | 250 | 0 | 17 | 0 | 268 | 0 | 0 | 0 | 160 | 13.8 | 14 | 0 | 0 | 18 | 70 | 0 | 0 | 62 | 50 | 76 | 0 | 100 | 100 | 0 | 40 | 70 | 20 | 575 | 160 | 0 | 41 | 16 | 105 | 184 | 0 | 0 | 0 | 612 | 0 | 51 | 127 | 8 | 0 | 359 | 335 | 50 | 181 | 34 | 96 | 30 | 200 | 29 | 15 | 114 | 40 | 52.2 | 0 | 43 | 305 | 208 | 348 | 39 | 0 | 0 | 153 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 24 | 91 | 168 | 0 | 0 | 0 | 12 | 8349 | 925 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 23 | 1121.52 | 0 | 48 | 0 | 113 | 20 | 97 | 113 | 29 | 43 | 0 | 30 | 0 | 132 | 0 | 123 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 160 | 50 | 115 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 16 | 307 | 11 | 110 | 220 | 0 | 347 | 1244 | 17 | 7275.72 | 15624.72 | 77.72
22:00 | 8 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 54 | 17 | 129 | 146 | 300 | 15 | 35 | 162 | 68 | 300 | 261 | 250 | 0 | 17 | 0 | 263 | 0 | 0 | 0 | 90 | 13.8 | 14 | 0 | 0 | 43 | 115 | 0 | 0 | 60 | 50 | 76 | 0 | 100 | 100 | 0 | 40 | 72 | 26 | 575 | 108 | 0 | 50 | 16 | 105 | 184 | 0 | 0 | 0 | 612 | 0 | 51 | 127 | 0 | 0 | 353 | 335 | 52 | 179 | 34 | 96 | 30 | 200 | 29 | 15 | 114 | 40 | 52.2 | 0 | 43 | 305 | 208 | 364 | 39 | 0 | 0 | 153 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 17 | 91 | 169 | 0 | 0 | 0 | 12 | 8221 | 925 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 38 | 1127.8 | 0 | 48 | 0 | 113 | 20 | 97 | 113 | 29 | 43 | 0 | 30 | 0 | 130 | 0 | 123 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 159 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 11 | 110 | 220 | 0 | 349 | 1150 | 17 | 7053 | 15274 | 77.76
23:00 | 8 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 54 | 16 | 129 | 112 | 300 | 15 | 35 | 162 | 68 | 340 | 270 | 250 | 0 | 17 | 0 | 270 | 0 | 0 | 0 | 90 | 13.8 | 0 | 0 | 0 | 53 | 115 | 0 | 0 | 52 | 50 | 76 | 0 | 100 | 100 | 0 | 40 | 91 | 29 | 575 | 108 | 0 | 33 | 16 | 105 | 184 | 0 | 0 | 0 | 612 | 0 | 51 | 117 | 0 | 0 | 354 | 335 | 52 | 179 | 33 | 95 | 0 | 200 | 29 | 6 | 114 | 42 | 52.2 | 0 | 37 | 310 | 208 | 311 | 39 | 0 | 0 | 137 | 0 | 0 | 85 | 0 | 0 | 0 | 101 | 17 | 92 | 158 | 0 | 0 | 0 | 12 | 8101 | 925 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 53 | 1129.61 | 0 | 48 | 0 | 113 | 20 | 97 | 113 | 24 | 43 | 0 | 30 | 0 | 130 | 0 | 121 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 152 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 90 | 220 | 0 | 347 | 1155 | 17 | 7055.81 | 15156.81 | 77.8
Total KWH | 434448 | 1301760 | 503520 | 0 | 0 | 0 | 0 | 0 | 8586000 | 0 | 0 | 1073160 | 335520 | 2972592 | 1835520 | 4532673 | 593007 | 885196 | 3248640 | 1052160 | 7827500 | 6969920 | 6256342 | 0 | 453101 | 0 | 6894567 | 0 | 0 | 199870 | 1648800 | 379200 | 349920 | 0 | 0 | 412745 | 1387527 | 79680 | 0 | 1154880 | 662120 | 1236576 | 46869 | 1872960 | 1407360 | 18801 | 926640 | 697527 | 409440 | 12930909.09 | 1560655 | 0 | 501600 | 307423.8 | 861455 | 4452268 | 0 | 0 | 0 | 24943634 | 24110 | 1155248 | 2054109 | 200727.27 | 0 | 8440500 | 7878000 | 1178880 | 4855000 | 737136 | 2165760 | 1318430 | 4315200 | 337680 | 292020 | 2618580 | 826560 | 1075445 | 137373 | 801632 | 7350000 | 4662800 | 8478000 | 919000 | 0 | 0 | 3355282 | 0 | 0 | 1931520 | 0 | 0 | 0 | 2421670 | 475560 | 1282800 | 3028800 | 0 | 15300 | 351470 | 234720 | 189123798.16 | 22088000 | 3404736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88992 | 334080 | 26858180 | 447360 | 24026182 | 0 | 537283 | 0 | 1802688 | 172460 | 856816 | 1231584 | 238930 | 270403 | 757510 | 265252 | 369000 | 3523182 | 0 | 3435309 | 0 | 0 | 0 | 8420509 | 0 | 31860 | 0 | 3788000 | 1124072 | 2713557 | 260500 | 2394614 | 0 | 0 | 66334.08 | 1343520 | 2086 | 35616 | 4691000 | 133837 | 2649000 | 5240700 | 0 | 7163636 | 27325090.91 | 94800 | 158186678.99 | 347310477.15

## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 29-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-05-2025 | during | 29-05-2025 | during | 29-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0.01 | 0.01 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0.01 | 0.01 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0.01 | 0.01 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0.01 | 0.01 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 361 | 362 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 300 | 450 | 450 | 330 | 330 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 304 | 264 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 281 | 268 | 335 | 335 | 301 | 301 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 40 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 50 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 77 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15.6 | 13.8 | 33 | 33 | 18.5 | 18.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 16 | 14 | 22 | 22 | 18 | 18 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 41 | 25 | 52.19 | 52.19 | 52.19 | 52.19 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 278 | 300 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 122 | 129 | 135 | 135 | 135 | 135 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 70 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 30 | 68 | 104 | 104 | 52 | 52 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 155 | 162 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 31 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 55 | 55 | 17 | 17 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 250 | 250 | 583 | 583 | 300 | 300 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 90 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 2571.6 | 2750.8 | 5253.9 | 5260.9 | 2968.57 | 2975.57
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 12 | 16 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 7 | 0 | 7 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 41 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 40 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 185 | 184 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 105 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 76 | 56 | 72 | 56 | 72 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 16 | 50 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 63 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 20 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 2.62 | 0 | 2.62 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 70 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 70 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 34 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 18 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 26 | 160 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 612 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 39 | 62 | 52 | 51 | 52 | 51 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 575 | 575 | 575 | 575 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2255 | 2299 | 3421.34 | 3441.72 | 3421.34 | 3441.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 210 | 181 | 221.43 | 221.43 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 343 | 359 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 335 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 28 | 34 | 46.7 | 46.7 | 35 | 35 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 44 | 50 | 55 | 55 | 54 | 54 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 16 | 16 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 38 | 127 | 150 | 150 | 135 | 135 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 15 | 43 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 50 | 30 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 136 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 16 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 22 | 52.2 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 14 | 15 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 29 | 113 | 113 | 28 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 91 | 96 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 4 | 0 | 60 | 0 | 60 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1519 | 1764.2 | 2444.43 | 2384.43 | 2060.55 | 2000.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 28-05-2025 | during | 29-05-2025 | during | 29-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 125 | 168 | 200 | 200 | 172 | 172 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 53 | 91 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 51.93 | 0 | 50 | 0 | 50 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 17 | 24 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 253.93 | 295 | 601.1 | 549 | 395.6 | 343.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 37 | 39 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 147 | 153 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 85 | 86 | 86 | 82 | 82 | Allocation limit by Titas, instructed by DS(Gen)
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 100 | 102 | 100 | 100 | 171 | 171 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 305 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 369 | 348 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 208 | 208 | 210 | 210 | 210 | 210 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1246 | 1240 | 1364 | 1364 | 1310 | 1310
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 924 | 925 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 152 | 123 | 410 | 410 | 280 | 280 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 23 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 50.88 | 0 | 62.5 | 0 | 62.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1011 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2137.88 | 2320.2 | 3574.7 | 3512.2 | 3444.7 | 3382.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 297 | 347 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 16 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 0 | 11 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 110 | 134 | 134 | 118 | 118 | FGMO
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1010 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.27 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1897.27 | 2272 | 2176 | 2175 | 2120 | 2119
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 151 | 132 | 214 | 214 | 166 | 166 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 134 | 123 | 220 | 220 | 162 | 162 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 377 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 22 | 22 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 97 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 10 | 113 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 3.11 | 0 | 5.85 | 0 | 5.85 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 1007.42 | 1121.52 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 35.35 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 84 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1838.88 | 2246.52 | 3192.72 | 3025.87 | 3036.93 | 2870.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 48 | 50 | 50 | 50 | 50 | 49 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 130 | 160 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 113 | 112 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 8 | 0 | 6.6 | 0 | 6.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 109 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 36 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 160 | 0 | 103.71 | 0 | 103.71 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 604 | 437 | 602.31 | 462 | 612.31 | 471
System Total |  |  |  |  | 28886.2 | 27110.055 | 14323.56 | 15624.72 | 22630.5 | 22175.12 | 19370 | 18913.62
Forecast Scenario (29-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 15200 | 14284 | 0 |  | 15200 | 14284
|  |  |  | 1:00 | 14284 | 14284 | 0 |  | 14284 | 14284
|  |  |  | 2:00 | 13834 | 13834 | 0 |  | 13834 | 13834
|  |  |  | 3:00 | 13444 | 13444 | 0 |  | 13444 | 13444
|  |  |  | 4:00 | 13164 | 13164 | 0 |  | 13164 | 13164
|  |  |  | 5:00 | 12692 | 12692 | 0 |  | 12692 | 12692
|  |  |  | 6:00 | 11877 | 11877 | 0 |  | 11877 | 11877
|  |  |  | 7:00 | 11585 | 11585 | 0 |  | 11585 | 11585
|  |  |  | 8:00 | 11040 | 11040 | 0 |  | 11040 | 11040
|  |  |  | 9:00 | 10722 | 10722 | 0 |  | 10722 | 10722
|  |  |  | 10:00 | 10736 | 10736 | 0 |  | 10736 | 10736
|  |  |  | 11:00 | 11000 |  | 0 |  | 11000
|  |  |  | 12:00 | 11500 |  | 0 |  | 11500
|  |  |  | 13:00 | 11700 |  | 0 |  | 11700
|  |  |  | 14:00 | 11500 |  | 0 |  | 11500
|  |  |  | 15:00 | 11550 |  | 0 |  | 11550
|  |  |  | 16:00 | 11600 |  | 0 |  | 11600
|  |  |  | 17:00 | 11800 |  | 0 |  | 11800
|  |  |  | 18:00 | 12500 |  | 0 |  | 12500
|  |  |  | 18:30 | 12800 |  | 0 |  | 12800
|  |  |  | 19:00 | 13800 |  | 0 |  | 13800
|  |  |  | 19:30 | 14000 |  | 0 |  | 14000
|  |  |  | 20:00 | 14100 |  | 0 |  | 14100
|  |  |  | 21:00 | 14200 |  | 0 |  | 14200
|  |  |  | 22:00 | 14050 |  | 0 |  | 14050
|  |  |  | 23:00 | 14000 |  | 0 |  | 14000
Probable Maximum Temperature: |  |  | 28.00°C
Probable Maximum Demand at Day Peak: |  |  | 14080.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Demand at Evening Peak: |  |  | 15700.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15700.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 337.03 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 10:21 hrs on 29-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 28-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 14323.56 | MW | 12:00 Hr. | Energy Generated |  |  | 347.3105 |  | MKWHr.
| Day Peak Demand |  |  | 14503.56 | MW | 12:00 Hr. | Energy Unserverd |  |  | 6.154 |  | MKWHr.
| Evening Peak Generation |  |  | 15624.72 | MW | 21:00 Hr. | Energy Demand |  |  | 353.4645 |  | MKWHr.
| Evening Peak Demand |  |  | 15801.72 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.3 |  | °C
| Minimum Generation of the Day |  |  | 12910.98 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 910.84 |  | MMCFD
| Maximum Generation of the Day |  |  | 15751.27 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 7.5166 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 37.2634 | 0 | 20.8701 | 0 | 0 | 0.19987 | 0 | 0 | 58.3334 | Gas | 124.1066 | Gas | 441967035.5859
| Chattogram Zone |  |  | 4.8617 | 37.8745 | 11.0345 | 0 | 0.92664 | 0.042911 | 0 | 1.1549 | 55.8952 | Coal | 108.8245 | Coal | 708484658.5397
| Cumilla Zone |  |  | 26.0559 | 0 | 13.3684 | 0 | 0 | 0.13737 | 0.82656 | 0 | 40.3883 | HFO | 61.4452 | HFO | 1144814566.946
| Mymensingh Zone |  |  | 0 | 0 | 5.0219 | 0 | 0 | 0.36677 | 0 | 0 | 5.3887 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 29.1183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.1183 | Hydro | 0.92664 | Hydro | 92664
| Khulna Zone |  |  | 3.4047 | 26.8582 | 0.53635 | 0 | 0 | 0.33408 | 22.088 | 0 | 53.2213 | Solar | 3.9118 | Solar | 65722189.3388
| Barishal Zone |  |  | 8.0235 | 39.1797 | 0.13042 | 0 | 0 | 0.002086 | 0 | 0 | 47.3358 | Import | 46.9407 | Import | 232616500.76
| Rajshahi Zone |  |  | 15.379 | 0 | 5.3754 | 0 | 0 | 1.1584 | 24.0262 | 0 | 45.939 | Wind | 1.1549 | Wind | 16907443.2
| Rangpur Zone |  |  | 0 | 4.9121 | 5.1082 | 0 | 0 | 1.6704 | 0 | 0 | 11.6906
| Total |  |  | 124.1066 | 108.8245 | 61.4452 | 0 | 0.92664 | 3.9118 | 46.9407 | 1.1549 | 347.3105
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 441967035.5859 |  | Hydro | 92664
|  |  |  | Coal | 708484658.5397 |  | Solar | 65722189.3388
|  |  |  | HFO | 1144814566.946 |  | Import | 232616500.76
|  |  |  | HSD | 0 |  | Wind | 16907443.2
[5 empty] | Total: | 261,06,05,058 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.088 | Peak Hr Flow | 925.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 48065072.8 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.0262 | Peak Hr Flow | 1121.52 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 782 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.82656 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 952 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 46.9407 | Peak Hr Flow | 2086.52 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 30 |  | 5758
|  |  |  | Chattogram |  | 0 |  | 1396
|  |  |  | Cumilla |  | 20 |  | 1486
|  |  |  | Mymensingh |  | 10 |  | 1224
|  |  |  | Sylhet |  | 0 |  | 581
|  |  |  | Khulna |  | 0 |  | 1815
|  |  |  | Barishal |  | 0 |  | 371
|  |  |  | Rajshahi |  | 0 |  | 1580
|  |  |  | Rangpur |  | 109 |  | 922
|  |  |  | Total |  | 169 |  | 15133
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:01 | Kishoreganj 132/33kV S/S Tr-1 (404T) HT is restored.
|  | 08:01 | Kishoreganj 132/33kV S/S Tr-1 (404T) LT is restored.
| 08:23 | 17:15 | Goalpara 132/33kV S/S Bus 2 Scheduled S/D
|  | 08:44 | Jhenaidah 132/33kV S/S Transformer T-1 LT is restored.
|  | 08:44 | Jhenaidah 132/33kV S/S Transformer T-1 HT is restored.
| 08:51 | 10:25 | Ishurdi 230/132kV S/S 230/132 kV T-03 HT Scheduled S/D Due to Redhot maintenance work
|  | 09:15 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT is restored.
|  | 09:15 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT is restored.
|  | 09:15 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) HT is restored.
|  | 09:15 | Chuadanga 132/33kV S/S 132kV Tr. T2(426T) LT is restored.
|  | 09:36 | Kushtia 132/33kV S/S T-3 HT is restored.
|  | 09:38 | Kushtia 132/33kV S/S T-3 LT is restored.
| 09:55 | 12:31 | Bogura 230/132kV S/S T-02 HT Forced S/D Due to Oil Refilling Inspection.
|  | 10:26 | Ishurdi 230/132kV S/S 230/132 kV T-03 LT is restored.
|  | 10:58 | Rajshahi-Rajshahi(New) 132kV Ckt-1 is restored.
| 11:56 | 12:45 | Joydebpur 132/33kV S/S GT-2 HT Forced S/D Due to Loop Maintenance
|  | 12:37 | Bogura 230/132kV S/S T-02 LT is restored.
| 12:39 | 14:04 | Niamatpur 132/33kV S/S Transformer-1(407T) HT Forced S/D
| 12:39 | 14:07 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Forced S/D Due to Poesha feeder red hot | [7 empty] | 12.0MW load
interrup.
| 12:45 | 14:55 | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-01 LT Scheduled S/D Due to High
temperature point maintenance
|  | 13:57 | Khulna(S) 230/132kV S/S TR-1 HT is restored.
|  | 13:58 | Khulna(S) 230/132kV S/S TR-1 LT is restored.
| 14:37 | 00:55 | Gopalganj 400/132kV S/S 400kV Bus-01 Project Work S/D
| 16:05 | 18:44 | Patuakhali-Payra 132kV Ckt-2 Scheduled S/D from Patuakhali 132/33kV end Due to Red-hot
maintenance work at Payra end. and from Payra 400/132/33kV end Due to High Temperature
| 16:13 | 20:04 | Madanganj 132/33kV S/S Madanganj -DPDC Char sayedpur 132k Ckt-1 Forced S/D Due to DPDC
work
| 16:26 | 16:43 | Noapara 132/33kV S/S T-2 LT Tripped showing SIPROTEC 7SJ81 (SIEMENS) relays Due to Earth | [7 empty] | 21.5MW load
|  |  | fault and over current fault occure in the feeder of REB-4 33kV. | [7 empty] | interrup.
| 16:26 | 16:41 | Noapara 132/33kV S/S T-1 LT Tripped showing SIPROTEC 7SJ81 (SIEMENS) relays Due to Earth | [7 empty] | 22.0MW load
|  |  | fault and over current fault occure in the feeder of REB-4 33kV. | [7 empty] | interrup.
| 16:50 | 17:42 | Cumilla(S) 132/33kV S/S Tripura Ckt-2 Tripped showing No relay. relays Due to Tripura end | [7 empty] | 18.0MW load
|  |  | Trip, Bangladesh end C.B not trip. | [7 empty] | interrup.
| 16:50 | 17:40 | Cumilla(S) 132/33kV S/S Tripura Ckt-1 Tripped showing No relay relays Due to Tripura end | [7 empty] | 18.0MW load
|  |  | Trip, Bangladesh end C.B not trip. | [7 empty] | interrup.
| 16:50 |  | Import (Tripura) Tripped
| 17:40 |  | Import (Tripura) Synchronized
| 17:48 | 17:54 | Bhaluka 132/33kV S/S Transformer- 01 LT Tripped showing df/dt(sps) relays Due to
Frequency low
| 17:49 | 17:54 | Bhaluka 132/33kV S/S Transformer- 02 LT Tripped showing df/dt relays Due to Low frequency
| 17:50 |  | SS Power Unit-1 tripped due to rotor earth fault
| 19:25 | 20:43 | Niamatpur 132/33kV S/S Transformer-2 (417T) LT Forced S/D Due to 33kV DS R Phase Red Hot | [7 empty] | 28.0MW load
interrup.
| 19:28 | 20:42 | Niamatpur 132/33kV S/S Transformer-2 (417T) HT Forced S/D Due to 33kV DS R Phase Red Hot | [7 empty] | 28.0MW load
interrup.
| 21:00 |  | Evening peak Generation is 15623 MW
|  | 01:15 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT is restored.
|  | 01:18 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT is restored.
| 05:17 | 05:26 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Ins o/c,deff o/ c. relays Due to 33 | [7 empty] | 10.0MW load
|  |  | kv feeder fault | [7 empty] | interrup.
| 06:05 | 07:35 | Bhangura 132/33kV S/S Tr-2(413T) LT Tripped showing O/C,E/F relays Due to Aux Tr-1 fuse | [7 empty] | 25.0MW load
|  |  | and insulator blast. | [7 empty] | interrup.
| 06:05 | 07:34 | Bhangura 132/33kV S/S Tr-1(403T) LT Tripped showing O/C,E/F relays Due to Aux Tr-1 fuse | [7 empty] | 25.0MW load
|  |  | and insulator blast. | [7 empty] | interrup.
| 06:26 |  | Ghorasal-Joydeb-B 132kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Hotspot
maintenance
| 06:45 |  | Kabirpur 132/33kV S/S XFR, T-2 HT Scheduled S/D Due to 33 KV Hi-tech Feeder 33 KV bus DS | [7 empty] | 100.0MW load
|  |  | high temperature maintenance work. | [7 empty] | interrup.
| 07:00 |  | Minimum generation 11585 MW
| 07:21 |  | Hathazari 230/132/33kV S/S T-02 HT Scheduled S/D Due to R ph cable puncture
| 07:21 |  | Hathazari 230/132/33kV S/S T-02 LT Scheduled S/D Due to R ph cable puncture
| 07:45 |  | Sylhet 132/33kV S/S T4 HT Scheduled S/D Due to work of PDB
| 07:45 |  | Sylhet 132/33kV S/S T4 LT Scheduled S/D Due to work of PDB | [7 empty] | 10.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 28-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 362 | 8586000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7827500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 264 | 6969920 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 55 | 593007 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 268 | 6894567 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 434448 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 1073160 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 1835520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 885196 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 453101 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 13.8 | 379200 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 349920 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 25 | 503520 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 300 | 4532673 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 129 | 2972592 | -
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 1301760 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 68 | 1052160 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3248640 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 199870 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 335520 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 250 | 6256342 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1648800 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2750.8 | 58333416
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Unit #1 Under Maintenance, Unit#2 Running at 150MW
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 307423.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 24110 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 41 | 501600 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 40 | 926640 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 184 | 4452268 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 105 | 861455 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 76 | 1236576 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 662120 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1872960 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 20 | 409440 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 79680 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 18801 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 70 | 1387527 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 46869 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 70 | 697527 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1407360 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 18 | 412745 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 160 | 1560655 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 612 | 24943634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 62 | 1154880 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 575 | 12930909.09 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2299 | 55895179.89
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4855000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 359 | 8440500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 335 | 7878000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 737136 | machine problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 50 | 1178880 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 200727.27 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1155248 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 127 | 2054109 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 43 | 801632 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 30 | 1318430 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 4315200 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 826560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 52.2 | 1075445 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 292020 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2618580 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 337680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 96 | 2165760 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 137373 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1764.2 | 40388280.27
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 15300 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 168 | 3028800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 91 | 1282800 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 351470 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 234720 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 24 | 475560 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 295 | 5388650
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 39 | 919000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | -
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 153 | 3355282 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Partial Shutdown due to maintenance
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1931520 | Allocation limit by Titas, instructed by DS(Gen)
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2421670 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 305 | 7350000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 348 | 8478000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 208 | 4662800 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1240 | 29118272
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 925 | 22088000 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 123 | 3404736 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 23 | 447360 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 88992 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 334080 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 26858180 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2320.2 | 53221348
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 347 | 7163636 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 16 | 35616 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 11 | 133837 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 110 | 2649000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27325090.91 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5240700 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 94800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4691000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2086 | -
Barishal Area Total |  |  |  |  | 2236 | 2272 | 47335765.91
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 48 | 537283 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 172460 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 238930 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 132 | 3523182 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 123 | 3435309 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 377 | 8420509 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 265252 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 43 | 270403 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 856816 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 1802688 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1231584 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 31860 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1121.52 | 24026182 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 369000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 757510 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2246.52 | 45938968
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1124072 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 160 | 3788000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 112 | 2394614 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 66334.08 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 2713557 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 260500 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1343520 | -
Rangpur Area Total |  |  |  |  | 950 | 437 | 11690597.08
Eastern Grid Total |  |  |  |  | 16771.895 | 8349 | 189123798.16
Western Grid Total |  |  |  |  | 10338.16 | 7275.72 | 158186678.99
National Grid Total |  |  |  |  | 27110.055 | 15624.72 | 347310477.15
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 28-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 10385.56 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4578.8 | MW
i) Dhaka area |  |  | 5728.33 |  | MW | i) Khulna area |  |  |  | 1815 | MW
ii) Chattogram area |  |  | 1396 |  | MW | ii) Barishal area |  |  |  | 371 | MW
iii) Cumilla area |  |  | 1466.23 |  | MW | iii) Rajshahi area |  |  |  | 1579.8 | MW
iv) Mymensingh area |  |  | 1214 |  | MW | iv) Rangpur area |  |  |  | 813 | MW
v) Sylhet area |  |  | 581 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14964.36 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 9 | 19:30 | 67 | Ishurdi | 88 | 19:30 | 133 | Patuakhali | 86 | 00:00
2 | AKSML | 96 | 14:00 | 68 | Jaldhaka | 71 | 22:00 | 134 | Payra | 32 | 00:00
3 | Aftabnagar | 40 | 00:00 | 69 | Jamalpur | 128 | 19:30 | 135 | Postogola | 61 | 00:00
4 | Agargaon | 145 | 14:00 | 70 | Jashore | 147 | 00:00 | 136 | Purbachal | 23 | 00:00
5 | Agrabad | 96 | 20:00 | 71 | Jhenaidah | 136 | 00:00 | 137 | Purbasadipur | 127 | 14:00
6 | Amnura | 39 | 00:00 | 72 | Joydebpur | 152 | 20:00 | 138 | Rahanpur | 32 | 21:00
7 | Ashuganj | 108 | 01:00 | 73 | Joypurhat | 68 | 00:00 | 139 | Rahim | 52 | 10:00
8 | BSRM | 200 | 18:30 | 74 | Juldah | 13.5 | 12:00 | 140 | Rajbari | 87 | 00:00
9 | Bagerhat | 89 | 00:00 | 75 | KSRM | 34 | 18:30 | 141 | Rajendrapur | 142 | 00:00
10 | Bajitpur | 58 | 00:00 | 76 | Kabirpur | 277 | 08:00 | 142 | Rajshahi | 135 | 20:00
11 | Bakulia | 94 | 19:00 | 77 | Kachua | 101 | 00:00 | 143 | Rajshahi-230 | 74 | 00:00
12 | Banani | 43.2 | 15:00 | 78 | Kallyanpur | 114 | 00:00 | 144 | Ramganj | 116 | 19:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kalurghat | 44 | 15:00 | 145 | Rampur | 44 | 00:00
14 | Barapukuria | 62 | 13:00 | 80 | Kamrangirchar | 69.4 | 13:00 | 146 | Rangamati | 18 | 19:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 144 | 16:00
16 | Barishal | 114 | 00:00 | 82 | Kasba | 39 | 21:00 | 148 | Ruppur | 8.8 | 10:00
17 | Barishal-230 | 108 | 00:00 | 83 | Kazla | 107 | 20:00 | 149 | SSM | 16 | 02:00
18 | Baroaulia | 72 | 14:00 | 84 | Keranigonj | 102 | 00:00 | 150 | Saidpur | 111 | 12:00
19 | Baroirhat | 66 | 00:00 | 85 | Khagrachori | 36 | 19:30 | 151 | Satkhira | 142 | 00:00
20 | Bashundhara | 217 | 16:00 | 86 | Khulna | 67 | 00:00 | 152 | Satmasjid | 114 | 13:00
21 | BashundharaCement | 9 | 16:00 | 87 | Khulshi | 188 | 19:30 | 153 | Savar | 232 | 11:00
22 | Beanibazar | 82 | 01:00 | 88 | Kishoreganj | 144 | 19:30 | 154 | SevenRings | 17.18 | 03:00
23 | Benapole | 66 | 00:00 | 89 | Kodda | 309 | 14:00 | 155 | ShahCement | 35 | 00:00
24 | Bhaluka | 190 | 19:00 | 90 | Kulaura | 52 | 00:00 | 156 | Shahjadpur | 90 | 12:00
25 | Bhandaria | 56 | 00:00 | 91 | Kurigram | 56 | 18:00 | 157 | Shahjibazar | 116 | 21:00
26 | Bhangura | 40 | 00:00 | 92 | Kushtia | 169 | 00:00 | 158 | Shahmirpur | 53 | 02:00
27 | Bheramara(GK) | 69 | 00:00 | 93 | Lalbag | 62 | 17:00 | 159 | Shariatpur | 90 | 22:00
28 | Bhulta | 238 | 09:00 | 94 | Lalmonirhat | 52 | 00:00 | 160 | Sherpur | 152 | 22:00
29 | Bog-Sherpur | 74 | 01:00 | 95 | MI_Cement | 17.8 | 20:00 | 161 | Shikalbaha | 27 | 11:00
30 | Bogura | 175 | 00:00 | 96 | Madanganj | 48 | 16:00 | 162 | Shitalakhya | 92 | 12:00
31 | Borhanuddin | 90 | 00:00 | 97 | Madaripur | 109 | 00:00 | 163 | Sholosohor | 47 | 15:00
32 | Brahmanbaria | 122 | 04:00 | 98 | Madartek | 99.02 | 00:00 | 164 | Shyampur | 180 | 00:00
33 | Cantonment | 166 | 13:00 | 99 | Madunaghat | 64 | 19:30 | 165 | Siddhirganj | 128 | 12:00
34 | Chandina | 22.98 | 22:00 | 100 | Magura | 68 | 19:30 | 166 | Sirajganj | 124 | 22:00
35 | Chandpur | 77 | 00:00 | 101 | Mahasthangarh | 96 | 00:00 | 167 | Sonargaon | 130 | 19:00
36 | Chandraghona | 37 | 19:00 | 102 | Manikganj | 139 | 19:30 | 168 | Sreemongol | 88 | 00:00
37 | Chapai | 74 | 23:00 | 103 | Maniknagar | 94 | 13:00 | 169 | Sreepur | 117 | 12:00
38 | Charsaidpur | 45 | 12:00 | 104 | Matarbari | 52 | 00:00 | 170 | Srinagar | 49.52 | 00:00
39 | Chauddagram | 78 | 00:00 | 105 | Matuail | 72 | 15:00 | 171 | Sunamganj | 61 | 01:00
40 | Chhatak | 42 | 00:00 | 106 | Millgate | 111 | 16:00 | 172 | Sylhet | 52 | 00:00
41 | Chowmuhani | 233 | 19:00 | 107 | Mirpur | 132 | 15:00 | 173 | Sylhet-132 | 123 | 14:00
42 | Chuadanga | 118 | 00:00 | 108 | Mirsorai | 12 | 12:00 | 174 | TK | 34.5 | 00:00
43 | Coxsbazar | 124 | 00:00 | 109 | Mirzapur | 48 | 20:00 | 175 | Tangail | 190 | 20:00
44 | Cumilla(N) | 161 | 00:00 | 110 | Mithapukur | 74 | 21:00 | 176 | Thakurgaon | 86 | 21:00
45 | Cumilla(S) | 177 | 14:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 146 | 15:00
46 | Daudkandi | 157 | 21:00 | 112 | Mogbazar | 166.4 | 15:00 | 178 | Ullahpara | 42 | 00:00
47 | Dhaka | 76 | 12:00 | 113 | Mongla | 52 | 11:00 | 179 | Ullon | 46 | 00:00
48 | Dhamrai | 144 | 06:00 | 114 | Motijheel | 45 | 13:00 | 180 | Uttara | 94 | 13:00
49 | Dhanmondi | 173.3 | 13:00 | 115 | Muktagacha | 36 | 22:00 | 181 | UttaraNew | 68 | 00:00
50 | Dohazari | 103 | 19:30 | 116 | Munshiganj | 126 | 00:00 | 182 | Zigatola | 80 | 16:00
51 | Faridpur | 171 | 00:00 | 117 | Muradnagar | 33 | 23:00
52 | Fatullah | 109 | 12:00 | 118 | Mymensingh | 197 | 15:00
53 | Fenchuganj | 46 | 00:00 | 119 | Naogaon | 145 | 00:00
54 | Feni | 123 | 00:00 | 120 | Narail | 62 | 00:00
55 | GPH | 92 | 03:00 | 121 | Narinda | 90 | 13:00
56 | Ghatail | 80 | 19:30 | 122 | Narshingdi | 202 | 19:30
57 | Ghorashal | 17 | 08:00 | 123 | Natore | 165 | 19:30
58 | Ghorashal-230 | 106 | 22:00 | 124 | Nawabganj | 60 | 00:00
59 | Goalpara | 38 | 00:00 | 125 | Netrakona | 125 | 20:00
60 | Gollamari | 108 | 00:00 | 126 | New | 97.1 | 16:00
61 | Gopalganj | 109 | 19:30 | 127 | Niamatpur | 75 | 00:00
62 | Gulshan | 142 | 15:00 | 128 | Noapara | 51 | 22:00
63 | Halishahar | 80 | 10:00 | 129 | PHP | 4 | 01:00
64 | HaripurSBU | 188 | 10:00 | 130 | Pabna | 126 | 01:00
65 | Hasnabad | 71 | 00:00 | 131 | Palashbari | 120 | 00:00
66 | Hathazari | 81 | 23:00 | 132 | Panchagarh | 49 | 03:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 28-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 15751.27 | 516 |  | 16290.49
1:00 | 15473.81 | 503 |  | 15999.81
2:00 | 14843.41 | 494 |  | 15359.41
3:00 | 14577.29 | 424 |  | 15020.29
4:00 | 14267.92 | 394 |  | 14679.92
5:00 | 14024.88 | 360 |  | 14400.88
6:00 | 13373.06 | 316 |  | 13703.06
7:00 | 13370.89 | 280 |  | 13663.89
8:00 | 12910.98 | 281 |  | 13204.98
9:00 | 13240.74 | 251 |  | 13502.74
10:00 | 13626.36 | 169 |  | 13803.36
11:00 | 13946.97 | 187 |  | 14141.97
12:00 | 14323.56 | 172 |  | 14503.56
13:00 | 14589.43 | 164 |  | 14760.43
14:00 | 14579.04 | 167 |  | 14754.04
15:00 | 14635.02 | 159 |  | 14801.02
16:00 | 14194.05 | 177 |  | 14379.05
17:00 | 13478.01 | 120 |  | 13603.01
18:00 | 12872.25 | 0 |  | 12872.25
19:00 | 14622.81 | 122 |  | 14749.81
19:30 | 15269.36 | 156 |  | 15432.36
20:00 | 15280.21 | 163 |  | 15450.21
21:00 | 15624.72 | 169 |  | 15801.72
22:00 | 15274 | 246 |  | 15531
23:00 | 15156.81 | 320 |  | 15490.81
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 28-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 8769.56 | 6981.71 | 15751.27 | DAILY GENERATION CURVE
00:30 | 8619.38 | 6993.16 | 15612.54
01:00 | 8469.2 | 7004.61 | 15473.81 | 28-05-2025
01:30 | 8281.7 | 6876.91 | 15158.61
02:00 | 8094.2 | 6749.21 | 14843.41
02:30 | 8010.2 | 6700.15 | 14710.35
03:00 | 7926.2 | 6651.09 | 14577.29
03:30 | 7804.95 | 6617.655 | 14422.605
04:00 | 7683.7 | 6584.22 | 14267.92
04:30 | 7630.2 | 6516.2 | 14146.4
05:00 | 7576.7 | 6448.18 | 14024.88
05:30 | 7396.695 | 6302.275 | 13698.97
06:00 | 7216.69 | 6156.37 | 13373.06
06:30 | 7177.42 | 6194.555 | 13371.975
07:00 | 7138.15 | 6232.74 | 13370.89
07:30 | 6995.77 | 6145.165 | 13140.935
08:00 | 6853.39 | 6057.59 | 12910.98
08:30 | 6937.38 | 6138.48 | 13075.86
09:00 | 7021.37 | 6219.37 | 13240.74
09:30 | 7076.585 | 6356.965 | 13433.55
10:00 | 7131.8 | 6494.56 | 13626.36
10:30 | 7343.37 | 6443.295 | 13786.665
11:00 | 7554.94 | 6392.03 | 13946.97
11:30 | 7700.235 | 6435.03 | 14135.265
12:00 | 7845.53 | 6478.03 | 14323.56
12:30 | 7960.885 | 6495.61 | 14456.495
13:00 | 8076.24 | 6513.19 | 14589.43
13:30 | 8039.81 | 6544.425 | 14584.235
14:00 | 8003.38 | 6575.66 | 14579.04
14:30 | 8044.84 | 6562.19 | 14607.03
15:00 | 8086.3 | 6548.72 | 14635.02
15:30 | 7994.235 | 6420.3 | 14414.535
16:00 | 7902.17 | 6291.88 | 14194.05
16:30 | 7735.43 | 6100.6 | 13836.03
17:00 | 7568.69 | 5909.32 | 13478.01
17:30 | 7303.02 | 5872.11 | 13175.13
18:00 | 7037.35 | 5834.9 | 12872.25
18:30 | 7514.025 | 6233.505 | 13747.53
19:00 | 7990.7 | 6632.11 | 14622.81
19:30 | 8220.2 | 7049.16 | 15269.36
20:00 | 8325.7 | 6954.51 | 15280.21
20:30 | 8337.35 | 7115.115 | 15452.465 |  | Executive Engineer
21:00 | 8349 | 7275.72 | 15624.72 |  | Network Operation Division
21:30 | 8285 | 7164.36 | 15449.36
22:00 | 8221 | 7053 | 15274
22:30 | 8161 | 7054.405 | 15215.405
23:00 | 8101 | 7055.81 | 15156.81

## En-Curve
QF-LDC-12
Date | 28-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3275 | 1854 | 782 | 0 | 42 | 1017.51 | 40 | 5096.2 | 0 | 569 | 3056.56 | 0 | 0 | 19 | 516 | DAILY ENERGY CURVE
00:30 | 3275.5 | 1831.5 | 852.5 | 0 | 41 | 1016.96 | 40 | 5040.7 | 0 | 508.5 | 2981.88 | 0 | 0 | 24 | 509.5 | 28-05-2025
01:00 | 3276 | 1809 | 923 | 0 | 40 | 1016.41 | 40 | 4985.2 | 0 | 448 | 2907.2 | 0 | 0 | 29 | 503
01:30 | 3339 | 1803.5 | 923 | 0 | 39 | 1019.71 | 40 | 4962.2 | 0 | 395 | 2607.2 | 0 | 0 | 30 | 498.5 | Energy Generated | 347.3105 |  | MKWHr
02:00 | 3402 | 1798 | 923 | 0 | 38 | 1023.01 | 40 | 4939.2 | 0 | 342 | 2307.2 | 0 | 0 | 31 | 494 | Energy not Served | 6.154 |  | MKWHr
02:30 | 3376 | 1801.5 | 923 | 0 | 38 | 1022.95 | 39.5 | 4939.7 | 0 | 322 | 2213.7 | 0 | 0 | 34 | 459 | Total Energy Requirement | 353.4645 |  | MKWHr
03:00 | 3350 | 1805 | 923 | 0 | 38 | 1022.89 | 39 | 4940.2 | 0 | 302 | 2120.2 | 0 | 0 | 37 | 424
03:30 | 3370 | 1809.75 | 923.5 | 0 | 38 | 1022.955 | 38.5 | 4940.2 | 0 | 258.5 | 1979.7 | 0 | 0 | 41.5 | 409
04:00 | 3390 | 1814.5 | 924 | 0 | 38 | 1023.02 | 38 | 4940.2 | 0 | 215 | 1839.2 | 0 | 0 | 46 | 394
04:30 | 3355.5 | 1787.5 | 924 | 0 | 37 | 1020 | 38 | 4915.7 | 0 | 210.5 | 1817.7 | 0 | 0 | 40.5 | 377
05:00 | 3321 | 1760.5 | 924 | 0 | 36 | 1016.98 | 38 | 4891.2 | 0 | 206 | 1796.2 | 0 | 0 | 35 | 360
05:30 | 3319.5 | 1764.5 | 924.5 | 0 | 36 | 1019.8 | 38.5 | 4737.1 | 14.37 | 187 | 1619.2 | 0 | 0 | 38.5 | 338
06:00 | 3318 | 1768.5 | 925 | 0 | 36 | 1022.62 | 39 | 4583 | 28.74 | 168 | 1442.2 | 0 | 0 | 42 | 316
06:30 | 3286 | 1767.25 | 924.5 | 0 | 35 | 1006.945 | 39.5 | 4582 | 83.08 | 168 | 1431.7 | 0 | 0 | 48 | 298
07:00 | 3254 | 1766 | 924 | 0 | 34 | 991.27 | 40 | 4581 | 137.42 | 168 | 1421.2 | 0 | 0 | 54 | 280
07:30 | 3267.5 | 1768.25 | 901 | 0 | 33 | 933.52 | 40 | 4550.5 | 189.565 | 152 | 1262.6 | 0 | 0 | 43 | 280.5
08:00 | 3281 | 1770.5 | 878 | 0 | 32 | 875.77 | 40 | 4520 | 241.71 | 136 | 1104 | 0 | 0 | 32 | 281
08:30 | 3356.5 | 1773 | 877.5 | 0 | 32 | 873.04 | 40 | 4524.5 | 297.32 | 166.5 | 1103 | 0 | 0 | 32.5 | 266
09:00 | 3432 | 1775.5 | 877 | 0 | 32 | 870.31 | 40 | 4529 | 352.93 | 197 | 1102 | 0 | 0 | 33 | 251
09:30 | 3459.5 | 1774 | 900.5 | 0 | 32 | 916.37 | 40 | 4533.5 | 388.68 | 202 | 1147.5 | 0 | 0 | 39.5 | 210
10:00 | 3487 | 1772.5 | 924 | 0 | 32 | 962.43 | 40 | 4538 | 424.43 | 207 | 1193 | 0 | 0 | 46 | 169
10:30 | 3513.5 | 1775.05 | 924 | 0 | 33 | 962.24 | 40 | 4551 | 395.375 | 230 | 1312 | 0 | 0 | 50.5 | 178
11:00 | 3540 | 1777.6 | 924 | 0 | 34 | 962.05 | 40 | 4564 | 366.32 | 253 | 1431 | 0 | 0 | 55 | 187
11:30 | 3509 | 1778.1 | 924 | 0 | 25 | 984.735 | 40 | 4554.5 | 417.93 | 298 | 1557 | 0 | 0 | 47 | 179.5
12:00 | 3478 | 1778.6 | 924 | 0 | 16 | 1007.42 | 40 | 4545 | 469.54 | 343 | 1683 | 0 | 0 | 39 | 172
12:30 | 3413.5 | 1749.3 | 924 | 0 | 23 | 1008.715 | 40 | 4540 | 509.38 | 341.5 | 1873.6 | 0 | 0 | 33.5 | 168
13:00 | 3349 | 1720 | 924 | 0 | 30 | 1010.01 | 40 | 4535 | 549.22 | 340 | 2064.2 | 0 | 0 | 28 | 164
13:30 | 3336 | 1738.3 | 923.5 | 0 | 30 | 1013.005 | 39 | 4384.5 | 499.23 | 392.5 | 2195.2 | 0 | 0 | 33 | 165.5
14:00 | 3323 | 1756.6 | 923 | 0 | 30 | 1016 | 38 | 4234 | 449.24 | 445 | 2326.2 | 0 | 0 | 38 | 167
14:30 | 3339.5 | 1735.3 | 923.5 | 0 | 35 | 1014.72 | 37.5 | 4276.5 | 405.81 | 443 | 2345.7 | 0 | 0 | 50.5 | 163
15:00 | 3356 | 1714 | 924 | 0 | 40 | 1013.44 | 37 | 4319 | 362.38 | 441 | 2365.2 | 0 | 0 | 63 | 159
15:30 | 3304.5 | 1694.5 | 923.5 | 0 | 38 | 1017.45 | 36.5 | 4296.5 | 332.385 | 445.5 | 2262.2 | 0 | 0 | 63.5 | 168
16:00 | 3253 | 1675 | 923 | 0 | 36 | 1021.46 | 36 | 4274 | 302.39 | 450 | 2159.2 | 0 | 0 | 64 | 177
16:30 | 3246 | 1681.5 | 923 | 0 | 18 | 1017.645 | 35.5 | 4117 | 191.685 | 499 | 2042.7 | 0 | 0 | 64 | 148.5
17:00 | 3239 | 1688 | 923 | 0 | 0 | 1013.83 | 35 | 3960 | 80.98 | 548 | 1926.2 | 0 | 0 | 64 | 120
17:30 | 3176 | 1676 | 923 | 0 | 19 | 1012.88 | 36 | 3694.5 | 60.05 | 590.5 | 1925.2 | 0 | 0 | 62 | 60
18:00 | 3113 | 1664 | 923 | 0 | 38 | 1011.93 | 37 | 3429 | 39.12 | 633 | 1924.2 | 0 | 0 | 60 | 0
18:30 | 3257.5 | 1713.75 | 899.5 | 0 | 40 | 1050.52 | 38 | 3752.5 | 19.56 | 723 | 2190.7 | 0 | 0 | 62.5 | 61
19:00 | 3402 | 1763.5 | 876 | 0 | 42 | 1089.11 | 39 | 4076 | 0 | 813 | 2457.2 | 0 | 0 | 65 | 122
19:30 | 3297 | 1750.5 | 877 | 0 | 40 | 1123.96 | 39 | 4414.2 | 0 | 818 | 2845.7 | 0 | 0 | 64 | 156
20:00 | 3296 | 1758 | 878 | 0 | 40 | 1117.51 | 40 | 4347 | 0 | 818 | 2921.7 | 0 | 0 | 64 | 163
20:30 | 3305.5 | 1758.9 | 901.5 | 0 | 40 | 1119.515 | 40 | 4438.1 | 0 | 814 | 2971.95 | 0 | 0 | 63 | 166
21:00 | 3315 | 1759.8 | 925 | 0 | 40 | 1121.52 | 40 | 4529.2 | 0 | 810 | 3022.2 | 0 | 0 | 62 | 169
21:30 | 3274 | 1758.3 | 925 | 0 | 40 | 1124.66 | 40 | 4454.2 | 0 | 774.5 | 2997.7 | 0 | 0 | 61 | 207.5
22:00 | 3233 | 1756.8 | 925 | 0 | 40 | 1127.8 | 40 | 4379.2 | 0 | 739 | 2973.2 | 0 | 0 | 60 | 246
22:30 | 3179 | 1760.3 | 925 | 0 | 41 | 1128.705 | 40 | 4393.2 | 0 | 716.5 | 2975.7 | 0 | 0 | 56 | 283
23:00 | 3125 | 1763.8 | 925 | 0 | 42 | 1129.61 | 40 | 4407.2 | 0 | 694 | 2978.2 | 0 | 0 | 52 | 320
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 28-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 383 | 18:00 | 366 | 00:00 | Payra | 413 | 16:00 | 406 | 00:00
Ashuganj | 396 | 18:00 | 368 | 11:00 | Rahanpur | 394 | 08:00 | 384 | 21:00
Bhulta | 393 | 05:00 | 365 | 10:00 | Rampal | 401 | 18:00 | 382 | 00:00
Bibiana | 388 | 17:00 | 381 | 12:00
BIPTC | 401 | 08:00 | 391 | 15:00
Bogura | 390 | 18:00 | 379 | 21:00
Gopalganj | 397 | 18:30 | 377 | 00:00
Kaliakoir | 373 | 18:00 | 359 | 10:00
Madunaghat | 393 | 23:00 | 383 | 12:00
Meghnaghat | 385 | 18:00 | 371 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 18:00 | 212 | 10:00 | Keranigonj | 221 | 18:00 | 209 | 11:00
AKSML | 232 | 21:00 | 221 | 00:00 | Khulna(S) | 230 | 18:00 | 213 | 00:00
Aminbazar | 222 | 04:00 | 22 | 06:00 | Madunaghat | 235 | 21:00 | 226 | 09:00
Ashuganj | 228 | 18:00 | 217 | 10:00 | Madunaghat-400 | 235 | 01:00 | 226 | 10:00
Ashuganj-400 | 228 | 18:00 | 217 | 10:00 | Maniknagar | 217 | 18:00 | 209 | 11:00
Baghabari | 230 | 05:00 | 223 | 11:00 | Meghnaghat | 228 | 18:00 | 218 | 00:00
Barapukuria | 223 | 18:30 | 219 | 02:00 | Meghnaghat-400 | 223 | 18:00 | 215 | 10:00
Barapukuria-230 | 223 | 18:30 | 219 | 02:00 | Mirsorai | 232 | 20:00 | 217 | 11:00
Barishal | 238 | 18:00 | 224 | 00:00 | Rajshahi | 233 | 06:00 | 223 | 13:00
Bheramara | 234 | 05:00 | 222 | 21:00 | Rampal | 229 | 18:00 | 215 | 00:00
Bhulta | 229 | 05:00 | 210 | 10:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 227 | 07:00 | 221 | 12:00 | Rampura | 228 | 05:00 | 209 | 09:00
BIPTC | 237 | 07:00 | 222 | 21:00 | Shikalbaha | 235 | 00:00 | 223 | 09:00
Bogura | 227 | 18:00 | 221 | 12:00 | Shyampur | 221 | 18:00 | 211 | 00:00
Bogura-400 | 226 | 18:00 | 220 | 12:00 | Siddhirganj | 220 | 17:00 | 212 | 11:00
Borhanuddin | 241 | 18:00 | 232 | 00:00 | Sirajgonj | 236 | 18:00 | 230 | 12:00
BSRM | 230 | 18:00 | 218 | 11:00 | Sreepur | 228 | 18:00 | 216 | 09:00
Cumilla(N) | 224 | 18:00 | 214 | 10:00 | Tongi | 224 | 17:00 | 210 | 07:00
Faridpur | 233 | 18:00 | 218 | 00:00
Fenchuganj | 231 | 18:00 | 218 | 01:00
Ghorashal | 220 | 00:00 | 220 | 00:00
Ghorashal-230 | 227 | 18:00 | 211 | 09:00
Gopalganj | 234 | 18:00 | 222 | 00:00
GPH | 232 | 21:00 | 220 | 12:00
Haripur | 220 | 18:00 | 211 | 11:00
Hasnabad | 231 | 18:00 | 211 | 11:00
Hathazari | 236 | 21:00 | 225 | 07:00
Ishurdi | 235 | 05:00 | 224 | 21:00
Jhenaidah | 230 | 08:00 | 216 | 21:00
Kaliakoir | 229 | 17:00 | 218 | 09:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 141 | 05:00 | 127 | 13:00 | Madartek | 138 | 04:00 | 126 | 11:00
Agargaon | 133 | 05:00 | 125 | 10:00 | Madunaghat | 134 | 00:00 | 127 | 11:00
Agrabad | 135 | 21:00 | 126 | 11:00 | Magura | 134 | 07:00 | 121 | 21:00
AKS | 132 | 20:00 | 125 | 12:00 | Mahasthangarh | 134 | 18:30 | 128 | 03:00
Aminbazar | 132 | 18:00 | 124 | 10:00 | Manikganj | 131 | 18:00 | 122 | 08:00
Amnura | 152 | 23:00 | 121 | 22:00 | Maniknagar | 131 | 06:00 | 124 | 11:00
Ashuganj | 135 | 04:00 | 130 | 09:00 | Matarbari | 126 | 17:00 | 114 | 04:00
Bagerhat | 131 | 18:30 | 118 | 00:00 | Matuail | 128 | 18:00 | 122 | 11:00
Bajitpur | 128 | 04:00 | 122 | 21:00 | Millgate | 133 | 04:00 | 124 | 09:00
Bakulia | 158 | 12:00 | 127 | 11:00 | Mirpur | 129 | 03:00 | 122 | 10:00
Banani | 140 | 05:00 | 127 | 16:00 | Mirzapur | 134 | 18:00 | 125 | 19:00
Bangabhaban | 130 | 08:00 | 124 | 11:00 | Mithapukur | 133 | 19:00 | 128 | 00:00
Barapukuria | 135 | 18:30 | 131 | 02:00 | MI_Cement | 130 | 18:00 | 122 | 10:00
Barguna | 136 | 22:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 132 | 18:00 | 122 | 00:00 | Mogbazar | 142 | 05:00 | 127 | 12:00
Barishal-230 | 132 | 18:00 | 122 | 00:00 | Mongla | 130 | 07:00 | 119 | 00:00
Baroaulia | 134 | 21:00 | 127 | 12:00 | Motijheel | 130 | 08:00 | 124 | 11:00
Baroirhat | 129 | 18:00 | 119 | 03:00 | Muktagacha | 134 | 18:00 | 122 | 19:00
Bashundhara | 139 | 03:00 | 125 | 11:00 | Munshiganj | 129 | 18:00 | 122 | 00:00
BashundharaCement | 130 | 18:00 | 121 | 11:00 | Muradnagar | 129 | 18:00 | 118 | 00:00
Beanibazar | 132 | 16:00 | 121 | 00:00 | Mymensingh | 135 | 18:00 | 109 | 21:00
Benapole | 131 | 18:00 | 116 | 00:00 | Naogaon | 131 | 18:30 | 124 | 02:00
Bhaluka | 135 | 18:00 | 120 | 10:00 | Narail | 134 | 07:00 | 120 | 21:00
Bhandaria | 128 | 17:00 | 110 | 00:00 | Narinda | 131 | 06:00 | 124 | 11:00
Bhangura | 132 | 18:30 | 126 | 21:00 | Narshingdi | 132 | 06:00 | 114 | 21:00
Bheramara | 136 | 07:00 | 130 | 21:00 | Natore | 135 | 18:30 | 128 | 12:00
Bheramara(GK) | 136 | 07:00 | 130 | 12:00 | Nawabganj | 130 | 06:00 | 124 | 00:00
Bhulta | 122 | 18:00 | 116 | 11:00 | Netrakona | 127 | 18:00 | 107 | 21:00
Bog-Sherpur | 133 | 18:30 | 127 | 12:00 | New | 135 | 05:00 | 125 | 09:00
Bogura | 135 | 18:30 | 130 | 11:00 | Niamatpur | 131 | 18:00 | 125 | 21:00
Bogura-230 | 136 | 18:00 | 130 | 12:00 | Noapara | 135 | 04:00 | 121 | 00:00
Brahmanbaria | 127 | 07:00 | 119 | 21:00 | Pabna | 134 | 18:30 | 127 | 21:00
Cantonment | 133 | 07:00 | 125 | 10:00 | Palashbari | 130 | 18:30 | 125 | 22:00
Chandina | 131 | 18:00 | 122 | 00:00 | Panchagarh | 138 | 20:00 | 130 | 13:00
Chandpur | 135 | 18:00 | 122 | 19:00 | Patuakhali | 135 | 18:30 | 129 | 00:00
Chandraghona | 133 | 21:00 | 127 | 11:00 | Payra | 136 | 17:00 | 132 | 00:00
Chapai | 128 | 18:00 | 122 | 23:00 | PHP | 131 | 18:00 | 117 | 02:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 18:00 | 122 | 11:00 | Postogola | 132 | 18:00 | 125 | 10:00
Chauddagram | 128 | 18:00 | 112 | 07:00 | Purbachal | 140 | 04:00 | 127 | 13:00
Chhatak | 129 | 16:00 | 117 | 00:00 | Purbasadipur | 133 | 20:00 | 126 | 06:00
Chowmuhani | 126 | 18:00 | 112 | 02:00 | Rahanpur | 132 | 18:00 | 127 | 21:00
Chuadanga | 135 | 08:00 | 119 | 21:00 | Rahanpur-400 | 132 | 08:00 | 127 | 21:00
Coxsbazar | 125 | 21:00 | 114 | 03:00 | Rahim | 127 | 07:00 | 123 | 10:00
Cumilla(N) | 131 | 03:00 | 121 | 02:00 | Rajbari | 136 | 18:00 | 123 | 00:00
Cumilla(S) | 132 | 05:00 | 121 | 00:00 | Rajendrapur | 131 | 06:00 | 118 | 10:00
Daudkandi | 127 | 18:00 | 117 | 11:00 | Rajshahi | 135 | 18:30 | 128 | 12:00
Dhaka | 139 | 03:00 | 129 | 09:00 | Rajshahi-230 | 135 | 18:30 | 116 | 21:00
Dhamrai | 135 | 18:00 | 127 | 09:00 | Ramganj | 125 | 18:00 | 112 | 23:00
Dhanmondi | 142 | 05:00 | 127.6 | 15:00 | Rampur | 134 | 21:00 | 127 | 09:00
Dohazari | 131 | 19:30 | 125 | 08:00 | Rampura | 141 | 05:00 | 128 | 09:00
Faridpur | 135 | 17:00 | 126 | 00:00 | Rangamati | 132 | 22:00 | 126 | 12:00
Fatullah | 130 | 18:00 | 123 | 10:00 | Rangpur | 132 | 16:00 | 127 | 00:00
Fenchuganj | 136 | 18:00 | 129 | 00:00 | Ruppur | 136 | 07:00 | 130 | 11:00
Feni | 125 | 18:30 | 117 | 19:00 | Saidpur | 131 | 16:00 | 126 | 02:00
Ghatail | 132 | 18:00 | 122 | 19:00 | Satkhira | 132 | 18:00 | 115 | 00:00
Ghorashal | 134 | 06:00 | 126 | 10:00 | Satmasjid | 132 | 07:00 | 125 | 11:00
Goalpara | 135 | 17:00 | 125 | 00:00 | Savar | 130 | 17:00 | 122 | 10:00
Gollamari | 137 | 18:00 | 126 | 00:00 | SevenRings | 135 | 05:00 | 126 | 09:00
Gopalganj | 135 | 18:00 | 124 | 00:00 | ShahCement | 130 | 18:00 | 122 | 11:00
Gopalganj-400 | 136 | 18:00 | 128 | 00:00 | Shahjadpur | 135 | 01:00 | 131 | 12:00
Gulshan | 140 | 05:00 | 128 | 11:00 | Shahjibazar | 129 | 18:00 | 122 | 12:00
Halishahar | 137 | 21:00 | 127 | 09:00 | Shahmirpur | 137 | 22:00 | 129 | 09:00
Haripur | 129 | 18:00 | 122 | 11:00 | Shariatpur | 134 | 18:00 | 124 | 00:00
HaripurSBU | 129 | 18:00 | 122 | 11:00 | Sherpur | 137 | 07:00 | 123 | 22:00
Hasnabad | 130 | 03:00 | 125 | 09:00 | Shikalbaha | 124 | 01:00 | 119 | 08:00
Hathazari | 136 | 23:00 | 129 | 12:00 | Shikalbaha-230 | 137 | 21:00 | 129 | 09:00
Ishurdi | 137 | 07:00 | 131 | 21:00 | Shitalakhya | 130 | 18:00 | 122 | 10:00
Jaldhaka | 130 | 18:30 | 122 | 02:00 | Sholosohor | 135 | 21:00 | 126 | 09:00
Jamalpur | 140 | 23:00 | 125 | 19:00 | Shyampur | 129 | 18:00 | 123 | 00:00
Jashore | 131 | 08:00 | 118 | 00:00 | Shyampur-230 | 128 | 05:00 | 120 | 18:30
Jhenaidah | 135 | 08:00 | 119 | 00:00 | Siddhirganj | 128 | 18:00 | 123 | 10:00
Jhenaidah-230 | 136 | 08:00 | 124 | 22:00 | Sirajganj | 130 | 08:00 | 125 | 21:00
Joydebpur | 134 | 18:00 | 120 | 10:00 | Sonargaon | 126 | 05:00 | 120 | 10:00
Joypurhat | 131 | 20:00 | 122 | 00:00 | Sreemongol | 130 | 15:00 | 123 | 00:00
Juldah | 137 | 21:00 | 128 | 11:00 | Sreepur | 134 | 18:00 | 124 | 09:00
Kabirpur | 135 | 17:00 | 121 | 09:00 | Srinagar | 131 | 05:00 | 124 | 00:00
Kachua | 132 | 18:00 | 120 | 19:00 | SSM | 138 | 00:00 | 131 | 08:00
Kaliakoir | 137 | 18:00 | 130 | 10:00 | Sunamganj | 128 | 16:00 | 115 | 01:00
Kallyanpur | 131 | 05:00 | 123 | 10:00 | Sylhet | 131 | 18:00 | 122 | 00:00
Kalurghat | 131 | 00:00 | 127 | 09:00 | Sylhet-132 | 130 | 16:00 | 123 | 00:00
Kamrangirchar | 130 | 05:00 | 123 | 11:00 | Tangail | 133 | 18:00 | 120 | 19:00
Kaptai | 135 | 1:00 | 130 | 9:00 | Thakurgaon | 138 | 20:00 | 130 | 03:00
Kasba | 129 | 18:00 | 118 | 00:00 | TK | 132 | 21:00 | 126 | 10:00
Kazla | 130 | 07:00 | 124 | 11:00 | Tongi | 136 | 17:00 | 127 | 07:00
Keranigonj | 132 | 18:00 | 124 | 11:00 | Ullahpara | 133 | 19:00 | 126 | 21:00
Khagrachori | 130 | 00:00 | 125 | 12:00 | Ullon | 140 | 05:00 | 128 | 09:00
Khulna | 135 | 18:00 | 122 | 00:00 | Uttara | 130 | 05:00 | 121 | 11:00
Khulna(S) | 137 | 18:00 | 126 | 00:00 | UttaraNew | 131 | 05:00 | 90 | 04:00
Khulshi | 134 | 21:00 | 126 | 09:00 | Zigatola | 131 | 07:00 | 124 | 11:00
Kishoreganj | 129 | 18:00 | 119 | 19:30
Kodda | 134 | 17:00 | 122 | 09:00
KSRM | 134 | 00:00 | 127 | 11:00
Kulaura | 134 | 15:00 | 128 | 00:00
Kurigram | 131 | 18:30 | 126 | 02:00
Kushtia | 134 | 08:00 | 124 | 00:00
Lalbag | 131 | 18:00 | 124 | 00:00
Lalmonirhat | 129 | 16:00 | 124 | 17:00
Madanganj | 130 | 18:00 | 121 | 11:00
Madaripur | 135 | 18:00 | 126 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division