## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 30-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-05-2025 | during | 30-05-2025 | during | 30-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 338 | 305 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 320 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 306 | 274 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 273 | 280 | 335 | 335 | 335 | 335 | -
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 17 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 48 | 16 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 0 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 13 | 14 | 33 | 33 | 18.5 | 18.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 11 | 0 | 22 | 22 | 17 | 17 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 34 | 16 | 52.19 | 52.19 | 52.19 | 52.19 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 124 | 16 | 135 | 135 | 134 | 134 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 34 | 105 | 105 | 88 | 88 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 80 | 80 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 35 | 0 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 2 | 0 | 28 | 0 | 28 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 5 | 0 | 55 | 55 | 0 | 0 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 250 | 300 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 0 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 1843 | 1609 | 5223.9 | 5227.9 | 3446.27 | 3450.27
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 3 | 0 | 3 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 37 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 159 | 184 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 12 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 2 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 2 | 0 | 2.14 | 0 | 2.14 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1060 | 955 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 65 | 48 | 50 | 32 | 50 | 32 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 502 | 450 | 360 | 360 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1830 | 1688 | 3227.86 | 3219.72 | 3442.86 | 3434.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 215 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 320 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 280 | 300 | 335 | 335 | 335 | 335 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 33 | 34 | 46.7 | 46.7 | 34 | 34 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 53 | 20 | 55 | 55 | 53 | 53 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 16 | 16 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 0 | 150 | 150 | 135 | 135 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 90 | 90 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 0 | 0 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 6 | 0 | 17.35 | 17.35 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 0 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 9 | 113 | 113 | 28 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 2 | 0 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 14 | 0 | 15 | 0 | 15 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1035 | 915 | 2403.6 | 2388.6 | 2018.55 | 2003.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 29-05-2025 | during | 30-05-2025 | during | 30-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 75 | 65 | 200 | 200 | 175 | 175 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 45 | 55 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 10.45 | 0 | 20 | 0 | 20 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 143.45 | 132 | 571.1 | 549 | 368.6 | 346.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 38 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 40 | 40 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 128 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 85 | 86 | 86 | 85 | 85 | Allocation limit by Titas, instructed by DS(Gen)
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 102 | 100 | 100 | 102 | 102 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 295 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 304 | 297 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 140 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1131 | 1265 | 1544 | 1544 | 1354 | 1354
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 932 | 883 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 40 | 40 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 93 | 143 | 410 | 410 | 350 | 350 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 23.25 | 0 | 60 | 0 | 60 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 859 | 910 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1907.25 | 1936 | 3572.2 | 3512.2 | 3510.2 | 3450.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 221 | 223 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 2 | 0 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 120 | 0 | 130 | 130 | 130 | 130 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 860 | 890 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 150 | 250 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.03 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1573.03 | 1583 | 2172 | 2171 | 2132 | 2131
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50 | 50 | 50 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 40 | 40 | shundown for maintenance work
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 123 | 143 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 120 | 0 | 220 | 220 | 220 | 220 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 300 | 300 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 0.71 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 861 | 929.15 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 10.57 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 40 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1455.28 | 1372.15 | 3156.37 | 2989.87 | 3154.58 | 2988.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 49 | 50 | 50 | 50 | 50 | 49 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 158 | 161 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 30 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 4.5 | 0 | 2.6 | 0 | 2.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 35 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 0 | 0 | 30 | 0 | 30 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 161 | 0 | 141.5 | 0 | 141.5 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 372.5 | 276 | 636.1 | 462 | 646.1 | 471
System Total |  |  |  |  | 28886.2 | 27110.055 | 11290.51 | 10776.15 | 22507.13 | 22064.29 | 20073.16 | 19629.32
Forecast Scenario (30-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 10230 |  | 0 |  | 10230
|  |  |  | 1:00 | 10010 |  | 0 |  | 10010
|  |  |  | 2:00 | 9830 |  | 0 |  | 9830
|  |  |  | 3:00 | 9600 |  | 0 |  | 9600
|  |  |  | 4:00 | 9340 |  | 0 |  | 9340
|  |  |  | 5:00 | 9160 |  | 0 |  | 9160
|  |  |  | 6:00 | 8260 |  | 0 |  | 8260
|  |  |  | 7:00 | 8000 |  | 0 |  | 8000
|  |  |  | 8:00 | 7650 |  | 0 |  | 7650
|  |  |  | 9:00 | 7840 |  | 0 |  | 7840
|  |  |  | 10:00 | 8280 |  | 0 |  | 8280
|  |  |  | 11:00 | 8660 |  | 0 |  | 8660
|  |  |  | 12:00 | 9110 |  | 0 |  | 9110
|  |  |  | 13:00 | 9650 |  | 0 |  | 9650
|  |  |  | 14:00 | 8910 |  | 0 |  | 8910
|  |  |  | 15:00 | 9040 |  | 0 |  | 9040
|  |  |  | 16:00 | 8520 |  | 0 |  | 8520
|  |  |  | 17:00 | 8680 |  | 0 |  | 8680
|  |  |  | 18:00 | 8660 |  | 0 |  | 8660
|  |  |  | 18:30 | 9300 |  | 0 |  | 9300
|  |  |  | 19:00 | 10480 |  | 0 |  | 10480
|  |  |  | 19:30 | 10580 |  | 0 |  | 10580
|  |  |  | 20:00 | 10660 |  | 0 |  | 10660
|  |  |  | 21:00 | 11080 |  | 0 |  | 11080
|  |  |  | 22:00 | 10880 |  | 0 |  | 10880
|  |  |  | 23:00 | 10600 |  | 0 |  | 10600
Probable Maximum Temperature: |  |  | 28.60°C
Probable Maximum Demand at Day Peak: |  |  | 9110.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 11080.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 11080.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 223.13 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:07 hrs on 30-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [6 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [6 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 29-05-2025 | [28 empty] | Date: | 29-05-2025 | [28 empty] | Date: | 29-05-2025 | [28 empty] | Date: | 29-05-2025 | [28 empty] | Date: | 29-05-2025 | [15 empty] | Date: | 29-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [28 empty] | Day: | Thursday | [15 empty] | Day: | Thursday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 8 | 52 | 16 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 17 | 129 | 81 | 300 | 15 | 35 | 162 | 68 | 350 | 268 | 280 | 0 | 17 | 0 | 267 | 0 | 0 | 0 | 90 | 13.8 | 11 | 0 | 0 | 17 | 50 | 0 | 0 | 52 | 0 | 76 | 0 | 100 | 100 | 0 | 40 | 91 | 30 | 575 | 54 | 0 | 33 | 8 | 105 | 184 | 0 | 0 | 0 | 852 | 0 | 51 | 115 | 0 | 0 | 356 | 300 | 52 | 179 | 33 | 77 | 0 | 200 | 14 | 6 | 114 | 40 | 52.2 | 0 | 38 | 295 | 15 | 346 | 39 | 0 | 0 | 131 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 17 | 92 | 160 | 0 | 0 | 0 | 12 | 7853 | 924 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 20 | 1098.84 | 0 | 0 | 0 | 113 | 0 | 97 | 113 | 0 | 43 | 0 | 22 | 0 | 130 | 0 | 120 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 150 | 50 | 115 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 110 | 220 | 0 | 350 | 1240 | 0 | 6913.04 | 14766.04 | 77.84
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 54 | 17 | 129 | 65 | 300 | 0 | 21 | 162 | 34 | 350 | 260 | 300 | 0 | 17 | 0 | 262 | 0 | 0 | 0 | 17 | 13.8 | 11 | 0 | 0 | 0 | 15 | 0 | 0 | 46 | 34 | 68 | 0 | 100 | 38 | 0 | 40 | 68 | 28 | 575 | 0 | 0 | 33 | 8 | 68 | 184 | 0 | 0 | 0 | 942 | 0 | 51 | 115 | 0 | 0 | 300 | 300 | 52 | 192 | 33 | 72 | 0 | 200 | 14 | 15 | 114 | 38 | 52.2 | 0 | 43 | 300 | 40 | 349 | 39 | 0 | 0 | 149 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 18 | 123 | 0 | 0 | 0 | 12 | 7437 | 925 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1103.98 | 0 | 48 | 0 | 113 | 0 | 95 | 0 | 24 | 0 | 0 | 22 | 0 | 130 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 158 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 6 | 110 | 220 | 0 | 349 | 1244 | 0 | 6849.18 | 14286.18 | 77.88
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 54 | 17 | 129 | 48 | 300 | 0 | 35 | 162 | 34 | 350 | 265 | 300 | 0 | 17 | 0 | 265 | 0 | 0 | 0 | 17 | 13.8 | 11 | 0 | 0 | 0 | 15 | 0 | 0 | 60 | 0 | 24 | 0 | 100 | 38 | 0 | 40 | 68 | 32 | 575 | 0 | 0 | 33 | 0 | 68 | 184 | 0 | 0 | 0 | 1007 | 0 | 51 | 117 | 0 | 0 | 300 | 300 | 52 | 196 | 32 | 74 | 0 | 200 | 9 | 15 | 114 | 38 | 52.2 | 0 | 43 | 295 | 60 | 352 | 39 | 0 | 0 | 147 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 13 | 18 | 123 | 0 | 0 | 0 | 8 | 7453 | 925 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1178 | 0 | 1005.94 | 0 | 48 | 0 | 113 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 130 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 156 | 50 | 115 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 7 | 110 | 220 | 0 | 349 | 1150 | 0 | 6382.94 | 13835.94 | 77.92
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 54 | 17 | 129 | 48 | 95 | 0 | 35 | 162 | 34 | 350 | 270 | 300 | 0 | 17 | 0 | 265 | 0 | 0 | 0 | 17 | 13.8 | 11 | 0 | 0 | 0 | 15 | 0 | 0 | 62 | 0 | 0 | 0 | 100 | 38 | 0 | 38 | 68 | 32 | 575 | 0 | 0 | 33 | 0 | 68 | 184 | 0 | 0 | 0 | 1032 | 0 | 51 | 118 | 0 | 0 | 300 | 300 | 52 | 203 | 32 | 74 | 0 | 200 | 9 | 15 | 114 | 36 | 25 | 0 | 0 | 290 | 60 | 370 | 39 | 0 | 0 | 148 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 17 | 18 | 123 | 0 | 0 | 0 | 9 | 7212.8 | 925 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1105 | 0 | 1023.59 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 134 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 120 | 220 | 0 | 350 | 1130 | 0 | 6232.59 | 13445.39 | 77.96
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 54 | 17 | 129 | 48 | 95 | 0 | 35 | 144 | 34 | 350 | 270 | 300 | 0 | 17 | 0 | 263 | 0 | 0 | 0 | 17 | 13.8 | 11 | 0 | 0 | 0 | 15 | 0 | 0 | 57 | 0 | 0 | 0 | 100 | 38 | 0 | 38 | 68 | 32 | 575 | 0 | 0 | 33 | 0 | 68 | 184 | 0 | 0 | 0 | 1033 | 0 | 51 | 118 | 0 | 0 | 300 | 300 | 52 | 204 | 32 | 73 | 0 | 200 | 9 | 15 | 114 | 18 | 8 | 0 | 0 | 310 | 60 | 353 | 39 | 0 | 0 | 151 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 17 | 18 | 123 | 0 | 0 | 0 | 12 | 7178.8 | 925 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 0 | 1018.36 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 131 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 116 | 220 | 0 | 349 | 1000 | 0 | 5986.36 | 13165.16 | 78
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 54 | 17 | 120 | 48 | 0 | 0 | 0 | 144 | 34 | 350 | 272 | 300 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 17 | 13.8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 70 | 0 | 0 | 36 | 68 | 32 | 575 | 0 | 0 | 19 | 0 | 68 | 184 | 0 | 0 | 0 | 1027 | 0 | 51 | 70 | 0 | 0 | 300 | 300 | 52 | 208 | 32 | 75 | 0 | 155 | 9 | 15 | 88 | 34 | 0 | 0 | 0 | 305 | 60 | 350 | 39 | 0 | 0 | 151 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 17 | 18 | 123 | 0 | 0 | 0 | 12 | 6809.8 | 924 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1047 | 0 | 1005.12 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 133 | 50 | 72 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 110 | 220 | 0 | 348 | 1000 | 0 | 5883.12 | 12692.92 | 78.04
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 342 | 0 | 0 | 24 | 17 | 113 | 48 | 0 | 0 | 0 | 17 | 21 | 350 | 285 | 300 | 0 | 0 | 0 | 264 | 0 | 0 | 3 | 17 | 13.8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 32 | 575 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1027 | 0 | 51 | 0 | 0 | 0 | 300 | 280 | 51 | 210 | 32 | 74 | 0 | 68 | 0 | 15 | 78 | 30 | 0 | 0 | 0 | 300 | 60 | 300 | 39 | 0 | 0 | 137 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 17 | 18 | 132 | 0 | 0 | 3.07 | 12 | 6164.87 | 925 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.27 | 1058 | 0 | 1009.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3.88 | 130 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0.32 | 0 | 132 | 50 | 35 | 1 | 0 | 0 | 0 | 0.3 | 4 | 0 | 0 | 150 | 0 | 90 | 180 | 0 | 349 | 1050 | 0 | 5714.83 | 11879.7 | 78.08
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 17 | 129 | 48 | 0 | 0 | 0 | 0 | 16 | 350 | 300 | 300 | 0 | 0 | 0 | 266 | 0 | 0 | 6 | 17 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 25 | 503 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1027 | 0 | 51 | 0 | 0 | 0 | 300 | 280 | 52 | 211 | 32 | 34 | 0 | 0 | 0 | 14 | 0 | 28 | 0 | 1 | 0 | 305 | 60 | 303 | 39 | 0 | 0 | 133 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 56 | 131 | 0 | 0 | 5.8 | 12 | 5911 | 925 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.16 | 1021 | 0 | 1013.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6.49 | 130 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0.55 | 0 | 161 | 50 | 35 | 5 | 0 | 0 | 0 | 1 | 26 | 0.01 | 0 | 150 | 0 | 90 | 180 | 0 | 319 | 1000 | 0 | 5676.37 | 11587.37 | 78.12
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 17 | 129 | 48 | 0 | 0 | 0 | 0 | 0 | 300 | 305 | 300 | 0 | 0 | 0 | 281 | 0 | 0 | 3 | 17 | 13 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 7 | 366 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 1035 | 0 | 51 | 0 | 0 | 0 | 300 | 280 | 52 | 214 | 33 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 0 | 300 | 60 | 345 | 39 | 0 | 0 | 130 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 56 | 130 | 0 | 1 | 16.26 | 12 | 5696.26 | 884 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 931 | 0 | 933.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 16.56 | 129 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 1.64 | 0 | 155 | 50 | 50 | 6 | 0 | 0 | 0 | 2.8 | 80 | 0.04 | 0 | 150 | 0 | 100 | 180 | 0 | 219 | 880 | 0 | 5347.49 | 11043.75 | 78.16
09:00 | 0 | 52 | 25 | 0 | 0 | 0 | 0 | 0 | 349 | 0 | 0 | 0 | 0 | 129 | 48 | 0 | 0 | 17 | 0 | 0 | 300 | 296 | 250 | 0 | 0 | 0 | 272 | 0 | 0 | 6 | 35 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 1 | 40 | 0 | 2 | 370 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 981 | 0 | 51 | 0 | 0 | 0 | 300 | 280 | 51 | 180 | 34 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 2 | 0 | 320 | 60 | 312 | 39 | 0 | 0 | 148 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 55 | 129 | 0 | 2 | 24.65 | 12 | 5646.65 | 883 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.28 | 796 | 0 | 903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 9.4 | 125 | 0 | 120 | 0 | 0 | 0 | 250 | 0 | 1.2 | 0 | 157 | 50 | 35 | 7 | 0 | 0 | 0 | 5.3 | 88 | 0 | 0 | 150 | 2 | 100 | 180 | 0 | 223 | 840 | 0 | 5077.18 | 10723.83 | 78.2
10:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 129 | 48 | 0 | 0 | 17 | 0 | 0 | 300 | 300 | 250 | 0 | 0 | 0 | 263 | 0 | 0 | 4 | 17 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 365 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 914 | 0 | 43 | 0 | 0 | 0 | 280 | 280 | 53 | 180 | 34 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 7 | 0 | 310 | 109 | 300 | 39 | 0 | 0 | 147 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 45 | 85 | 0 | 1 | 6.05 | 12 | 5467.05 | 912 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.93 | 859 | 0 | 916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 9.93 | 124 | 0 | 120 | 0 | 0 | 0 | 250 | 0 | 0.89 | 0 | 158 | 49 | 35 | 15 | 0 | 0 | 0 | 4.4 | 132 | 0.03 | 0 | 150 | 0 | 90 | 180 | 0 | 221 | 890 | 0 | 5272.18 | 10739.23 | 78.22
11:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 122 | 48 | 0 | 0 | 17 | 25 | 0 | 300 | 311 | 250 | 0 | 0 | 0 | 282 | 0 | 0 | 3 | 17 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 406 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 907 | 0 | 43 | 0 | 0 | 0 | 349 | 280 | 53 | 214 | 31 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 19 | 0 | 310 | 125 | 337 | 40 | 0 | 0 | 145 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 75 | 0 | 1 | 10.14 | 12 | 5729.14 | 931 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.02 | 857 | 0 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 14.95 | 124 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0.97 | 0 | 155 | 49 | 0 | 26 | 0 | 0 | 0 | 4.8 | 136 | 0.04 | 0 | 150 | 2 | 120 | 220 | 0 | 220 | 850 | 0 | 5251.78 | 10980.92 | 78.23
12:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 5 | 124 | 48 | 0 | 0 | 17 | 35 | 0 | 300 | 306 | 250 | 0 | 0 | 0 | 273 | 0 | 0 | 2 | 17 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 2 | 40 | 0 | 2 | 502 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 0 | 0 | 1060 | 0 | 43 | 0 | 0 | 0 | 355 | 280 | 53 | 215 | 33 | 2 | 0 | 0 | 0 | 6 | 34 | 0 | 0 | 14 | 0 | 305 | 140 | 304 | 39 | 0 | 0 | 156 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 75 | 0 | 1 | 10.45 | 12 | 5982.45 | 932 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.25 | 859 | 0 | 861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10.57 | 123 | 0 | 120 | 0 | 0 | 0 | 300 | 0 | 0.71 | 0 | 158 | 49 | 0 | 0 | 0 | 0 | 0 | 4.5 | 161 | 0.03 | 0 | 150 | 2 | 120 | 220 | 0 | 221 | 860 | 0 | 5308.06 | 11290.51 | 78.23
13:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 94 | 48 | 0 | 0 | 17 | 80 | 0 | 300 | 311 | 250 | 0 | 0 | 0 | 283 | 0 | 0 | 10 | 17 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 551 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1100 | 0 | 43 | 0 | 0 | 0 | 280 | 280 | 53 | 180 | 30 | 50 | 0 | 17 | 6 | 6 | 34 | 34 | 0 | 4 | 0 | 310 | 171 | 390 | 39 | 0 | 0 | 143 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 75 | 0 | 1 | 6.81 | 5 | 6161.81 | 932 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.65 | 858 | 0 | 864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 19.31 | 127 | 0 | 98 | 0 | 0 | 0 | 260 | 0 | 1.88 | 0 | 158 | 50 | 0 | 12 | 0 | 0 | 0 | 4.7 | 10 | 0.06 | 0 | 150 | 2 | 110 | 180 | 0 | 223 | 850 | 0 | 5077.6 | 11239.41 | 78.23
14:00 | 0 | 70 | 34 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 16 | 81 | 48 | 0 | 0 | 17 | 72 | 0 | 300 | 287 | 250 | 0 | 0 | 0 | 274 | 0 | 0 | 5 | 17 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 1 | 39 | 0 | 2 | 500 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 1068 | 0 | 43 | 0 | 0 | 0 | 280 | 280 | 53 | 162 | 32 | 18 | 0 | 17 | 9 | 6 | 17 | 0 | 0 | 2 | 0 | 315 | 227 | 362 | 39 | 0 | 0 | 136 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 75 | 0 | 0 | 14.7 | 1 | 5947.7 | 932 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.59 | 859 | 0 | 867.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 12.64 | 145 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 1.01 | 0 | 155 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0.07 | 0 | 150 | 2 | 100 | 180 | 0 | 224 | 840 | 0 | 5025.44 | 10973.14 | 78.23
15:00 | 0 | 52 | 34 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 34 | 32 | 0 | 0 | 35 | 35 | 0 | 300 | 297 | 250 | 0 | 0 | 0 | 290 | 0 | 0 | 1 | 17 | 13 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 1 | 36 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 997 | 0 | 43 | 0 | 0 | 0 | 320 | 280 | 48 | 162 | 31 | 18 | 0 | 0 | 9 | 8 | 17 | 0 | 0 | 6 | 0 | 300 | 320 | 382 | 39 | 0 | 0 | 131 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 65 | 0 | 1 | 6.61 | 8 | 5836.61 | 932 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.96 | 780 | 0 | 866.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 4.79 | 143 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0.54 | 0 | 157 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0.05 | 0 | 150 | 5 | 100 | 180 | 0 | 224 | 770 | 0 | 4821.53 | 10658.14 | 78.23
16:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 35 | 17 | 0 | 300 | 306 | 280 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 454 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 955 | 0 | 43 | 0 | 0 | 0 | 320 | 280 | 46 | 183 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 320 | 370 | 40 | 0 | 0 | 140 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 55 | 55 | 0 | 0 | 2.89 | 12 | 5754.89 | 932 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.09 | 755 | 0 | 863.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 2.55 | 143 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0.19 | 0 | 158 | 50 | 0 | 7 | 0 | 0 | 0 | 0 | 18 | 0.11 | 0 | 150 | 0 | 100 | 215 | 0 | 224 | 725 | 0 | 4750.18 | 10505.07 | 78.23
17:00 | 0 | 34 | 17 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 17 | 0 | 300 | 283 | 280 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 400 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 920 | 0 | 43 | 0 | 0 | 0 | 320 | 280 | 50 | 181 | 31 | 11 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0 | 290 | 320 | 349 | 38 | 0 | 0 | 135 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 55 | 55 | 0 | 0 | 3.41 | 12 | 5567.41 | 933 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.68 | 758 | 0 | 823.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 1.63 | 143 | 0 | 0 | 0 | 0 | 0 | 270 | 0 | 0.18 | 0 | 135 | 50 | 0 | 7 | 0 | 0 | 0 | 2.8 | 18 | 0.12 | 0 | 150 | 3 | 0 | 220 | 0 | 221 | 740 | 0 | 4613.73 | 10181.14 | 78.23
18:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 311 | 250 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 361 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 830 | 0 | 43 | 0 | 0 | 0 | 280 | 290 | 32 | 180 | 34 | 16 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 290 | 320 | 312 | 38 | 0 | 0 | 136 | 0 | 0 | 51 | 0 | 0 | 0 | 102 | 0 | 45 | 45 | 0 | 0 | 0.71 | 12 | 5279.71 | 932 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.28 | 758 | 0 | 824.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 126 | 50 | 0 | 3 | 0 | 0 | 0 | 0.5 | 2 | 0.01 | 0 | 150 | 0 | 0 | 180 | 0 | 224 | 700 | 0 | 4573.35 | 9853.06 | 78.23
19:00 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 9 | 0 | 16 | 16 | 0 | 0 | 11 | 0 | 0 | 320 | 282 | 300 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 17 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 12 | 0 | 0 | 35 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 0 | 0 | 320 | 300 | 28 | 181 | 34 | 16 | 0 | 0 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 305 | 320 | 307 | 38 | 0 | 0 | 136 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 55 | 65 | 0 | 0 | 0 | 12 | 5671 | 884 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 0 | 974.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 161 | 50 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 210 | 0 | 220 | 755 | 0 | 5042.9 | 10713.9 | 78.23
19:30 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 17 | 0 | 16 | 16 | 0 | 0 | 17 | 0 | 0 | 320 | 274 | 300 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 12 | 0 | 0 | 37 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 0 | 0 | 320 | 300 | 20 | 181 | 34 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 320 | 297 | 38 | 0 | 0 | 128 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 55 | 65 | 0 | 0 | 0 | 12 | 5609 | 883 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 0 | 929.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 161 | 50 | 35 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 220 | 0 | 223 | 890 | 0 | 5167.15 | 10776.15
20:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 289 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 17 | 0 | 0 | 320 | 266 | 300 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 2 | 450 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 955 | 0 | 51 | 0 | 0 | 0 | 320 | 300 | 20 | 181 | 34 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 320 | 287 | 38 | 0 | 0 | 129 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 5538 | 884 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 0 | 930.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 162 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 220 | 0 | 222 | 900 | 0 | 5070.79 | 10608.79 | 78.23
21:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 300 | 280 | 270 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 400 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 900 | 0 | 51 | 0 | 0 | 0 | 320 | 300 | 20 | 181 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 320 | 297 | 38 | 0 | 0 | 134 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 5385 | 932 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 0 | 856.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 162 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 220 | 0 | 222 | 800 | 0 | 4905.08 | 10290.08 | 78.23
22:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 240 | 270 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 400 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 828 | 0 | 51 | 0 | 0 | 0 | 300 | 280 | 20 | 181 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 320 | 306 | 37 | 0 | 0 | 129 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 45 | 55 | 0 | 0 | 0 | 12 | 5208 | 932 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 802 | 0 | 830.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 165 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 220 | 0 | 223 | 720 | 0 | 4693.47 | 9901.47 | 78.23
23:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 220 | 270 | 0 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 805 | 0 | 51 | 0 | 0 | 0 | 300 | 280 | 20 | 181 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 320 | 309 | 39 | 0 | 0 | 141 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 8 | 24 | 0 | 0 | 0 | 12 | 5078 | 932 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 758 | 0 | 826.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 166 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 2 | 0 | 220 | 0 | 221 | 691 | 0 | 4620.02 | 9698.02 | 78.23
Total KWH | 0 | 871680 | 425760 | 0 | 0 | 0 | 0 | 0 | 7984800 | 0 | 0 | 322200 | 183600 | 1897200 | 865440 | 966502 | 4525 | 371370 | 1154880 | 225600 | 7800000 | 6743098 | 6745750 | 0 | 82170 | 0 | 6622539 | 0 | 0 | 39196 | 361200 | 279000 | 176760 | 0 | 0 | 11291 | 70255 | 0 | 0 | 1442400 | 50368 | 139056 | 0 | 537600 | 176640 | 9000 | 917340 | 411489 | 239040 | 11214545.46 | 0 | 0 | 165120 | 13005 | 403964 | 4079894 | 0 | 0 | 0 | 23072725 | 0 | 1119560 | 625600 | 0 | 0 | 7675000 | 7074000 | 1038720 | 4599000 | 786744 | 698880 | 0 | 1157760 | 106680 | 156450 | 784320 | 302400 | 179510 | 72973 | 125600 | 7382000 | 4300200 | 8451000 | 924000 | 0 | 0 | 3379745 | 0 | 0 | 1973760 | 0 | 0 | 0 | 2447300 | 97200 | 956400 | 2112000 | 0 | 6000 | 117190 | 262080 | 145989074.46 | 22293090 | 2963232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237600 | 21643640 | 6240 | 22040727 | 0 | 133704 | 0 | 578688 | 14222 | 120352 | 32640 | 63265 | 8640 | 286590 | 55549 | 119256 | 3448482 | 0 | 1655727 | 0 | 0 | 0 | 7232872 | 0 | 11220 | 0 | 3718000 | 1124072 | 884772 | 112569 | 494236 | 0 | 0 | 25266.48 | 803520 | 657 | 0 | 4211000 | 52031 | 1758000 | 5164710 | 0 | 7163640 | 21989818.18 | 0 | 130448027.66 | 276437102.12

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 29-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 11290.51 | MW | 12:00 Hr. | Energy Generated |  |  | 276.4371 |  | MKWHr.
| Day Peak Demand |  |  | 11312.51 | MW | 12:00 Hr. | Energy Unserverd |  |  | 2.586 |  | MKWHr.
| Evening Peak Generation |  |  | 10776.15 | MW | 19:30 Hr. | Energy Demand |  |  | 279.0231 |  | MKWHr.
| Evening Peak Demand |  |  | 10776.15 | MW | 19:30 Hr. | Maximum Temperature |  |  | 26.2 |  | °C
| Minimum Generation of the Day |  |  | 9698.02 | MW | 23:00 Hr. | Total Gas Supplied |  |  | 785.56 |  | MMCFD
| Maximum Generation of the Day |  |  | 14766.04 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 5.9117 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 36.3519 | 0 | 7.7321 | 0 | 0 | 0.039196 | 0 | 0 | 44.1233 | Gas | 114.2534 | Gas | 407011723.19
| Chattogram Zone |  |  | 4.3189 | 34.2873 | 1.9788 | 0 | 0.91734 | 0.009 | 0 | 1.4424 | 42.9537 | Coal | 94.1374 | Coal | 604339441.7706
| Cumilla Zone |  |  | 22.4495 | 0 | 3.6784 | 0 | 0 | 0.072973 | 0.3024 | 0 | 26.5032 | HFO | 19.2093 | HFO | 356094246
| Mymensingh Zone |  |  | 0 | 0 | 3.4277 | 0 | 0 | 0.12319 | 0 | 0 | 3.5509 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 28.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.858 | Hydro | 0.91734 | Hydro | 91734
| Khulna Zone |  |  | 2.9632 | 21.6436 | 0.00624 | 0 | 0 | 0.2376 | 22.2931 | 0 | 47.1438 | Solar | 1.841 | Solar | 31305212.4828
| Barishal Zone |  |  | 6.9747 | 33.3645 | 0 | 0 | 0 | 0.000657 | 0 | 0 | 40.3399 | Import | 44.6362 | Import | 214260462.66
| Rajshahi Zone |  |  | 12.3371 | 0 | 1.0071 | 0 | 0 | 0.41707 | 22.0407 | 0 | 35.8019 | Wind | 1.4424 | Wind | 21116736
| Rangpur Zone |  |  | 0 | 4.8421 | 1.379 | 0 | 0 | 0.94136 | 0 | 0 | 7.1624
| Total |  |  | 114.2534 | 94.1374 | 19.2093 | 0 | 0.91734 | 1.841 | 44.6362 | 1.4424 | 276.4371
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 407011723.19 |  | Hydro | 91734
|  |  |  | Coal | 604339441.7706 |  | Solar | 31305212.4828
|  |  |  | HFO | 356094246 |  | Import | 214260462.66
|  |  |  | HSD | 0 |  | Wind | 21116736
[5 empty] | Total: | 163,42,19,556 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2931 | Peak Hr Flow | 883.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 44912563.71 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 22.0407 | Peak Hr Flow | 929.15 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 518 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.3024 | Peak Hr Flow | 0
Maximum Power Flow: |  |  | MW: | 988 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 44.6362 | Peak Hr Flow | 1812.15 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4252
|  |  |  | Chattogram |  | 0 |  | 1020
|  |  |  | Cumilla |  | 0 |  | 446
|  |  |  | Mymensingh |  | 0 |  | 514
|  |  |  | Sylhet |  | 0 |  | 516
|  |  |  | Khulna |  | 0 |  | 1356
|  |  |  | Barishal |  | 0 |  | 210
|  |  |  | Rajshahi |  | 0 |  | 1123
|  |  |  | Rangpur |  | 0 |  | 791
|  |  |  | Total |  | 0 |  | 10228
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:05 | Kabirpur 132/33kV S/S XFR, T-2 HT is restored.
| 09:14 |  | Bibiyana South 400MW CCPP ST was synchronized.
| 09:14 |  | Bibiyana South 400 MW Synchronized with remarks:- st
| 09:35 | 11:02 | Srinagar 132/33kV S/S Tr-01 HT Scheduled S/D Due to ৩৩ কেভি ইনকামার-০১ এর backup energy
meter প্রতিস্থাপনের জন্য
|  | 10:07 | Hathazari 230/132/33kV S/S T-02 HT is restored.
|  | 10:07 | Hathazari 230/132/33kV S/S T-02 LT is restored.
|  | 10:37 | Sylhet 132/33kV S/S T4 HT is restored.
|  | 10:37 | Sylhet 132/33kV S/S T4 LT is restored.
| 10:48 |  | Import (Tripura) Synchronized
| 11:03 | 11:59 | Srinagar 132/33kV S/S Tr-02 HT Scheduled S/D Due to ৩৩ কেভি ইনকামার-০২ এর backup energy
meter প্রতিস্থাপনের জন্য Shutdown নেয়া হয়।
| 11:12 | 15:58 | Savar 132/33kV S/S T-4 LT Scheduled S/D Due to busbar protection work | [7 empty] | 41.0MW load
interrup.
| 11:13 | 15:58 | Savar 132/33kV S/S T-4 HT Scheduled S/D Due to busbar protection work | [7 empty] | 41.0MW load
interrup.
| 11:15 | 15:57 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to busbar protection work | [7 empty] | 41.0MW load
interrup.
| 11:17 | 15:57 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to busbar protection work | [7 empty] | 41.0MW load
interrup.
| 11:34 | 18:49 | Gopalganj 400/132kV S/S 400kV Bus-02 Project Work S/D
| 11:35 | 13:13 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D | [7 empty] | 10.0MW load
interrup.
|  | 11:37 | Ghorasal-Joydeb-B 132kV Ckt-2 is restored.
| 11:37 | 13:11 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D | [7 empty] | 10.0MW load
interrup.
|  | 11:59 | Haripur-Narsingdi 132kV Ckt-1 is restored.
| 12:00 |  | Day Peak Gen. 11290 MW
| 12:03 | 12:07 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 44.0MW load
interrup.
| 12:03 | 12:07 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Tripped showing FBCPU relays Due to df/dt | [7 empty] | 48.0MW load
interrup.
| 12:54 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- ST
| 12:54 |  | Sirajgonj 225MW CCPP Unit-2 ST Shutdown with remarks:- None
| 13:01 |  | Sirajgonj 225MW CCPP Unit-2 Shutdown with remarks:- GT
| 13:01 |  | Sirajgonj 225MW CCPP Unit-2 GT Shutdown with remarks:- None
| 13:01 |  | Sirajganj Unit-2 was shutdown due to gas shortage.
| 13:16 | 15:37 | Khulna(S) 230/132kV S/S 230 KV Main Bus 1 Scheduled S/D
| 13:38 |  | Import (Tripura) Tripped
| 13:44 | 14:29 | Keraniganj-Nawabganj 132kV Ckt-2 Scheduled S/D from Nawabganj 132/33kV end Due to
Replacing energy meter by metering division.
| 13:55 | 14:42 | Barishal 230/132kV S/S T-5 HT Tripped showing Over current relays Due to Korapur 33kv | [7 empty] | 13.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 13:55 | 15:55 | Barishal 230/132kV S/S T-4 LT Tripped showing Over current relays Due to 33kv Korapur | [7 empty] | 13.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 13:55 | 14:43 | Barishal 230/132kV S/S T-5 LT Tripped showing Over current relays Due to 33 kv Korapur | [7 empty] | 13.0MW load
|  |  | feeder fault | [7 empty] | interrup.
| 14:05 | 15:04 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Forced S/D Due to maintenance of Jack Bus
| 14:06 | 15:04 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Forced S/D Due to maintenance of Jack Bus
| 14:40 | 15:50 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to 33kv Busbar maintenance due to Korapur | [7 empty] | 12.0MW load
|  |  | 33kv feeder fault | [7 empty] | interrup.
| 15:26 | 16:12 | Nawabganj 132/33kV S/S TR-2 LT Scheduled S/D Due to Replacing energy meter by metering
division.
| 15:28 | 16:11 | Nawabganj 132/33kV S/S TR-2 HT Scheduled S/D Due to Replacing energy meter by metering
division.
| 15:37 | 15:44 | Nawabganj 132/33kV S/S TR-1 LT Tripped showing Lock out relay 1,2 relays Due to 33 kV | [7 empty] | 12.0MW load
|  |  | Sholla feeder | [7 empty] | interrup.
| 17:37 | 17:42 | Nawabganj 132/33kV S/S TR-1 LT Tripped showing Lock out relay1,2 relays Due to Incomer 1 | [7 empty] | 12.0MW load
|  |  | tripped due to Sholla feeder fault | [7 empty] | interrup.
| 17:37 | 17:43 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Lock out relay 1,2 relays Due to Tripped | [7 empty] | 12.5MW load
|  |  | due to Sholla feeder fault | [7 empty] | interrup.
| 20:02 |  | Borhanuddin 230/33 Transformer(PDB) Tripped Due to Oil Overflow. | [7 empty] | 8MW load interrup.
| 21:21 |  | Borhanuddin 230/33 Transformer(PDB) Tripped Due to Oil Overflow. | [7 empty] | 8MW load interrup.
| 22:23 | 22:38 | Narshingdi 132/33kV S/S T-4 LT Tripped showing Lockout operated relays Due to df/dt fault | [7 empty] | 2.0MW load
interrup.
| 23:40 | 23:51 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing RET670,REF615 relays Due to 33 KV Laksham | [7 empty] | 4.0MW load
|  |  | REB feeder fault. | [7 empty] | interrup.
| 01:15 |  | TK chemical 132/33 kV T2 transformer was forced shut down at 01:15hr due to 33kV yellow
phase bushing connector torn. No interruption is occurring due to bad weather.
| 01:30 | 01:38 | Barishal 132/33kV S/S T-2 (415T) LT Tripped showing Instt. OC, Definite OC, Lock out. | [7 empty] | 34.0MW load
|  |  | relays Due to 33 kV nolcity feeder trip. | [7 empty] | interrup.
| 03:35 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 LT Tripped showing Diff, Master trip relays Due to
Diff trip C phase
| 03:35 |  | Chuadanga 132/33kV S/S 132kV Tr. T3 HT Tripped showing Diff, Master trip relays Due to
Diff trip C phase
| 03:43 | 04:23 | Halishahar 132/33kV S/S 415T(TR-2) HT Tripped showing Transformer relay. relays Due to | [7 empty] | 13.0MW load
|  |  | Over voltage | [7 empty] | interrup.
| 03:43 | 04:22 | Halishahar 132/33kV S/S 405T(TR-1) HT Tripped showing Transformer relay. relays Due to | [7 empty] | 12.0MW load
|  |  | Over voltage. | [7 empty] | interrup.
| 03:44 |  | Meghnaghat CCPP(Summit) Shutdown with remarks:- GT1
| 03:44 |  | Meghnaghat CCPP(Summit) GT-1 Shutdown with remarks:- NLDC asked for one unit Shut down,
GT-1 Shut down given at 3:44 hrs.
| 03:45 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT-2(False)
| 03:48 | 04:38 | Halishahar-Khulshi 132kV Ckt-1 Tripped from Halishahar 132/33kV end showing Feeder
relay,line distance relay relays Due to Over voltage.
| 04:14 |  | Meghnaghat CCPP(Summit), FGMO is OFF with remarks:-
| 04:21 |  | Sirajgonj 225MW CCPP Unit-1 ST Shutdown with remarks:- ST has been subjected to shutdown
as per instruction of NLDC.
| 04:21 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- ST
| 04:51 |  | Sirajgonj 225MW CCPP Unit-1 GT Shutdown with remarks:- GT has been subjected to shutdown
as per instruction of NLDC.
| 04:51 |  | Sirajgonj 225MW CCPP Unit-1 Shutdown with remarks:- GT
| 05:57 | 06:12 | Narshingdi 132/33kV S/S T-4 LT Tripped showing Lockout relays Due to df/dt | [7 empty] | 4.0MW load
interrup.
| 06:00 |  | Minimum Generation is 7297 MW
| 06:00 |  | Minimum generation 7297 MW
| 06:12 |  | Khulna(C )-Khulna (S) 132kV Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end. and from
Khulna (C) end Due to RED HOT MAINTENANCE.
| 06:35 |  | Tongi 230/132/33kV S/S T-03 HT Scheduled S/D Due to Spare Transformer Charge.
| 06:35 |  | Tongi 230/132/33kV S/S T-03 LT Scheduled S/D Due to Spare Transformer Charge.
| 07:17 |  | Bogura 230/132kV S/S T-02 LT Tripped showing No relay indication relays.
| 07:17 |  | Bogura 230/132kV S/S T-02 HT Tripped showing RET316*4 relays Due to PRD/winding Trip
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 29-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 305 | 7984800 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7800000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 274 | 6743098 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 4525 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6622539 | FGMO
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 17 | 322200 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 16 | 865440 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 371370 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 82170 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 14 | 279000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 0 | 176760 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 16 | 425760 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 966502 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 16 | 1897200 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 34 | 871680 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 225600 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 1154880 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 39196 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 183600 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 300 | 6745750 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 0 | 361200 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 1609 | 44123270
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 13005 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 0 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 165120 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 37 | 917340 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 184 | 4079894 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 403964 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 139056 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 50368 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 537600 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 2 | 239040 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 9000 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 70255 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 411489 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 176640 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 11291 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 955 | 23072725 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 48 | 1442400 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 450 | 11214545.46 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 1688 | 42953732.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4599000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 320 | 7675000 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 300 | 7074000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 34 | 786744 | machine problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 20 | 1038720 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 0 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1119560 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 625600 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 125600 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 0 | 1157760 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 0 | 302400 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 179510 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 0 | 156450 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 784320 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 106680 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 0 | 698880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 72973 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 915 | 26503197
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6000 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 65 | 2112000 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 55 | 956400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 117190 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 262080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 97200 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 132 | 3550870
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 38 | 924000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 128 | 3379745 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1973760 | Allocation limit by Titas, instructed by DS(Gen)
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2447300 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7382000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 297 | 8451000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 4300200 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1265 | 28858005
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 883 | 22293090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 143 | 2963232 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 6240 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 237600 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 910 | 21643640 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 1936 | 47143802
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 223 | 7163640 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 0 | 52031 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 1758000 | FGMO
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 890 | 21989818.18 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5164710 | MVAR Subjected to Grid Voltage.
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 4211000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 657 | -
Barishal Area Total |  |  |  |  | 2236 | 1583 | 40339856.18
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 133704 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 14222 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 63265 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 143 | 3448482 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 1655727 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 300 | 7232872 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 55549 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 8640 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 120352 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 578688 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 32640 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 11220 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 929.15 | 22040727 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 119256 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 286590 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1372.15 | 35801934
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1124072 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 3718000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 30 | 494236 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 25266.48 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 35 | 884772 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 112569 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 803520 | -
Rangpur Area Total |  |  |  |  | 950 | 276 | 7162435.48
Eastern Grid Total |  |  |  |  | 16771.895 | 5609 | 145989074.46
Western Grid Total |  |  |  |  | 10338.16 | 5167.15 | 130448027.66
National Grid Total |  |  |  |  | 27110.055 | 10776.15 | 276437102.12
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 29-05-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 6747.23 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 3480.1 | MW
i) Dhaka area |  |  | 4251.5 |  | MW | i) Khulna area |  |  |  | 1356 | MW
ii) Chattogram area |  |  | 1020 |  | MW | ii) Barishal area |  |  |  | 210.5 | MW
iii) Cumilla area |  |  | 445.73 |  | MW | iii) Rajshahi area |  |  |  | 1122.6 | MW
iv) Mymensingh area |  |  | 514 |  | MW | iv) Rangpur area |  |  |  | 791 | MW
v) Sylhet area |  |  | 516 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 10227.33 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 10 | 10:00 | 67 | Ishurdi | 78 | 00:00 | 133 | Patuakhali | 45 | 00:00
2 | AKSML | 132 | 00:00 | 68 | Jaldhaka | 80 | 02:00 | 134 | Payra | 18 | 19:30
3 | Aftabnagar | 38 | 00:00 | 69 | Jamalpur | 109 | 09:00 | 135 | Postogola | 58 | 00:00
4 | Agargaon | 127 | 00:00 | 70 | Jashore | 135 | 00:00 | 136 | Purbachal | 21 | 00:00
5 | Agrabad | 86 | 12:00 | 71 | Jhenaidah | 124 | 00:00 | 137 | Purbasadipur | 132 | 02:00
6 | Amnura | 37 | 00:00 | 72 | Joydebpur | 137 | 12:00 | 138 | Rahanpur | 30 | 00:00
7 | Ashuganj | 90 | 00:00 | 73 | Joypurhat | 65 | 00:00 | 139 | Rahim | 54 | 00:00
8 | BSRM | 201 | 00:00 | 74 | Juldah | 13.5 | 00:00 | 140 | Rajbari | 78 | 00:00
9 | Bagerhat | 74 | 20:00 | 75 | KSRM | 21 | 07:00 | 141 | Rajendrapur | 133 | 01:00
10 | Bajitpur | 55 | 00:00 | 76 | Kabirpur | 272 | 00:00 | 142 | Rajshahi | 124 | 01:00
11 | Bakulia | 89 | 12:00 | 77 | Kachua | 90 | 00:00 | 143 | Rajshahi-230 | 74 | 00:00
12 | Banani | 34 | 11:00 | 78 | Kallyanpur | 108 | 00:00 | 144 | Ramganj | 108 | 00:00
13 | Bangabhaban | 17 | 12:00 | 79 | Kalurghat | 39 | 09:00 | 145 | Rampur | 41 | 00:00
14 | Barapukuria | 60 | 02:00 | 80 | Kamrangirchar | 66.2 | 13:00 | 146 | Rangamati | 15 | 19:00
15 | Barguna | 12 | 22:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 137 | 03:00
16 | Barishal | 103 | 00:00 | 82 | Kasba | 37 | 00:00 | 148 | Ruppur | 7.6 | 15:00
17 | Barishal-230 | 84 | 00:00 | 83 | Kazla | 104 | 00:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 66 | 12:00 | 84 | Keranigonj | 98 | 00:00 | 150 | Saidpur | 108 | 08:00
19 | Baroirhat | 60 | 00:00 | 85 | Khagrachori | 28 | 00:00 | 151 | Satkhira | 132 | 20:00
20 | Bashundhara | 182 | 12:00 | 86 | Khulna | 67 | 19:00 | 152 | Satmasjid | 100 | 01:00
21 | BashundharaCement | 9 | 15:00 | 87 | Khulshi | 180 | 19:00 | 153 | Savar | 200 | 00:00
22 | Beanibazar | 78 | 01:00 | 88 | Kishoreganj | 134 | 00:00 | 154 | SevenRings | 22.95 | 13:00
23 | Benapole | 64 | 00:00 | 89 | Kodda | 305 | 10:00 | 155 | ShahCement | 28 | 00:00
24 | Bhaluka | 136 | 00:00 | 90 | Kulaura | 46 | 01:00 | 156 | Shahjadpur | 70 | 00:00
25 | Bhandaria | 43 | 20:00 | 91 | Kurigram | 56 | 02:00 | 157 | Shahjibazar | 109 | 05:00
26 | Bhangura | 33 | 01:00 | 92 | Kushtia | 156 | 00:00 | 158 | Shahmirpur | 58 | 00:00
27 | Bheramara(GK) | 61 | 00:00 | 93 | Lalbag | 60 | 12:00 | 159 | Shariatpur | 64 | 02:00
28 | Bhulta | 219 | 15:00 | 94 | Lalmonirhat | 52 | 21:00 | 160 | Sherpur | 128 | 00:00
29 | Bog-Sherpur | 72 | 00:00 | 95 | MI_Cement | 17.3 | 04:00 | 161 | Shikalbaha | 22 | 23:00
30 | Bogura | 159 | 01:00 | 96 | Madanganj | 50 | 00:00 | 162 | Shitalakhya | 82.2 | 12:00
31 | Borhanuddin | 25 | 00:00 | 97 | Madaripur | 98 | 00:00 | 163 | Sholosohor | 44 | 12:00
32 | Brahmanbaria | 113 | 01:00 | 98 | Madartek | 94 | 00:00 | 164 | Shyampur | 176 | 00:00
33 | Cantonment | 136 | 12:00 | 99 | Madunaghat | 52 | 00:00 | 165 | Siddhirganj | 112 | 00:00
34 | Chandina | 24.75 | 03:00 | 100 | Magura | 62 | 00:00 | 166 | Sirajganj | 112 | 00:00
35 | Chandpur | 63 | 01:00 | 101 | Mahasthangarh | 92 | 00:00 | 167 | Sonargaon | 126 | 00:00
36 | Chandraghona | 33 | 19:00 | 102 | Manikganj | 109 | 08:00 | 168 | Sreemongol | 69 | 21:00
37 | Chapai | 72 | 00:00 | 103 | Maniknagar | 80 | 00:00 | 169 | Sreepur | 101 | 00:00
38 | Charsaidpur | 38 | 11:00 | 104 | Matarbari | 39 | 00:00 | 170 | Srinagar | 45.1 | 00:00
39 | Chauddagram | 69 | 00:00 | 105 | Matuail | 66 | 00:00 | 171 | Sunamganj | 61 | 00:00
40 | Chhatak | 33 | 21:00 | 106 | Millgate | 99 | 09:00 | 172 | Sylhet | 53 | 09:00
41 | Chowmuhani | 217 | 00:00 | 107 | Mirpur | 115 | 00:00 | 173 | Sylhet-132 | 112 | 19:00
42 | Chuadanga | 111 | 00:00 | 108 | Mirsorai | 10 | 09:00 | 174 | TK | 33 | 00:00
43 | Coxsbazar | 101 | 00:00 | 109 | Mirzapur | 45 | 22:00 | 175 | Tangail | 140 | 04:00
44 | Cumilla(N) | 134 | 00:00 | 110 | Mithapukur | 70 | 00:00 | 176 | Thakurgaon | 100 | 03:00
45 | Cumilla(S) | 170 | 00:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 128 | 11:00
46 | Daudkandi | 144 | 00:00 | 112 | Mogbazar | 137.7 | 12:00 | 178 | Ullahpara | 37 | 00:00
47 | Dhaka | 64 | 13:00 | 113 | Mongla | 45 | 16:00 | 179 | Ullon | 42 | 00:00
48 | Dhamrai | 134 | 12:00 | 114 | Motijheel | 37 | 12:00 | 180 | Uttara | 76 | 13:00
49 | Dhanmondi | 139 | 13:00 | 115 | Muktagacha | 27 | 08:00 | 181 | UttaraNew | 60 | 00:00
50 | Dohazari | 98 | 00:00 | 116 | Munshiganj | 104 | 01:00 | 182 | Zigatola | 74 | 01:00
51 | Faridpur | 166 | 00:00 | 117 | Muradnagar | 31 | 00:00
52 | Fatullah | 103 | 12:00 | 118 | Mymensingh | 184 | 00:00
53 | Fenchuganj | 40 | 00:00 | 119 | Naogaon | 143 | 00:00
54 | Feni | 114 | 00:00 | 120 | Narail | 54 | 00:00
55 | GPH | 98 | 12:00 | 121 | Narinda | 81 | 13:00
56 | Ghatail | 66 | 00:00 | 122 | Narshingdi | 180 | 00:00
57 | Ghorashal | 15 | 00:00 | 123 | Natore | 159 | 00:00
58 | Ghorashal-230 | 102 | 00:00 | 124 | Nawabganj | 54.4 | 00:00
59 | Goalpara | 32 | 00:00 | 125 | Netrakona | 127 | 08:00
60 | Gollamari | 94 | 00:00 | 126 | New | 90 | 10:00
61 | Gopalganj | 90 | 01:00 | 127 | Niamatpur | 71 | 00:00
62 | Gulshan | 112 | 13:00 | 128 | Noapara | 48 | 20:00
63 | Halishahar | 88 | 19:00 | 129 | PHP | 3 | 03:00
64 | HaripurSBU | 176 | 13:00 | 130 | Pabna | 114 | 00:00
65 | Hasnabad | 67 | 00:00 | 131 | Palashbari | 108 | 00:00
66 | Hathazari | 66 | 00:00 | 132 | Panchagarh | 55 | 02:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 29-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14766.04 | 365 |  | 15147.47
1:00 | 14286.18 | 474 |  | 14781.18
2:00 | 13835.94 | 378 |  | 14230.94
3:00 | 13445.39 | 321 |  | 13780.39
4:00 | 13165.16 | 273 |  | 13450.16
5:00 | 12692.92 | 218 |  | 12920.92
6:00 | 11879.7 | 165 |  | 12051.7
7:00 | 11587.37 | 81 |  | 11672.37
8:00 | 11043.75 | 19 |  | 11063.75
9:00 | 10723.83 | 22 |  | 10746.83
10:00 | 10739.23 | 32 |  | 10772.23
11:00 | 10980.92 | 35 |  | 11017.92
12:00 | 11290.51 | 21 |  | 11312.51
13:00 | 11239.41 | 0 |  | 11239.41
14:00 | 10973.14 | 75 |  | 11051.14
15:00 | 10658.14 | 53 |  | 10713.14
16:00 | 10505.07 | 54 |  | 10561.07
17:00 | 10181.14 | 0 |  | 10181.14
18:00 | 9853.06 | 0 |  | 9853.06
19:00 | 10713.9 | 0 |  | 10713.9
19:30 | 10776.15 | 0 |  | 10776.15
20:00 | 10608.79 | 0 |  | 10608.79
21:00 | 10290.08 | 0 |  | 10290.08
22:00 | 9901.47 | 0 |  | 9901.47
23:00 | 9698.02 | 0 |  | 9698.02
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 29-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7853 | 6913.04 | 14766.04 | DAILY GENERATION CURVE
00:30 | 7645 | 6881.11 | 14526.11
01:00 | 7437 | 6849.18 | 14286.18 | 29-05-2025
01:30 | 7445 | 6616.06 | 14061.06
02:00 | 7453 | 6382.94 | 13835.94
02:30 | 7332.9 | 6307.765 | 13640.665
03:00 | 7212.8 | 6232.59 | 13445.39
03:30 | 7195.8 | 6109.475 | 13305.275
04:00 | 7178.8 | 5986.36 | 13165.16
04:30 | 6994.3 | 5934.74 | 12929.04
05:00 | 6809.8 | 5883.12 | 12692.92
05:30 | 6487.335 | 5798.975 | 12286.31
06:00 | 6164.87 | 5714.83 | 11879.7
06:30 | 6037.935 | 5695.6 | 11733.535
07:00 | 5911 | 5676.37 | 11587.37
07:30 | 5803.63 | 5511.93 | 11315.56
08:00 | 5696.26 | 5347.49 | 11043.75
08:30 | 5671.455 | 5212.335 | 10883.79
09:00 | 5646.65 | 5077.18 | 10723.83
09:30 | 5556.85 | 5174.68 | 10731.53
10:00 | 5467.05 | 5272.18 | 10739.23
10:30 | 5598.095 | 5261.98 | 10860.075
11:00 | 5729.14 | 5251.78 | 10980.92
11:30 | 5855.795 | 5279.92 | 11135.715
12:00 | 5982.45 | 5308.06 | 11290.51
12:30 | 6072.13 | 5192.83 | 11264.96
13:00 | 6161.81 | 5077.6 | 11239.41
13:30 | 6054.755 | 5051.52 | 11106.275
14:00 | 5947.7 | 5025.44 | 10973.14
14:30 | 5892.155 | 4923.485 | 10815.64
15:00 | 5836.61 | 4821.53 | 10658.14
15:30 | 5795.75 | 4785.855 | 10581.605
16:00 | 5754.89 | 4750.18 | 10505.07
16:30 | 5661.15 | 4681.955 | 10343.105
17:00 | 5567.41 | 4613.73 | 10181.14
17:30 | 5423.56 | 4593.54 | 10017.1
18:00 | 5279.71 | 4573.35 | 9853.06
18:30 | 5475.355 | 4808.125 | 10283.48
19:00 | 5671 | 5042.9 | 10713.9
19:30 | 5609 | 5167.15 | 10776.15
20:00 | 5538 | 5070.79 | 10608.79
20:30 | 5461.5 | 4987.935 | 10449.435 |  | Executive Engineer
21:00 | 5385 | 4905.08 | 10290.08 |  | Network Operation Division
21:30 | 5296.5 | 4799.275 | 10095.775
22:00 | 5208 | 4693.47 | 9901.47
22:30 | 5143 | 4656.745 | 9799.745
23:00 | 5078 | 4620.02 | 9698.02

## En-Curve
QF-LDC-12
Date | 29-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2910 | 1792.8 | 924 | 0 | 40 | 1098.84 | 40 | 4701.2 | 0 | 487 | 2720.2 | 0 | 0 | 52 | 365 | DAILY ENERGY CURVE
00:30 | 2917 | 1816.8 | 924.5 | 0 | 39 | 1101.41 | 40 | 4751.7 | 0 | 464 | 2422.7 | 0 | 0 | 49 | 419.5 | 29-05-2025
01:00 | 2924 | 1840.8 | 925 | 0 | 38 | 1103.98 | 40 | 4802.2 | 0 | 441 | 2125.2 | 0 | 0 | 46 | 474
01:30 | 2932 | 1842.3 | 925 | 0 | 38 | 1054.96 | 40 | 4733.6 | 0 | 335 | 2107.2 | 0 | 0 | 53 | 426 | Energy Generated | 276.4371 |  | MKWHr
02:00 | 2940 | 1843.8 | 925 | 0 | 38 | 1005.94 | 40 | 4665 | 0 | 229 | 2089.2 | 0 | 0 | 60 | 378 | Energy not Served | 2.586 |  | MKWHr
02:30 | 2959.5 | 1844.8 | 925 | 0 | 37 | 1014.765 | 39 | 4620.5 | 0 | 159.5 | 1979.6 | 0 | 0 | 61 | 349.5 | Total Energy Requirement | 279.0231 |  | MKWHr
03:00 | 2979 | 1845.8 | 925 | 0 | 36 | 1023.59 | 38 | 4576 | 0 | 90 | 1870 | 0 | 0 | 62 | 321
03:30 | 2976 | 1853.3 | 925 | 0 | 27 | 1020.975 | 38 | 4462 | 0 | 90 | 1853.5 | 0 | 0 | 59.5 | 297
04:00 | 2973 | 1860.8 | 925 | 0 | 18 | 1018.36 | 38 | 4348 | 0 | 90 | 1837 | 0 | 0 | 57 | 273
04:30 | 2970 | 1859.3 | 924.5 | 0 | 26 | 1011.74 | 37 | 4364 | 0 | 90 | 1587 | 0 | 0 | 59.5 | 245.5
05:00 | 2967 | 1857.8 | 924 | 0 | 34 | 1005.12 | 36 | 4380 | 0 | 90 | 1337 | 0 | 0 | 62 | 218
05:30 | 2920 | 1834.3 | 924.5 | 0 | 32 | 1007.09 | 36.5 | 4385.5 | 11.42 | 90 | 981.5 | 0 | 0 | 63.5 | 191.5
06:00 | 2873 | 1810.8 | 925 | 0 | 30 | 1009.06 | 37 | 4391 | 22.84 | 90 | 626 | 0 | 0 | 65 | 165
06:30 | 2876.5 | 1809.5 | 925 | 0 | 29 | 1011.11 | 38.5 | 4311 | 50.925 | 90 | 528 | 0 | 0 | 64 | 123
07:00 | 2880 | 1808.2 | 925 | 0 | 28 | 1013.16 | 40 | 4231 | 79.01 | 90 | 430 | 0 | 0 | 63 | 81
07:30 | 2903 | 1776.6 | 904.5 | 0 | 14 | 973.355 | 40 | 4008.5 | 130.605 | 90 | 412 | 0 | 0 | 63 | 50
08:00 | 2926 | 1745 | 884 | 0 | 0 | 933.55 | 40 | 3786 | 182.2 | 90 | 394 | 0 | 0 | 63 | 19
08:30 | 2865.5 | 1734 | 883.5 | 0 | 0 | 918.275 | 40 | 3676.5 | 191.515 | 125 | 385.5 | 0 | 0 | 64 | 20.5
09:00 | 2805 | 1723 | 883 | 0 | 0 | 903 | 40 | 3567 | 200.83 | 160 | 377 | 0 | 0 | 65 | 22
09:30 | 2791 | 1713 | 897.5 | 0 | 0 | 909.5 | 40 | 3586.5 | 221.53 | 164.5 | 350 | 0 | 0 | 58 | 27
10:00 | 2777 | 1703 | 912 | 0 | 0 | 916 | 40 | 3606 | 242.23 | 169 | 323 | 0 | 0 | 51 | 32
10:30 | 2910.5 | 1726.5 | 921.5 | 0 | 0 | 870 | 40 | 3600 | 255.575 | 169 | 309.5 | 0 | 0 | 57.5 | 33.5
11:00 | 3044 | 1750 | 931 | 0 | 0 | 824 | 40 | 3594 | 268.92 | 169 | 296 | 0 | 0 | 64 | 35
11:30 | 3019 | 1751 | 931.5 | 0 | 0 | 842.5 | 40 | 3726.5 | 269.215 | 169 | 322.5 | 0 | 0 | 64.5 | 28
12:00 | 2994 | 1752 | 932 | 0 | 0 | 861 | 40 | 3859 | 269.51 | 169 | 349 | 0 | 0 | 65 | 21
12:30 | 2956 | 1730.5 | 932 | 0 | 17 | 862.5 | 40 | 3899.5 | 207.46 | 169 | 386 | 0 | 0 | 65 | 10.5
13:00 | 2918 | 1709 | 932 | 0 | 34 | 864 | 40 | 3940 | 145.41 | 169 | 423 | 0 | 0 | 65 | 0
13:30 | 2871.5 | 1689.5 | 932 | 0 | 17 | 865.565 | 39.5 | 3892.5 | 169.21 | 169 | 395.5 | 0 | 0 | 65 | 37.5
14:00 | 2825 | 1670 | 932 | 0 | 0 | 867.13 | 39 | 3845 | 193.01 | 169 | 368 | 0 | 0 | 65 | 75
14:30 | 2912.5 | 1671.5 | 932 | 0 | 0 | 866.66 | 37.5 | 3711.5 | 149.98 | 152 | 317 | 0 | 0 | 65 | 64
15:00 | 3000 | 1673 | 932 | 0 | 0 | 866.19 | 36 | 3578 | 106.95 | 135 | 266 | 0 | 0 | 65 | 53
15:30 | 3016 | 1708 | 932 | 0 | 0 | 864.715 | 35.5 | 3524.5 | 81.39 | 109.5 | 245 | 0 | 0 | 65 | 53.5
16:00 | 3032 | 1743 | 932 | 0 | 0 | 863.24 | 35 | 3471 | 55.83 | 84 | 224 | 0 | 0 | 65 | 54
16:30 | 2983.5 | 1725 | 932.5 | 0 | 0 | 843.28 | 34.5 | 3422.5 | 48.825 | 84 | 204 | 0 | 0 | 65 | 27
17:00 | 2935 | 1707 | 933 | 0 | 0 | 823.32 | 34 | 3374 | 41.82 | 84 | 184 | 0 | 0 | 65 | 0
17:30 | 2964 | 1658.5 | 932.5 | 0 | 0 | 823.94 | 34.5 | 3286.5 | 24.66 | 66.5 | 161 | 0 | 0 | 65 | 0
18:00 | 2993 | 1610 | 932 | 0 | 0 | 824.56 | 35 | 3199 | 7.5 | 49 | 138 | 0 | 0 | 65 | 0
18:30 | 3001 | 1671.5 | 908 | 0 | 0 | 899.73 | 35 | 3455 | 3.75 | 57.5 | 195.5 | 0 | 0 | 56.5 | 0
19:00 | 3009 | 1733 | 884 | 0 | 0 | 974.9 | 35 | 3711 | 0 | 66 | 253 | 0 | 0 | 48 | 0
19:30 | 2947 | 1709 | 883 | 0 | 0 | 929.15 | 37 | 3889 | 0 | 66 | 268 | 0 | 0 | 48 | 0
20:00 | 2932 | 1702 | 884 | 0 | 0 | 930.79 | 39 | 3819 | 0 | 66 | 189 | 0 | 0 | 47 | 0
20:30 | 2959 | 1686.5 | 908 | 0 | 0 | 893.435 | 39.5 | 3666.5 | 0 | 66 | 176 | 0 | 0 | 54.5 | 0
21:00 | 2986 | 1671 | 932 | 0 | 0 | 856.08 | 40 | 3514 | 0 | 66 | 163 | 0 | 0 | 62 | 0
21:30 | 2946 | 1651 | 932 | 0 | 0 | 843.275 | 40 | 3426 | 0 | 58 | 137.5 | 0 | 0 | 62 | 0
22:00 | 2906 | 1631 | 932 | 0 | 0 | 830.47 | 40 | 3338 | 0 | 50 | 112 | 0 | 0 | 62 | 0
22:30 | 2909.5 | 1630.5 | 932 | 0 | 0 | 828.245 | 40 | 3269.5 | 0 | 50 | 78 | 0 | 0 | 62 | 0
23:00 | 2913 | 1630 | 932 | 0 | 0 | 826.02 | 40 | 3201 | 0 | 50 | 44 | 0 | 0 | 62 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 29-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 388 | 23:00 | 373 | 00:00 | Payra | 417 | 15:00 | 408 | 00:00
Ashuganj | N/A | N/A | N/A | N/A | Rahanpur | 398 | 17:00 | 385 | 02:00
Bhulta | 400 | 21:00 | 373 | 11:00 | Rampal | 405 | 08:00 | 390 | 00:00
Bibiana | 393 | 20:00 | 383 | 00:00
BIPTC | 402 | 08:00 | 391 | 00:00
Bogura | 394 | 17:00 | 378 | 07:00
Gopalganj | 400 | 08:00 | 384 | 00:00
Kaliakoir | 380 | 21:00 | 364 | 12:00
Madunaghat | 400 | 23:00 | 386 | 12:00
Meghnaghat | 393 | 21:00 | 375 | 12:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 21:00 | 215 | 12:00 | Keranigonj | 225 | 21:00 | 214 | 12:00
AKSML | 235 | 21:00 | 222 | 11:00 | Khulna(S) | 233 | 08:00 | 221 | 00:00
Aminbazar | 227 | 22:00 | 216 | 12:00 | Madunaghat | 237 | 22:00 | 226 | 11:00
Ashuganj | 237 | 23:00 | 221 | 11:00 | Madunaghat-400 | 238 | 23:00 | 226 | 12:00
Ashuganj-400 | 237 | 23:00 | 221 | 11:00 | Maniknagar | 225 | 21:00 | 212 | 12:00
Baghabari | 234 | 18:00 | 225 | 00:00 | Meghnaghat | 232 | 21:00 | 220 | 00:00
Barapukuria | 224 | 14:00 | 214 | 07:00 | Meghnaghat-400 | 229 | 21:00 | 217 | 12:00
Barapukuria-230 | 224 | 14:00 | 214 | 07:00 | Mirsorai | 233 | 23:00 | 221 | 01:00
Barishal | 240 | 07:00 | 232 | 00:00 | Rajshahi | 266 | 19:30 | 226 | 00:00
Bheramara | 234 | 17:00 | 226 | 00:00 | Rampal | 232 | 08:00 | 220 | 01:00
Bhulta | 232 | 21:00 | 213 | 12:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 231 | 21:00 | 223 | 01:00 | Rampura | 232 | 23:00 | 213 | 12:00
BIPTC | 237 | 18:30 | 226 | 00:00 | Shikalbaha | 235 | 22:00 | 223 | 14:00
Bogura | 229 | 17:00 | 219 | 07:00 | Shyampur | 226 | 21:00 | 214 | 12:00
Bogura-400 | 228 | 17:00 | 218 | 07:00 | Siddhirganj | 228 | 22:00 | 216 | 00:00
Borhanuddin | 245 | 08:00 | 238 | 00:00 | Sirajgonj | 237 | 17:00 | 232 | 00:00
BSRM | 234 | 23:00 | 220 | 12:00 | Sreepur | 233 | 23:00 | 218 | 12:00
Cumilla(N) | 230 | 21:00 | 214 | 11:00 | Tongi | 225 | 23:00 | 215 | 11:00
Faridpur | 238 | 08:00 | 224 | 00:00
Fenchuganj | 232 | 17:00 | 224 | 04:00
Ghorashal | 220 | 00:00 | 220 | 00:00
Ghorashal-230 | 231 | 21:00 | 216 | 12:00
Gopalganj | 238 | 08:00 | 227 | 00:00
GPH | 236 | 23:00 | 222 | 11:00
Haripur | 227 | 21:00 | 214 | 12:00
Hasnabad | 225 | 22:00 | 215 | 00:00
Hathazari | 238 | 23:00 | 224 | 12:00
Ishurdi | 236 | 18:30 | 228 | 00:00
Jhenaidah | 232 | 08:00 | 220 | 00:00
Kaliakoir | 232 | 21:00 | 221 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 139 | 08:00 | 129 | 12:00 | Madartek | 138 | 17:00 | 128 | 19:30
Agargaon | 137 | 23:00 | 129 | 12:00 | Madunaghat | 135 | 23:00 | 127 | 11:00
Agrabad | 136 | 23:00 | 126 | 11:00 | Magura | 137 | 10:00 | 125 | 00:00
AKS | 134 | 23:00 | 124 | 12:00 | Mahasthangarh | 134 | 23:00 | 126 | 02:00
Aminbazar | 132 | 19:30 | 127 | 12:00 | Manikganj | 134 | 18:00 | 124 | 12:00
Amnura | 137 | 17:00 | 122 | 00:00 | Maniknagar | 136 | 21:00 | 127 | 11:00
Ashuganj | 142 | 21:00 | 132 | 00:00 | Matarbari | 135 | 23:00 | 119 | 02:00
Bagerhat | 136 | 08:00 | 123 | 20:00 | Matuail | 134 | 21:00 | 124 | 12:00
Bajitpur | 138 | 23:00 | 124 | 00:00 | Millgate | 137 | 21:00 | 126 | 12:00
Bakulia | 136 | 23:00 | 127 | 12:00 | Mirpur | 131 | 03:00 | 125 | 12:00
Banani | 137 | 02:00 | 128 | 19:00 | Mirzapur | 135 | 16:00 | 129 | 02:00
Bangabhaban | 136 | 21:00 | 127 | 12:00 | Mithapukur | 133 | 13:00 | 121 | 07:00
Barapukuria | 138 | 14:00 | 125 | 01:00 | MI_Cement | 133 | 21:00 | 124 | 12:00
Barguna | 138 | 23:00 | 133 | 02:00 | Modern | 0 | 0:00 | 0 | 0:00
Barishal | 136 | 08:00 | 128 | 00:00 | Mogbazar | 139 | 08:00 | 130 | 12:00
Barishal-230 | 135 | 07:00 | 128 | 00:00 | Mongla | 135 | 10:00 | 124 | 19:00
Baroaulia | 136 | 22:00 | 129 | 12:00 | Motijheel | 136 | 21:00 | 127 | 12:00
Baroirhat | 136 | 23:00 | 119 | 00:00 | Muktagacha | 140 | 23:00 | 125 | 05:00
Bashundhara | 138 | 17:00 | 127 | 11:00 | Munshiganj | 132 | 20:00 | 123 | 12:00
BashundharaCement | 132 | 21:00 | 124 | 12:00 | Muradnagar | 134 | 23:00 | 120 | 00:00
Beanibazar | 128 | 08:00 | 121 | 02:00 | Mymensingh | 140 | 23:00 | 114 | 06:00
Benapole | 135 | 10:00 | 123 | 19:30 | Naogaon | 132 | 12:00 | 124 | 02:00
Bhaluka | 137 | 23:00 | 123 | 00:00 | Narail | 140 | 08:00 | 125 | 00:00
Bhandaria | 135 | 08:00 | 125 | 01:00 | Narinda | 136 | 21:00 | 127 | 11:00
Bhangura | 134 | 17:00 | 128 | 02:00 | Narshingdi | 138 | 19:30 | 117 | 01:00
Bheramara | 137 | 10:00 | 131 | 00:00 | Natore | 135 | 12:00 | 129 | 01:00
Bheramara(GK) | 137 | 10:00 | 131 | 00:00 | Nawabganj | 134 | 08:00 | 126 | 00:00
Bhulta | 128 | 21:00 | 116 | 12:00 | Netrakona | 136 | 23:00 | 115 | 00:00
Bog-Sherpur | 134 | 12:00 | 127 | 07:00 | New | 138 | 20:00 | 127 | 12:00
Bogura | 135 | 12:00 | 129 | 07:00 | Niamatpur | 132 | 12:00 | 125 | 00:00
Bogura-230 | 136 | 17:00 | 129 | 07:00 | Noapara | 137 | 09:00 | 127 | 19:00
Brahmanbaria | 138 | 21:00 | 122 | 00:00 | Pabna | 136 | 18:00 | 129 | 00:00
Cantonment | 136 | 20:00 | 128 | 12:00 | Palashbari | 131 | 23:00 | 122 | 20:00
Chandina | 136 | 23:00 | 122 | 00:00 | Panchagarh | 137 | 00:00 | 120 | 22:00
Chandpur | 132 | 19:00 | 112 | 11:00 | Patuakhali | 137 | 17:00 | 133 | 00:00
Chandraghona | 136 | 22:00 | 126 | 12:00 | Payra | 138 | 08:00 | 135 | 00:00
Chapai | 130 | 12:00 | 123 | 00:00 | PHP | 136 | 23:00 | 117 | 01:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 133 | 21:00 | 124 | 12:00 | Postogola | 135 | 21:00 | 127 | 12:00
Chauddagram | 134 | 20:00 | 117 | 00:00 | Purbachal | 139 | 17:00 | 128 | 19:00
Chhatak | 128 | 23:00 | 120 | 00:00 | Purbasadipur | 135 | 14:00 | 119 | 19:00
Chowmuhani | 135 | 23:00 | 109 | 01:00 | Rahanpur | 133 | 17:00 | 128 | 00:00
Chuadanga | 138 | 10:00 | 122 | 00:00 | Rahanpur-400 | 133 | 12:00 | 128 | 00:00
Coxsbazar | 130 | 19:00 | 119 | 02:00 | Rahim | 146 | 06:00 | 124 | 12:00
Cumilla(N) | 135 | 20:00 | 122 | 11:00 | Rajbari | 139 | 08:00 | 128 | 00:00
Cumilla(S) | 136 | 23:00 | 120 | 11:00 | Rajendrapur | 138 | 23:00 | 122 | 12:00
Daudkandi | 132 | 20:00 | 118 | 00:00 | Rajshahi | 135 | 12:00 | 131 | 01:00
Dhaka | 139 | 08:00 | 129 | 19:00 | Rajshahi-230 | 135 | 10:00 | 117 | 00:00
Dhamrai | 139 | 21:00 | 129 | 11:00 | Ramganj | 132 | 20:00 | 112 | 00:00
Dhanmondi | 139 | 08:00 | 130 | 19:00 | Rampur | 136 | 23:00 | 127 | 12:00
Dohazari | 134 | 19:00 | 127 | 10:00 | Rampura | 138 | 08:00 | 126 | 19:00
Faridpur | 139 | 08:00 | 130 | 00:00 | Rangamati | 136 | 23:00 | 127 | 11:00
Fatullah | 134 | 22:00 | 124 | 12:00 | Rangpur | 132 | 14:00 | 119 | 07:00
Fenchuganj | 136 | 06:00 | 131 | 00:00 | Ruppur | 138 | 18:30 | 132 | 00:00
Feni | 133 | 23:00 | 117 | 11:00 | Saidpur | 135 | 14:00 | 119 | 19:00
Ghatail | 138 | 23:00 | 127 | 12:00 | Satkhira | 135 | 08:00 | 123 | 19:00
Ghorashal | 136 | 09:00 | 130 | 00:00 | Satmasjid | 136 | 23:00 | 128 | 12:00
Goalpara | 140 | 08:00 | 128 | 19:30 | Savar | 131 | 20:00 | 125 | 12:00
Gollamari | 139 | 08:00 | 130 | 19:30 | SevenRings | 138 | 22:00 | 131 | 00:00
Gopalganj | 138 | 08:00 | 131 | 00:00 | ShahCement | 133 | 21:00 | 124 | 12:00
Gopalganj-400 | 139 | 08:00 | 132 | 00:00 | Shahjadpur | 136 | 02:00 | 134 | 00:00
Gulshan | 138 | 17:00 | 129 | 19:00 | Shahjibazar | 136 | 21:00 | 124 | 00:00
Halishahar | 137 | 23:00 | 126 | 11:00 | Shahmirpur | 137 | 23:00 | 128 | 11:00
Haripur | 133 | 21:00 | 124 | 12:00 | Shariatpur | 138 | 08:00 | 129 | 01:00
HaripurSBU | 133 | 21:00 | 125 | 11:00 | Sherpur | 137 | 19:30 | 123 | 18:30
Hasnabad | 135 | 21:00 | 128 | 10:00 | Shikalbaha | 126 | 22:00 | 120 | 02:00
Hathazari | 138 | 23:00 | 129 | 13:00 | Shikalbaha-230 | 138 | 22:00 | 129 | 11:00
Ishurdi | 139 | 18:30 | 133 | 00:00 | Shitalakhya | 133 | 21:00 | 124 | 12:00
Jaldhaka | 133 | 14:00 | 118 | 01:00 | Sholosohor | 137 | 23:00 | 127 | 11:00
Jamalpur | 138 | 00:00 | 125 | 18:30 | Shyampur | 133 | 21:00 | 125 | 00:00
Jashore | 138 | 08:00 | 121 | 00:00 | Shyampur-230 | 133 | 21:00 | 124 | 12:00
Jhenaidah | 139 | 10:00 | 121 | 00:00 | Siddhirganj | 133 | 21:00 | 125 | 11:00
Jhenaidah-230 | 138 | 08:00 | 128 | 00:00 | Sirajganj | 134 | 17:00 | 127 | 00:00
Joydebpur | 140 | 17:00 | 126 | 15:00 | Sonargaon | 135 | 18:00 | 123 | 00:00
Joypurhat | 132 | 13:00 | 123 | 00:00 | Sreemongol | 134 | 01:00 | 125 | 00:00
Juldah | 137 | 23:00 | 128 | 11:00 | Sreepur | 138 | 23:00 | 126 | 01:00
Kabirpur | 137 | 08:00 | 124 | 12:00 | Srinagar | 134 | 08:00 | 126 | 12:00
Kachua | 133 | 23:00 | 115 | 11:00 | SSM | 138 | 22:00 | 124 | 08:00
Kaliakoir | 142 | 21:00 | 132 | 11:00 | Sunamganj | 127 | 23:00 | 117 | 00:00
Kallyanpur | 133 | 19:30 | 127 | 12:00 | Sylhet | 129 | 08:00 | 124 | 00:00
Kalurghat | 137 | 22:00 | 128 | 10:00 | Sylhet-132 | 130 | 23:00 | 125 | 00:00
Kamrangirchar | 135 | 21:00 | 126 | 12:00 | Tangail | 135 | 19:30 | 124 | 02:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 136 | 00:00 | 119 | 22:00
Kasba | 132 | 20:00 | 120 | 00:00 | TK | 134 | 22:00 | 127 | 11:00
Kazla | 136 | 22:00 | 126 | 12:00 | Tongi | 136 | 04:00 | 130 | 11:00
Keranigonj | 135 | 23:00 | 126 | 12:00 | Ullahpara | 135 | 17:00 | 129 | 07:00
Khagrachori | 135 | 23:00 | 126 | 12:00 | Ullon | 138 | 08:00 | 130 | 12:00
Khulna | 137 | 09:00 | 129 | 19:30 | Uttara | 131 | 03:00 | 125 | 12:00
Khulna(S) | 139 | 08:00 | 130 | 19:30 | UttaraNew | 131 | 03:00 | 126 | 12:00
Khulshi | 135 | 22:00 | 126 | 11:00 | Zigatola | 134 | 21:00 | 127 | 00:00
Kishoreganj | 138 | 23:00 | 122 | 00:00
Kodda | 135 | 08:00 | 124 | 17:00
KSRM | 137 | 19:30 | 127 | 11:00
Kulaura | 135 | 21:00 | 130 | 00:00
Kurigram | 132 | 13:00 | 118 | 07:00
Kushtia | 136 | 10:00 | 126 | 00:00
Lalbag | 134 | 21:00 | 127 | 00:00
Lalmonirhat | 130 | 12:00 | 121 | 06:00
Madanganj | 132 | 21:00 | 124 | 12:00
Madaripur | 139 | 08:00 | 130 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division