## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 31-05-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-05-2025 | during | 31-05-2025 | during | 31-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 334 | 328 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 149 | 133 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 185 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 35 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 0 | 147 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 17 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 15 | 17 | 33 | 33 | 18.5 | 18.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 16 | 18 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 0 | 24 | 52.19 | 52.19 | 52.19 | 52.19 | Liquid fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 33 | 51 | 135 | 135 | 134 | 134 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 70 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 80 | 80 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 0 | 108 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 12 | 0 | 12 | 0 | 12 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 583 | 583 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 35 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 1562 | 2272 | 5240.9 | 5260.9 | 3461.52 | 3481.52
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 0 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 4 | 0 | 4 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 38 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 218 | 220 | 180 | 180 | 180 | 180 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 17 | 105 | 105 | 105 | 105
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 84 | 84 | 84 | 84 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 5 | 36 | 5 | 20 | 5 | 20 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 15 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 700 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 0 | 62 | 50 | 48 | 50 | 48 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 343 | 360 | 360 | 360 | 575 | 575 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1306 | 2072 | 3226.72 | 3235.72 | 3441.72 | 3450.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 193 | 181 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 349 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 340 | 335 | 335 | 335 | 335 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 26 | 31 | 46.7 | 46.7 | 34 | 34 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 27 | 46 | 55 | 55 | 46 | 46 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 8 | 8 | 195 | 195 | 16 | 16 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 11 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 40 | 150 | 150 | 135 | 135 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 136 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 10 | 20 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 5 | 17.35 | 17.35 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 70 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 36 | 113 | 113 | 28 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 0 | 68 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 17 | 0 | 15 | 0 | 15 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 976 | 1388 | 2403.6 | 2388.6 | 1921.55 | 1906.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 30-05-2025 | during | 31-05-2025 | during | 31-05-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 0.5 | 0 | 0.5 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 35 | 118 | 200 | 200 | 175 | 175 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 8 | 83 | 115 | 115 | 105 | 105 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 16.57 | 0 | 20 | 0 | 20 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 60.57 | 213 | 569.5 | 549 | 367 | 346.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 39 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 40 | 40 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 148 | 151 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 30 | 30 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | -
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 102 | 102 | 100 | 100 | 100 | 100 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 285 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 314 | 350 | 385 | 385 | 357 | 357 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1290 | 1330 | 1546 | 1546 | 1353 | 1353
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 689 | 926 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 40 | 40 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 208 | 223 | 410 | 410 | 160 | 160 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 36.2 | 0 | 43 | 0 | 43 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 745 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 1678.2 | 2383.2 | 3555.2 | 3512.2 | 3303.2 | 3260.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 2 | 4 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | -
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 580 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.23 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1002.23 | 1775 | 2042 | 2041 | 2002 | 2001
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50 | 50 | 50 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 | 40 | 40 | shundown for maintenance work
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | 5 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 96 | 96 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 70 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 1.31 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 829.12 | 1016 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 13.59 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 14 | 0 | 80 | 0 | 80 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1272.02 | 1505 | 3136.37 | 2989.87 | 3134.58 | 2988.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 50 | 49 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 159 | 162 | 150 | 150 | 160 | 160 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 1.9 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 5 | 0 | 28 | 0 | 28 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 54 | 0 | 71.62 | 0 | 71.62 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 269.9 | 361 | 567.22 | 462 | 577.22 | 471
System Total |  |  |  |  | 28886.2 | 27110.055 | 9416.92 | 13299.2 | 22287.51 | 21985.29 | 19561.79 | 19258.57
Forecast Scenario (31-05-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 12280 |  | 0 |  | 12280
|  |  |  | 1:00 | 11690 |  | 0 |  | 11690
|  |  |  | 2:00 | 11180 |  | 0 |  | 11180
|  |  |  | 3:00 | 11020 |  | 0 |  | 11020
|  |  |  | 4:00 | 10760 |  | 0 |  | 10760
|  |  |  | 5:00 | 10550 |  | 0 |  | 10550
|  |  |  | 6:00 | 10080 |  | 0 |  | 10080
|  |  |  | 7:00 | 10140 |  | 0 |  | 10140
|  |  |  | 8:00 | 10200 |  | 0 |  | 10200
|  |  |  | 9:00 | 10410 |  | 0 |  | 10410
|  |  |  | 10:00 | 10630 |  | 0 |  | 10630
|  |  |  | 11:00 | 11010 |  | 0 |  | 11010
|  |  |  | 12:00 | 11350 |  | 0 |  | 11350
|  |  |  | 13:00 | 11680 |  | 0 |  | 11680
|  |  |  | 14:00 | 11630 |  | 0 |  | 11630
|  |  |  | 15:00 | 11750 |  | 0 |  | 11750
|  |  |  | 16:00 | 11620 |  | 0 |  | 11620
|  |  |  | 17:00 | 11210 |  | 0 |  | 11210
|  |  |  | 18:00 | 10910 |  | 0 |  | 10910
|  |  |  | 18:30 | 11500 |  | 0 |  | 11500
|  |  |  | 19:00 | 12460 |  | 0 |  | 12460
|  |  |  | 19:30 | 13220 |  | 0 |  | 13220
|  |  |  | 20:00 | 13300 |  | 0 |  | 13300
|  |  |  | 21:00 | 13400 |  | 0 |  | 13400
|  |  |  | 22:00 | 13270 |  | 0 |  | 13270
|  |  |  | 23:00 | 13210 |  | 0 |  | 13210
Probable Maximum Temperature: |  |  | 28.10°C
Probable Maximum Demand at Day Peak: |  |  | 11350.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13400.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 275.74 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:29 hrs on 31-05-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [6 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [6 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 30-05-2025 | [28 empty] | Date: | 30-05-2025 | [28 empty] | Date: | 30-05-2025 | [28 empty] | Date: | 30-05-2025 | [28 empty] | Date: | 30-05-2025 | [15 empty] | Date: | 30-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [28 empty] | Day: | Friday | [15 empty] | Day: | Friday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 17 | 3 | 0 | 0 | 0 | 0 | 0 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 231 | 250 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 258 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 800 | 0 | 5 | 0 | 0 | 0 | 300 | 280 | 20 | 170 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 320 | 296 | 40 | 0 | 0 | 138 | 0 | 0 | 85 | 0 | 0 | 0 | 102 | 0 | 8 | 24 | 0 | 0 | 0 | 12 | 4833 | 931 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 822.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 165 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 2 | 0 | 220 | 0 | 196 | 715 | 0 | 4611.55 | 9444.55 | 78.23
01:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 244 | 250 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 278 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 650 | 0 | 5 | 0 | 0 | 0 | 280 | 280 | 10 | 171 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 320 | 290 | 39 | 0 | 0 | 131 | 0 | 0 | 31 | 0 | 0 | 0 | 102 | 0 | 8 | 8 | 0 | 0 | 0 | 12 | 4586 | 932 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 757 | 0 | 827.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 165 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 220 | 0 | 193 | 560 | 0 | 4430.77 | 9016.77 | 78.26
02:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 267 | 250 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 25 | 310 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 608 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 285 | 320 | 290 | 39 | 0 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4360 | 926 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 825.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 164 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 220 | 0 | 186 | 500 | 0 | 4289.03 | 8649.03 | 78.29
03:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 231 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 280 | 260 | 0 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 320 | 291 | 39 | 0 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4030 | 926 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 818.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 128 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 190 | 0 | 203 | 500 | 0 | 4220.17 | 8250.17 | 78.32
04:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 280 | 260 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 280 | 278 | 30 | 0 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3818 | 539 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 742 | 0 | 823.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 128 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 190 | 0 | 207 | 500 | 0 | 3807.11 | 7625.11 | 78.35
05:00 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 280 | 276 | 30 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3790 | 498 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 0 | 826.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 129 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 220 | 0 | 125 | 500 | 0 | 3582.53 | 7372.53 | 78.38
06:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 14 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 280 | 318 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 1.03 | 0 | 3829.03 | 497 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.24 | 743 | 0 | 824.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.25 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0.09 | 0 | 137 | 50 | 0 | 0 | 0 | 0 | 0 | 0.3 | 3 | 0 | 0 | 140 | 0 | 0 | 220 | 0 | 0 | 500 | 0 | 3468.93 | 7297.96 | 78.41
07:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 180 | 280 | 276 | 30 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 4.79 | 0 | 3847.79 | 498 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 744 | 0 | 823.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.75 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0.18 | 0 | 138 | 50 | 0 | 1 | 0 | 0 | 0 | 0.8 | 8 | 0.02 | 0 | 140 | 0 | 0 | 220 | 0 | 0 | 500 | 0 | 3535.51 | 7383.3 | 78.44
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 120 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 0 | 613 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 180 | 320 | 298 | 30 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 2.81 | 0 | 3915.81 | 451 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.49 | 744 | 0 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 15.77 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.6 | 0 | 135 | 50 | 0 | 2 | 0 | 0 | 0 | 1 | 13 | 0.1 | 0 | 140 | 0 | 0 | 220 | 0 | 0 | 500 | 0 | 3576.96 | 7492.77 | 78.47
09:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 141 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 15 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0 | 602 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 0 | 198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 200 | 320 | 318 | 39 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 8.96 | 0 | 4034.96 | 451 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.85 | 743 | 0 | 818.66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 26.93 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 1.04 | 0 | 139 | 50 | 0 | 6 | 0 | 0 | 0 | 2.8 | 15 | 0.22 | 0 | 140 | 0 | 0 | 220 | 0 | 0 | 500 | 0 | 3598.5 | 7633.46 | 78.52
10:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 144 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 609 | 0 | 0 | 0 | 0 | 0 | 280 | 280 | 7 | 191 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 11 | 0 | 290 | 320 | 335 | 39 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 1 | 7.57 | 0 | 4247.57 | 590 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.74 | 742 | 0 | 828.47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8.26 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.84 | 0 | 135 | 50 | 0 | 4 | 0 | 0 | 0 | 0.8 | 54 | 0.2 | 0 | 140 | 0 | 0 | 180 | 0 | 0 | 500 | 0 | 3752.31 | 7999.88 | 78.57
11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 143 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 344 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | 0 | 618 | 0 | 1 | 0 | 8 | 0 | 341 | 335 | 10 | 211 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 11 | 0 | 300 | 320 | 397 | 40 | 0 | 0 | 154 | 0 | 0 | 22 | 0 | 0 | 0 | 102 | 0 | 2 | 2 | 0 | 1 | 5.11 | 0 | 4904.11 | 520 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.76 | 745 | 0 | 826.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 15.78 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.24 | 0 | 158 | 50 | 0 | 5 | 0 | 0 | 0 | 3.2 | 25 | 0.21 | 0 | 140 | 0 | 0 | 220 | 0 | 0 | 500 | 0 | 3887.95 | 8792.06 | 78.62
12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 149 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 5 | 343 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 700 | 0 | 11 | 0 | 8 | 0 | 349 | 335 | 27 | 193 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 17 | 0 | 285 | 320 | 314 | 39 | 0 | 0 | 148 | 0 | 0 | 82 | 0 | 0 | 0 | 102 | 0 | 8 | 35 | 0 | 1 | 16.57 | 0 | 5194.57 | 689 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.2 | 745 | 0 | 829.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 13.59 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.31 | 0 | 159 | 50 | 0 | 5 | 0 | 0 | 0 | 1.9 | 54 | 0.23 | 0 | 200 | 2 | 0 | 220 | 0 | 0 | 580 | 0 | 4222.35 | 9416.92 | 78.64
13:00 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 4 | 0 | 0 | 420 | 143 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 7 | 343 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 705 | 3 | 20 | 0 | 8 | 0 | 346 | 335 | 38 | 189 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 13 | 0 | 295 | 320 | 350 | 39 | 0 | 0 | 142 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 8 | 35 | 0 | 0 | 18.92 | 0 | 5261.92 | 688 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.63 | 810 | 0 | 929.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 11.57 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.94 | 0 | 159 | 50 | 0 | 5 | 0 | 0 | 0 | 4.1 | 50 | 0.4 | 0 | 250 | 3 | 0 | 220 | 0 | 0 | 718 | 0 | 4592.04 | 9853.96 | 78.72
14:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 17 | 0 | 0 | 420 | 144 | 500 | 0 | 0 | 0 | 33 | 0 | 0 | 12 | 0 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 342 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 680 | 6 | 43 | 0 | 8 | 0 | 349 | 335 | 38 | 188 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 10 | 0 | 290 | 320 | 365 | 39 | 0 | 0 | 129 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 8 | 8 | 0 | 0 | 13.12 | 0 | 5187.12 | 689 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65.88 | 780 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 3.19 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.37 | 0 | 159 | 50 | 0 | 11 | 0 | 0 | 0 | 3.8 | 91 | 0.16 | 0 | 150 | 2 | 0 | 220 | 0 | 0 | 700 | 0 | 4531.4 | 9718.52 | 78.77
15:00 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 20 | 0 | 0 | 420 | 146 | 583 | 0 | 0 | 0 | 24 | 0 | 0 | 6 | 0 | 15 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 3 | 344 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 713 | 5 | 43 | 0 | 8 | 0 | 350 | 345 | 41 | 197 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 22 | 0 | 285 | 320 | 357 | 39 | 0 | 0 | 149 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 8 | 36 | 0 | 0 | 2.55 | 0 | 5407.55 | 688 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.51 | 856 | 0 | 926 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 5.45 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.5 | 0 | 160 | 50 | 0 | 23 | 0 | 0 | 0 | 1.1 | 24 | 0.28 | 0 | 200 | 3 | 0 | 220 | 0 | 0 | 740 | 0 | 4577.84 | 9985.39 | 78.82
16:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 0 | 30 | 32 | 0 | 0 | 35 | 0 | 0 | 370 | 151 | 500 | 0 | 0 | 0 | 94 | 0 | 0 | 7 | 0 | 16 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 2 | 343 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 730 | 3 | 51 | 0 | 8 | 0 | 300 | 340 | 43 | 202 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 15 | 0 | 290 | 320 | 365 | 38 | 0 | 0 | 148 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 24 | 64 | 0 | 0 | 1.01 | 0 | 5440.01 | 688 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.35 | 857 | 0 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 11.31 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 1 | 0 | 158 | 50 | 0 | 18 | 0 | 0 | 0 | 2.1 | 23 | 0.2 | 0 | 200 | 4 | 0 | 220 | 0 | 0 | 870 | 0 | 4646.96 | 10086.97 | 78.87
17:00 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 33 | 64 | 0 | 0 | 35 | 0 | 0 | 370 | 145 | 500 | 0 | 0 | 0 | 186 | 0 | 0 | 4 | 0 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 341 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 800 | 1 | 51 | 0 | 8 | 0 | 300 | 340 | 45 | 192 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 5 | 0 | 290 | 320 | 347 | 39 | 0 | 0 | 150 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 24 | 64 | 0 | 1 | 0.92 | 0 | 5595.92 | 689 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.88 | 857 | 0 | 915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.53 | 0 | 152 | 50 | 0 | 0 | 0 | 0 | 0 | 1 | 84 | 0.11 | 0 | 200 | 3 | 0 | 220 | 0 | 0 | 870 | 0 | 4640.22 | 10236.14 | 78.92
18:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 0 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 17 | 0 | 0 | 320 | 140 | 450 | 0 | 0 | 0 | 186 | 0 | 0 | 1 | 0 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 341 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 975 | 0 | 51 | 0 | 8 | 0 | 300 | 340 | 47 | 183 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 1 | 0 | 280 | 320 | 373 | 38 | 0 | 0 | 138 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 35 | 63 | 0 | 0 | 1.9 | 0 | 5700.9 | 926 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.94 | 866 | 0 | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 2.98 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0.25 | 0 | 162 | 49 | 0 | 2 | 0 | 0 | 0 | 0.5 | 7 | 0.02 | 0 | 200 | 3 | 0 | 220 | 0 | 0 | 875 | 0 | 4811.69 | 10512.59 | 79
19:00 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 347 | 0 | 0 | 0 | 20 | 33 | 110 | 0 | 0 | 17 | 17 | 0 | 420 | 150 | 450 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 24 | 0 | 0 | 36 | 0 | 34 | 360 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 1160 | 0 | 51 | 0 | 8 | 0 | 350 | 330 | 45 | 204 | 31 | 18 | 0 | 33 | 7 | 0 | 52 | 20 | 0 | 0 | 0 | 275 | 320 | 388 | 40 | 0 | 0 | 135 | 0 | 0 | 83 | 0 | 0 | 0 | 103 | 0 | 65 | 109 | 0 | 0 | 0 | 6 | 6415 | 925 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 986 | 0 | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 160 | 49 | 77 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 243 | 5 | 0 | 220 | 0 | 0 | 1020 | 0 | 5276 | 11691 | 79.08
19:30 | 0 | 70 | 16 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 0 | 54 | 33 | 112 | 0 | 0 | 17 | 45 | 0 | 450 | 140 | 583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 48 | 0 | 0 | 36 | 0 | 36 | 360 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1210 | 0 | 51 | 0 | 8 | 0 | 340 | 340 | 45 | 203 | 31 | 34 | 0 | 85 | 28 | 0 | 70 | 22 | 0 | 0 | 0 | 275 | 320 | 385 | 39 | 0 | 0 | 152 | 0 | 0 | 83 | 0 | 0 | 0 | 103 | 0 | 65 | 118 | 0 | 0 | 0 | 12 | 6726 | 926 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1126 | 0 | 1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 49 | 110 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 5 | 0 | 220 | 0 | 0 | 1210 | 0 | 5811 | 12537 | 79.08
20:00 | 0 | 77 | 16 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 8 | 54 | 45 | 147 | 0 | 0 | 17 | 95 | 0 | 450 | 144 | 500 | 0 | 10 | 0 | 23 | 0 | 0 | 0 | 35 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 100 | 0 | 0 | 37 | 0 | 36 | 360 | 0 | 0 | 0 | 0 | 1 | 216 | 0 | 0 | 0 | 1224 | 0 | 51 | 3 | 8 | 0 | 354 | 340 | 46 | 192 | 31 | 41 | 0 | 77 | 32 | 0 | 70 | 20 | 0 | 0 | 0 | 275 | 320 | 350 | 39 | 0 | 0 | 152 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 83 | 118 | 0 | 0 | 0 | 12 | 6786 | 925 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1016 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 162 | 50 | 110 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 0 | 220 | 0 | 0 | 1220 | 0 | 5884.2 | 12670.2 | 79.16
21:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 35 | 54 | 51 | 147 | 0 | 0 | 17 | 108 | 0 | 450 | 133 | 583 | 0 | 17 | 0 | 185 | 0 | 0 | 0 | 35 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 100 | 0 | 0 | 38 | 15 | 36 | 360 | 0 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 | 1224 | 0 | 51 | 40 | 8 | 0 | 356 | 340 | 46 | 181 | 31 | 68 | 0 | 136 | 36 | 5 | 70 | 20 | 0 | 0 | 0 | 285 | 320 | 350 | 39 | 0 | 0 | 151 | 0 | 0 | 83 | 0 | 0 | 0 | 102 | 0 | 83 | 118 | 0 | 0 | 0 | 12 | 7275 | 926 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1016 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 4 | 0 | 220 | 0 | 0 | 1244 | 0 | 6024.2 | 13299.2 | 79.26
22:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 35 | 54 | 33 | 130 | 0 | 0 | 0 | 72 | 0 | 370 | 148 | 500 | 0 | 20 | 0 | 188 | 0 | 0 | 0 | 35 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 100 | 0 | 0 | 39 | 0 | 36 | 360 | 0 | 0 | 0 | 0 | 17 | 217 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 8 | 0 | 349 | 340 | 46 | 206 | 32 | 68 | 0 | 138 | 37 | 5 | 76 | 12 | 0 | 0 | 0 | 285 | 320 | 388 | 39 | 0 | 0 | 153 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 83 | 130 | 0 | 0 | 0 | 12 | 7086 | 926 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1016 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 164 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 0 | 220 | 0 | 0 | 1244 | 0 | 6002.2 | 13088.2 | 79.36
23:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 54 | 33 | 130 | 0 | 0 | 0 | 126 | 0 | 370 | 149 | 400 | 0 | 35 | 0 | 187 | 0 | 0 | 0 | 35 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 36 | 360 | 0 | 0 | 0 | 1 | 38 | 215 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 8 | 0 | 346 | 340 | 46 | 207 | 32 | 84 | 0 | 168 | 37 | 11 | 114 | 16 | 0 | 0 | 0 | 310 | 320 | 388 | 39 | 0 | 0 | 152 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 83 | 129 | 0 | 0 | 0 | 12 | 7183 | 926 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1015 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0 | 0 | 161 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 4 | 0 | 220 | 0 | 0 | 1244 | 0 | 6026.2 | 13209.2 | 79.46
Total KWH | 0 | 610560 | 152640 | 0 | 0 | 0 | 0 | 0 | 7603200 | 0 | 0 | 184320 | 360000 | 491904 | 875520 | 0 | 0 | 194789 | 489600 | 0 | 8335500 | 3753600 | 9510273 | 0 | 108503 | 0 | 1714337 | 0 | 0 | 67395 | 158400 | 354600 | 290880 | 0 | 0 | 0 | 0 | 0 | 0 | 1116000 | 0 | 0 | 0 | 471360 | 0 | 476 | 588060 | 23418 | 259200 | 8174545.46 | 0 | 0 | 0 | 7722 | 131309 | 4629461 | 0 | 0 | 0 | 18943634 | 16065 | 549128 | 60218 | 117091 | 0 | 7836500 | 7548000 | 583200 | 4484000 | 421560 | 373440 | 0 | 734400 | 189840 | 28440 | 476520 | 224640 | 0 | 106009 | 0 | 6349000 | 7520100 | 8465000 | 892000 | 0 | 0 | 3391036 | 0 | 0 | 1121280 | 0 | 0 | 0 | 2456050 | 0 | 602400 | 1024800 | 0 | 3050 | 91000 | 86160 | 125352133.46 | 17589090 | 4714848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338400 | 21061820 | 0 | 21349091 | 0 | 0 | 0 | 327840 | 0 | 0 | 0 | 0 | 0 | 264750 | 0 | 111744 | 724664 | 0 | 0 | 0 | 0 | 0 | 8106036 | 0 | 9600 | 0 | 3745000 | 1144145 | 596928 | 77842 | 201984 | 0 | 0 | 23335.92 | 403920 | 2112 | 0 | 4961000 | 52501 | 0 | 5322570 | 0 | 6246960 | 18689454.55 | 0 | 116065635.47 | 241417768.93

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 30-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 9416.92 | MW | 12:00 Hr. | Energy Generated |  |  | 241.4178 |  | MKWHr.
| Day Peak Demand |  |  | 9416.92 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0 |  | MKWHr.
| Evening Peak Generation |  |  | 13299.2 | MW | 21:00 Hr. | Energy Demand |  |  | 241.4178 |  | MKWHr.
| Evening Peak Demand |  |  | 13299.2 | MW | 21:00 Hr. | Maximum Temperature |  |  | 28.5 |  | °C
| Minimum Generation of the Day |  |  | 7297.96 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 827.4 |  | MMCFD
| Maximum Generation of the Day |  |  | 13299.2 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 5.4282 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 31.5624 | 0 | 3.6262 | 0 | 0 | 0.067395 | 0 | 0 | 35.256 | Gas | 107.1341 | Gas | 373020836.2
| Chattogram Zone |  |  | 4.8887 | 27.1182 | 0.63381 | 0 | 0.58806 | 0.016541 | 0 | 1.116 | 34.3613 | Coal | 82.9666 | Coal | 533995011.5185
| Cumilla Zone |  |  | 21.5679 | 0 | 1.8344 | 0 | 0 | 0.10601 | 0.22464 | 0 | 23.733 | HFO | 8.9346 | HFO | 165593164.69
| Mymensingh Zone |  |  | 0 | 0 | 1.7134 | 0 | 0 | 0.09405 | 0 | 0 | 1.8074 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.1945 | Hydro | 0.58806 | Hydro | 58806
| Khulna Zone |  |  | 4.7148 | 21.0618 | 0 | 0 | 0 | 0.3384 | 17.5891 | 0 | 43.7042 | Solar | 1.5157 | Solar | 24910107.3912
| Barishal Zone |  |  | 5.3751 | 29.8974 | 0 | 0 | 0 | 0.002112 | 0 | 0 | 35.2746 | Import | 39.1628 | Import | 196550804.98
| Rajshahi Zone |  |  | 8.8307 | 0 | 0.32784 | 0 | 0 | 0.38609 | 21.3491 | 0 | 30.8937 | Wind | 1.116 | Wind | 16338240
| Rangpur Zone |  |  | 0 | 4.8891 | 0.79891 | 0 | 0 | 0.5051 | 0 | 0 | 6.1932
| Total |  |  | 107.1341 | 82.9666 | 8.9346 | 0 | 0.58806 | 1.5157 | 39.1628 | 1.116 | 241.4178
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 373020836.2 |  | Hydro | 58806
|  |  |  | Coal | 533995011.5185 |  | Solar | 24910107.3912
|  |  |  | HFO | 165593164.69 |  | Import | 196550804.98
|  |  |  | HSD | 0 |  | Wind | 16338240
[5 empty] | Total: | 131,04,66,970 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 17.5891 | Peak Hr Flow | 926.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 33707618.23 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 21.3491 | Peak Hr Flow | 1016.00 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 518 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.22464 | Peak Hr Flow | 20.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 988 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 39.1628 | Peak Hr Flow | 1962.00 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4678
|  |  |  | Chattogram |  | 0 |  | 1270
|  |  |  | Cumilla |  | 0 |  | 1193
|  |  |  | Mymensingh |  | 0 |  | 994
|  |  |  | Sylhet |  | 0 |  | 453
|  |  |  | Khulna |  | 0 |  | 1665
|  |  |  | Barishal |  | 0 |  | 381
|  |  |  | Rajshahi |  | 0 |  | 1349
|  |  |  | Rangpur |  | 0 |  | 840
|  |  |  | Total |  | 0 |  | 12823
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[7 empty] | 4 | Sylhet 225 MW CCPP ST |  |  | 89
[5 empty] | Total | 300 |  |  |  | Total | 489
|  |  |  | Total Unavailable Capacity |  |  |  | 789
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:05 | 09:48 | Kushtia 132/33kV S/S T2 HT Scheduled S/D | [7 empty] | 30.0MW load
interrup.
| 08:46 | 09:58 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Bus D/S Redhot Maintenance. | [7 empty] | 20.0MW load
interrup.
| 08:47 | 09:57 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Bus D/S Redhot Maintenance. | [7 empty] | 20.0MW load
interrup.
| 09:01 | 15:08 | Kabirpur -Tongi 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Tongi ckt-1
45 no tower line conductor replacement work. and from Tongi 230/132/33kV end Due to
Shutdown taken by Kabirpur grid substations
| 09:03 | 19:40 | Kabirpur -Tongi 132kV Ckt-2 Tripped from Tongi 230/132/33kV end showing No relay
operated relays.
|  | 09:28 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
|  | 09:28 | Khulna(C )-Khulna (S) 132kV Ckt-1 is restored.
| 09:30 | 10:02 | Chowmuhani 132/33kV S/S TR1-415T LT Forced S/D Due to DS A Phase Red Hot Maintenance | [7 empty] | 15.0MW load
interrup.
| 09:31 | 11:48 | Khulna(C )-Khulna (S) 132kV Ckt-2 Scheduled S/D from Khulna(S) 230/132kV end.
| 09:53 |  | Import (Tripura) Synchronized
| 10:34 | 12:43 | Cumilla(N) 230/132/33kV S/S 132KV T-03 HT Scheduled S/D Due to 33kv bus section redhot
maintenance
| 10:34 | 12:43 | Cumilla(N) 230/132/33kV S/S 132KV T-03 LT Scheduled S/D Due to 33kv bus section DS redhot
maintenance
| 11:22 | 11:30 | Cox'sbazar-Dohazari 132 kV Ckt-2 Tripped from Dohazari 132/33kV end showing Distance
Relay relays.
| 11:22 | 11:45 | Cox'sbazar-Dohazari 132 kV Ckt-1 Tripped from Dohazari 132/33kV end showing Distance
Relay (A Phase) relays.
| 11:49 | 18:29 | Khagrachori 132/33kV S/S TR-1 LT Forced S/D Due to Fire incident at 33 kV incomer-1
cable(Y Phase).
| 12:00 |  | Day Peak Generation: 9414 MW.
|  | 12:33 | Bogura 230/132kV S/S T-02 HT is restored.
|  | 12:34 | Bogura 230/132kV S/S T-02 LT is restored.
| 12:51 | 18:26 | Khagrachori 132/33kV S/S TR-1 HT Forced S/D Due to Fire incident at 33 kV incomer-1
cable(Y Phase).
|  | 12:57 | Tongi 230/132/33kV S/S T-03 LT is restored.
|  | 12:57 | Tongi 230/132/33kV S/S T-03 HT is restored.
| 13:43 |  | Siddhirganj CCPP 335 MW GT was sync.
| 13:51 | 14:01 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Tripped showing O/C relays Due to from 33KV
feeder fault.
| 13:51 | 14:01 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Tripped showing o/c relays Due to fromm 33kv
feeder fault
| 15:09 | 19:40 | Kabirpur -Tongi 132kV Ckt-2 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown
taken by Kabirpur grid substations
| 15:10 | 16:56 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to Hot spot | [7 empty] | 30.0MW load
|  |  | maintenance | [7 empty] | interrup.
| 15:24 | 17:23 | Goalpara 132/33kV S/S T-5 HT Scheduled S/D Due to Red hot maintenance work in 33 kV | [7 empty] | 5.0MW load
|  |  | Chandanimohol Feeder | [7 empty] | interrup.
| 15:24 | 17:24 | Goalpara 132/33kV S/S T-5 LT Scheduled S/D Due to Red hot maintenance work in 33 kV | [7 empty] | 5.0MW load
|  |  | Chandanimohol Feeder | [7 empty] | interrup.
| 15:24 | 16:58 | Savar 132/33kV S/S T-2 HT Scheduled S/D Due to Hot spot maintenance
| 15:24 | 16:58 | Savar 132/33kV S/S T-2 LT Scheduled S/D Due to Hot spot maintenance
| 15:26 | 17:20 | Goalpara 132/33kV S/S T-6 LT Scheduled S/D Due to Red hot maintenance work in 33 kV | [7 empty] | 5.0MW load
|  |  | Chandanimohol Feeder | [7 empty] | interrup.
| 15:27 | 17:20 | Goalpara 132/33kV S/S T-6 HT Scheduled S/D Due to Red hot maintenance work in 33 kV | [7 empty] | 5.0MW load
|  |  | Chandanimohol Feeder | [7 empty] | interrup.
| 15:44 | 17:30 | Rangpur 132/33kV S/S T-2 (404T) LT Scheduled S/D Due to KV BUS SECTION RED HOT | [7 empty] | 25.0MW load
interrup.
| 15:44 |  | Siddhirganj CCPP 335 MW ST was sync.
| 15:48 | 17:28 | Rangpur 132/33kV S/S T-2 (404T) HT Scheduled S/D Due to None | [7 empty] | 25.0MW load
interrup.
| 15:53 | 16:26 | BIPTC S/S 10CF25 Forced S/D
| 16:36 | 17:30 | Lalmonirhat 132/33kV S/S T-2 (415T) LT Tripped showing MCCG 51G relays Due to Pbs1 feeder | [7 empty] | 10.5MW load
|  |  | fault | [7 empty] | interrup.
| 16:36 | 20:05 | Lalmonirhat 132/33kV S/S T-1 (425T) LT Tripped showing MCGG 51G relays Due to Pbs ckt -1 | [7 empty] | 10.5MW load
|  |  | feeder fault | [7 empty] | interrup.
| 16:40 | 17:34 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D | [7 empty] | 9.0MW load
interrup.
| 16:42 | 17:32 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D | [7 empty] | 9.0MW load
interrup.
| 17:40 | 19:04 | Bhangura 132/33kV S/S Tr-1(403T) LT Forced S/D | [7 empty] | 10.0MW load
interrup.
| 17:42 | 19:02 | Bhangura 132/33kV S/S Tr-1(403T) HT Forced S/D | [7 empty] | 10.0MW load
interrup.
| 19:02 |  | Siddhirganj CCPP 335 MW tripped due to gas turbine's exciter trip.
| 19:34 |  | Siddhirganj CCPP 335 MW GT was sync.
| 20:30 |  | Siddhirganj CCPP 335 MW ST was sync.
| 20:54 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- GT
| 20:54 |  | Sirajgonj 225MW CCPP Unit-1 GT Synchronized with remarks:- GT has been synchronized with
grid at 20:54 hrs as per instruction of NLDC and ST startup process is going on.
| 20:54 |  | Sirajgonj Unit-1 GT was sync.
| 21:00 |  | Evening Peak Gen. 13299 MW
| 21:22 | 22:48 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) LT Forced S/D Due to Red hot maintenance of | [7 empty] | 40.0MW load
|  |  | 33kV busber | [7 empty] | interrup.
| 21:23 | 22:46 | Chuadanga 132/33kV S/S 132kV Tr. T1(416T) HT Forced S/D Due to Red hot maintenance of | [7 empty] | 40.0MW load
|  |  | 33kV busber | [7 empty] | interrup.
| 23:42 |  | Sirajgonj 225MW CCPP Unit-1 ST Synchronized with remarks:- ST has been synchronized with
grid at 23:42 hrs as per instruction of NLDC.
| 23:42 |  | Sirajgonj 225MW CCPP Unit-1 Synchronized with remarks:- ST
| 00:04 |  | Unique Meghnaghat Power Limited (UMPL) record a general event:- Plant was shutdown as per
NLDC due to Allocation limit by Titas, instructed by DS(Gen).
| 00:05 |  | Unique Meghnaghat Power Limited (UMPL) GT Shutdown with remarks:- 23, May 2025 at 22:10
Plant was shutdown as per NLDC due to Allocation limit by Titas, instructed by DS(Gen).
| 00:07 |  | Unique Meghnaghat Power Limited (UMPL) ST Shutdown with remarks:- 23, May 2025 at 22:10
Plant was shutdown as per NLDC due to Allocation limit by Titas, instructed by DS(Gen).
| 04:52 |  | Hasnabad 230/132kV S/S AUTO TR-1 HT Tripped showing 230 kV ATR-1 Differential Relay
(87T) Gen. Trip R,Y,B Stage-1 86-T1,86-T2 relays Due to 230 kV ATR-1 Differential
Relay (87T)
| 04:52 |  | Hasnabad 230/132kV S/S AUTO TR-1 LT Tripped showing 230 kV ATR-1 Differential Relay
(87T) Gen. Trip R,Y,B Stage-1 86-T1,86-T2 relays Due to 230 kV ATR-1 Differential
Relay (87T)
| 05:36 | 07:17 | Mongla 132/33kV S/S Main Bus Project Work S/D Due to Project work | [7 empty] | 33.0MW load
interrup.
| 05:38 | 07:16 | Bagerhat-Mongla 132 kV Ckt-1 Project Work S/D from Bagerhat 132/33kV end Due to Due to
project work of Mongla ss
| 05:39 | 07:16 | Bagerhat-Mongla 132 kV Ckt-2 Project Work S/D from Bagerhat 132/33kV end Due to Due to
project work of Mongla SS.
| 06:01 |  | Bheramara P/S-Ishurdi 132 kV Ckt-1 Project Work S/D from Ishurdi 132/33kV end.
| 06:01 |  | Bheramara P/S-Ishurdi 132 kV Ckt-2 Project Work S/D from Ishurdi 132/33kV end.
| 06:04 |  | Bheramara-HVDC Bheramara 230 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to | [7 empty] | 60.0MW load
|  |  | Ruppur 400 KV line charge and from BIPTC end Due to Shutdown has been taken for withdrawn | [7 empty] | interrup. Bheramara
|  |  | of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit Transmission Line | [7 empty] | 230/132kV end
Project.
| 06:11 |  | Bheramara-HVDC Bheramara 230 kV Ckt-2 Scheduled S/D from BIPTC end Due to Shutdown has | [7 empty] | and 60.0MW load
|  |  | been taken for withdrawn of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit | [7 empty] | interrup. Bheramara
|  |  | Transmission Line Project. and from Bheramara 230/132kV end Due to Ruppur 400 kv line | [7 empty] | 230/132kV end
charge
| 06:19 |  | Bheramara P/S-Ishurdi 132 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to | [7 empty] | 46.0MW load
|  |  | Ruppur 400 kv line charge | [7 empty] | interrup. Bheramara
230/132kV end
| 06:20 |  | Bheramara P/S-Ishurdi 132 kV Ckt-2 Scheduled S/D from Bheramara 230/132kV end Due to | [7 empty] | 46.0MW load
|  |  | Ruppur 400 kv line charge | [7 empty] | interrup. Bheramara
230/132kV end
| 07:01 |  | HVDC Bheramera- Jhenaidah 230kV Ckt-1 Scheduled S/D from BIPTC end Due to Shutdown has
been taken for withdrawn of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit
Transmission Line Project.
| 07:02 |  | HVDC Bheramera-Jhenaidah 230kV Ckt-2 Scheduled S/D from BIPTC end Due to Shutdown has
been taken for withdrawn of the cradle guard under Rooppur-Gopalganj 400KV Single Circuit
Transmission Line Project.
| 07:27 |  | Bogura 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot | [7 empty] | 20.0MW load
interrup.
| 07:27 |  | Bogura 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot. | [7 empty] | 20.0MW load
interrup.
| 07:50 |  | Cox'sbazar-Dohazari 132 kV Ckt-1 Tripped from Coxsbazar 132/33kV end showing QUADRAMHO | [7 empty] | 25.0MW load
|  |  | SHPM-101 relays Due to Phase A & zone 1 fault and from Dohazari 132/33kV end showing | [7 empty] | interrup. Coxsbazar
|  |  | Distance Relay (C phase) relays. | [7 empty] | 132/33kV end and
66.0MW load
interrup. Dohazari
132/33kV end
| 07:51 |  | Cox'sbazar-Dohazari 132 kV Ckt-2 Tripped from Coxsbazar 132/33kV end showing Simens | [7 empty] | 64.0MW load
|  |  | SIPROTEC 7SA87 relays Due to Phase R & B, Zone-1 fault and from Dohazari 132/33kV end | [7 empty] | interrup. Coxsbazar
|  |  | showing Numerical Relay relays. | [7 empty] | 132/33kV end and
55.0MW load
interrup. Dohazari
132/33kV end
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 30-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | -
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 328 | 7603200 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8335500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 133 | 3753600 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 185 | 1714337 | -
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 35 | 184320 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 147 | 875520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 17 | 194789 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 108503 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 17 | 354600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 18 | 290880 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 152640 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 51 | 491904 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 610560 | Liquid fuel shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 0 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 489600 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 67395 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 360000 | Liquid fuel shortage
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 583 | 9510273 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | Gas shortage
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 35 | 158400 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2272 | 35256021
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 0 | 7722 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 16065 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 38 | 588060 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 220 | 4629461 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 131309 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 471360 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 36 | 259200 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 476 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 0 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 15 | 23418 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 18943634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 62 | 1116000 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 360 | 8174545.46 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2072 | 34361250.46
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 181 | 4484000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 7836500 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7548000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 31 | 421560 | machine problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 46 | 583200 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 8 | 117091 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 549128 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 40 | 60218 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 136 | 734400 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 20 | 224640 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 5 | 28440 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 70 | 476520 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 36 | 189840 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 68 | 373440 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 106009 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1388 | 23732986
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 3050 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 118 | 1024800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 83 | 602400 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 91000 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 86160 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 0 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 213 | 1807410
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 39 | 892000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 151 | 3391036 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1121280 | Allocation limit by Titas, instructed by DS(Gen)
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 102 | 2456050 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 6349000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 350 | 8465000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7520100 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1330 | 30194466
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 926 | 17589090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 223 | 4714848 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 0 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 338400 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 21061820 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2383.2 | 43704158
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 6246960 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 4 | 52501 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 0 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 18689454.55 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5322570 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 4961000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2112 | -
Barishal Area Total |  |  |  |  | 2236 | 1775 | 35274597.55
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | shundown for maintenance work
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 5 | 724664 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8106036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 327840 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 9600 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1016 | 21349091 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 111744 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 264750 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1505 | 30893725
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1144145 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 162 | 3745000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 201984 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 23335.92 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 596928 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 77842 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 403920 | -
Rangpur Area Total |  |  |  |  | 950 | 361 | 6193154.92
Eastern Grid Total |  |  |  |  | 16771.895 | 7275 | 125352133.46
Western Grid Total |  |  |  |  | 10338.16 | 6024.2 | 116065635.47
National Grid Total |  |  |  |  | 27110.055 | 13299.2 | 241417768.93
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 30-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 8588.53 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4235 | MW
i) Dhaka area |  |  | 4677.54 |  | MW | i) Khulna area |  |  |  | 1664.6 | MW
ii) Chattogram area |  |  | 1270.5 |  | MW | ii) Barishal area |  |  |  | 381 | MW
iii) Cumilla area |  |  | 1193.49 |  | MW | iii) Rajshahi area |  |  |  | 1349.4 | MW
iv) Mymensingh area |  |  | 994 |  | MW | iv) Rangpur area |  |  |  | 840 | MW
v) Sylhet area |  |  | 453 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 12823.53 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 18 | 08:00 | 67 | Ishurdi | 73 | 21:00 | 133 | Patuakhali | 64.5 | 23:00
2 | AKSML | 75 | 12:00 | 68 | Jaldhaka | 80 | 19:30 | 134 | Payra | 30 | 23:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jamalpur | 103 | 20:00 | 135 | Postogola | 47 | 13:00
4 | Agargaon | 108 | 13:00 | 70 | Jashore | 137 | 21:00 | 136 | Purbachal | 17 | 00:00
5 | Agrabad | 84 | 23:00 | 71 | Jhenaidah | 115 | 21:00 | 137 | Purbasadipur | 136 | 20:00
6 | Amnura | 35 | 22:00 | 72 | Joydebpur | 117 | 16:00 | 138 | Rahanpur | 28 | 22:00
7 | Ashuganj | 83 | 19:00 | 73 | Joypurhat | 60 | 21:00 | 139 | Rahim | 39 | 02:00
8 | BSRM | 198 | 02:00 | 74 | Juldah | 17.5 | 20:00 | 140 | Rajbari | 72 | 19:30
9 | Bagerhat | 89 | 19:00 | 75 | KSRM | 21 | 20:00 | 141 | Rajendrapur | 108 | 21:00
10 | Bajitpur | 35 | 21:00 | 76 | Kabirpur | 218 | 23:00 | 142 | Rajshahi | 100 | 00:00
11 | Bakulia | 93 | 21:00 | 77 | Kachua | 59 | 23:00 | 143 | Rajshahi-230 | 77 | 13:00
12 | Banani | 27.4 | 12:00 | 78 | Kallyanpur | 93 | 13:00 | 144 | Ramganj | 82 | 23:00
13 | Bangabhaban | 4 | 13:00 | 79 | Kalurghat | 36 | 11:00 | 145 | Rampur | 38 | 21:00
14 | Barapukuria | 59 | 19:30 | 80 | Kamrangirchar | 58.7 | 00:00 | 146 | Rangamati | 14 | 19:30
15 | Barguna | 20 | 21:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 141 | 20:00
16 | Barishal | 100 | 19:30 | 82 | Kasba | 31 | 21:00 | 148 | Ruppur | 7 | 11:00
17 | Barishal-230 | 94 | 22:00 | 83 | Kazla | 92 | 13:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 48 | 23:00 | 84 | Keranigonj | 79 | 21:00 | 150 | Saidpur | 108 | 19:30
19 | Baroirhat | 64 | 22:00 | 85 | Khagrachori | 32 | 20:00 | 151 | Satkhira | 140 | 22:00
20 | Bashundhara | 156 | 21:00 | 86 | Khulna | 66 | 00:00 | 152 | Satmasjid | 89 | 21:00
21 | BashundharaCement | 8 | 17:00 | 87 | Khulshi | 163 | 00:00 | 153 | Savar | 184 | 12:00
22 | Beanibazar | 64 | 00:00 | 88 | Kishoreganj | 109 | 23:00 | 154 | SevenRings | 15.12 | 03:00
23 | Benapole | 58 | 21:00 | 89 | Kodda | 274 | 03:00 | 155 | ShahCement | 24 | 01:00
24 | Bhaluka | 136 | 21:00 | 90 | Kulaura | 43 | 23:00 | 156 | Shahjadpur | 70 | 19:30
25 | Bhandaria | 54.8 | 23:00 | 91 | Kurigram | 50 | 20:00 | 157 | Shahjibazar | 109 | 21:00
26 | Bhangura | 35 | 21:00 | 92 | Kushtia | 138 | 21:00 | 158 | Shahmirpur | 40 | 23:00
27 | Bheramara(GK) | 58 | 19:30 | 93 | Lalbag | 52 | 01:00 | 159 | Shariatpur | 82 | 19:30
28 | Bhulta | 256 | 23:00 | 94 | Lalmonirhat | 38 | 23:00 | 160 | Sherpur | 128 | 22:00
29 | Bog-Sherpur | 64 | 22:00 | 95 | MI_Cement | 15.8 | 16:00 | 161 | Shikalbaha | 22 | 19:00
30 | Bogura | 156 | 22:00 | 96 | Madanganj | 38 | 14:00 | 162 | Shitalakhya | 56.1 | 15:00
31 | Borhanuddin | 60 | 23:00 | 97 | Madaripur | 108 | 19:30 | 163 | Sholosohor | 42 | 00:00
32 | Brahmanbaria | 120 | 22:00 | 98 | Madartek | 80.58 | 13:00 | 164 | Shyampur | 132 | 00:00
33 | Cantonment | 120 | 12:00 | 99 | Madunaghat | 47 | 19:30 | 165 | Siddhirganj | 95 | 22:00
34 | Chandina | 16.81 | 19:30 | 100 | Magura | 59 | 21:00 | 166 | Sirajganj | 88 | 20:00
35 | Chandpur | 74 | 21:00 | 101 | Mahasthangarh | 74 | 21:00 | 167 | Sonargaon | 108 | 23:00
36 | Chandraghona | 33 | 23:00 | 102 | Manikganj | 122 | 21:00 | 168 | Sreemongol | 65 | 23:00
37 | Chapai | 66 | 23:00 | 103 | Maniknagar | 64 | 13:00 | 169 | Sreepur | 89 | 19:00
38 | Charsaidpur | 30 | 20:00 | 104 | Matarbari | 33 | 21:00 | 170 | Srinagar | 44.05 | 22:00
39 | Chauddagram | 68 | 21:00 | 105 | Matuail | 55 | 23:00 | 171 | Sunamganj | 44 | 23:00
40 | Chhatak | 27 | 00:00 | 106 | Millgate | 79 | 10:00 | 172 | Sylhet | 40 | 21:00
41 | Chowmuhani | 190 | 23:00 | 107 | Mirpur | 109 | 19:30 | 173 | Sylhet-132 | 98 | 00:00
42 | Chuadanga | 96 | 19:00 | 108 | Mirsorai | 7 | 08:00 | 174 | TK | 29.5 | 23:00
43 | Coxsbazar | 107 | 23:00 | 109 | Mirzapur | 50 | 19:30 | 175 | Tangail | 158 | 20:00
44 | Cumilla(N) | 136 | 22:00 | 110 | Mithapukur | 56 | 19:30 | 176 | Thakurgaon | 105 | 19:30
45 | Cumilla(S) | 126 | 23:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 92 | 20:00
46 | Daudkandi | 148 | 21:00 | 112 | Mogbazar | 109.9 | 16:00 | 178 | Ullahpara | 33 | 19:30
47 | Dhaka | 34 | 12:00 | 113 | Mongla | 38 | 12:00 | 179 | Ullon | 36 | 12:00
48 | Dhamrai | 128 | 22:00 | 114 | Motijheel | 31 | 13:00 | 180 | Uttara | 85 | 13:00
49 | Dhanmondi | 110 | 12:00 | 115 | Muktagacha | 32 | 21:00 | 181 | UttaraNew | 50 | 21:00
50 | Dohazari | 60 | 21:00 | 116 | Munshiganj | 110 | 22:00 | 182 | Zigatola | 66 | 13:00
51 | Faridpur | 145 | 21:00 | 117 | Muradnagar | 13 | 00:00
52 | Fatullah | 78 | 12:00 | 118 | Mymensingh | 163 | 21:00
53 | Fenchuganj | 36 | 23:00 | 119 | Naogaon | 118 | 21:00
54 | Feni | 105 | 22:00 | 120 | Narail | 53 | 19:30
55 | GPH | 89 | 01:00 | 121 | Narinda | 56 | 13:00
56 | Ghatail | 68 | 20:00 | 122 | Narshingdi | 149 | 21:00
57 | Ghorashal | 12 | 19:30 | 123 | Natore | 139 | 23:00
58 | Ghorashal-230 | 90 | 23:00 | 124 | Nawabganj | 52 | 22:00
59 | Goalpara | 36 | 00:00 | 125 | Netrakona | 101 | 21:00
60 | Gollamari | 90 | 23:00 | 126 | New | 72.7 | 12:00
61 | Gopalganj | 101.1 | 22:00 | 127 | Niamatpur | 70 | 23:00
62 | Gulshan | 88 | 13:00 | 128 | Noapara | 44 | 00:00
63 | Halishahar | 56.5 | 00:00 | 129 | PHP | 4 | 09:00
64 | HaripurSBU | 170 | 22:00 | 130 | Pabna | 105 | 21:00
65 | Hasnabad | 56 | 20:00 | 131 | Palashbari | 82 | 20:00
66 | Hathazari | 73 | 22:00 | 132 | Panchagarh | 66 | 19:30
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 30-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 9444.55 | 0 |  | 9444.55
1:00 | 9016.77 | 0 |  | 9016.77
2:00 | 8649.03 | 0 |  | 8649.03
3:00 | 8250.17 | 0 |  | 8250.17
4:00 | 7625.11 | 0 |  | 7625.11
5:00 | 7372.53 | 0 |  | 7372.53
6:00 | 7297.96 | 0 |  | 7297.96
7:00 | 7383.3 | 0 |  | 7383.3
8:00 | 7492.77 | 0 |  | 7492.77
9:00 | 7633.46 | 0 |  | 7633.46
10:00 | 7999.88 | 0 |  | 7999.88
11:00 | 8792.06 | 0 |  | 8792.06
12:00 | 9416.92 | 0 |  | 9416.92
13:00 | 9853.96 | 0 |  | 9853.96
14:00 | 9718.52 | 0 |  | 9718.52
15:00 | 9985.39 | 0 |  | 9985.39
16:00 | 10086.97 | 0 |  | 10086.97
17:00 | 10236.14 | 0 |  | 10236.14
18:00 | 10512.59 | 0 |  | 10512.59
19:00 | 11691 | 0 |  | 11691
19:30 | 12537 | 0 |  | 12537
20:00 | 12670.2 | 0 |  | 12670.2
21:00 | 13299.2 | 0 |  | 13299.2
22:00 | 13088.2 | 0 |  | 13088.2
23:00 | 13209.2 | 0 |  | 13209.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 30-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 4833 | 4611.55 | 9444.55 | DAILY GENERATION CURVE
00:30 | 4709.5 | 4521.16 | 9230.66
01:00 | 4586 | 4430.77 | 9016.77 | 30-05-2025
01:30 | 4473 | 4359.9 | 8832.9
02:00 | 4360 | 4289.03 | 8649.03
02:30 | 4195 | 4254.6 | 8449.6
03:00 | 4030 | 4220.17 | 8250.17
03:30 | 3924 | 4013.64 | 7937.64
04:00 | 3818 | 3807.11 | 7625.11
04:30 | 3804 | 3694.82 | 7498.82
05:00 | 3790 | 3582.53 | 7372.53
05:30 | 3809.515 | 3525.73 | 7335.245
06:00 | 3829.03 | 3468.93 | 7297.96
06:30 | 3838.41 | 3502.22 | 7340.63
07:00 | 3847.79 | 3535.51 | 7383.3
07:30 | 3881.8 | 3556.235 | 7438.035
08:00 | 3915.81 | 3576.96 | 7492.77
08:30 | 3975.385 | 3587.73 | 7563.115
09:00 | 4034.96 | 3598.5 | 7633.46
09:30 | 4141.265 | 3675.405 | 7816.67
10:00 | 4247.57 | 3752.31 | 7999.88
10:30 | 4575.84 | 3820.13 | 8395.97
11:00 | 4904.11 | 3887.95 | 8792.06
11:30 | 5049.34 | 4055.15 | 9104.49
12:00 | 5194.57 | 4222.35 | 9416.92
12:30 | 5228.245 | 4407.195 | 9635.44
13:00 | 5261.92 | 4592.04 | 9853.96
13:30 | 5224.52 | 4561.72 | 9786.24
14:00 | 5187.12 | 4531.4 | 9718.52
14:30 | 5297.335 | 4554.62 | 9851.955
15:00 | 5407.55 | 4577.84 | 9985.39
15:30 | 5423.78 | 4612.4 | 10036.18
16:00 | 5440.01 | 4646.96 | 10086.97
16:30 | 5517.965 | 4643.59 | 10161.555
17:00 | 5595.92 | 4640.22 | 10236.14
17:30 | 5648.41 | 4725.955 | 10374.365
18:00 | 5700.9 | 4811.69 | 10512.59
18:30 | 6057.95 | 5043.845 | 11101.795
19:00 | 6415 | 5276 | 11691
19:30 | 6726 | 5811 | 12537
20:00 | 6786 | 5884.2 | 12670.2
20:30 | 7030.5 | 5954.2 | 12984.7 |  | Executive Engineer
21:00 | 7275 | 6024.2 | 13299.2 |  | Network Operation Division
21:30 | 7180.5 | 6013.2 | 13193.7
22:00 | 7086 | 6002.2 | 13088.2
22:30 | 7134.5 | 6014.2 | 13148.7
23:00 | 7183 | 6026.2 | 13209.2

## En-Curve
QF-LDC-12
Date | 30-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 2856 | 1580 | 931 | 0 | 0 | 822.55 | 40 | 3090 | 0 | 20 | 44 | 0 | 0 | 61 | 0 | DAILY ENERGY CURVE
00:30 | 2819.5 | 1545 | 931.5 | 0 | 0 | 825.16 | 40 | 2941.5 | 0 | 22.5 | 44 | 0 | 0 | 61.5 | 0 | 30-05-2025
01:00 | 2783 | 1510 | 932 | 0 | 0 | 827.77 | 40 | 2793 | 0 | 25 | 44 | 0 | 0 | 62 | 0
01:30 | 2683.5 | 1490 | 929 | 0 | 0 | 826.4 | 39.5 | 2755.5 | 0 | 16.5 | 30.5 | 0 | 0 | 62 | 0 | Energy Generated | 241.4178 |  | MKWHr
02:00 | 2584 | 1470 | 926 | 0 | 0 | 825.03 | 39 | 2718 | 0 | 8 | 17 | 0 | 0 | 62 | 0 | Energy not Served | 0 |  | MKWHr
02:30 | 2492.5 | 1408.5 | 926 | 0 | 0 | 821.6 | 19.5 | 2694.5 | 0 | 8 | 17 | 0 | 0 | 62 | 0 | Total Energy Requirement | 241.4178 |  | MKWHr
03:00 | 2401 | 1347 | 926 | 0 | 0 | 818.17 | 0 | 2671 | 0 | 8 | 17 | 0 | 0 | 62 | 0
03:30 | 2351 | 1276 | 732.5 | 0 | 0 | 820.64 | 0 | 2679 | 0 | 8 | 8.5 | 0 | 0 | 62 | 0
04:00 | 2301 | 1205 | 539 | 0 | 0 | 823.11 | 0 | 2687 | 0 | 8 | 0 | 0 | 0 | 62 | 0
04:30 | 2235.5 | 1200 | 518.5 | 0 | 0 | 824.82 | 0 | 2650 | 0 | 8 | 0 | 0 | 0 | 62 | 0
05:00 | 2170 | 1195 | 498 | 0 | 0 | 826.53 | 0 | 2613 | 0 | 8 | 0 | 0 | 0 | 62 | 0
05:30 | 2192.5 | 1195 | 497.5 | 0 | 0 | 825.29 | 0 | 2554 | 4.955 | 4 | 0 | 0 | 0 | 62 | 0
06:00 | 2215 | 1195 | 497 | 0 | 0 | 824.05 | 0 | 2495 | 9.91 | 0 | 0 | 0 | 0 | 62 | 0
06:30 | 2237.5 | 1195 | 497.5 | 0 | 0 | 823.655 | 0 | 2509.5 | 18.975 | 0 | 0 | 0 | 0 | 58.5 | 0
07:00 | 2260 | 1195 | 498 | 0 | 0 | 823.26 | 0 | 2524 | 28.04 | 0 | 0 | 0 | 0 | 55 | 0
07:30 | 2326 | 1203 | 474.5 | 0 | 0 | 821.63 | 0 | 2524.5 | 51.905 | 0 | 0 | 0 | 0 | 36.5 | 0
08:00 | 2392 | 1211 | 451 | 0 | 0 | 820 | 0 | 2525 | 75.77 | 0 | 0 | 0 | 0 | 18 | 0
08:30 | 2411 | 1237 | 451 | 0 | 0 | 819.33 | 0 | 2521 | 89.785 | 0 | 0 | 0 | 0 | 34 | 0
09:00 | 2430 | 1263 | 451 | 0 | 0 | 818.66 | 0 | 2517 | 103.8 | 0 | 0 | 0 | 0 | 50 | 0
09:30 | 2474.5 | 1299 | 520.5 | 0 | 2 | 823.565 | 0 | 2518 | 116.605 | 0 | 9 | 0 | 0 | 53.5 | 0
10:00 | 2519 | 1335 | 590 | 0 | 4 | 828.47 | 0 | 2519 | 129.41 | 0 | 18 | 0 | 0 | 57 | 0
10:30 | 2725 | 1524.5 | 555 | 0 | 5 | 827.615 | 0 | 2537 | 134.855 | 0 | 27.5 | 0 | 0 | 59.5 | 0
11:00 | 2931 | 1714 | 520 | 0 | 6 | 826.76 | 0 | 2555 | 140.3 | 0 | 37 | 0 | 0 | 62 | 0
11:30 | 2891.5 | 1842.5 | 604.5 | 0 | 8 | 827.94 | 20 | 2666 | 156.55 | 0 | 56.5 | 0 | 0 | 31 | 0
12:00 | 2852 | 1971 | 689 | 0 | 10 | 829.12 | 40 | 2777 | 172.8 | 0 | 76 | 0 | 0 | 0 | 0
12:30 | 2863 | 1982.5 | 688.5 | 0 | 15 | 879.26 | 40 | 2906 | 177.68 | 3 | 78 | 0 | 0 | 2.5 | 0
13:00 | 2874 | 1994 | 688 | 0 | 20 | 929.4 | 40 | 3035 | 182.56 | 6 | 80 | 0 | 0 | 5 | 0
13:30 | 2895 | 1950.5 | 688.5 | 0 | 22 | 923.2 | 40 | 2948 | 232.04 | 11.5 | 65.5 | 0 | 0 | 10 | 0
14:00 | 2916 | 1907 | 689 | 0 | 24 | 917 | 40 | 2861 | 281.52 | 17 | 51 | 0 | 0 | 15 | 0
14:30 | 2932 | 1959 | 688.5 | 0 | 22 | 921.5 | 40 | 2962 | 213.955 | 27 | 66 | 0 | 0 | 20 | 0
15:00 | 2948 | 2011 | 688 | 0 | 20 | 926 | 40 | 3063 | 146.39 | 37 | 81 | 0 | 0 | 25 | 0
15:30 | 2918 | 1954.5 | 688 | 0 | 22 | 925 | 40 | 3135.5 | 144.68 | 51.5 | 117 | 0 | 0 | 40 | 0
16:00 | 2888 | 1898 | 688 | 0 | 24 | 924 | 40 | 3208 | 142.97 | 66 | 153 | 0 | 0 | 55 | 0
16:30 | 2924 | 1900 | 688.5 | 0 | 19 | 919.5 | 37 | 3239 | 140.555 | 82 | 154.5 | 0 | 0 | 57.5 | 0
17:00 | 2960 | 1902 | 689 | 0 | 14 | 915 | 34 | 3270 | 138.14 | 98 | 156 | 0 | 0 | 60 | 0
17:30 | 2963 | 1848.5 | 807.5 | 0 | 17 | 916.5 | 34.5 | 3369 | 82.365 | 124 | 152 | 0 | 0 | 60 | 0
18:00 | 2966 | 1795 | 926 | 0 | 20 | 918 | 35 | 3468 | 26.59 | 150 | 148 | 0 | 0 | 60 | 0
18:30 | 3058.5 | 1853 | 925.5 | 0 | 20 | 918.5 | 35.5 | 3723 | 13.295 | 165 | 330.5 | 0 | 0 | 59 | 0
19:00 | 3151 | 1911 | 925 | 0 | 20 | 919 | 36 | 3978 | 0 | 180 | 513 | 0 | 0 | 58 | 0
19:30 | 2990 | 2083 | 926 | 0 | 22 | 1013 | 36 | 4424 | 0 | 233 | 765 | 0 | 0 | 45 | 0
20:00 | 2854 | 2006 | 925 | 0 | 20 | 1016 | 37 | 4557.2 | 0 | 275 | 937 | 0 | 0 | 43 | 0
20:30 | 2974 | 2048 | 925.5 | 0 | 20 | 1016 | 37.5 | 4569.2 | 0 | 275.5 | 1066.5 | 0 | 0 | 52.5 | 0
21:00 | 3094 | 2090 | 926 | 0 | 20 | 1016 | 38 | 4581.2 | 0 | 276 | 1196 | 0 | 0 | 62 | 0
21:30 | 3142 | 2018.5 | 926 | 0 | 16 | 1016 | 38.5 | 4582.2 | 0 | 267.5 | 1127.5 | 0 | 0 | 59.5 | 0
22:00 | 3190 | 1947 | 926 | 0 | 12 | 1016 | 39 | 4583.2 | 0 | 259 | 1059 | 0 | 0 | 57 | 0
22:30 | 3168.5 | 1912 | 926 | 0 | 14 | 1015.5 | 39.5 | 4581.7 | 0 | 259 | 1177 | 0 | 0 | 55.5 | 0
23:00 | 3147 | 1877 | 926 | 0 | 16 | 1015 | 40 | 4580.2 | 0 | 259 | 1295 | 0 | 0 | 54 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 30-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 394 | 04:00 | 379 | 19:00 | Payra | 420 | 04:00 | 407 | 22:00
Ashuganj | 413 | 5:00 | 383 | 21:00 | Rahanpur | 407 | 03:00 | 383 | 22:00
Bhulta | 408 | 05:00 | 383 | 23:00 | Rampal | 411 | 03:00 | 289 | 22:00
Bibiana | 398 | 03:00 | 385 | 19:30
BIPTC | 409 | 08:00 | 390 | 23:00
Bogura | 404 | 04:00 | 375 | 22:00
Gopalganj | 407 | 06:00 | 383 | 19:30
Kaliakoir | 385 | 05:00 | 369 | 19:00
Madunaghat | 405 | 04:00 | 390 | 22:00
Meghnaghat | 397 | 04:00 | 382 | 19:30
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 231 | 03:00 | 220 | 19:00 | Keranigonj | 230 | 06:00 | 218 | 19:30
AKSML | 243 | 04:00 | 228 | 18:00 | Khulna(S) | 237 | 06:00 | 214 | 19:30
Aminbazar | 233 | 06:00 | 222 | 22:00 | Madunaghat | 242 | 04:00 | 230 | 19:30
Ashuganj | 238 | 03:00 | 223 | 23:00 | Madunaghat-400 | 242 | 04:00 | 231 | 22:00
Ashuganj-400 | 234 | 5:00 | 220 | 21:00 | Maniknagar | 227 | 04:00 | 217 | 19:00
Baghabari | 235 | 05:00 | 222 | 19:30 | Meghnaghat | 234 | 07:00 | 225 | 19:00
Barapukuria | 226 | 01:00 | 215 | 20:00 | Meghnaghat-400 | 230 | 04:00 | 221 | 19:00
Barapukuria-230 | 225 | 1:00 | 216 | 20:00 | Mirsorai | 239 | 03:00 | 221 | 19:30
Barishal | 243 | 03:00 | 226 | 22:00 | Rajshahi | 236 | 04:00 | 229 | 00:00
Bheramara | 234 | 02:00 | 221 | 19:00 | Rampal | 236 | 03:00 | 216 | 23:00
Bhulta | 236 | 03:00 | 222 | 22:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 235 | 04:00 | 197 | 20:00 | Rampura | 237 | 04:00 | 220 | 19:00
BIPTC | 236 | 03:00 | 222 | 15:00 | Shikalbaha | 240 | 04:00 | 228 | 22:00
Bogura | 234 | 03:00 | 217 | 19:30 | Shyampur | 230 | 07:00 | 219 | 19:30
Bogura-400 | 235 | 04:00 | 217 | 19:30 | Siddhirganj | 228 | 01:00 | 220 | 19:30
Borhanuddin | 248 | 05:00 | 232 | 23:00 | Sirajgonj | 239 | 04:00 | 228 | 19:30
BSRM | 238 | 03:00 | 222 | 19:30 | Sreepur | 233 | 00:00 | 218 | 23:00
Cumilla(N) | 233 | 06:00 | 219 | 22:00 | Tongi | 233 | 07:00 | 219 | 20:00
Faridpur | 240 | 04:00 | 224 | 19:30
Fenchuganj | 236 | 11:00 | 226 | 23:00
Ghorashal | 240 | 03:00 | 230 | 00:00
Ghorashal-230 | 235 | 04:00 | 219 | 22:00
Gopalganj | 241 | 03:00 | 225 | 23:00
GPH | 241 | 04:00 | 226 | 19:30
Haripur | 228 | 02:00 | 218 | 19:30
Hasnabad | 230 | 05:00 | 219 | 19:30
Hathazari | 243 | 03:00 | 229 | 19:00
Ishurdi | 236 | 02:00 | 224 | 19:00
Jhenaidah | 234 | 00:00 | 215 | 19:30
Kaliakoir | 237 | 07:00 | 226 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 138 | 03:00 | 127 | 18:30 | Madartek | 136 | 03:00 | 126 | 21:00
Agargaon | 140 | 03:00 | 133 | 19:00 | Madunaghat | 138 | 11:00 | 130 | 19:30
Agrabad | 144 | 04:00 | 131 | 18:00 | Magura | 137 | 04:00 | 121 | 19:30
AKS | 137 | 05:00 | 128 | 00:00 | Mahasthangarh | 140 | 03:00 | 125 | 20:00
Aminbazar | 135 | 07:00 | 131 | 13:00 | Manikganj | 134 | 01:00 | 127 | 15:00
Amnura | 136 | 03:00 | 122 | 22:00 | Maniknagar | 138 | 04:00 | 131 | 19:30
Ashuganj | 142 | 07:00 | 135 | 19:00 | Matarbari | 139 | 04:00 | 122 | 23:00
Bagerhat | 140 | 02:00 | 116 | 23:00 | Matuail | 134 | 07:00 | 128 | 20:00
Bajitpur | 139 | 00:00 | 126 | 23:00 | Millgate | 141 | 03:00 | 133 | 19:00
Bakulia | 140 | 04:00 | 132 | 19:00 | Mirpur | 135 | 03:00 | 128 | 19:00
Banani | 137 | 03:00 | 126 | 19:00 | Mirzapur | 135 | 00:00 | 129 | 19:00
Bangabhaban | 138 | 08:00 | 131 | 19:00 | Mithapukur | 140 | 03:00 | 122 | 19:30
Barapukuria | 138 | 00:00 | 123 | 20:00 | MI_Cement | 134 | 03:00 | 129 | 22:00
Barguna | 139 | 03:00 | 130 | 22:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 138 | 03:00 | 122 | 23:00 | Mogbazar | 138 | 01:00 | 128 | 19:00
Barishal-230 | 138 | 03:00 | 123 | 22:00 | Mongla | 140 | 02:00 | 119 | 19:00
Baroaulia | 138 | 04:00 | 132 | 21:00 | Motijheel | 138 | 08:00 | 131 | 19:00
Baroirhat | 140 | 04:00 | 121 | 18:00 | Muktagacha | 138 | 00:00 | 123 | 13:00
Bashundhara | 139 | 03:00 | 126 | 19:00 | Munshiganj | 133 | 05:00 | 128 | 19:00
BashundharaCement | 133 | 04:00 | 128 | 19:30 | Muradnagar | 139 | 03:00 | 123 | 00:00
Beanibazar | 139 | 08:00 | 125 | 23:00 | Mymensingh | 138 | 00:00 | 117 | 19:00
Benapole | 138 | 03:00 | 116 | 13:00 | Naogaon | 139 | 04:00 | 123 | 19:30
Bhaluka | 137 | 00:00 | 122 | 19:00 | Narail | 136 | 06:00 | 120 | 19:30
Bhandaria | 135 | 01:00 | 114 | 23:00 | Narinda | 138 | 4:00 | 131 | 19:30
Bhangura | 136 | 02:00 | 126 | 19:30 | Narshingdi | 138 | 03:00 | 118 | 23:00
Bheramara | 138 | 03:00 | 131 | 19:30 | Natore | 137 | 02:00 | 127 | 19:00
Bheramara(GK) | 137 | 03:00 | 131 | 19:30 | Nawabganj | 137 | 03:00 | 130 | 19:30
Bhulta | 125 | 02:00 | 120 | 21:00 | Netrakona | 137 | 02:00 | 117 | 23:00
Bog-Sherpur | 139 | 04:00 | 125 | 19:30 | New | 141 | 03:00 | 134 | 19:00
Bogura | 141 | 04:00 | 129 | 19:30 | Niamatpur | 135 | 03:00 | 125 | 22:00
Bogura-230 | 141 | 04:00 | 128 | 19:30 | Noapara | 140 | 03:00 | 119 | 15:00
Brahmanbaria | 137 | 00:00 | 123 | 23:00 | Pabna | 136 | 02:00 | 128 | 19:30
Cantonment | 140 | 07:00 | 133 | 19:00 | Palashbari | 139 | 03:00 | 120 | 20:00
Chandina | 140 | 03:00 | 125 | 19:00 | Panchagarh | 137 | 01:00 | 124 | 17:00
Chandpur | 140 | 03:00 | 113 | 18:00 | Patuakhali | 138 | 06:00 | 130 | 22:00
Chandraghona | 141 | 04:00 | 131 | 19:00 | Payra | 139 | 05:00 | 133 | 22:00
Chapai | 134 | 03:00 | 122 | 22:00 | PHP | 141 | 04:00 | 119 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 134 | 03:00 | 129 | 19:30 | Postogola | 137 | 03:00 | 131 | 19:00
Chauddagram | 140 | 04:00 | 118 | 18:00 | Purbachal | 138 | 03:00 | 126 | 22:00
Chhatak | 136 | 06:00 | 123 | 23:00 | Purbasadipur | 133 | 01:00 | 122 | 18:00
Chowmuhani | 140 | 05:00 | 115 | 18:00 | Rahanpur | 135 | 04:00 | 130 | 10:00
Chuadanga | 137 | 06:00 | 119 | 23:00 | Rahanpur-400 | 136 | 03:00 | 127 | 22:00
Coxsbazar | 140 | 06:00 | 122 | 22:00 | Rahim | 133 | 02:00 | 128 | 20:00
Cumilla(N) | 139 | 06:00 | 126 | 18:00 | Rajbari | 140 | 07:00 | 127 | 23:00
Cumilla(S) | 138 | 04:00 | 122 | 18:00 | Rajendrapur | 138 | 00:00 | 123 | 22:00
Daudkandi | 136 | 03:00 | 121 | 23:00 | Rajshahi | 137 | 05:00 | 127 | 19:30
Dhaka | 136 | 06:00 | 127 | 23:00 | Rajshahi-230 | 137 | 04:00 | 117 | 21:00
Dhamrai | 138 | 07:00 | 128 | 22:00 | Ramganj | 140 | 03:00 | 110 | 18:00
Dhanmondi | 136 | 03:00 | 128 | 23:00 | Rampur | 143 | 04:00 | 131 | 18:00
Dohazari | 139 | 07:00 | 128 | 23:00 | Rampura | 137 | 03:00 | 126 | 19:00
Faridpur | 140 | 04:00 | 130 | 07:00 | Rangamati | 139 | 04:00 | 130 | 18:00
Fatullah | 135 | 04:00 | 129 | 19:00 | Rangpur | 139 | 05:00 | 121 | 20:00
Fenchuganj | 141 | 06:00 | 133 | 23:00 | Ruppur | 138 | 05:00 | 131 | 19:00
Feni | 139 | 04:00 | 116 | 18:00 | Saidpur | 133 | 07:00 | 122 | 18:00
Ghatail | 137 | 00:00 | 125 | 15:00 | Satkhira | 141 | 04:00 | 116 | 21:00
Ghorashal | 140 | 05:00 | 132 | 18:30 | Satmasjid | 140 | 04:00 | 132 | 19:30
Goalpara | 142 | 04:00 | 123 | 19:30 | Savar | 133 | 06:00 | 121 | 21:00
Gollamari | 142 | 04:00 | 125 | 23:00 | SevenRings | 139 | 03:00 | 131 | 19:00
Gopalganj | 140 | 05:00 | 126 | 19:30 | ShahCement | 134 | 03:00 | 129 | 19:30
Gopalganj-400 | 140 | 04:00 | 130 | 19:30 | Shahjadpur | 137 | 04:00 | 131 | 19:30
Gulshan | 137 | 03:00 | 127 | 19:00 | Shahjibazar | 138 | 00:00 | 125 | 23:00
Halishahar | 144 | 04:00 | 131 | 19:00 | Shahmirpur | 141 | 07:00 | 133 | 19:00
Haripur | 134 | 03:00 | 128 | 19:30 | Shariatpur | 139 | 04:00 | 124 | 19:30
HaripurSBU | 139 | 10:00 | 128 | 20:00 | Sherpur | 140 | 00:00 | 124 | 10:00
Hasnabad | 137 | 03:00 | 132 | 19:00 | Shikalbaha | 132 | 04:00 | 120 | 19:00
Hathazari | 142 | 05:00 | 132 | 19:00 | Shikalbaha-230 | 142 | 04:00 | 132 | 19:00
Ishurdi | 138 | 02:00 | 131 | 19:30 | Shitalakhya | 134 | 03:00 | 129 | 22:00
Jaldhaka | 133 | 04:00 | 120 | 20:00 | Sholosohor | 143 | 04:00 | 130 | 19:00
Jamalpur | 140 | 00:00 | 125 | 10:00 | Shyampur | 134 | 08:00 | 132 | 00:00
Jashore | 135 | 04:00 | 118 | 13:00 | Shyampur-230 | 135 | 03:00 | 129 | 19:30
Jhenaidah | 138 | 03:00 | 121 | 21:00 | Siddhirganj | 133 | 02:00 | 128 | 18:30
Jhenaidah-230 | 138 | 03:00 | 124 | 23:00 | Sirajganj | 136 | 04:00 | 125 | 22:00
Joydebpur | 138 | 11:00 | 124 | 19:00 | Sonargaon | 135 | 09:00 | 125 | 23:00
Joypurhat | 139 | 03:00 | 119 | 19:30 | Sreemongol | 138 | 07:00 | 128 | 22:00
Juldah | 140 | 07:00 | 132 | 19:00 | Sreepur | 137 | 00:00 | 126 | 23:00
Kabirpur | 138 | 04:00 | 130 | 19:00 | Srinagar | 138 | 05:00 | 130 | 21:00
Kachua | 141 | 03:00 | 120 | 17:00 | SSM | 140 | 07:00 | 130 | 14:00
Kaliakoir | 140 | 00:00 | 131 | 21:00 | Sunamganj | 136 | 06:00 | 122 | 23:00
Kallyanpur | 135 | 03:00 | 129 | 19:00 | Sylhet | 139 | 08:00 | 128 | 21:00
Kalurghat | 140 | 04:00 | 130 | 21:00 | Sylhet-132 | 137 | 07:00 | 127 | 23:00
Kamrangirchar | 138 | 04:00 | 130 | 22:00 | Tangail | 134 | 00:00 | 125 | 19:30
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 134 | 01:00 | 121 | 11:00
Kasba | 139 | 03:00 | 122 | 19:00 | TK | 139 | 07:00 | 130 | 19:00
Kazla | 138 | 04:00 | 131 | 20:00 | Tongi | 140 | 06:00 | 132 | 05:00
Keranigonj | 138 | 03:00 | 131 | 19:30 | Ullahpara | 136 | 04:00 | 127 | 19:30
Khagrachori | 140 | 04:00 | 129 | 19:00 | Ullon | 137 | 03:00 | 127 | 19:00
Khulna | 141 | 03:00 | 123 | 19:30 | Uttara | 135 | 04:00 | 128 | 19:00
Khulna(S) | 143 | 04:00 | 125 | 19:30 | UttaraNew | 135 | 05:00 | 128 | 18:30
Khulshi | 142 | 04:00 | 130 | 19:00 | Zigatola | 138 | 06:00 | 131 | 21:00
Kishoreganj | 138 | 00:00 | 122 | 23:00
Kodda | 136 | 18:30 | 124 | 19:00
KSRM | 141 | 03:00 | 131 | 22:00
Kulaura | 141 | 07:00 | 132 | 22:00
Kurigram | 139 | 05:00 | 117 | 20:00
Kushtia | 135 | 04:00 | 127 | 21:00
Lalbag | 138 | 03:00 | 131 | 19:00
Lalmonirhat | 137 | 03:00 | 119 | 19:30
Madanganj | 133 | 04:00 | 128 | 19:30
Madaripur | 139 | 04:00 | 128 | 19:30
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division