## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 01-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-05-2025 | during | 01-06-2025 | during | 01-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 350 | 314 | 400.75 | 400.75 | 372 | 372 | FGMO
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 450 | 450 | 450 | 450 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 135 | 145 | 335 | 335 | 301.5 | 301.5 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 270 | 335 | 335 | 335 | 335 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 54 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 80 | 144 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 17 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 16 | 15 | 33 | 33 | 18.5 | 18.5 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 14 | 14 | 22 | 22 | 22 | 22 | -
23 | Maona 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 24 | 52.19 | 52.19 | 14 | 14 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 60 | 195 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 68 | 112 | 135 | 149 | 112 | 112 | Machine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105 | 88 | 88 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 22 | 64 | 104 | 104 | 80 | 80 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 118 | 144 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 35 | 0 | 18 | 0 | 18 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 22 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 250 | 320 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 70 | 108 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6189 | 6005.724 | 2053 | 2434 | 5213.9 | 5303.9 | 3407.33 | 3483.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 8 | 16 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 2 | 0 | 6 | 0 | 6 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 3 | 47 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 82 | 81 | 40 | 40 | 40 | 40 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 221 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 20 | 86 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 55 | 56 | 70 | 55 | 55 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 47 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 89 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 0 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1 | 0 | 2.14 | 0 | 2.14 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 16 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 10 | 61 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 23 | 100 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 22 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 17 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 22 | 10 | 16 | 20 | 16 | 20 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 360 | 360 | 360 | 360 | 360 | 360 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 2075 | 2478 | 3213.86 | 3230.72 | 3212.86 | 3215.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 177 | 197 | 221.43 | 221.43 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 353 | 357 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 300 | 340 | 340 | 340 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 31 | 10 | 46.7 | 46.7 | 34 | 34 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 41 | 8 | 55 | 55 | 46 | 46 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 0 | 195 | 195 | 16 | 16 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 65 | 113 | 150 | 150 | 135 | 135 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 39 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 51 | 163 | 163 | 70 | 70 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 63 | 200 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 30 | 40 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 11 | 10 | 17.75 | 17.75 | 15 | 15 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 12 | 28 | 113 | 113 | 18 | 18 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 72 | 91 | 115 | 115 | 90 | 90 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 44 | 0 | 50 | 0 | 50 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1340 | 1692 | 2444.43 | 2394.43 | 1996.55 | 1946.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 31-05-2025 | during | 01-06-2025 | during | 01-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 0 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 1 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 100 | 121 | 200 | 200 | 175 | 175 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 63 | 73 | 115 | 115 | 60 | 60 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 25.07 | 0 | 28 | 0 | 28 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 2 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 202.07 | 223 | 579.1 | 549 | 331.6 | 301.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 39 | 38 | 36 | 36 | 36 | 36 | -
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 155 | 132 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 0 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 86 | 86 | 86 | 86 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 65 | 160 | 170 | 170 | 170 | 170 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 250 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 301 | 288 | 286 | 286 | 286 | 286 | Load can't given Full, due to to Gas shortage
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 300 | 275 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1236 | 1257 | 1475 | 1475 | 1382 | 1382
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 917 | 916 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 40 | 40 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 180 | 142 | 410 | 410 | 250 | 250 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 89 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 105.07 | 0 | 61.5 | 0 | 61.5 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | -
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2436.27 | 2396.2 | 3573.7 | 3512.2 | 3411.7 | 3350.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 4 | 6 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 0 | 130 | 130 | 0 | 0 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1215 | 1244 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 20 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1746 | 1797 | 2172 | 2171 | 2002 | 2001
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 50 | 50 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 140 | 172 | 214 | 214 | 214 | 214 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 330 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 90 | 95 | 95 | 96 | 96 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 113 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 5.96 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 979.8 | 1204.68 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 47.25 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 117 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1620.01 | 2058.68 | 3192.37 | 3025.87 | 2934.58 | 2768.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 50 | 49 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 162 | 161 | 150 | 150 | 150 | 150 | Machine Problem
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.7 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 0 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 16 | 0 | 27 | 0 | 27 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 170 | 0 | 137.57 | 0 | 137.57 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 405.7 | 360 | 618.17 | 448 | 618.17 | 447
System Total |  |  |  |  | 28886.2 | 27110.055 | 13114.05 | 14695.88 | 22482.53 | 22110.12 | 19296.79 | 18895.38
Forecast Scenario (01-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14550 |  | 0 |  | 14550
|  |  |  | 1:00 | 14280 |  | 0 |  | 14280
|  |  |  | 2:00 | 13770 |  | 0 |  | 13770
|  |  |  | 3:00 | 13510 |  | 0 |  | 13510
|  |  |  | 4:00 | 13240 |  | 0 |  | 13240
|  |  |  | 5:00 | 13000 |  | 0 |  | 13000
|  |  |  | 6:00 | 12440 |  | 0 |  | 12440
|  |  |  | 7:00 | 12560 |  | 0 |  | 12560
|  |  |  | 8:00 | 12540 |  | 0 |  | 12540
|  |  |  | 9:00 | 13110 |  | 0 |  | 13110
|  |  |  | 10:00 | 13240 |  | 0 |  | 13240
|  |  |  | 11:00 | 13470 |  | 0 |  | 13470
|  |  |  | 12:00 | 13910 |  | 0 |  | 13910
|  |  |  | 13:00 | 14080 |  | 0 |  | 14080
|  |  |  | 14:00 | 13860 |  | 0 |  | 13860
|  |  |  | 15:00 | 13880 |  | 0 |  | 13880
|  |  |  | 16:00 | 13480 |  | 0 |  | 13480
|  |  |  | 17:00 | 13360 |  | 0 |  | 13360
|  |  |  | 18:00 | 13000 |  | 0 |  | 13000
|  |  |  | 18:30 | 13750 |  | 0 |  | 13750
|  |  |  | 19:00 | 14550 |  | 0 |  | 14550
|  |  |  | 19:30 | 15100 |  | 0 |  | 15100
|  |  |  | 20:00 | 14720 |  | 0 |  | 14720
|  |  |  | 21:00 | 14830 |  | 0 |  | 14830
|  |  |  | 22:00 | 14660 |  | 0 |  | 14660
|  |  |  | 23:00 | 14800 |  | 0 |  | 14800
Probable Maximum Temperature: |  |  | 29.70°C
Probable Maximum Demand at Day Peak: |  |  | 13910.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15100.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 15100.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 328.84 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:51 hrs on 01-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [6 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [6 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 31-05-2025 | [28 empty] | Date: | 31-05-2025 | [28 empty] | Date: | 31-05-2025 | [28 empty] | Date: | 31-05-2025 | [28 empty] | Date: | 31-05-2025 | [15 empty] | Date: | 31-05-2025
|  | 14:00-22:00 | [22 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [28 empty] | Day: | Saturday | [15 empty] | Day: | Saturday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 25 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 54 | 54 | 33 | 130 | 0 | 0 | 0 | 126 | 0 | 360 | 139 | 400 | 0 | 35 | 0 | 266 | 0 | 0 | 0 | 35 | 14.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 100 | 0 | 0 | 40 | 0 | 42 | 360 | 0 | 0 | 0 | 8 | 51 | 218 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 8 | 0 | 356 | 340 | 46 | 181 | 32 | 90 | 0 | 170 | 37 | 11 | 114 | 16 | 0 | 0 | 0 | 310 | 320 | 348 | 39 | 0 | 0 | 153 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 83 | 122 | 0 | 0 | 0 | 12 | 7212.5 | 927 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1013 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 163 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 4 | 0 | 220 | 0 | 0 | 1244 | 0 | 6029.2 | 13241.7 | 79.56
01:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 37 | 54 | 33 | 112 | 0 | 0 | 0 | 72 | 0 | 320 | 145 | 400 | 0 | 35 | 0 | 287 | 0 | 0 | 0 | 35 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 24 | 0 | 0 | 80 | 0 | 42 | 360 | 0 | 0 | 0 | 8 | 8 | 216 | 0 | 0 | 0 | 1180 | 0 | 51 | 0 | 8 | 0 | 354 | 340 | 45 | 196 | 31 | 89 | 0 | 136 | 38 | 11 | 114 | 16 | 0 | 0 | 0 | 310 | 320 | 375 | 39 | 0 | 0 | 147 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 37 | 103 | 0 | 0 | 0 | 12 | 6854 | 926 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 1024 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 160 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 7 | 0 | 220 | 0 | 0 | 1129 | 0 | 5744 | 12598 | 79.66
02:00 | 0 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 0 | 33 | 95 | 0 | 0 | 0 | 35 | 0 | 320 | 147 | 400 | 0 | 0 | 0 | 286 | 0 | 0 | 0 | 17 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 42 | 360 | 0 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1150 | 0 | 43 | 0 | 8 | 0 | 354 | 340 | 46 | 195 | 31 | 89 | 0 | 85 | 13 | 11 | 114 | 16 | 0 | 0 | 0 | 310 | 320 | 365 | 39 | 0 | 0 | 152 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 37 | 104 | 0 | 0 | 0 | 9 | 6542 | 927 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1164 | 0 | 1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 162 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 7 | 0 | 220 | 0 | 0 | 1105 | 0 | 5669 | 12211 | 79.76
03:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 33 | 95 | 0 | 0 | 0 | 0 | 0 | 320 | 147 | 400 | 0 | 0 | 0 | 288 | 0 | 0 | 0 | 17 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 31 | 360 | 0 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1100 | 0 | 43 | 0 | 8 | 0 | 354 | 340 | 46 | 194 | 32 | 90 | 0 | 51 | 9 | 9 | 114 | 16 | 0 | 0 | 0 | 305 | 320 | 370 | 39 | 0 | 0 | 149 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 37 | 104 | 0 | 0 | 0 | 10 | 6366 | 926 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1110 | 0 | 1008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 165 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 6 | 0 | 220 | 0 | 0 | 1100 | 0 | 5570 | 11936 | 79.86
04:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 16 | 33 | 80 | 0 | 0 | 0 | 0 | 0 | 320 | 145 | 400 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 36 | 360 | 0 | 0 | 0 | 8 | 0 | 220 | 0 | 0 | 0 | 1105 | 0 | 43 | 0 | 8 | 0 | 354 | 340 | 46 | 191 | 32 | 89 | 0 | 51 | 9 | 9 | 114 | 16 | 0 | 0 | 0 | 305 | 320 | 361 | 39 | 0 | 0 | 150 | 0 | 0 | 84 | 0 | 0 | 0 | 102 | 0 | 37 | 104 | 0 | 0 | 0 | 12 | 6328 | 926 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1090 | 0 | 1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 165 | 47 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 6 | 0 | 220 | 0 | 0 | 1049 | 0 | 5484 | 11812 | 79.96
05:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 322 | 0 | 0 | 0 | 35 | 33 | 62 | 0 | 0 | 0 | 0 | 0 | 320 | 148 | 400 | 0 | 0 | 0 | 301 | 0 | 0 | 0 | 0 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 31 | 360 | 0 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1080 | 0 | 43 | 0 | 8 | 0 | 350 | 340 | 46 | 207 | 32 | 68 | 0 | 51 | 9 | 9 | 114 | 14 | 0 | 0 | 0 | 300 | 320 | 381 | 39 | 0 | 0 | 151 | 0 | 0 | 82 | 0 | 0 | 0 | 102 | 0 | 37 | 104 | 0 | 0 | 0 | 12 | 6306 | 926 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 164 | 48 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 6 | 0 | 220 | 0 | 0 | 1000 | 0 | 5261 | 11567 | 80.06
06:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 345 | 0 | 0 | 0 | 35 | 17 | 62 | 0 | 0 | 0 | 0 | 0 | 320 | 149 | 400 | 0 | 0 | 0 | 296 | 0 | 0 | 2 | 0 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 42 | 360 | 0 | 0 | 0 | 8 | 0 | 218 | 0 | 0 | 0 | 1010 | 0 | 43 | 0 | 8 | 0 | 350 | 340 | 46 | 204 | 32 | 68 | 0 | 51 | 9 | 9 | 88 | 14 | 0 | 3 | 0 | 305 | 320 | 381 | 39 | 0 | 0 | 155 | 0 | 0 | 82 | 0 | 0 | 0 | 102 | 0 | 37 | 104 | 0 | 0 | 0.86 | 12 | 6216.86 | 926 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.36 | 160 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0.14 | 0 | 162 | 47 | 0 | 1 | 0 | 0 | 0 | 0.3 | 14 | 0.04 | 0 | 200 | 6 | 0 | 220 | 0 | 0 | 995 | 0 | 5166.84 | 11383.7 | 80.16
07:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 35 | 25 | 48 | 0 | 0 | 1 | 17 | 0 | 320 | 147 | 400 | 0 | 0 | 0 | 272 | 0 | 0 | 6 | 0 | 14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 0 | 35 | 360 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 1107 | 1 | 43 | 0 | 0 | 0 | 351 | 300 | 48 | 210 | 32 | 68 | 0 | 51 | 9 | 11 | 88 | 14 | 0 | 11 | 0 | 300 | 320 | 366 | 39 | 0 | 0 | 153 | 0 | 0 | 83 | 0 | 0 | 0 | 45 | 0 | 64 | 113 | 0 | 0 | 7.33 | 12 | 6315.33 | 678 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 6.98 | 183 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.51 | 0 | 158 | 48 | 0 | 1 | 0 | 0 | 0 | 0.2 | 1 | 0.06 | 0 | 250 | 6 | 0 | 220 | 0 | 0 | 1072 | 0 | 5297.75 | 11613.08 | 80.26
08:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 35 | 50 | 48 | 0 | 0 | 17 | 17 | 0 | 320 | 143 | 400 | 0 | 0 | 0 | 290 | 0 | 0 | 14 | 17 | 16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 77 | 0 | 3 | 360 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 1150 | 0 | 43 | 0 | 0 | 0 | 343 | 300 | 46 | 203 | 32 | 68 | 0 | 51 | 9 | 11 | 88 | 12 | 0 | 20 | 0 | 308 | 320 | 360 | 39 | 0 | 0 | 155 | 0 | 0 | 83 | 0 | 0 | 0 | 20 | 0 | 63 | 103 | 0 | 1 | 24.28 | 12 | 6393.28 | 631 | 223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.84 | 1109 | 15 | 915.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 22.63 | 201 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.28 | 0 | 158 | 50 | 0 | 2 | 0 | 0 | 0 | 1.9 | 3 | 0.34 | 0 | 284 | 4 | 0 | 220 | 0 | 0 | 1100 | 0 | 5441.85 | 11835.13 | 80.36
09:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 15 | 0 | 55 | 48 | 0 | 0 | 27 | 54 | 0 | 320 | 137 | 350 | 0 | 0 | 0 | 280 | 0 | 0 | 14 | 17 | 16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 48 | 0 | 0 | 78 | 0 | 3 | 360 | 0 | 0 | 0 | 8 | 0 | 219 | 0 | 0 | 0 | 1214 | 1 | 43 | 1 | 0 | 0 | 346 | 300 | 45 | 191 | 25 | 68 | 0 | 51 | 8 | 11 | 88 | 12 | 0 | 37 | 0 | 295 | 320 | 350 | 39 | 0 | 0 | 155 | 0 | 0 | 78 | 0 | 0 | 0 | 20 | 0 | 63 | 101 | 0 | 1 | 17.5 | 12 | 6453.5 | 631 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.98 | 1204 | 30 | 915.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 28.39 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.31 | 0 | 156 | 50 | 0 | 10 | 0 | 0 | 0 | 5.1 | 23 | 0.34 | 0 | 307 | 3 | 0 | 220 | 0 | 0 | 1125 | 0 | 5651.97 | 12105.47 | 80.44
10:00 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 18 | 0 | 68 | 48 | 0 | 0 | 35 | 51 | 0 | 320 | 149 | 350 | 0 | 0 | 0 | 304 | 0 | 0 | 29 | 17 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 48 | 0 | 0 | 80 | 0 | 2 | 360 | 0 | 0 | 0 | 8 | 0 | 217 | 0 | 0 | 0 | 1224 | 4 | 43 | 15 | 0 | 0 | 339 | 300 | 41 | 189 | 22 | 68 | 0 | 49 | 9 | 11 | 82 | 14 | 0 | 65 | 0 | 295 | 320 | 392 | 39 | 0 | 0 | 138 | 0 | 0 | 78 | 0 | 0 | 0 | 50 | 0 | 63 | 91 | 0 | 1 | 23.64 | 11 | 6582.64 | 678 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.87 | 1234.2 | 0 | 965.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 28.26 | 198 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 2.69 | 0 | 155 | 50 | 0 | 16 | 0 | 0 | 0 | 7 | 60 | 0.66 | 0 | 307 | 3 | 0 | 220 | 0 | 0 | 1190 | 0 | 5826.35 | 12408.99 | 80.52
11:00 | 0 | 90 | 24 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 54 | 0 | 68 | 48 | 0 | 0 | 35 | 82 | 0 | 300 | 145 | 250 | 0 | 5 | 0 | 270 | 0 | 0 | 32 | 60 | 16 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 48 | 0 | 0 | 82 | 0 | 2 | 360 | 0 | 0 | 0 | 8 | 0 | 213 | 0 | 0 | 0 | 1224 | 3 | 43 | 48 | 0 | 0 | 330 | 300 | 38 | 195 | 27 | 68 | 0 | 49 | 9 | 11 | 80 | 36 | 0 | 53 | 0 | 300 | 320 | 391 | 39 | 0 | 0 | 152 | 0 | 0 | 78 | 0 | 0 | 0 | 65 | 0 | 62 | 91 | 0 | 1 | 35.78 | 11 | 6635.78 | 821 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.54 | 1234.2 | 0 | 988.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 23.03 | 140 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 1.06 | 0 | 155 | 50 | 0 | 13 | 0 | 0 | 0 | 7.8 | 131 | 0.13 | 0 | 307 | 4 | 0 | 220 | 0 | 0 | 1190 | 0 | 5859.7 | 12495.48 | 80.6
12:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 54 | 22 | 68 | 80 | 60 | 0 | 35 | 118 | 22 | 300 | 135 | 250 | 0 | 35 | 0 | 260 | 0 | 0 | 35 | 70 | 16 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 22 | 0 | 0 | 0 | 89 | 23 | 1 | 82 | 10 | 2 | 360 | 0 | 0 | 3 | 8 | 20 | 214 | 0 | 0 | 0 | 1224 | 2 | 43 | 65 | 0 | 0 | 353 | 300 | 41 | 177 | 31 | 72 | 0 | 63 | 12 | 11 | 98 | 30 | 0 | 44 | 0 | 295 | 300 | 301 | 39 | 0 | 0 | 155 | 0 | 0 | 81 | 0 | 0 | 0 | 65 | 2 | 63 | 100 | 0 | 1 | 25.07 | 11 | 6906.07 | 917 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.07 | 1234.2 | 0 | 979.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 47.25 | 140 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 5.96 | 0 | 162 | 50 | 0 | 16 | 0 | 0 | 0 | 7.7 | 170 | 0 | 0 | 307 | 4 | 0 | 220 | 0 | 0 | 1215 | 0 | 6207.98 | 13114.05 | 80.68
13:00 | 8 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 313 | 0 | 0 | 54 | 17 | 90 | 32 | 15 | 0 | 35 | 126 | 16 | 300 | 139 | 250 | 0 | 17 | 0 | 260 | 0 | 0 | 32 | 35 | 16 | 14 | 0 | 0 | 13 | 15 | 0 | 0 | 22 | 16 | 8 | 0 | 89 | 12 | 2 | 83 | 50 | 2 | 360 | 0 | 0 | 22 | 8 | 86 | 213 | 0 | 0 | 0 | 1180 | 5 | 51 | 60 | 0 | 0 | 338 | 300 | 42 | 157 | 31 | 91 | 0 | 112 | 11 | 14 | 93 | 26 | 0 | 67 | 0 | 240 | 270 | 301 | 39 | 0 | 0 | 149 | 0 | 0 | 83 | 0 | 0 | 0 | 64 | 17 | 45 | 65 | 0 | 0 | 5.02 | 9 | 6764.02 | 866 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.12 | 1234.2 | 35 | 967.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 56.73 | 160 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 4.8 | 0 | 162 | 50 | 0 | 20 | 0 | 0 | 0 | 4.4 | 180 | 0.6 | 0 | 250 | 3 | 0 | 220 | 0 | 0 | 1180 | 0 | 6028.15 | 12792.17 | 80.76
14:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 39 | 17 | 0 | 0 | 15 | 0 | 35 | 126 | 16 | 300 | 148 | 250 | 0 | 17 | 0 | 260 | 0 | 0 | 5 | 35 | 15 | 0 | 0 | 0 | 17 | 15 | 0 | 0 | 45 | 16 | 16 | 0 | 60 | 12 | 1 | 83 | 51 | 2 | 360 | 0 | 0 | 19 | 8 | 105 | 214 | 0 | 0 | 0 | 1180 | 6 | 51 | 60 | 0 | 0 | 350 | 300 | 0 | 199 | 28 | 91 | 0 | 162 | 10 | 11 | 64 | 34 | 0 | 37 | 0 | 240 | 270 | 301 | 39 | 0 | 0 | 148 | 0 | 0 | 83 | 0 | 0 | 0 | 81 | 0 | 45 | 65 | 0 | 1 | 2.02 | 6 | 6590.02 | 916 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.45 | 1234.2 | 39 | 964.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 54.08 | 160 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 5.55 | 0 | 163 | 50 | 0 | 20 | 0 | 0 | 0 | 2.63 | 89 | 0.2 | 0 | 200 | 3 | 0 | 220 | 0 | 0 | 1140 | 0 | 5830.57 | 12420.59 | 80.84
15:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 35 | 17 | 17 | 40 | 15 | 0 | 35 | 144 | 16 | 300 | 135 | 250 | 0 | 17 | 0 | 260 | 0 | 0 | 1 | 35 | 15 | 14 | 0 | 0 | 17 | 15 | 0 | 0 | 47 | 16 | 16 | 0 | 60 | 12 | 1 | 81 | 51 | 0 | 360 | 0 | 0 | 19 | 8 | 105 | 215 | 0 | 0 | 0 | 1224 | 7 | 51 | 60 | 0 | 0 | 355 | 300 | 3 | 208 | 29 | 92 | 0 | 157 | 18 | 13 | 64 | 0 | 0 | 2 | 0 | 240 | 270 | 292 | 40 | 0 | 0 | 151 | 0 | 0 | 81 | 0 | 0 | 0 | 81 | 0 | 45 | 64 | 0 | 1 | 0.38 | 6 | 6688.38 | 916 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.02 | 1150 | 53 | 970.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 14.19 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 1.07 | 0 | 154 | 49 | 61 | 18 | 0 | 0 | 0 | 1.8 | 95 | 0.05 | 0 | 200 | 4 | 0 | 220 | 0 | 0 | 1140 | 0 | 5847.84 | 12536.22 | 80.92
16:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 17 | 26 | 16 | 0 | 0 | 35 | 90 | 16 | 300 | 129 | 250 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 16 | 16 | 0 | 48 | 0 | 0 | 76 | 38 | 0 | 360 | 0 | 0 | 0 | 8 | 0 | 216 | 0 | 0 | 0 | 1224 | 6 | 51 | 0 | 0 | 0 | 280 | 300 | 10 | 182 | 10 | 92 | 0 | 136 | 10 | 13 | 59 | 32 | 0 | 20 | 0 | 240 | 270 | 289 | 39 | 0 | 0 | 129 | 0 | 0 | 79 | 0 | 0 | 0 | 95 | 0 | 16 | 91 | 0 | 0 | 1.62 | 6 | 6089.62 | 917 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1156 | 17 | 986.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 6.67 | 167 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0.56 | 0 | 155 | 49 | 35 | 13 | 0 | 0 | 0 | 2.2 | 38 | 0.09 | 0 | 150 | 2 | 0 | 205 | 0 | 0 | 1150 | 0 | 5520.88 | 11610.5 | 81
17:00 | 0 | 105 | 8 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 300 | 139 | 250 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 16 | 14 | 0 | 50 | 0 | 0 | 72 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 0 | 0 | 1125 | 2 | 34 | 0 | 0 | 0 | 347 | 340 | 10 | 214 | 10 | 92 | 0 | 136 | 9 | 13 | 68 | 32 | 0 | 3 | 0 | 240 | 270 | 288 | 40 | 0 | 0 | 144 | 0 | 0 | 52 | 0 | 0 | 0 | 97 | 0 | 35 | 111 | 0 | 0 | 0 | 8 | 5991 | 917 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.29 | 983 | 17 | 968.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 3.7 | 149 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.3 | 0 | 163 | 50 | 42 | 2 | 8 | 0 | 0 | 2.3 | 10 | 0.01 | 0 | 225 | 6 | 0 | 220 | 0 | 0 | 1050 | 0 | 5387.34 | 11378.34 | 81.08
18:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 375 | 0 | 0 | 17 | 10 | 12 | 6 | 0 | 0 | 7 | 17 | 16 | 300 | 144 | 250 | 0 | 0 | 0 | 299 | 0 | 0 | 1 | 12 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 16 | 15 | 0 | 100 | 12 | 0 | 72 | 0 | 0 | 360 | 0 | 0 | 9 | 3 | 0 | 220 | 0 | 0 | 0 | 1063 | 0 | 51 | 18 | 0 | 0 | 347 | 340 | 10 | 214 | 10 | 90 | 0 | 159 | 18 | 7 | 62 | 30 | 0 | 1 | 0 | 250 | 270 | 288 | 40 | 0 | 0 | 143 | 0 | 0 | 84 | 0 | 0 | 0 | 106 | 0 | 64 | 120 | 0 | 0 | 0 | 12 | 6267 | 917 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.27 | 1066 | 17 | 983.85 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 1.95 | 171 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.16 | 0 | 163 | 50 | 78 | 1 | 25 | 0 | 0 | 0 | 18 | 0.09 | 0 | 264 | 4 | 0 | 220 | 0 | 0 | 1110 | 0 | 5694.32 | 11961.32 | 81.16
19:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 378 | 0 | 0 | 43 | 35 | 23 | 20 | 15 | 0 | 30 | 95 | 31 | 300 | 150 | 250 | 0 | 17 | 0 | 306 | 0 | 0 | 0 | 70 | 15 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 31 | 0 | 100 | 74 | 0 | 72 | 0 | 0 | 360 | 0 | 0 | 13 | 8 | 0 | 217 | 0 | 0 | 0 | 1175 | 0 | 51 | 45 | 0 | 0 | 343 | 340 | 10 | 214 | 10 | 92 | 51 | 194 | 27 | 5 | 114 | 36 | 8 | 0 | 12 | 250 | 270 | 289 | 38 | 0 | 0 | 141 | 0 | 0 | 85 | 0 | 0 | 0 | 110 | 0 | 82 | 130 | 0 | 0 | 0 | 12 | 6957 | 869 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1170 | 22 | 1109.52 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 50 | 115 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 0 | 220 | 0 | 0 | 1140 | 0 | 5998.52 | 12955.52 | 81.28
19:30 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 54 | 35 | 40 | 70 | 83 | 0 | 35 | 126 | 44 | 300 | 139 | 300 | 0 | 17 | 0 | 288 | 0 | 0 | 0 | 80 | 15 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 25 | 16 | 40 | 0 | 100 | 100 | 0 | 76 | 5 | 0 | 360 | 0 | 0 | 30 | 10 | 17 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 90 | 0 | 0 | 356 | 340 | 10 | 196 | 17 | 92 | 52 | 200 | 27 | 7 | 114 | 34 | 25 | 0 | 40 | 250 | 270 | 289 | 39 | 0 | 0 | 154 | 0 | 0 | 85 | 0 | 0 | 0 | 160 | 0 | 73 | 129 | 0 | 0 | 0 | 12 | 7465 | 868 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1190 | 60 | 1088.02 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 163 | 50 | 115 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 8 | 0 | 220 | 0 | 0 | 1244 | 0 | 6216.02 | 13681.02
20:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 54 | 39 | 82 | 102 | 145 | 0 | 35 | 144 | 60 | 300 | 142 | 320 | 0 | 17 | 0 | 293 | 0 | 0 | 0 | 145 | 6 | 14 | 0 | 0 | 0 | 15 | 0 | 0 | 24 | 41 | 50 | 0 | 90 | 100 | 0 | 79 | 20 | 0 | 360 | 0 | 0 | 35 | 16 | 25 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 83 | 0 | 0 | 356 | 340 | 10 | 209 | 20 | 92 | 50 | 200 | 29 | 7 | 114 | 38 | 26 | 0 | 32 | 250 | 275 | 288 | 39 | 0 | 0 | 156 | 0 | 0 | 85 | 0 | 0 | 0 | 160 | 6 | 73 | 121 | 0 | 0 | 0 | 12 | 7812 | 868 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1193 | 70 | 1225.85 | 0 | 0 | 0 | 105 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 50 | 115 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 0 | 220 | 0 | 0 | 1244 | 0 | 6366.85 | 14178.85 | 81.4
21:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 54 | 54 | 112 | 144 | 195 | 0 | 35 | 144 | 64 | 300 | 145 | 320 | 0 | 17 | 0 | 270 | 0 | 0 | 0 | 108 | 15 | 14 | 0 | 0 | 22 | 15 | 0 | 0 | 10 | 47 | 55 | 16 | 100 | 100 | 0 | 81 | 61 | 0 | 360 | 17 | 0 | 47 | 16 | 86 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 113 | 0 | 0 | 357 | 340 | 8 | 197 | 10 | 91 | 51 | 200 | 28 | 10 | 114 | 40 | 43 | 0 | 39 | 250 | 275 | 288 | 38 | 0 | 0 | 132 | 0 | 0 | 84 | 30 | 0 | 0 | 160 | 17 | 73 | 121 | 0 | 0 | 0 | 12 | 8084 | 916 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 89 | 1204.68 | 0 | 0 | 0 | 113 | 0 | 90 | 35 | 0 | 0 | 0 | 30 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 161 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 6 | 0 | 220 | 0 | 0 | 1244 | 20 | 6611.88 | 14695.88 | 81.52
22:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 54 | 54 | 112 | 144 | 195 | 0 | 35 | 144 | 66 | 300 | 136 | 320 | 0 | 35 | 0 | 265 | 0 | 0 | 0 | 52 | 15 | 15 | 0 | 0 | 35 | 45 | 0 | 0 | 19 | 47 | 55 | 0 | 100 | 100 | 0 | 82 | 68 | 3 | 360 | 0 | 0 | 47 | 8 | 90 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 117 | 0 | 0 | 355 | 340 | 5 | 208 | 10 | 100 | 51 | 200 | 29 | 14 | 114 | 40 | 8 | 0 | 39 | 250 | 270 | 289 | 38 | 0 | 0 | 130 | 0 | 0 | 84 | 30 | 0 | 0 | 160 | 17 | 73 | 121 | 0 | 0 | 0 | 12 | 8038 | 917 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 89 | 1209 | 0 | 0 | 0 | 113 | 0 | 88 | 0 | 0 | 0 | 0 | 30 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 162 | 50 | 115 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 0 | 220 | 0 | 0 | 1244 | 64 | 6632.2 | 14670.2 | 81.64
23:00 | 0 | 105 | 24 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 54 | 54 | 117 | 144 | 145 | 0 | 35 | 144 | 66 | 300 | 151 | 320 | 0 | 35 | 0 | 290 | 0 | 0 | 0 | 35 | 15 | 16 | 0 | 0 | 35 | 45 | 0 | 0 | 17 | 48 | 55 | 0 | 100 | 72 | 0 | 83 | 68 | 2 | 360 | 0 | 0 | 43 | 8 | 105 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 125 | 0 | 0 | 354 | 340 | 5 | 215 | 10 | 115 | 51 | 200 | 29 | 14 | 114 | 42 | 8 | 0 | 39 | 250 | 270 | 287 | 37 | 0 | 0 | 130 | 0 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 64 | 120 | 0 | 0 | 0 | 12 | 8018 | 917 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 88 | 1217 | 0 | 0 | 0 | 113 | 0 | 88 | 0 | 0 | 0 | 0 | 30 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 163 | 50 | 115 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 11 | 0 | 220 | 0 | 0 | 1244 | 100 | 6644.2 | 14662.2 | 81.76
Total KWH | 5645 | 2073149 | 424320 | 0 | 0 | 0 | 0 | 0 | 8028000 | 0 | 0 | 683424 | 695520 | 1295136 | 1618560 | 869400 | 0 | 534472 | 1828800 | 443520 | 7623500 | 3410356 | 7921818 | 0 | 304256 | 0 | 6739839 | 0 | 0 | 137036 | 741600 | 335400 | 329040 | 0 | 0 | 190691 | 218291 | 0 | 0 | 796320 | 314576 | 443622 | 45950 | 1331520 | 564448 | 10688 | 1893260 | 513525 | 336960 | 8661818.18 | 41818 | 0 | 328320 | 214858.8 | 828836 | 5260760 | 0 | 0 | 0 | 28063634 | 40500 | 1050152 | 1017018 | 66909 | 0 | 8665700 | 7868000 | 669120 | 4771000 | 565344 | 2090880 | 216820 | 2874720 | 382200 | 243250 | 2305080 | 586560 | 119054 | 359636 | 181504 | 6612500 | 7112700 | 8321000 | 927000 | 0 | 0 | 3513354 | 0 | 0 | 1921920 | 111264 | 0 | 0 | 2229040 | 128160 | 1279200 | 2476800 | 0 | 6950 | 135220 | 261120 | 165212361.98 | 20966545 | 4519872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56160 | 434880 | 27934540 | 648960 | 24087272 | 0 | 0 | 0 | 746112 | 0 | 311844 | 64032 | 0 | 0 | 576890 | 99099 | 300000 | 4131636 | 0 | 0 | 0 | 0 | 0 | 8972509 | 0 | 25260 | 0 | 3975000 | 1103999 | 1018777 | 124150 | 445785 | 0 | 0 | 42500.76 | 842400 | 3554 | 0 | 6153000 | 141951 | 0 | 5354980 | 0 | 0 | 27912727.27 | 266400 | 141260835.03 | 306473197.01

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 31-05-2025
Power Supply Scenario
| Day Peak Generation |  |  | 13114.05 | MW | 12:00 Hr. | Energy Generated |  |  | 306.4732 |  | MKWHr.
| Day Peak Demand |  |  | 13114.05 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.098 |  | MKWHr.
| Evening Peak Generation |  |  | 14695.88 | MW | 21:00 Hr. | Energy Demand |  |  | 306.5712 |  | MKWHr.
| Evening Peak Demand |  |  | 14695.88 | MW | 21:00 Hr. | Maximum Temperature |  |  | 34.2 |  | °C
| Minimum Generation of the Day |  |  | 11378.34 | MW | 17:00 Hr. | Total Gas Supplied |  |  | 819.98 |  | MMCFD
| Maximum Generation of the Day |  |  | 14695.88 | MW | 21:00 Hr. | Production Cost per KWHr |  |  | 6.6563 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 34.388 | 0 | 11.5178 | 0 | 0 | 0.13704 | 0 | 0 | 46.0428 | Gas | 117.9717 | Gas | 414723960.83
| Chattogram Zone |  |  | 5.5977 | 36.7255 | 5.0365 | 0 | 1.8933 | 0.051188 | 0 | 0.79632 | 50.1004 | Coal | 103.8047 | Coal | 721649803.7809
| Cumilla Zone |  |  | 24.1163 | 0 | 8.9705 | 0 | 0 | 0.35964 | 0.58656 | 0 | 34.0329 | HFO | 33.3272 | HFO | 615530901.346
| Mymensingh Zone |  |  | 0 | 0 | 4.1453 | 0 | 0 | 0.14217 | 0 | 0 | 4.2874 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 30.7488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.7488 | Hydro | 1.8933 | Hydro | 189326
| Khulna Zone |  |  | 4.5199 | 27.9345 | 0.70512 | 0 | 0 | 0.43488 | 20.9665 | 0 | 54.561 | Solar | 3.0397 | Solar | 48373483.9136
| Barishal Zone |  |  | 5.4969 | 34.0657 | 0.2664 | 0 | 0 | 0.003554 | 0 | 0 | 39.8326 | Import | 45.6404 | Import | 227847955.06
| Rajshahi Zone |  |  | 13.1041 | 0 | 1.2211 | 0 | 0 | 0.90215 | 24.0873 | 0 | 39.3147 | Wind | 0.79632 | Wind | 11658124.8
| Rangpur Zone |  |  | 0 | 5.079 | 1.4646 | 0 | 0 | 1.0091 | 0 | 0 | 7.5526
| Total |  |  | 117.9717 | 103.8047 | 33.3272 | 0 | 1.8933 | 3.0397 | 45.6404 | 0.79632 | 306.4732
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 414723960.83 |  | Hydro | 189326
|  |  |  | Coal | 721649803.7809 |  | Solar | 48373483.9136
|  |  |  | HFO | 615530901.346 |  | Import | 227847955.06
|  |  |  | HSD | 0 |  | Wind | 11658124.8
[5 empty] | Total: | 203,99,73,555 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 20.9665 | Peak Hr Flow | 916.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 38772200.05 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 24.0873 | Peak Hr Flow | 1204.68 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 564 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.58656 | Peak Hr Flow | 40.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 876 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 45.6404 | Peak Hr Flow | 2160.68 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5283
|  |  |  | Chattogram |  | 0 |  | 1544
|  |  |  | Cumilla |  | 0 |  | 1360
|  |  |  | Mymensingh |  | 0 |  | 998
|  |  |  | Sylhet |  | 0 |  | 448
|  |  |  | Khulna |  | 0 |  | 1861
|  |  |  | Barishal |  | 0 |  | 466
|  |  |  | Rajshahi |  | 0 |  | 1531
|  |  |  | Rangpur |  | 0 |  | 868
|  |  |  | Total |  | 0 |  | 14359
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:01 | 10:40 | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to Regular Maintenace
Work
| 08:02 | 10:39 | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Regular Maintenance | [7 empty] | 20.0MW load
|  |  | Work Before Eid Ul Adha | [7 empty] | interrup.
|  | 08:05 | Cox'sbazar-Dohazari 132 kV Ckt-2 is restored.
|  | 08:08 | Cox'sbazar-Dohazari 132 kV Ckt-1 is restored.
| 09:10 | 12:55 | Rahanpur 400/132kV S/S HV 400 KV BUS Project Work S/D Due to Es operation checking
| 09:24 | 11:24 | Benapole 132/33kV S/S Transformer-2(416T) LT Scheduled S/D Due to 33 KV Purapara feeder | [7 empty] | 28.0MW load
|  |  | Ds red hot maintenance. | [7 empty] | interrup.
| 09:26 | 11:23 | Benapole 132/33kV S/S Transformer-2(416T) HT Scheduled S/D Due to 33 KV Purapara feeder | [7 empty] | 28.0MW load
|  |  | Ds red hot maintenance. | [7 empty] | interrup.
| 09:37 | 13:42 | Khagrachori 132/33kV S/S TR-1 HT Forced S/D Due to S/D for fire incident at incomer
cable(Y Phase).
|  | 09:40 | Bogura 132/33kV S/S Transformer-1 HT is restored.
|  | 09:40 | Bogura 132/33kV S/S Transformer-1 LT is restored.
| 10:07 | 10:50 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Forced S/D Due to Jumper Maintenance of 33kv | [7 empty] | 25.0MW load
|  |  | side | [7 empty] | interrup.
| 10:07 | 10:47 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Forced S/D Due to Jumper Maintenance of 33kv | [7 empty] | 25.0MW load
|  |  | side | [7 empty] | interrup.
| 10:48 | 13:03 | Rajshahi 132/33kV S/S Transformer T-2(415T) LT Scheduled S/D
| 10:49 | 13:02 | Rajshahi 132/33kV S/S Transformer T-2(415T) HT Scheduled S/D
| 12:00 |  | Day peak generation 13071 MW
|  | 12:20 | Feni 132/33kV S/S T-1(405T) HT is restored.
|  | 12:20 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 12:26 | 12:40 | Jamalpur-Mymensingh 132kV Ckt-1 Tripped from Jamalpur 132/33kV end showing Micom P443
relays Due to Fault
|  | 12:49 | Kodda-Rajendrapur 132kV Ckt-1 is restored.
|  | 13:07 | Bheramara-HVDC Bheramara 230 kV Ckt-1 is restored.
|  | 13:07 | Bheramara-HVDC Bheramara 230 kV Ckt-1 is restored.
|  | 13:08 | Bheramara-HVDC Bheramara 230 kV Ckt-2 is restored.
|  | 13:08 | Bheramara-HVDC Bheramara 230 kV Ckt-2 is restored.
| 13:12 | 15:17 | Rajshahi 132/33kV S/S Transformer T-1(405T) LT Scheduled S/D
| 13:13 | 15:15 | Rajshahi 132/33kV S/S Transformer T-1(405T) HT Scheduled S/D
| 13:19 | 16:20 | Rahanpur 400/132kV S/S HV 400 KV BUS Project Work S/D Due to Project work at BUS 02 400
kv
| 13:24 |  | 132kV Ashuganj-Ghorashal, both circuits tripped.
|  | 13:27 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 is restored.
|  | 13:27 | HVDC Bheramera- Jhenaidah 230kV Ckt-1 is restored.
|  | 13:28 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 is restored.
|  | 13:28 | HVDC Bheramera-Jhenaidah 230kV Ckt-2 is restored.
|  | 13:48 | Bheramara P/S-Ishurdi 132 kV Ckt-1 is restored.
|  | 13:49 | Bheramara P/S-Ishurdi 132 kV Ckt-2 is restored.
| 14:56 | 15:07 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Lock out relay, over current relay relays | [7 empty] | 17.0MW load
|  |  | Due to Due to Sholla feeder fault | [7 empty] | interrup.
| 14:56 | 15:06 | Nawabganj 132/33kV S/S TR-1 LT Tripped showing Lock out relay,over current relay relays | [7 empty] | 17.0MW load
|  |  | Due to Due to Sholla feeder fault | [7 empty] | interrup.
| 15:42 | 16:22 | Barishal 230/132kV S/S 230kV BUS Scheduled S/D Due to TCS check
| 15:42 | 16:22 | Barishal 230/132kV S/S 230kV BUS Scheduled S/D Due to TCS check
| 16:10 | 16:18 | Bhulta-Rampura 230 kV Ckt-4 Tripped from Rampura 230/132kV end showing Distance Backup
21B (Z1,CN) relays Due to N/A
| 18:28 |  | Rangpur-Saidpur 132kV Ckt-1 Forced S/D from Rangpur 132/33kV end.
|  | 18:47 | Chuadanga 132/33kV S/S 132kV Tr. T3 HT is restored.
|  | 18:47 | Chuadanga 132/33kV S/S 132kV Tr. T3 LT is restored.
|  | 20:20 | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 is restored.
| 20:20 | 21:01 | Cumilla(S) 132/33kV S/S TR-2 LT Tripped showing RET -650 relays Due to 33KV Laksam REB & | [7 empty] | 46.0MW load
|  |  | Chauddagram REB feeder fault. | [7 empty] | interrup.
| 21:00 |  | Evening Peak Generation: 14695 MW.
| 21:38 |  | Bibiyana-III 400 MW CCPP, FGMO is OFF with remarks:-
| 22:56 | 23:56 | Panchagar-Thakurgaon 132kV Ckt-1 Tripped from Panchagarh 132/33kV end showing Dist.
Relay MiCom P442 relays. and from Thakurgaon 132/33kV end showing Areva: Micom P442
relays Due to Thundering and Heavy Rain
| 23:27 |  | Chandpur CCPP was forced shutdown due to turbine vibration problem.
| 00:42 | 02:09 | Narshingdi 132/33kV S/S T-1 LT Forced S/D Due to Red hot at R-Phase in 33 KV T-1 | [7 empty] | 40.0MW load
|  |  | Transformer Load side. Shut down has been taken from narsingdi palli biddhut-2 | [7 empty] | interrup.
| 03:41 | 04:40 | Fenchuganj-Sylhet (T at Bianibazar) 132kV Ckt-2 Tripped from Beanibazar 132/33kV end | [7 empty] | 9.0MW load
|  |  | showing REL670 relays Due to Heavy Rain and from Fenchuganj 230/132/33kV end showing REL | [7 empty] | interrup.
|  |  | 670, REC 650 relays Due to Bad Weather | [7 empty] | Beanibazar 132/33kV
end and 17.0MW load
interrup.
Fenchuganj
230/132/33kV end
| 03:41 | 04:38 | Fenchuganj -Sylhet 132kV Ckt-1 Tripped from Beanibazar 132/33kV end showing REL670 | [7 empty] | 9.0MW load
|  |  | relays Due to Heavy Rain | [7 empty] | interrup.
Beanibazar 132/33kV
end
| 03:41 | 04:40 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-2 Tripped showing Distance Relay.
relays Due to extreamly Bad Weather.
| 03:41 | 04:40 | Sylhet (South) S/S Sylhet (S)-Fenchugonj 132KV Ckt-1 Tripped showing Distance relay.
relays Due to Extreamly bad weather.
| 05:20 | 05:32 | Sylhet 132/33kV S/S T1 LT Tripped showing 51 relays Due to Ins O/C | [7 empty] | 23.0MW load
interrup.
| 05:20 | 05:32 | Sylhet 132/33kV S/S T1 HT Tripped showing 51 relays Due to Ins O/C | [7 empty] | 23.0MW load
interrup.
| 05:50 | 07:45 | Full load interruption occured under Daudkandi Substatio due to a fire at 33kV
switchyard of PBS.
| 06:00 |  | Min. Gen. 11687 MW
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 31-05-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 314 | 8028000 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7623500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 145 | 3410356 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6739839 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 5645 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 683424 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 144 | 1618560 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 534472 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 17 | 304256 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 15 | 335400 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 14 | 329040 | -
23 | Maona 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | Contract Expired
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 24 | 424320 | Liquid fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 195 | 869400 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 112 | 1295136 | One unit stop for 24k Schedule Maintenance
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 2073149 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 64 | 443520 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 1828800 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 137036 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 695520 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 320 | 7921818 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 108 | 741600 | -
Dhaka Area Total |  |  |  |  | 6005.724 | 2434 | 46042791
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 16 | 214858.8 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 40500 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 47 | 328320 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 81 | 1893260 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 221 | 5260760 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 86 | 828836 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 55 | 443622 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 47 | 314576 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1331520 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 0 | 336960 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 10688 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 218291 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 16 | 45950 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 61 | 513525 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 564448 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 22 | 190691 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 17 | 41818 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28063634 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 10 | 796320 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 360 | 8661818.18 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2478 | 50100395.98
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 197 | 4771000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 357 | 8665700 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 7868000 | Machine Problem
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 10 | 565344 | -
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 8 | 669120 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 0 | 66909 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1050152 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 113 | 1017018 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 39 | 181504 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 216820 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 200 | 2874720 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 40 | 586560 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 119054 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 10 | 243250 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2305080 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 382200 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 91 | 2090880 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 359636 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1692 | 34032947
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 6950 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 121 | 2476800 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 73 | 1279200 | Liquid fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 135220 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 261120 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 128160 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 223 | 4287450
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 38 | 927000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 132 | 3513354 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 111264 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1921920 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | -
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 160 | 2229040 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 250 | 6612500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 288 | 8321000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 275 | 7112700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1257 | 30748778
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 916 | 20966545 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 142 | 4519872 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 89 | 648960 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 56160 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 434880 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1234.2 | 27934540 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2396.2 | 54560957
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 6 | 141951 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 0 | 0 | -
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 27912727.27 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5354980 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 20 | 266400 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 307 | 6153000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 3554 | -
Barishal Area Total |  |  |  |  | 2236 | 1797 | 39832612.27
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | shundown for maintenance work
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 172 | 4131636 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8972509 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 99099 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 311844 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 113 | 746112 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 64032 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 25260 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1204.68 | 24087272 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 300000 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 576890 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 2058.68 | 39314654
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1103999 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 3975000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 445785 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 42500.76 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1018777 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 124150 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 842400 | -
Rangpur Area Total |  |  |  |  | 950 | 360 | 7552611.76
Eastern Grid Total |  |  |  |  | 16771.895 | 8084 | 165212361.98
Western Grid Total |  |  |  |  | 10338.16 | 6611.88 | 141260835.03
National Grid Total |  |  |  |  | 27110.055 | 14695.88 | 306473197.01
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 31-05-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9632.59 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4725.3 | MW
i) Dhaka area |  |  | 5282.71 |  | MW | i) Khulna area |  |  |  | 1861 | MW
ii) Chattogram area |  |  | 1543.9 |  | MW | ii) Barishal area |  |  |  | 465.5 | MW
iii) Cumilla area |  |  | 1359.98 |  | MW | iii) Rajshahi area |  |  |  | 1530.8 | MW
iv) Mymensingh area |  |  | 998 |  | MW | iv) Rangpur area |  |  |  | 868 | MW
v) Sylhet area |  |  | 448 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14357.89 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 13 | 10:00 | 67 | Ishurdi | 86 | 15:00 | 133 | Patuakhali | 82.5 | 22:00
2 | AKSML | 145 | 21:00 | 68 | Jaldhaka | 82 | 21:00 | 134 | Payra | 36 | 22:00
3 | Aftabnagar | 36 | 13:00 | 69 | Jamalpur | 120 | 23:00 | 135 | Postogola | 57 | 12:00
4 | Agargaon | 128 | 13:00 | 70 | Jashore | 148 | 22:00 | 136 | Purbachal | 20 | 13:00
5 | Agrabad | 100 | 15:00 | 71 | Jhenaidah | 129 | 22:00 | 137 | Purbasadipur | 146 | 22:00
6 | Amnura | 39 | 22:00 | 72 | Joydebpur | 133 | 20:00 | 138 | Rahanpur | 31 | 22:00
7 | Ashuganj | 88 | 00:00 | 73 | Joypurhat | 60 | 23:00 | 139 | Rahim | 57 | 15:00
8 | BSRM | 176 | 19:30 | 74 | Juldah | 18 | 00:00 | 140 | Rajbari | 80 | 21:00
9 | Bagerhat | 89 | 20:00 | 75 | KSRM | 19 | 02:00 | 141 | Rajendrapur | 136 | 21:00
10 | Bajitpur | 43 | 23:00 | 76 | Kabirpur | 272 | 11:00 | 142 | Rajshahi | 115 | 21:00
11 | Bakulia | 92 | 15:00 | 77 | Kachua | 99 | 22:00 | 143 | Rajshahi-230 | 95 | 21:00
12 | Banani | 36 | 12:00 | 78 | Kallyanpur | 105 | 22:00 | 144 | Ramganj | 114 | 23:00
13 | Bangabhaban | 8 | 11:00 | 79 | Kalurghat | 40 | 12:00 | 145 | Rampur | 33 | 00:00
14 | Barapukuria | 73 | 20:00 | 80 | Kamrangirchar | 63 | 16:00 | 146 | Rangamati | 15 | 21:00
15 | Barguna | 24 | 23:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 152 | 20:00
16 | Barishal | 115 | 21:00 | 82 | Kasba | 32 | 01:00 | 148 | Ruppur | 5.4 | 11:00
17 | Barishal-230 | 100 | 21:00 | 83 | Kazla | 101 | 11:00 | 149 | SSM | 14 | 23:00
18 | Baroaulia | 57 | 08:00 | 84 | Keranigonj | 95 | 13:00 | 150 | Saidpur | 115 | 12:00
19 | Baroirhat | 71 | 20:00 | 85 | Khagrachori | 28 | 19:00 | 151 | Satkhira | 139 | 20:00
20 | Bashundhara | 198 | 12:00 | 86 | Khulna | 69 | 13:00 | 152 | Satmasjid | 104 | 14:00
21 | BashundharaCement | 10 | 12:00 | 87 | Khulshi | 188 | 13:00 | 153 | Savar | 234 | 12:00
22 | Beanibazar | 56 | 00:00 | 88 | Kishoreganj | 116 | 00:00 | 154 | SevenRings | 19.08 | 16:00
23 | Benapole | 69 | 22:00 | 89 | Kodda | 307 | 08:00 | 155 | ShahCement | 19 | 21:00
24 | Bhaluka | 140 | 12:00 | 90 | Kulaura | 44 | 00:00 | 156 | Shahjadpur | 84 | 20:00
25 | Bhandaria | 57 | 22:00 | 91 | Kurigram | 53 | 14:00 | 157 | Shahjibazar | 112 | 21:00
26 | Bhangura | 38 | 19:30 | 92 | Kushtia | 164 | 21:00 | 158 | Shahmirpur | 44 | 14:00
27 | Bheramara(GK) | 67 | 21:00 | 93 | Lalbag | 58 | 17:00 | 159 | Shariatpur | 93 | 15:00
28 | Bhulta | 269 | 22:00 | 94 | Lalmonirhat | 45 | 22:00 | 160 | Sherpur | 130 | 20:00
29 | Bog-Sherpur | 68 | 22:00 | 95 | MI_Cement | 18 | 03:00 | 161 | Shikalbaha | 27 | 22:00
30 | Bogura | 172 | 21:00 | 96 | Madanganj | 50 | 12:00 | 162 | Shitalakhya | 89.2 | 15:00
31 | Borhanuddin | 86 | 22:00 | 97 | Madaripur | 118 | 23:00 | 163 | Sholosohor | 48 | 15:00
32 | Brahmanbaria | 130 | 22:00 | 98 | Madartek | 86.44 | 22:00 | 164 | Shyampur | 182 | 13:00
33 | Cantonment | 148 | 12:00 | 99 | Madunaghat | 60 | 21:00 | 165 | Siddhirganj | 125 | 12:00
34 | Chandina | 19.37 | 23:00 | 100 | Magura | 64 | 21:00 | 166 | Sirajganj | 110 | 20:00
35 | Chandpur | 75 | 23:00 | 101 | Mahasthangarh | 78 | 23:00 | 167 | Sonargaon | 113 | 12:00
36 | Chandraghona | 34 | 18:30 | 102 | Manikganj | 126 | 22:00 | 168 | Sreemongol | 63 | 00:00
37 | Chapai | 75 | 21:00 | 103 | Maniknagar | 76 | 12:00 | 169 | Sreepur | 92 | 12:00
38 | Charsaidpur | 39 | 17:00 | 104 | Matarbari | 53 | 22:00 | 170 | Srinagar | 46.59 | 22:00
39 | Chauddagram | 73 | 22:00 | 105 | Matuail | 70 | 12:00 | 171 | Sunamganj | 43 | 19:30
40 | Chhatak | 29 | 20:00 | 106 | Millgate | 102 | 12:00 | 172 | Sylhet | 40 | 00:00
41 | Chowmuhani | 234 | 22:00 | 107 | Mirpur | 121 | 15:00 | 173 | Sylhet-132 | 97 | 21:00
42 | Chuadanga | 120 | 23:00 | 108 | Mirsorai | 8 | 09:00 | 174 | TK | 34 | 22:00
43 | Coxsbazar | 126 | 18:30 | 109 | Mirzapur | 47 | 21:00 | 175 | Tangail | 172 | 21:00
44 | Cumilla(N) | 151 | 21:00 | 110 | Mithapukur | 72 | 19:00 | 176 | Thakurgaon | 120 | 21:00
45 | Cumilla(S) | 164 | 14:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 126 | 21:00
46 | Daudkandi | 152 | 21:00 | 112 | Mogbazar | 148.3 | 12:00 | 178 | Ullahpara | 39 | 19:00
47 | Dhaka | 58 | 12:00 | 113 | Mongla | 42 | 12:00 | 179 | Ullon | 38 | 12:00
48 | Dhamrai | 130 | 09:00 | 114 | Motijheel | 40 | 12:00 | 180 | Uttara | 83 | 13:00
49 | Dhanmondi | 145 | 12:00 | 115 | Muktagacha | 30 | 11:00 | 181 | UttaraNew | 59 | 12:00
50 | Dohazari | 102 | 19:30 | 116 | Munshiganj | 112 | 23:00 | 182 | Zigatola | 75 | 15:00
51 | Faridpur | 167 | 21:00 | 117 | Muradnagar | 24 | 22:00
52 | Fatullah | 103 | 15:00 | 118 | Mymensingh | 174 | 21:00
53 | Fenchuganj | 37 | 03:00 | 119 | Naogaon | 142 | 21:00
54 | Feni | 125 | 21:00 | 120 | Narail | 53 | 23:00
55 | GPH | 93 | 18:00 | 121 | Narinda | 82 | 12:00
56 | Ghatail | 64 | 19:00 | 122 | Narshingdi | 160 | 02:00
57 | Ghorashal | 12 | 00:00 | 123 | Natore | 158 | 20:00
58 | Ghorashal-230 | 95 | 21:00 | 124 | Nawabganj | 58.8 | 22:00
59 | Goalpara | 40 | 22:00 | 125 | Netrakona | 104 | 06:00
60 | Gollamari | 102 | 19:00 | 126 | New | 90.2 | 12:00
61 | Gopalganj | 111 | 20:00 | 127 | Niamatpur | 76 | 23:00
62 | Gulshan | 114 | 12:00 | 128 | Noapara | 53 | 21:00
63 | Halishahar | 82 | 16:00 | 129 | PHP | 2 | 01:00
64 | HaripurSBU | 178 | 11:00 | 130 | Pabna | 126 | 20:00
65 | Hasnabad | 75 | 23:00 | 131 | Palashbari | 104 | 20:00
66 | Hathazari | 71 | 23:00 | 132 | Panchagarh | 59 | 19:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 31-05-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13241.7 | 0 |  | 13241.7
1:00 | 12598 | 0 |  | 12598
2:00 | 12211 | 0 |  | 12211
3:00 | 11936 | 0 |  | 11936
4:00 | 11812 | 0 |  | 11812
5:00 | 11567 | 0 |  | 11567
6:00 | 11383.7 | 0 |  | 11383.7
7:00 | 11613.08 | 0 |  | 11613.08
8:00 | 11835.13 | 0 |  | 11835.13
9:00 | 12105.47 | 0 |  | 12105.47
10:00 | 12408.99 | 0 |  | 12408.99
11:00 | 12495.48 | 0 |  | 12495.48
12:00 | 13114.05 | 0 |  | 13114.05
13:00 | 12792.17 | 0 |  | 12792.17
14:00 | 12420.59 | 0 |  | 12420.59
15:00 | 12536.22 | 0 |  | 12536.22
16:00 | 11610.5 | 0 |  | 11610.5
17:00 | 11378.34 | 0 |  | 11378.34
18:00 | 11961.32 | 0 |  | 11961.32
19:00 | 12955.52 | 0 |  | 12955.52
19:30 | 13681.02 | 47 |  | 13730.02
20:00 | 14178.85 | 69 |  | 14250.85
21:00 | 14695.88 | 0 |  | 14695.88
22:00 | 14670.2 | 29 |  | 14700.2
23:00 | 14662.2 | 0 |  | 14662.2
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 31-05-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7212.5 | 6029.2 | 13241.7 | DAILY GENERATION CURVE
00:30 | 7033.25 | 5886.6 | 12919.85
01:00 | 6854 | 5744 | 12598 | 31-05-2025
01:30 | 6698 | 5706.5 | 12404.5
02:00 | 6542 | 5669 | 12211
02:30 | 6454 | 5619.5 | 12073.5
03:00 | 6366 | 5570 | 11936
03:30 | 6347 | 5527 | 11874
04:00 | 6328 | 5484 | 11812
04:30 | 6317 | 5372.5 | 11689.5
05:00 | 6306 | 5261 | 11567
05:30 | 6261.43 | 5213.92 | 11475.35
06:00 | 6216.86 | 5166.84 | 11383.7
06:30 | 6266.095 | 5232.295 | 11498.39
07:00 | 6315.33 | 5297.75 | 11613.08
07:30 | 6354.305 | 5369.8 | 11724.105
08:00 | 6393.28 | 5441.85 | 11835.13
08:30 | 6423.39 | 5546.91 | 11970.3
09:00 | 6453.5 | 5651.97 | 12105.47
09:30 | 6518.07 | 5739.16 | 12257.23
10:00 | 6582.64 | 5826.35 | 12408.99
10:30 | 6609.21 | 5843.025 | 12452.235
11:00 | 6635.78 | 5859.7 | 12495.48
11:30 | 6770.925 | 6033.84 | 12804.765
12:00 | 6906.07 | 6207.98 | 13114.05
12:30 | 6835.045 | 6118.065 | 12953.11
13:00 | 6764.02 | 6028.15 | 12792.17
13:30 | 6677.02 | 5929.36 | 12606.38
14:00 | 6590.02 | 5830.57 | 12420.59
14:30 | 6639.2 | 5839.205 | 12478.405
15:00 | 6688.38 | 5847.84 | 12536.22
15:30 | 6389 | 5684.36 | 12073.36
16:00 | 6089.62 | 5520.88 | 11610.5
16:30 | 6040.31 | 5454.11 | 11494.42
17:00 | 5991 | 5387.34 | 11378.34
17:30 | 6129 | 5540.83 | 11669.83
18:00 | 6267 | 5694.32 | 11961.32
18:30 | 6612 | 5846.42 | 12458.42
19:00 | 6957 | 5998.52 | 12955.52
19:30 | 7465 | 6216.02 | 13681.02
20:00 | 7812 | 6366.85 | 14178.85
20:30 | 7948 | 6489.365 | 14437.365 |  | Executive Engineer
21:00 | 8084 | 6611.88 | 14695.88 |  | Network Operation Division
21:30 | 8061 | 6622.04 | 14683.04
22:00 | 8038 | 6632.2 | 14670.2
22:30 | 8028 | 6638.2 | 14666.2
23:00 | 8018 | 6644.2 | 14662.2

## En-Curve
QF-LDC-12
Date | 31-05-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3142 | 1860.5 | 927 | 0 | 16 | 1013 | 40 | 4582.2 | 0 | 260 | 1351 | 0 | 0 | 50 | 0 | DAILY ENERGY CURVE
00:30 | 3195.5 | 1841.25 | 926.5 | 0 | 16 | 1018.5 | 60 | 4450.6 | 0 | 228.5 | 1127.5 | 0 | 0 | 55.5 | 0 | 31-05-2025
01:00 | 3249 | 1822 | 926 | 0 | 16 | 1024 | 80 | 4319 | 0 | 197 | 904 | 0 | 0 | 61 | 0
01:30 | 3277 | 1822 | 926.5 | 0 | 16 | 1018.5 | 80 | 4265 | 0 | 179.5 | 758.5 | 0 | 0 | 61.5 | 0 | Energy Generated | 306.4732 |  | MKWHr
02:00 | 3305 | 1822 | 927 | 0 | 16 | 1013 | 80 | 4211 | 0 | 162 | 613 | 0 | 0 | 62 | 0 | Energy not Served | 0.098 |  | MKWHr
02:30 | 3305.5 | 1811 | 926.5 | 0 | 16 | 1010.5 | 80 | 4158 | 0 | 158 | 551.5 | 0 | 0 | 56.5 | 0 | Total Energy Requirement | 306.5712 |  | MKWHr
03:00 | 3306 | 1800 | 926 | 0 | 16 | 1008 | 80 | 4105 | 0 | 154 | 490 | 0 | 0 | 51 | 0
03:30 | 3293.5 | 1802 | 926 | 0 | 16 | 1006.5 | 79 | 4070.5 | 0 | 138 | 498.5 | 0 | 0 | 44 | 0
04:00 | 3281 | 1804 | 926 | 0 | 16 | 1005 | 78 | 4036 | 0 | 122 | 507 | 0 | 0 | 37 | 0
04:30 | 3306.5 | 1800 | 926 | 0 | 15 | 961 | 75 | 3964 | 0 | 113 | 498 | 0 | 0 | 31 | 0
05:00 | 3332 | 1796 | 926 | 0 | 14 | 917 | 72 | 3892 | 0 | 104 | 489 | 0 | 0 | 25 | 0
05:30 | 3356 | 1806.5 | 926 | 0 | 14 | 872.5 | 72 | 3837 | 13.85 | 104 | 459 | 0 | 0 | 14.5 | 0
06:00 | 3380 | 1817 | 926 | 0 | 14 | 828 | 72 | 3782 | 27.7 | 104 | 429 | 0 | 0 | 4 | 0
06:30 | 3348 | 1807.5 | 802 | 0 | 14 | 874 | 72.5 | 3938.5 | 38.89 | 132.5 | 460 | 0 | 0 | 10.5 | 0
07:00 | 3316 | 1798 | 678 | 0 | 14 | 920 | 73 | 4095 | 50.08 | 161 | 491 | 0 | 0 | 17 | 0
07:30 | 3310 | 1784 | 654.5 | 0 | 13 | 917.93 | 75 | 4153 | 113.175 | 169.5 | 525.5 | 0 | 0 | 8.5 | 0
08:00 | 3304 | 1770 | 631 | 0 | 12 | 915.86 | 77 | 4211 | 176.27 | 178 | 560 | 0 | 0 | 0 | 0
08:30 | 3281.5 | 1732 | 631 | 0 | 12 | 915.855 | 77.5 | 4313.5 | 211.445 | 186 | 594.5 | 0 | 0 | 15 | 0
09:00 | 3259 | 1694 | 631 | 0 | 12 | 915.85 | 78 | 4416 | 246.62 | 194 | 629 | 0 | 0 | 30 | 0
09:30 | 3292 | 1687 | 654.5 | 0 | 13 | 940.76 | 79 | 4468.1 | 287.87 | 186.5 | 622.5 | 0 | 0 | 26 | 0
10:00 | 3325 | 1680 | 678 | 0 | 14 | 965.67 | 80 | 4520.2 | 329.12 | 179 | 616 | 0 | 0 | 22 | 0
10:30 | 3185.5 | 1626.5 | 749.5 | 0 | 25 | 977.305 | 81 | 4520.2 | 392.73 | 200.5 | 667 | 0 | 0 | 27 | 0
11:00 | 3046 | 1573 | 821 | 0 | 36 | 988.94 | 82 | 4520.2 | 456.34 | 222 | 718 | 0 | 0 | 32 | 0
11:30 | 3043 | 1570 | 869 | 0 | 33 | 984.37 | 82 | 4536.2 | 516.695 | 250.5 | 893 | 0 | 0 | 27 | 0
12:00 | 3040 | 1567 | 917 | 0 | 30 | 979.8 | 82 | 4552.2 | 577.05 | 279 | 1068 | 0 | 0 | 22 | 0
12:30 | 2994 | 1545 | 891.5 | 0 | 28 | 973.55 | 82.5 | 4484.2 | 543.36 | 249.5 | 1139.5 | 0 | 0 | 22 | 0
13:00 | 2948 | 1523 | 866 | 0 | 26 | 967.3 | 83 | 4416.2 | 509.67 | 220 | 1211 | 0 | 0 | 22 | 0
13:30 | 2979 | 1497 | 891 | 0 | 30 | 965.88 | 83 | 4371.7 | 402.8 | 200 | 1152.5 | 0 | 0 | 33.5 | 0
14:00 | 3010 | 1471 | 916 | 0 | 34 | 964.46 | 83 | 4327.2 | 295.93 | 180 | 1094 | 0 | 0 | 45 | 0
14:30 | 3074 | 1474 | 916 | 0 | 17 | 967.585 | 82 | 4302.1 | 243.22 | 208 | 1148.5 | 0 | 0 | 46 | 0
15:00 | 3138 | 1477 | 916 | 0 | 0 | 970.71 | 81 | 4277 | 190.51 | 236 | 1203 | 0 | 0 | 47 | 0
15:30 | 2988.5 | 1449.5 | 916.5 | 0 | 16 | 978.535 | 78.5 | 4260.5 | 163.325 | 198.5 | 971.5 | 0 | 0 | 52 | 0
16:00 | 2839 | 1422 | 917 | 0 | 32 | 986.36 | 76 | 4244 | 136.14 | 161 | 740 | 0 | 0 | 57 | 0
16:30 | 2993 | 1423 | 917 | 0 | 32 | 977.55 | 74 | 4100 | 96.87 | 152 | 674.5 | 0 | 0 | 54.5 | 0
17:00 | 3147 | 1424 | 917 | 0 | 32 | 968.74 | 72 | 3956 | 57.6 | 143 | 609 | 0 | 0 | 52 | 0
17:30 | 3201.5 | 1453 | 917 | 0 | 31 | 976.295 | 72 | 4016 | 44.535 | 160.5 | 747.5 | 0 | 0 | 50.5 | 0
18:00 | 3256 | 1482 | 917 | 0 | 30 | 983.85 | 72 | 4076 | 31.47 | 178 | 886 | 0 | 0 | 49 | 0
18:30 | 3287 | 1487.5 | 893 | 0 | 33 | 1046.685 | 72 | 4220 | 15.735 | 228 | 1143.5 | 0 | 0 | 32 | 0
19:00 | 3318 | 1493 | 869 | 0 | 36 | 1109.52 | 72 | 4364 | 0 | 278 | 1401 | 0 | 0 | 15 | 0
19:30 | 3318 | 1553 | 868 | 0 | 34 | 1088.02 | 76 | 4538 | 0 | 375 | 1806 | 0 | 0 | 25 | 47
20:00 | 3355 | 1567 | 868 | 0 | 38 | 1225.85 | 79 | 4540 | 0 | 499 | 1983 | 0 | 0 | 24 | 69
20:30 | 3317 | 1561 | 892 | 0 | 39 | 1215.265 | 80 | 4560.1 | 0 | 578 | 2178 | 0 | 0 | 17 | 34.5
21:00 | 3279 | 1555 | 916 | 0 | 40 | 1204.68 | 81 | 4580.2 | 0 | 657 | 2373 | 0 | 0 | 10 | 0
21:30 | 3284 | 1554.5 | 916.5 | 0 | 40 | 1206.84 | 81.5 | 4580.7 | 0 | 628 | 2376.5 | 0 | 0 | 14.5 | 14.5
22:00 | 3289 | 1554 | 917 | 0 | 40 | 1209 | 82 | 4581.2 | 0 | 599 | 2380 | 0 | 0 | 19 | 29
22:30 | 3282.5 | 1561.5 | 917 | 0 | 41 | 1213 | 82.5 | 4581.7 | 0 | 591 | 2378 | 0 | 0 | 18 | 14.5
23:00 | 3276 | 1569 | 917 | 0 | 42 | 1217 | 83 | 4582.2 | 0 | 583 | 2376 | 0 | 0 | 17 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 31-05-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 384 | 06:00 | 365 | 11:00 | Payra | 412 | 06:00 | 405 | 11:00
Ashuganj | N/A | N/A | N/A | N/A | Rahanpur | 395 | 06:00 | 383 | 20:00
Bhulta | 395 | 04:00 | 370 | 11:00 | Rampal | 400 | 16:00 | 381 | 12:00
Bibiana | 390 | 06:00 | 382 | 11:00
BIPTC | 407 | 07:00 | 389 | 00:00
Bogura | 389 | 06:00 | 374 | 20:00
Gopalganj | 393 | 06:00 | 378 | 11:00
Kaliakoir | 377 | 16:00 | 359 | 11:00
Madunaghat | 395 | 21:00 | 386 | 11:00
Meghnaghat | 387 | 06:00 | 369 | 11:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 255 | 16:00 | 211 | 11:00 | Keranigonj | 222 | 05:00 | 210 | 11:00
AKSML | 233 | 20:00 | 224 | 10:00 | Khulna(S) | 227 | 06:00 | 207 | 12:00
Aminbazar | 227 | 16:00 | 212 | 11:00 | Madunaghat | 235 | 20:00 | 227 | 10:00
Ashuganj | 231 | 16:00 | 214 | 11:00 | Madunaghat-400 | 236 | 21:00 | 227 | 10:00
Ashuganj-400 | 231 | 16:00 | 214 | 11:00 | Maniknagar | 220 | 05:00 | 210 | 11:00
Baghabari | 232 | 06:00 | 222 | 20:00 | Meghnaghat | 229 | 05:00 | 220 | 10:00
Barapukuria | 220 | 18:00 | 213 | 20:00 | Meghnaghat-400 | 224 | 05:00 | 214 | 11:00
Barapukuria-230 | 220 | 18:00 | 213 | 20:00 | Mirsorai | 229 | 18:30 | 219 | 11:00
Barishal | 234 | 06:00 | 225 | 22:00 | Rajshahi | 234 | 08:00 | 221 | 20:00
Bheramara | 233 | 06:00 | 222 | 14:00 | Rampal | 227 | 06:00 | 210 | 12:00
Bhulta | 229 | 04:00 | 211 | 11:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 230 | 16:00 | 223 | 11:00 | Rampura | 229 | 06:00 | 211 | 11:00
BIPTC | 237 | 07:00 | 222 | 11:00 | Shikalbaha | 234 | 21:00 | 224 | 10:00
Bogura | 225 | 06:00 | 217 | 20:00 | Shyampur | 223 | 06:00 | 211 | 11:00
Bogura-400 | 225 | 06:00 | 217 | 20:00 | Siddhirganj | 224 | 16:00 | 213 | 11:00
Borhanuddin | 238 | 05:00 | 230 | 23:00 | Sirajgonj | 235 | 04:00 | 228 | 23:00
BSRM | 229 | 18:30 | 218 | 11:00 | Sreepur | 228 | 16:00 | 217 | 11:00
Cumilla(N) | 224 | 16:00 | 214 | 10:00 | Tongi | 226 | 07:00 | 217 | 10:00
Faridpur | 233 | 16:00 | 221 | 12:00
Fenchuganj | 233 | 16:00 | 225 | 11:00
Ghorashal | 235 | 05:00 | 230 | 00:00
Ghorashal-230 | 227 | 06:00 | 213 | 11:00
Gopalganj | 233 | 16:00 | 224 | 11:00
GPH | 231 | 18:30 | 222 | 11:00
Haripur | 222 | 05:00 | 212 | 11:00
Hasnabad | 223 | 16:00 | 213 | 12:00
Hathazari | 233 | 17:00 | 225 | 10:00
Ishurdi | 235 | 06:00 | 223 | 11:00
Jhenaidah | 227 | 06:00 | 195 | 13:00
Kaliakoir | 233 | 16:00 | 218 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 04:00 | 122 | 11:00 | Madartek | 132 | 06:00 | 122 | 11:00
Agargaon | 137 | 00:00 | 126 | 11:00 | Madunaghat | 135 | 19:30 | 128 | 10:00
Agrabad | 135 | 20:00 | 128 | 10:00 | Magura | 130 | 16:00 | 114 | 13:00
AKS | 131 | 21:00 | 126 | 09:00 | Mahasthangarh | 130 | 06:00 | 124 | 19:30
Aminbazar | 133 | 16:00 | 124 | 11:00 | Manikganj | 135 | 16:00 | 124 | 11:00
Amnura | 136 | 08:00 | 119 | 20:00 | Maniknagar | 134 | 04:00 | 126 | 11:00
Ashuganj | 137 | 06:00 | 132 | 11:00 | Matarbari | 127 | 18:30 | 119 | 05:00
Bagerhat | 134 | 14:00 | 116 | 00:00 | Matuail | 129.5 | 06:00 | 123 | 11:00
Bajitpur | 134 | 14:00 | 125 | 23:00 | Millgate | 137 | 03:00 | 125 | 11:00
Bakulia | 136 | 20:00 | 130 | 10:00 | Mirpur | 133 | 16:00 | 122 | 11:00
Banani | 132 | 04:00 | 122 | 11:00 | Mirzapur | 134 | 16:00 | 125 | 23:00
Bangabhaban | 134 | 05:00 | 125 | 11:00 | Mithapukur | 128 | 18:00 | 120 | 14:00
Barapukuria | 134 | 18:00 | 121 | 20:00 | MI_Cement | 130 | 03:00 | 123 | 11:00
Barguna | 134 | 18:00 | 129 | 00:00 | Modern | 0 | 00:00 | 0 | 00:00
Barishal | 129 | 16:00 | 122 | 22:00 | Mogbazar | 133 | 05:00 | 25 | 15:00
Barishal-230 | 128 | 04:00 | 123 | 00:00 | Mongla | 132 | 14:00 | 118 | 12:00
Baroaulia | 136 | 06:00 | 129 | 11:00 | Motijheel | 134 | 05:00 | 125 | 11:00
Baroirhat | 128 | 19:00 | 119 | 11:00 | Muktagacha | 134 | 18:00 | 122 | 23:00
Bashundhara | 137 | 04:00 | 122 | 11:00 | Munshiganj | 130 | 00:00 | 123 | 11:00
BashundharaCement | 129 | 04:00 | 122 | 11:00 | Muradnagar | 128 | 18:00 | 120 | 10:00
Beanibazar | 134 | 17:00 | 126 | 00:00 | Mymensingh | 136 | 12:00 | 117 | 23:00
Benapole | 130 | 15:00 | 116 | 12:00 | Naogaon | 131 | 06:00 | 124 | 15:00
Bhaluka | 134 | 16:00 | 122 | 23:00 | Narail | 132 | 16:00 | 113 | 13:00
Bhandaria | 125 | 18:30 | 112 | 22:00 | Narinda | 134 | 04:00 | 126 | 11:00
Bhangura | 133 | 06:00 | 126 | 11:00 | Narshingdi | 137 | 16:00 | 117 | 01:00
Bheramara | 137 | 06:00 | 129 | 21:00 | Natore | 134 | 06:00 | 126 | 20:00
Bheramara(GK) | 137 | 06:00 | 129 | 13:00 | Nawabganj | 134 | 16:00 | 124 | 11:00
Bhulta | 124 | 16:00 | 117 | 11:00 | Netrakona | 131 | 16:00 | 117 | 01:00
Bog-Sherpur | 132 | 06:00 | 126 | 15:00 | New | 139 | 16:00 | 126 | 11:00
Bogura | 132 | 03:00 | 128 | 22:00 | Niamatpur | 130 | 08:00 | 125 | 19:30
Bogura-230 | 134 | 06:00 | 128 | 20:00 | Noapara | 133 | 06:00 | 120 | 12:00
Brahmanbaria | 135 | 18:00 | 123 | 00:00 | Pabna | 135 | 06:00 | 126 | 20:00
Cantonment | 136 | 04:00 | 126 | 11:00 | Palashbari | 127 | 04:00 | 117 | 20:00
Chandina | 130 | 18:30 | 122 | 11:00 | Panchagarh | 136 | 23:00 | 117 | 14:00
Chandpur | 134 | 18:00 | 120 | 10:00 | Patuakhali | 136 | 23:00 | 130 | 00:00
Chandraghona | 134 | 20:00 | 129 | 10:00 | Payra | 135 | 05:00 | 133 | 00:00
Chapai | 127 | 04:00 | 121 | 20:00 | PHP | 128 | 18:30 | 118 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 16:00 | 123 | 11:00 | Postogola | 132 | 00:00 | 124 | 11:00
Chauddagram | 128 | 15:00 | 118 | 10:00 | Purbachal | 132 | 04:00 | 120 | 11:00
Chhatak | 132 | 14:00 | 123 | 00:00 | Purbasadipur | 130 | 18:00 | 113 | 14:00
Chowmuhani | 126 | 15:00 | 110 | 23:00 | Rahanpur | 131 | 05:00 | 126 | 20:00
Chuadanga | 128 | 05:00 | 113 | 12:00 | Rahanpur-400 | 132 | 06:00 | 127 | 20:00
Coxsbazar | 126 | 19:30 | 119 | 03:00 | Rahim | 129 | 00:00 | 123 | 11:00
Cumilla(N) | 129 | 17:00 | 122 | 11:00 | Rajbari | 135 | 16:00 | 126 | 22:00
Cumilla(S) | 134 | 04:00 | 121 | 10:00 | Rajendrapur | 133 | 13:00 | 121 | 11:00
Daudkandi | 125 | 17:00 | 118 | 10:00 | Rajshahi | 134 | 06:00 | 127 | 20:00
Dhaka | 132 | 04:00 | 122 | 11:00 | Rajshahi-230 | 136 | 08:00 | 113 | 20:00
Dhamrai | 132 | 04:00 | 123 | 11:00 | Ramganj | 130 | 18:30 | 115 | 03:00
Dhanmondi | 133 | 05:00 | 123 | 11:00 | Rampur | 134 | 20:00 | 128 | 10:00
Dohazari | 132 | 20:00 | 126 | 10:00 | Rampura | 133 | 06:00 | 121 | 11:00
Faridpur | 136 | 16:00 | 128 | 12:00 | Rangamati | 133 | 19:30 | 128 | 10:00
Fatullah | 130 | 00:00 | 123 | 11:00 | Rangpur | 126 | 07:00 | 116 | 20:00
Fenchuganj | 138 | 14:00 | 133 | 01:00 | Ruppur | 136 | 05:00 | 130 | 20:00
Feni | 126 | 15:00 | 117 | 22:00 | Saidpur | 131 | 18:30 | 117 | 14:00
Ghatail | 130 | 12:00 | 120 | 23:00 | Satkhira | 131 | 15:00 | 116 | 12:00
Ghorashal | 135 | 04:00 | 129 | 11:00 | Satmasjid | 136 | 06:00 | 126 | 11:00
Goalpara | 134 | 06:00 | 120 | 12:00 | Savar | 132 | 16:00 | 121 | 11:00
Gollamari | 134 | 06:00 | 123 | 12:00 | SevenRings | 136 | 16:00 | 127 | 11:00
Gopalganj | 134 | 16:00 | 125 | 12:00 | ShahCement | 130 | 16:00 | 123 | 11:00
Gopalganj-400 | 135 | 06:00 | 129 | 11:00 | Shahjadpur | 136 | 01:00 | 130 | 20:00
Gulshan | 132 | 04:00 | 121 | 11:00 | Shahjibazar | 137 | 18:00 | 125 | 03:00
Halishahar | 135 | 19:30 | 127 | 11:00 | Shahmirpur | 136 | 20:00 | 130 | 10:00
Haripur | 130 | 06:00 | 123 | 11:00 | Shariatpur | 130 | 06:00 | 124 | 00:00
HaripurSBU | 130 | 04:00 | 123 | 11:00 | Sherpur | 136 | 07:00 | 122 | 23:00
Hasnabad | 133 | 00:00 | 125 | 10:00 | Shikalbaha | 124 | 19:30 | 118 | 11:00
Hathazari | 135 | 14:00 | 130 | 10:00 | Shikalbaha-230 | 137 | 21:00 | 130 | 10:00
Ishurdi | 138 | 06:00 | 130 | 20:00 | Shitalakhya | 130 | 04:00 | 123 | 11:00
Jaldhaka | 128 | 03:00 | 115 | 14:00 | Sholosohor | 134 | 19:30 | 127 | 10:00
Jamalpur | 139 | 18:00 | 124 | 01:00 | Shyampur | 133 | 00:00 | 121 | 11:00
Jashore | 127 | 06:00 | 108 | 13:00 | Shyampur-230 | 130 | 00:00 | 122 | 11:00
Jhenaidah | 133 | 16:00 | 114 | 13:00 | Siddhirganj | 130 | 04:00 | 123 | 11:00
Jhenaidah-230 | 132 | 06:00 | 115 | 13:00 | Sirajganj | 130 | 05:00 | 124 | 20:00
Joydebpur | 137 | 16:00 | 123 | 11:00 | Sonargaon | 130 | 16:00 | 121 | 11:00
Joypurhat | 129 | 05:00 | 121 | 20:00 | Sreemongol | 137 | 18:00 | 127 | 00:00
Juldah | 136 | 19:30 | 130 | 10:00 | Sreepur | 134 | 16:00 | 125 | 23:00
Kabirpur | 141 | 16:00 | 123 | 11:00 | Srinagar | 134 | 16:00 | 125 | 11:00
Kachua | 131 | 15:00 | 119 | 02:00 | SSM | 138 | 13:00 | 132 | 06:00
Kaliakoir | 140 | 16:00 | 129 | 11:00 | Sunamganj | 132 | 17:00 | 122 | 01:00
Kallyanpur | 135 | 16:00 | 124 | 11:00 | Sylhet | 133 | 14:00 | 127 | 01:00
Kalurghat | 133 | 20:00 | 128 | 10:00 | Sylhet-132 | 133 | 16:00 | 128 | 00:00
Kamrangirchar | 134 | 06:00 | 125 | 11:00 | Tangail | 130 | 18:30 | 120 | 21:00
Kaptai | N/A | N/A | N/A | N/A | Thakurgaon | 135 | 18:30 | 114 | 14:00
Kasba | 128 | 18:30 | 118 | 11:00 | TK | 132 | 20:00 | 128 | 09:00
Kazla | 133 | 02:00 | 125 | 12:00 | Tongi | 138 | 07:00 | 127 | 10:00
Keranigonj | 134 | 05:00 | 125 | 11:00 | Ullahpara | 133 | 06:00 | 126 | 20:00
Khagrachori | 133 | 20:00 | 126 | 11:00 | Ullon | 132 | 04:00 | 121 | 11:00
Khulna | 134 | 15:00 | 123 | 12:00 | Uttara | 133 | 16:00 | 122 | 11:00
Khulna(S) | 135 | 06:00 | 123 | 12:00 | UttaraNew | 132 | 15:00 | 122 | 11:00
Khulshi | 133 | 20:00 | 127 | 10:00 | Zigatola | 134 | 06:00 | 125 | 12:00
Kishoreganj | 133 | 14:00 | 123 | 00:00
Kodda | 139 | 16:00 | 122 | 11:00
KSRM | 135 | 19:30 | 128 | 10:00
Kulaura | 138 | 17:00 | 132 | 00:00
Kurigram | 124 | 19:00 | 115 | 14:00
Kushtia | 135 | 06:00 | 123 | 13:00
Lalbag | 134 | 04:00 | 125 | 11:00
Lalmonirhat | 126 | 19:00 | 117 | 07:00
Madanganj | 129 | 05:00 | 122 | 11:00
Madaripur | 132 | 16:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division