## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 02-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-06-2025 | during | 02-06-2025 | during | 02-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 174.8 | 174.8 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 352 | 362 | 400.75 | 400.75 | 400.75 | 400.75 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 330 | 400 | 450 | 450 | 360 | 360 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 147 | 150 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 305 | 295 | 335 | 335 | 306 | 306 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 40 | 8 | 40 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 35 | 0 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 80 | 145 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 35 | 0 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 17 | 0 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 20 | 22 | 33 | 33 | 20 | 20 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 0 | 22 | 22 | 22 | 22 | 22 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 33 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 33 | 52.19 | 52.19 | 24 | 24 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 68 | 69 | 149 | 149 | 149 | 149 | Machine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 70 | 70 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 0 | 104 | 104 | 90 | 90 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 90 | 17 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 29 | 0 | 25 | 0 | 25 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 54 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 300 | 400 | 583 | 583 | 583 | 583 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 0 | 70 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6156 | 5972.724 | 1938 | 2127 | 5234.9 | 5241.9 | 3398.13 | 3405.13
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 1 | 0 | 2 | 0 | 2 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 118 | 115 | 80 | 80 | 80 | 80 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 222 | 222 | 225 | 225 | 225 | 225 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 0 | 105 | 105 | 105 | 105 | Bill delay
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 56 | 82 | 55 | 55 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 51 | 51 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 48 | 0 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 2 | 25 | 2 | 22 | 2 | 22 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 0 | 0 | 4.39 | 0 | 4.39 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 0 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1177 | 1224 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 8 | 14 | 40 | 50 | 40 | 50 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 360 | 360 | 360 | 360 | 360 | 360 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1970 | 1968 | 3273.11 | 3322.72 | 3272.11 | 3295.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 209 | 202 | 221.43 | 221.43 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 356 | 355 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 335 | 340 | 330 | 330 | 330 | 330 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 24 | 33 | 46.7 | 46.7 | 32 | 32 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 5 | 47 | 55 | 55 | 48 | 48 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 0 | 36 | 195 | 195 | 8 | 8 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 70 | 0 | 150 | 150 | 138 | 138 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 52 | 52 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 172 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 32 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 8 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 14 | 17.35 | 17.35 | 14 | 14 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 106 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 29 | 113 | 113 | 28 | 28 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 68 | 115 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 29 | 0 | 35 | 0 | 35 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1332 | 1546 | 2419.03 | 2384.03 | 1982.55 | 1947.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 01-06-2025 | during | 02-06-2025 | during | 02-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 0 | 16 | 157.5 | 157.5 | 0 | 0 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 94 | 112 | 200 | 200 | 175 | 175 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 73 | 115 | 115 | 95 | 95 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 18.29 | 0 | 25 | 0 | 25 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 0 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 181.29 | 213 | 576.1 | 549 | 363.6 | 336.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 34 | 34 | 36 | 36 | 34 | 34 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 30 | 0 | 0 | 0 | 0 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 156 | 155 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 83 | 86 | 86 | 85 | 85 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 162 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18 | 0 | 0 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 0 | 25 | 25 | 0 | 0 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 260 | 265 | 341 | 341 | 307 | 307 | FGMO
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 346 | 360 | 385 | 385 | 385 | 385 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 270 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1342 | 1457 | 1564 | 1564 | 1468 | 1468
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 921 | 922 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 221 | 252 | 410 | 410 | 224 | 224 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 63.15 | 0 | 70 | 0 | 70 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 1157 | 1061 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2362.15 | 2235 | 3582.2 | 3512.2 | 3396.2 | 3326.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 5 | 9 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 0 | 65 | 65 | 65 | 0 | 0 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 1120 | 1232 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 250 | 250 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.31 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1595.31 | 1776 | 2107 | 2106 | 2002 | 2001
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 8 | 0 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 176 | 179 | 214 | 214 | 201 | 201 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 374 | 414 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 48 | 0 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 0 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.28 | 0 | 5.2 | 0 | 5.2 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 964 | 1317.03 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 57.46 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 78 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1744.74 | 1910.03 | 3192.07 | 3025.87 | 2917.28 | 2751.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 50 | 50 | 50 | 50 | 50 | 49 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 157 | 200 | 150 | 150 | 200 | 200 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 34 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 5.6 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 115 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 15 | 0 | 27 | 0 | 27 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 117 | 0 | 93.14 | 0 | 93.14 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 414.6 | 399 | 587.74 | 462 | 637.74 | 511
System Total |  |  |  |  | 28853.2 | 27077.055 | 12880.09 | 13631.03 | 22536.15 | 22167.72 | 19437.61 | 19042.18
Forecast Scenario (02-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14200 |  | 0 |  | 14200
|  |  |  | 1:00 | 13800 |  | 0 |  | 13800
|  |  |  | 2:00 | 13300 |  | 0 |  | 13300
|  |  |  | 3:00 | 13000 |  | 0 |  | 13000
|  |  |  | 4:00 | 12640 |  | 0 |  | 12640
|  |  |  | 5:00 | 12420 |  | 0 |  | 12420
|  |  |  | 6:00 | 11820 |  | 0 |  | 11820
|  |  |  | 7:00 | 11850 |  | 0 |  | 11850
|  |  |  | 8:00 | 11750 |  | 0 |  | 11750
|  |  |  | 9:00 | 11950 |  | 0 |  | 11950
|  |  |  | 10:00 | 10800 |  | 0 |  | 10800
|  |  |  | 11:00 | 12150 |  | 0 |  | 12150
|  |  |  | 12:00 | 12400 |  | 0 |  | 12400
|  |  |  | 13:00 | 12500 |  | 0 |  | 12500
|  |  |  | 14:00 | 12600 |  | 0 |  | 12600
|  |  |  | 15:00 | 12700 |  | 0 |  | 12700
|  |  |  | 16:00 | 12500 |  | 0 |  | 12500
|  |  |  | 17:00 | 12200 |  | 0 |  | 12200
|  |  |  | 18:00 | 12300 |  | 0 |  | 12300
|  |  |  | 18:30 | 12100 |  | 0 |  | 12100
|  |  |  | 19:00 | 12900 |  | 0 |  | 12900
|  |  |  | 19:30 | 13100 |  | 0 |  | 13100
|  |  |  | 20:00 | 13200 |  | 0 |  | 13200
|  |  |  | 21:00 | 13300 |  | 0 |  | 13300
|  |  |  | 22:00 | 13200 |  | 0 |  | 13200
|  |  |  | 23:00 | 13100 |  | 0 |  | 13100
Probable Maximum Temperature: |  |  | 32.60°C
Probable Maximum Demand at Day Peak: |  |  | 12400.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 13300.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 13300.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 316.04658 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 11:37 hrs on 02-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [6 empty] | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [6 empty] | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 01-06-2025 | [28 empty] | Date: | 01-06-2025 | [28 empty] | Date: | 01-06-2025 | [28 empty] | Date: | 01-06-2025 | [28 empty] | Date: | 01-06-2025 | [15 empty] | Date: | 01-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [28 empty] | Day: | Sunday | [15 empty] | Day: | Sunday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Rupganj 33 MW PP(Summit) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Hobiganj 11MW PP Cofidence-E | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Ullapara 11 MW PP (Summit) | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 33.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 0.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 0.000 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 70 | 8 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 54 | 54 | 131 | 144 | 145 | 0 | 35 | 144 | 67 | 300 | 127 | 280 | 0 | 35 | 0 | 265 | 0 | 0 | 0 | 35 | 17 | 16 | 0 | 0 | 35 | 45 | 0 | 0 | 23 | 48 | 55 | 0 | 89 | 72 | 0 | 83 | 70 | 12 | 360 | 0 | 0 | 48 | 8 | 105 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 123 | 0 | 0 | 357 | 340 | 5 | 186 | 10 | 115 | 0 | 200 | 12 | 14 | 114 | 42 | 8 | 0 | 39 | 245 | 270 | 286 | 37 | 0 | 0 | 136 | 0 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 64 | 120 | 0 | 0 | 0 | 12 | 7812 | 917 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 1234.2 | 89 | 1159 | 0 | 0 | 0 | 113 | 0 | 88 | 18 | 0 | 0 | 0 | 30 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 162 | 50 | 115 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 11 | 0 | 220 | 0 | 0 | 1244 | 134 | 6661.2 | 14473.2 | 81.88
01:00 | 0 | 34 | 8 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 54 | 54 | 131 | 80 | 45 | 0 | 0 | 108 | 67 | 300 | 147 | 280 | 0 | 35 | 0 | 269 | 0 | 0 | 0 | 35 | 16.5 | 16 | 0 | 0 | 0 | 15 | 0 | 0 | 19 | 48 | 55 | 0 | 89 | 12 | 0 | 83 | 99 | 17 | 360 | 0 | 0 | 49 | 8 | 95 | 222 | 0 | 0 | 0 | 1187 | 0 | 51 | 118 | 0 | 0 | 330 | 340 | 5 | 215 | 10 | 115 | 0 | 200 | 9 | 14 | 114 | 36 | 8 | 0 | 39 | 250 | 270 | 288 | 35 | 0 | 0 | 128 | 0 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 45 | 95 | 0 | 0 | 0 | 12 | 7341.5 | 917 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 53 | 1122 | 0 | 0 | 0 | 70 | 0 | 88 | 0 | 0 | 0 | 36 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 163 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 11 | 0 | 220 | 0 | 0 | 1244 | 134 | 6303.2 | 13644.7 | 82.08
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 54 | 54 | 124 | 80 | 45 | 0 | 0 | 72 | 62 | 300 | 151 | 280 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 35 | 18.5 | 18 | 0 | 0 | 0 | 15 | 0 | 0 | 26 | 48 | 15.5 | 0 | 48 | 12 | 0 | 83 | 56 | 17 | 360 | 0 | 0 | 19 | 8 | 68 | 221 | 0 | 0 | 0 | 1187 | 0 | 51 | 70 | 0 | 0 | 330 | 340 | 5 | 204 | 10 | 115 | 0 | 200 | 9 | 14 | 114 | 38 | 8 | 0 | 39 | 245 | 270 | 289 | 35 | 0 | 0 | 131 | 0 | 0 | 84 | 30 | 0 | 0 | 161 | 17 | 45 | 103 | 0 | 0 | 0 | 12 | 7065 | 917 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 53 | 1014 | 0 | 0 | 0 | 35 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 162 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 11 | 0 | 220 | 0 | 0 | 1244 | 134 | 6003.2 | 13068.2 | 82.28
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 54 | 40 | 79 | 80 | 0 | 0 | 0 | 72 | 51 | 300 | 141 | 280 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 35 | 18.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 16 | 15.5 | 0 | 48 | 0 | 0 | 83 | 51 | 17 | 360 | 0 | 0 | 19 | 8 | 68 | 221 | 0 | 0 | 0 | 1187 | 0 | 51 | 70 | 0 | 0 | 330 | 340 | 5 | 184 | 10 | 93 | 0 | 200 | 9 | 14 | 114 | 38 | 8 | 0 | 39 | 245 | 270 | 289 | 35 | 0 | 0 | 133 | 0 | 0 | 81 | 30 | 0 | 0 | 161 | 17 | 37 | 104 | 0 | 0 | 0 | 12 | 6806 | 917 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 166 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 11 | 0 | 220 | 0 | 0 | 1244 | 72 | 5891.2 | 12697.2 | 82.48
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 311 | 0 | 0 | 54 | 54 | 68 | 80 | 0 | 0 | 0 | 35 | 35 | 300 | 138 | 280 | 0 | 0 | 0 | 266 | 0 | 0 | 0 | 35 | 18.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 0 | 0 | 48 | 0 | 0 | 83 | 17 | 17 | 360 | 0 | 0 | 0 | 8 | 17 | 222 | 0 | 0 | 0 | 1185 | 0 | 51 | 20 | 0 | 0 | 330 | 340 | 5 | 182 | 10 | 90 | 0 | 200 | 9 | 14 | 114 | 38 | 8 | 0 | 16 | 245 | 270 | 290 | 35 | 0 | 0 | 132 | 0 | 0 | 81 | 30 | 0 | 0 | 161 | 0 | 37 | 104 | 0 | 0 | 0 | 12 | 6537.5 | 917 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 166 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 10 | 0 | 220 | 0 | 0 | 1244 | 10 | 5823.2 | 12360.7 | 82.68
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 35 | 54 | 68 | 80 | 0 | 0 | 0 | 0 | 16 | 300 | 140 | 280 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 17 | 18.5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 16 | 0 | 0 | 48 | 0 | 0 | 81 | 0 | 18 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1180 | 0 | 51 | 0 | 0 | 0 | 330 | 340 | 5 | 192 | 10 | 90 | 0 | 155 | 9 | 14 | 114 | 36 | 0 | 0 | 16 | 245 | 270 | 290 | 35 | 0 | 0 | 139 | 0 | 0 | 81 | 30 | 0 | 0 | 160 | 0 | 37 | 104 | 0 | 0 | 0 | 12 | 6393.5 | 916 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 168 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 10 | 0 | 220 | 0 | 0 | 1244 | 0 | 5803.2 | 12196.7 | 82.88
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 24 | 54 | 68 | 80 | 0 | 0 | 0 | 0 | 0 | 300 | 150 | 280 | 0 | 0 | 0 | 293 | 0 | 0 | 2 | 0 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 18 | 361 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1187 | 0 | 51 | 0 | 0 | 0 | 300 | 340 | 5 | 208 | 10 | 34 | 0 | 68 | 9 | 12 | 52 | 34 | 0 | 0 | 0 | 250 | 270 | 290 | 35 | 0 | 0 | 132 | 0 | 0 | 81 | 30 | 0 | 0 | 160 | 0 | 37 | 104 | 0 | 0 | 0 | 12 | 6065 | 917 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.64 | 1148 | 0 | 1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 2.11 | 175 | 0 | 0 | 0 | 0 | 0 | 390 | 0 | 0.14 | 0 | 167 | 50 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0.02 | 0 | 260 | 8 | 0 | 220 | 0 | 0 | 1100 | 0 | 5622.91 | 11687.91 | 83.08
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 54 | 68 | 80 | 0 | 0 | 0 | 0 | 0 | 300 | 147 | 280 | 0 | 0 | 0 | 278 | 0 | 0 | 2 | 0 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 16 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1187 | 1 | 51 | 0 | 0 | 0 | 330 | 340 | 5 | 189 | 10 | 34 | 0 | 68 | 9 | 12 | 52 | 34 | 0 | 0 | 0 | 245 | 270 | 290 | 35 | 0 | 0 | 138 | 0 | 0 | 81 | 30 | 0 | 0 | 160 | 0 | 65 | 104 | 0 | 0 | 0 | 12 | 6078 | 916 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.44 | 1110 | 0 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 9.59 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.86 | 0 | 167 | 50 | 0 | 5 | 0 | 0 | 0 | 0.5 | 28 | 0.06 | 0 | 307 | 7 | 0 | 220 | 0 | 0 | 1100 | 0 | 5710.45 | 11788.45 | 83.28
08:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 0 | 54 | 69 | 80 | 0 | 0 | 2 | 0 | 0 | 300 | 151 | 280 | 0 | 0 | 0 | 298 | 0 | 0 | 11 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1187 | 2 | 51 | 0 | 0 | 0 | 330 | 340 | 5 | 204 | 10 | 35 | 0 | 71 | 7 | 12 | 52 | 32 | 0 | 1 | 0 | 250 | 270 | 292 | 35 | 0 | 0 | 132 | 0 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 55 | 104 | 0 | 0 | 0.08 | 12 | 6107.08 | 873 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.49 | 1109 | 0 | 1014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 2.79 | 176 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0.35 | 0 | 160 | 48 | 0 | 3 | 0 | 0 | 0 | 0.8 | 45 | 0.13 | 0 | 307 | 7 | 0 | 220 | 0 | 0 | 1100 | 0 | 5696.56 | 11803.64 | 83.48
09:00 | 0 | 53 | 24 | 0 | 0 | 0 | 0 | 0 | 353 | 0 | 0 | 12 | 54 | 68 | 80 | 0 | 0 | 17 | 35 | 0 | 300 | 141 | 280 | 0 | 0 | 0 | 292 | 0 | 0 | 8 | 0 | 19 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 48 | 0 | 0 | 83 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1228 | 4 | 51 | 3 | 0 | 0 | 357 | 335 | 5 | 222 | 15 | 68 | 0 | 100 | 9 | 14 | 52 | 30 | 0 | 5 | 0 | 245 | 270 | 293 | 34 | 0 | 0 | 150 | 0 | 0 | 82 | 30 | 0 | 0 | 160 | 0 | 55 | 105 | 0 | 0 | 0.61 | 12 | 6463.61 | 873 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.74 | 1159 | 0 | 1017 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 25.43 | 176 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 1.85 | 0 | 158 | 49 | 0 | 6 | 0 | 0 | 0 | 1.8 | 43 | 0.26 | 0 | 307 | 5 | 0 | 220 | 0 | 0 | 1145 | 0 | 5781.08 | 12244.69 | 83.68
10:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 348 | 0 | 0 | 35 | 54 | 68 | 80 | 0 | 0 | 26 | 90 | 0 | 300 | 142 | 280 | 0 | 17 | 0 | 268 | 0 | 0 | 25 | 0 | 19.5 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 48 | 0 | 0 | 83 | 1 | 2 | 360 | 0 | 0 | 0 | 0 | 1 | 223 | 0 | 0 | 0 | 1224 | 4 | 43 | 30 | 0 | 0 | 325 | 300 | 5 | 180 | 20 | 68 | 0 | 100 | 9 | 14 | 52 | 32 | 0 | 2 | 0 | 245 | 270 | 293 | 34 | 0 | 0 | 152 | 0 | 0 | 82 | 30 | 0 | 0 | 161 | 0 | 54 | 95 | 0 | 1 | 5.89 | 12 | 6438.39 | 921 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.53 | 1156 | 0 | 1001 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 27.54 | 175 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 3.89 | 0 | 159 | 50 | 0 | 13 | 35 | 0 | 0 | 2 | 158 | 0.35 | 0 | 291 | 5 | 0 | 220 | 0 | 0 | 1150 | 0 | 5997.31 | 12435.7 | 83.88
11:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 355 | 0 | 0 | 35 | 54 | 68 | 80 | 0 | 0 | 35 | 90 | 0 | 330 | 141 | 300 | 0 | 17 | 0 | 270 | 0 | 0 | 29 | 0 | 19.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 48 | 0 | 0 | 118 | 16 | 2 | 360 | 0 | 0 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 1182 | 5 | 43 | 70 | 0 | 0 | 357 | 335 | 5 | 198 | 18 | 68 | 0 | 100 | 9 | 14 | 52 | 30 | 0 | 12 | 0 | 245 | 270 | 306 | 34 | 0 | 0 | 153 | 0 | 0 | 79 | 30 | 0 | 0 | 163 | 0 | 55 | 95 | 0 | 1 | 16.02 | 12 | 6663.52 | 921 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.08 | 1125 | 0 | 964 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 48.48 | 176 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 4.3 | 0 | 160 | 50 | 35 | 21 | 35 | 0 | 0 | 1.3 | 121 | 0.53 | 0 | 250 | 6 | 0 | 220 | 0 | 0 | 1100 | 0 | 5973.69 | 12637.21 | 84.02
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 35 | 54 | 68 | 80 | 0 | 0 | 35 | 90 | 0 | 330 | 147 | 300 | 0 | 17 | 0 | 305 | 0 | 0 | 29 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 48 | 0 | 0 | 118 | 17 | 2 | 360 | 0 | 0 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 1177 | 1 | 43 | 70 | 0 | 0 | 356 | 335 | 5 | 209 | 24 | 68 | 0 | 100 | 9 | 0 | 52 | 32 | 0 | 29 | 0 | 260 | 270 | 346 | 34 | 0 | 0 | 156 | 0 | 0 | 84 | 30 | 0 | 0 | 162 | 0 | 55 | 94 | 0 | 2 | 18.29 | 12 | 6763.29 | 921 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.15 | 1157 | 0 | 964 | 0 | 0 | 0 | 35 | 0 | 48 | 0 | 8 | 0 | 78 | 0 | 57.46 | 176 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 4.28 | 0 | 157 | 50 | 35 | 15 | 35 | 0 | 0 | 5.6 | 117 | 0.31 | 0 | 250 | 5 | 0 | 220 | 0 | 0 | 1120 | 0 | 6116.8 | 12880.09 | 84.1
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 35 | 54 | 68 | 80 | 0 | 0 | 35 | 90 | 0 | 330 | 126 | 300 | 0 | 17 | 0 | 263 | 0 | 0 | 25 | 0 | 16.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 14 | 0 | 50 | 0 | 0 | 118 | 17 | 2 | 360 | 0 | 0 | 0 | 0 | 29 | 222 | 0 | 0 | 0 | 1224 | 0 | 43 | 70 | 8 | 0 | 300 | 280 | 5 | 180 | 32 | 68 | 0 | 118 | 9 | 6 | 52 | 26 | 0 | 19 | 0 | 265 | 320 | 329 | 34 | 0 | 0 | 143 | 0 | 0 | 83 | 30 | 0 | 0 | 163 | 0 | 63 | 105 | 0 | 2 | 36.38 | 11 | 6727.88 | 921 | 208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.3 | 1234.2 | 0 | 1016 | 0 | 0 | 0 | 54 | 0 | 48 | 0 | 24 | 0 | 77 | 0 | 29.79 | 176 | 0 | 0 | 0 | 0 | 0 | 327 | 0 | 2.2 | 0 | 156 | 49 | 65 | 7 | 35 | 0 | 0 | 4.8 | 124 | 0.07 | 0 | 307 | 7 | 0 | 220 | 0 | 0 | 1190 | 0 | 6319.36 | 13047.24 | 84.22
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 332 | 0 | 0 | 35 | 35 | 70 | 80 | 0 | 0 | 35 | 86 | 0 | 330 | 143 | 300 | 0 | 17 | 0 | 296 | 0 | 0 | 25 | 0 | 17.5 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 24 | 0 | 50 | 0 | 1 | 150 | 17 | 5 | 360 | 0 | 0 | 0 | 0 | 51 | 222 | 0 | 0 | 0 | 1169 | 2 | 43 | 70 | 8 | 0 | 349 | 310 | 5 | 200 | 32 | 68 | 0 | 132 | 13 | 14 | 49 | 32 | 0 | 1 | 0 | 260 | 320 | 321 | 34 | 10 | 0 | 142 | 0 | 0 | 83 | 30 | 0 | 0 | 162 | 5 | 63 | 112 | 0 | 2 | 24.73 | 11 | 6867.23 | 920 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.64 | 1160 | 0 | 1014.06 | 0 | 40 | 0 | 70 | 0 | 48 | 0 | 27 | 0 | 54 | 0 | 28.07 | 176 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 2.67 | 0 | 156 | 49 | 70 | 10 | 35 | 0 | 0 | 0 | 136 | 0.12 | 0 | 250 | 5 | 0 | 220 | 0 | 0 | 1150 | 0 | 6193.56 | 13060.79 | 84.34
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 35 | 35 | 70 | 80 | 0 | 0 | 35 | 83 | 0 | 330 | 148 | 350 | 0 | 17 | 0 | 280 | 0 | 0 | 2 | 35 | 21 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 32 | 0 | 40 | 0 | 0 | 150 | 17 | 2 | 360 | 0 | 0 | 0 | 0 | 51 | 223 | 0 | 0 | 0 | 1153 | 2 | 43 | 70 | 8 | 0 | 353 | 335 | 5 | 188 | 26 | 68 | 0 | 126 | 13 | 14 | 50 | 28 | 0 | 2 | 0 | 265 | 320 | 358 | 34 | 10 | 0 | 151 | 0 | 0 | 81 | 30 | 0 | 0 | 162 | 17 | 63 | 112 | 0 | 0 | 21.9 | 11 | 6929.9 | 920 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.49 | 1164 | 0 | 1011.18 | 0 | 47 | 0 | 70 | 0 | 51 | 0 | 27 | 0 | 55 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 159 | 49 | 70 | 11 | 35 | 0 | 0 | 3.9 | 132 | 0.06 | 0 | 250 | 3 | 0 | 220 | 0 | 0 | 1180 | 0 | 6186.63 | 13116.53 | 84.46
16:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 312 | 0 | 0 | 28 | 35 | 70 | 80 | 0 | 0 | 35 | 54 | 0 | 330 | 149 | 350 | 0 | 17 | 0 | 280 | 0 | 0 | 0 | 35 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 50 | 0 | 0 | 115 | 17 | 5 | 360 | 0 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 1162 | 2 | 43 | 20 | 8 | 0 | 353 | 340 | 5 | 193 | 28 | 68 | 0 | 108 | 9 | 14 | 50 | 30 | 0 | 1 | 0 | 265 | 320 | 359 | 34 | 10 | 0 | 140 | 0 | 0 | 80 | 30 | 0 | 0 | 162 | 17 | 72 | 112 | 0 | 0 | 3.98 | 11 | 6796.98 | 921 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.32 | 1132 | 0 | 1010.06 | 0 | 46 | 0 | 35 | 0 | 54 | 0 | 28 | 0 | 36 | 0 | 2.54 | 173 | 0 | 0 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 152 | 49 | 35 | 10 | 35 | 0 | 0 | 3.8 | 61 | 0.07 | 0 | 250 | 6 | 0 | 220 | 0 | 0 | 1140 | 0 | 5969.79 | 12766.77 | 84.58
17:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 17 | 35 | 70 | 80 | 0 | 0 | 35 | 48 | 0 | 330 | 149 | 350 | 0 | 17 | 0 | 285 | 0 | 0 | 1 | 35 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 70 | 0 | 50 | 0 | 0 | 115 | 17 | 5 | 360 | 0 | 0 | 0 | 0 | 17 | 222 | 0 | 0 | 0 | 1064 | 0 | 43 | 20 | 8 | 0 | 349 | 340 | 5 | 195 | 30 | 68 | 0 | 93 | 9 | 14 | 51 | 32 | 0 | 3 | 0 | 265 | 320 | 300 | 34 | 10 | 0 | 135 | 0 | 0 | 79 | 30 | 0 | 0 | 163 | 17 | 72 | 116 | 22 | 0 | 0.86 | 12 | 6635.86 | 920 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.23 | 1082 | 0 | 926.21 | 0 | 45 | 0 | 35 | 0 | 54 | 0 | 28 | 0 | 11 | 0 | 4 | 171 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 | 0 | 133 | 49 | 35 | 8 | 35 | 0 | 0 | 1.9 | 18 | 0.06 | 0 | 250 | 6 | 0 | 220 | 0 | 0 | 1050 | 0 | 5719.4 | 12355.26 | 84.7
18:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 0 | 17 | 43 | 70 | 80 | 0 | 0 | 35 | 47 | 0 | 300 | 131 | 300 | 0 | 17 | 0 | 267 | 0 | 0 | 1 | 52 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 70 | 0 | 64 | 0 | 0 | 113 | 17 | 9 | 360 | 0 | 0 | 0 | 0 | 17 | 223 | 0 | 0 | 0 | 1051 | 0 | 43 | 20 | 8 | 0 | 300 | 340 | 18 | 182 | 27 | 68 | 0 | 91 | 20 | 14 | 47 | 26 | 0 | 1 | 0 | 265 | 320 | 300 | 34 | 20 | 0 | 130 | 0 | 0 | 80 | 30 | 0 | 18 | 162 | 17 | 72 | 118 | 22 | 0 | 0.11 | 12 | 6573.11 | 920 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.07 | 1064 | 0 | 1011.77 | 0 | 44 | 0 | 35 | 0 | 54 | 0 | 28 | 0 | 9 | 0 | 3.46 | 172 | 0 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 180 | 49 | 35 | 3 | 35 | 0 | 0 | 0.7 | 6 | 0.01 | 0 | 250 | 6 | 40 | 220 | 0 | 0 | 1050 | 0 | 5787.01 | 12360.12 | 84.75
19:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 29 | 54 | 88 | 145 | 95 | 0 | 35 | 72 | 10 | 350 | 144 | 250 | 0 | 17 | 0 | 285 | 0 | 0 | 0 | 70 | 21 | 22 | 0 | 0 | 0 | 30 | 0 | 0 | 10 | 33 | 70 | 0 | 64 | 12 | 0 | 148 | 17 | 12 | 360 | 5 | 0 | 6 | 4 | 17 | 223 | 0 | 0 | 0 | 1160 | 0 | 51 | 46 | 8 | 0 | 285 | 280 | 45 | 195 | 30 | 74 | 0 | 106 | 28 | 14 | 65 | 32 | 22 | 0 | 48 | 270 | 320 | 360 | 34 | 20 | 0 | 130 | 0 | 0 | 82 | 30 | 0 | 18 | 162 | 17 | 72 | 111 | 18 | 0 | 0 | 12 | 7280 | 873 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 988 | 27 | 1123.42 | 0 | 40 | 0 | 35 | 0 | 95 | 35 | 28 | 8 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 343 | 0 | 0 | 0 | 185 | 50 | 110 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 60 | 180 | 0 | 0 | 960 | 11 | 5824.42 | 13104.42 | 84.95
19:30 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 35 | 54 | 110 | 145 | 0 | 0 | 21 | 125 | 16 | 350 | 128 | 350 | 0 | 17 | 0 | 264 | 0 | 0 | 0 | 70 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 33 | 60 | 0 | 78 | 0 | 0 | 115 | 0 | 15 | 360 | 0 | 0 | 0 | 8 | 8 | 225 | 0 | 0 | 0 | 1180 | 0 | 51 | 50 | 8 | 0 | 354 | 325 | 47 | 180 | 33 | 115 | 0 | 158 | 28 | 14 | 90 | 32 | 52.2 | 0 | 46 | 265 | 320 | 338 | 33 | 20 | 0 | 139 | 0 | 0 | 82 | 30 | 0 | 18 | 162 | 17 | 72 | 111 | 18 | 0 | 0 | 12 | 7507.2 | 873 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1035 | 17 | 1234.3 | 0 | 0 | 0 | 35 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 190 | 50 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 65 | 220 | 0 | 0 | 1020 | 0 | 5996.3 | 13503.5
20:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 36 | 54 | 102 | 145 | 0 | 0 | 17 | 108 | 20 | 350 | 152 | 350 | 0 | 0 | 0 | 281 | 0 | 0 | 0 | 70 | 21 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 33 | 8 | 0 | 12 | 0 | 0 | 115 | 0 | 18 | 360 | 0 | 0 | 0 | 8 | 0 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 8 | 8 | 0 | 300 | 330 | 47 | 191 | 33 | 114 | 0 | 164 | 28 | 14 | 98 | 30 | 8 | 0 | 0 | 265 | 320 | 360 | 34 | 30 | 0 | 148 | 0 | 0 | 82 | 30 | 0 | 18 | 162 | 0 | 73 | 112 | 16 | 0 | 0 | 12 | 7327 | 873 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1057 | 0 | 1262.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 200 | 50 | 115 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 65 | 220 | 0 | 0 | 1100 | 0 | 6005.13 | 13332.13 | 85.15
21:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 54 | 69 | 145 | 0 | 0 | 0 | 17 | 0 | 400 | 150 | 400 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 70 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 0 | 25 | 360 | 0 | 0 | 0 | 8 | 0 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 47 | 202 | 33 | 115 | 0 | 172 | 29 | 14 | 106 | 38 | 8 | 0 | 0 | 265 | 320 | 360 | 34 | 30 | 0 | 155 | 0 | 0 | 83 | 30 | 0 | 18 | 162 | 0 | 73 | 112 | 16 | 0 | 0 | 12 | 7311 | 922 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 0 | 1317.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 200 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 65 | 220 | 0 | 0 | 1232 | 0 | 6320.03 | 13631.03 | 85.35
22:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0 | 0 | 54 | 64 | 145 | 0 | 0 | 0 | 15 | 0 | 400 | 149 | 400 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 70 | 22 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 29 | 360 | 0 | 0 | 0 | 8 | 0 | 221 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 48 | 199 | 33 | 115 | 0 | 156 | 29 | 14 | 100 | 38 | 8 | 0 | 0 | 265 | 320 | 371 | 34 | 30 | 0 | 152 | 0 | 0 | 83 | 30 | 0 | 18 | 162 | 0 | 73 | 112 | 22 | 0 | 0 | 12 | 7307 | 922 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1365.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 200 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 65 | 220 | 0 | 0 | 1244 | 0 | 6442.11 | 13749.11 | 85.55
23:00 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 54 | 66 | 145 | 0 | 0 | 0 | 15 | 0 | 400 | 150 | 400 | 0 | 0 | 0 | 295 | 0 | 0 | 0 | 70 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 26 | 360 | 0 | 0 | 0 | 8 | 0 | 222 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 354 | 340 | 51 | 198 | 31 | 115 | 0 | 158 | 29 | 14 | 107 | 38 | 8 | 0 | 0 | 260 | 320 | 375 | 34 | 30 | 0 | 153 | 0 | 0 | 83 | 28 | 0 | 18 | 162 | 0 | 73 | 110 | 22 | 0 | 0 | 12 | 7322 | 921 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1112 | 0 | 1374.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 201 | 50 | 115 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 60 | 220 | 0 | 0 | 1244 | 0 | 6447.27 | 13769.27 | 85.75
Total KWH | 0 | 1218547 | 482875 | 0 | 0 | 0 | 0 | 0 | 8107200 | 0 | 0 | 635256 | 1212840 | 1866096 | 2303520 | 268473 | 0 | 452791 | 1306080 | 282240 | 8075500 | 3450502 | 7660000 | 0 | 242506 | 0 | 6843130 | 0 | 0 | 147017 | 735600 | 462600 | 408600 | 0 | 0 | 21164 | 99862 | 0 | 0 | 559680 | 217041 | 447112 | 0 | 929280 | 59620 | 1359 | 2634960 | 458325 | 266880 | 8669090.91 | 1672 | 0 | 108480 | 90045 | 588800 | 5117185 | 0 | 0 | 0 | 28374543 | 19980 | 1118104 | 995272 | 184000 | 0 | 8431800 | 8026000 | 397440 | 4761000 | 525456 | 2011200 | 0 | 3252960 | 342720 | 289680 | 1868460 | 801600 | 126720 | 89491 | 220960 | 6172000 | 7067700 | 8063000 | 813000 | 220000 | 0 | 3423027 | 5232 | 0 | 1962240 | 713760 | 0 | 126000 | 4417540 | 166320 | 1401600 | 2522400 | 97920 | 7700 | 130440 | 286080 | 165865273.91 | 22053090 | 4943808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20304 | 375840 | 27410910 | 206020 | 25934947 | 0 | 250451 | 0 | 715008 | 0 | 586992 | 69024 | 172497 | 4531 | 585484 | 30935 | 249752 | 4244545 | 0 | 0 | 0 | 0 | 0 | 8721600 | 0 | 20940 | 0 | 4140000 | 1114036 | 1142629 | 120712 | 631881 | 0 | 0 | 28659.36 | 951840 | 2224 | 0 | 6371000 | 174055 | 387000 | 5403540 | 0 | 0 | 28474181.82 | 414000 | 145952436.18 | 311817710.09

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 01-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12880.09 | MW | 12:00 Hr. | Energy Generated |  |  | 311.8177 |  | MKWHr.
| Day Peak Demand |  |  | 12880.09 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.434 |  | MKWHr.
| Evening Peak Generation |  |  | 13631.03 | MW | 21:00 Hr. | Energy Demand |  |  | 312.2517 |  | MKWHr.
| Evening Peak Demand |  |  | 13631.03 | MW | 21:00 Hr. | Maximum Temperature |  |  | 32.1 |  | °C
| Minimum Generation of the Day |  |  | 11687.91 | MW | 06:00 Hr. | Total Gas Supplied |  |  | 891.3 |  | MMCFD
| Maximum Generation of the Day |  |  | 14473.2 | MW | 00:00 Hr. | Production Cost per KWHr |  |  | 6.5216 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 35.0075 | 0 | 11.0068 | 0 | 0 | 0.14702 | 0 | 0 | 46.1614 | Gas | 121.081 | Gas | 426587397.31
| Chattogram Zone |  |  | 5.3841 | 37.0436 | 3.0214 | 0 | 2.635 | 0.021339 | 0 | 0.55968 | 48.6651 | Coal | 104.5538 | Coal | 725818390.4794
| Cumilla Zone |  |  | 23.7335 | 0 | 8.8183 | 0 | 0 | 0.089491 | 0.8016 | 0 | 33.4429 | HFO | 31.4672 | HFO | 581836914.77
| Mymensingh Zone |  |  | 0.09792 | 0 | 4.3764 | 0 | 0 | 0.13814 | 0 | 0 | 4.6125 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 32.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.9835 | Hydro | 2.635 | Hydro | 263496
| Khulna Zone |  |  | 4.9438 | 27.4109 | 0.22632 | 0 | 0 | 0.37584 | 22.0531 | 0 | 55.01 | Solar | 2.7314 | Solar | 45250032.0396
| Barishal Zone |  |  | 5.9646 | 34.8452 | 0.414 | 0 | 0 | 0.002224 | 0 | 0 | 41.226 | Import | 48.7896 | Import | 245610246.26
| Rajshahi Zone |  |  | 12.9661 | 0 | 1.8294 | 0 | 0 | 0.85618 | 25.9349 | 0 | 41.5867 | Wind | 0.55968 | Wind | 8193715.2
| Rangpur Zone |  |  | 0 | 5.254 | 1.7745 | 0 | 0 | 1.1012 | 0 | 0 | 8.1298
| Total |  |  | 121.081 | 104.5538 | 31.4672 | 0 | 2.635 | 2.7314 | 48.7896 | 0.55968 | 311.8177
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 426587397.31 |  | Hydro | 263496
|  |  |  | Coal | 725818390.4794 |  | Solar | 45250032.0396
|  |  |  | HFO | 581836914.77 |  | Import | 245610246.26
|  |  |  | HSD | 0 |  | Wind | 8193715.2
[5 empty] | Total: | 203,35,60,192 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.0531 | Peak Hr Flow | 922.00 MW at 21:00 hrs.
Energy Flow from West to East: |  |  | KWHr: | 41360436.44 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.9349 | Peak Hr Flow | 1317.03 MW at 21:00 hrs.
Power Flow during Peak Demand: |  |  | MW: | 806 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.8016 | Peak Hr Flow | 38.00 MW at 21:00 hrs.
Maximum Power Flow: |  |  | MW: | 932 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.7896 | Peak Hr Flow | 2277.03 MW at 21:00 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (21:00 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 4984
|  |  |  | Chattogram |  | 0 |  | 1162
|  |  |  | Cumilla |  | 0 |  | 1293
|  |  |  | Mymensingh |  | 0 |  | 1070
|  |  |  | Sylhet |  | 0 |  | 500
|  |  |  | Khulna |  | 0 |  | 1592
|  |  |  | Barishal |  | 0 |  | 476
|  |  |  | Rajshahi |  | 0 |  | 1145
|  |  |  | Rangpur |  | 0 |  | 917
|  |  |  | Total |  | 0 |  | 13139
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
| 08:17 | 08:17 | Sylhet 132/33kV S/S T1 LT Tripped showing 51 relays Due to Ins OC | [7 empty] | 13.0MW load
interrup.
| 08:27 | 09:46 | Hathazari-Madunaghat 132kV Ckt-2 Tripped from Madunaghat 132/33kV end showing REL-670
relays Due to general trip,zone-1,zcom,R-Phase
| 08:52 | 09:18 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Relay relays.
| 10:40 | 12:52 | Mymensingh 132/33kV S/S Transformer-1 (404T) LT Scheduled S/D Due to High temperature
maintenance.
| 10:40 | 12:52 | Mymensingh 132/33kV S/S Transformer-1 (404T) HT Scheduled S/D Due to High temperature
maintenance.
| 10:51 |  | At Gopalgonj (N) S/S 400 KV Dia -07 ( Pooppur Bay ) Shut-down.
| 11:36 | 11:54 | Bhaluka 132/33kV S/S Transformer-03 LT Tripped showing 50/51 relays Due to 33kv Beacon | [7 empty] | 17.0MW load
|  |  | feeder not trip. | [7 empty] | interrup.
| 12:00 |  | Day peak generation 12878 MW
| 12:16 |  | Bibiyana-III 400 MW CCPP, FGMO is ON with remarks:-
| 12:30 | 13:16 | Mymensingh RPCL-Tangail 132kV Ckt-2 Forced S/D from Ghatail 132/33kV end.
| 12:40 | 17:37 | Shikalbaha 230/132kV S/S Intermediate-2 Tripped showing F1 & F2 relays.
| 12:55 | 16:10 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to High temperature
maintenance
| 12:55 | 16:10 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT Scheduled S/D Due to High temperature
maintenance
| 13:13 | 13:51 | Satkhira 132/33kV S/S Transformer-2 (T-2) HT Tripped showing Lock out relay relays Due to | [7 empty] | 64.0MW load
|  |  | Winding temperature trip. | [7 empty] | interrup.
| 14:15 | 14:58 | Faridpur 132/33kV S/S Transformer-1 LT Tripped showing 33kV O/C & 33kV E/F relays Due to | [7 empty] | 63.0MW load
|  |  | 33kV Modhukhali wz & 33kV Goalondo wz feeder fault. | [7 empty] | interrup.
| 14:15 | 14:59 | Faridpur 132/33kV S/S Transformer-2 LT Tripped showing 33kV O/C & 33kV E/F relays Due to | [7 empty] | 63.0MW load
|  |  | 33kV Modhukhali wz & 33kV Goalondo wz feeder fault | [7 empty] | interrup.
| 14:16 | 14:50 | Bakulia-Sikalbaha 132 kV Ckt-1 Tripped from Bakulia 132/33kV end showing Siemens relays.
and from Shikalbaha 230/132kV end showing F1 relays.
| 14:23 | 14:43 | Bakulia-Sikalbaha 132 kV Ckt-2 Tripped from Shikalbaha 230/132kV end showing F1 relays
Due to None and from Bakulia 132/33kV end showing Siemens relays.
| 15:48 | 21:06 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to Jack Bus repair
| 15:48 | 21:06 | Sreepur 230/132/33kV S/S 132/33 kV T-1 LT Scheduled S/D Due to Jack Bus repair | [7 empty] | 35.0MW load
interrup.
| 17:00 |  | Khagrachori 132/33kV S/S TR-1 LT Forced S/D Due to Burning of 33kV T-01 ( R phase )
incomer underground cable
| 17:02 | 18:23 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to T-1 33kv bus s/d | [7 empty] | 11.0MW load
interrup.
| 17:02 | 18:23 | Palashbari 132/33kV S/S TR1-414T LT Forced S/D Due to T-1 33kv bus s/d | [7 empty] | 11.0MW load
interrup.
| 17:02 |  | Khagrachori 132/33kV S/S TR-1 HT Forced S/D Due to Burning of 33 kV T-01 incomer ( R
phase ) underground cable
| 17:02 | 18:40 | Faridpur 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Red hot | [7 empty] | 40.0MW load
interrup.
| 17:02 | 18:40 | Faridpur 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Red hot | [7 empty] | 40.0MW load
interrup.
| 17:03 | 18:22 | Palashbari 132/33kV S/S TR1-414T HT Forced S/D Due to T-1 33kv bus s/d | [7 empty] | 11.0MW load
interrup.
| 18:50 |  | Muradnagar 132/33kV S/S 132KV Transformar-01 HT Forced S/D Due to Red Hot
| 19:33 |  | Laxmipur 132/33kV T1 (80/120MVA) transformer was switched on without load at 19:33hr. for
the first time.
| 19:50 | 00:08 | Madanganj 132/33kV S/S GT-2 LT Tripped showing Phase inst relay relays Due to For 33 kv | [7 empty] | 18.0MW load
|  |  | Mirkadim-1 feeder trip | [7 empty] | interrup.
| 19:50 | 20:14 | Madanganj 132/33kV S/S GT-1 LT Tripped showing Over current relay relays Due to For 33 kv | [7 empty] | 18.0MW load
|  |  | Mirkadim-1 feeder trip | [7 empty] | interrup.
| 19:50 | 20:10 | Madanganj 132/33kV S/S GT-1 HT Tripped showing Backup protection trip relays Due to For | [7 empty] | 18.0MW load
|  |  | 33kv Mirkadim -1 feeder trip | [7 empty] | interrup.
| 19:50 | 23:58 | Madanganj 132/33kV S/S GT-2 HT Tripped showing Backup protection trip relays Due to For | [7 empty] | 18.0MW load
|  |  | 33 kv Mirkadim-1 feeder trip | [7 empty] | interrup.
| 21:00 |  | Evening peak Generation is 13631 MW
| 22:19 | 23:17 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to Redhot 33kv CB | [7 empty] | 18.0MW load
interrup.
| 22:20 | 23:17 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to redhot 33kv CB | [7 empty] | 18.0MW load
interrup.
| 00:20 |  | Madanganj 132/33kV S/S GT-2 LT Tripped showing Phase inst fault relays Due to PBS 33 kv
T2 feeder fault
| 00:20 |  | Madanganj 132/33kV S/S GT-2 HT Tripped showing Backup protection trip relays Due to PBS
33 kv T2 feeder fault
| 06:40 |  | Magura 132/33kV S/S T-2 (415T) HT Scheduled S/D Due to 33kV CB of Rawtara feeder replace | [7 empty] | 17.0MW load
interrup.
| 07:00 |  | Minimum generation 10593 MW
| 07:06 |  | Madaripur 132/33kV S/S T3-426T LT Scheduled S/D Due to Hot Spot maintenance
| 07:06 |  | Madaripur 132/33kV S/S T3-426T HT Scheduled S/D Due to Hot spot maintenance
| 07:07 | 07:58 | Bhangura 132/33kV S/S Tr-2(413T) LT Forced S/D Due to 33KV feeder Sky wire | [7 empty] | 12.0MW load
|  |  | maintenance(pbs) | [7 empty] | interrup.
| 07:10 | 07:57 | Bhangura 132/33kV S/S Tr-2(413T) HT Forced S/D Due to 33KV feeder Sky wire | [7 empty] | 12.0MW load
|  |  | maintenance(pbs) | [7 empty] | interrup.
| 07:33 |  | Haripur-Madanganj 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Distance Realy
Trip(21), DEF Trip (21), AIDED TRIP relays.
| 07:54 |  | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Red hot | [7 empty] | 6.0MW load
interrup.
| 07:54 |  | Faridpur 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Red hot | [7 empty] | 6.0MW load
interrup.
| 07:59 |  | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Red hot | [7 empty] | 20.0MW load
interrup.
| 07:59 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot | [7 empty] | 20.0MW load
interrup.
| 07:59 |  | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Red hot | [7 empty] | 20.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 01-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 362 | 8107200 | FGMO
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8075500 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3450502 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 295 | 6843130 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 0 | 635256 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 2303520 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 0 | 452791 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 0 | 242506 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 22 | 462600 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 408600 | -
24 | Rupganj 33 MW PP(Summit) |  | IPP | 4*8.73 | 33 | 0 | 0 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 482875 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 268473 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 69 | 1866096 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1218547 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 0 | 282240 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 1306080 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 147017 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 1212840 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 400 | 7660000 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 70 | 735600 | -
Dhaka Area Total |  |  |  |  | 5972.724 | 2127 | 46161373
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 90045 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 19980 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 108480 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 115 | 2634960 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 222 | 5117185 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 0 | 588800 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 447112 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 217041 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 0 | 929280 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 25 | 266880 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 1359 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 0 | 99862 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 0 | 458325 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 59620 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 21164 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 1672 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1224 | 28374543 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 14 | 559680 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 360 | 8669090.91 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 1968 | 48665078.91
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 202 | 4761000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 355 | 8431800 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8026000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 525456 | machine problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 47 | 397440 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 36 | 184000 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 51 | 1118104 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 0 | 995272 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 220960 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 172 | 3252960 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 801600 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 8 | 126720 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 14 | 289680 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 106 | 1868460 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 29 | 342720 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 2011200 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 89491 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1546 | 33442863
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 16 | 97920 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 7700 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 112 | 2522400 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 73 | 1401600 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 130440 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 286080 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 0 | 166320 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 213 | 4612460
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 34 | 813000 | -
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 220000 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3423027 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 713760 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1962240 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 4417540 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 126000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 0 | 5232 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 6172000 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 360 | 8063000 | Load can't given Full, due to to Gas shortage
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7067700 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1457 | 32983499
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 922 | 22053090 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 252 | 4943808 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 206020 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 20304 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 375840 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | -
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1061 | 27410910 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2235 | 55009972
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 9 | 174055 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 65 | 387000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1232 | 28474181.82 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5403540 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 414000 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 250 | 6371000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2224 | -
Barishal Area Total |  |  |  |  | 2236 | 1776 | 41226000.82
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 250451 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 172497 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 179 | 4244545 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 414 | 8721600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 30935 | Engine Problem
128 | Ullapara 11 MW PP (Summit) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 4531 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 586992 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 0 | 715008 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 69024 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 20940 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1317.03 | 25934947 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 249752 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 585484 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1910.03 | 41586706
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1114036 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4140000 | Machine Problem
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 631881 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 28659.36 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 115 | 1142629 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 120712 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 951840 | -
Rangpur Area Total |  |  |  |  | 950 | 399 | 8129757.36
Eastern Grid Total |  |  |  |  | 16738.895 | 7311 | 165865273.91
Western Grid Total |  |  |  |  | 10338.16 | 6320.03 | 145952436.18
National Grid Total |  |  |  |  | 27077.055 | 13631.03 | 311817710.09
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 01-06-2025
Zone Total Scenario at Evening Peak Hour (21:00 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9009.13 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4129 | MW
i) Dhaka area |  |  | 4984.49 |  | MW | i) Khulna area |  |  |  | 1591.5 | MW
ii) Chattogram area |  |  | 1162 |  | MW | ii) Barishal area |  |  |  | 475.5 | MW
iii) Cumilla area |  |  | 1292.64 |  | MW | iii) Rajshahi area |  |  |  | 1145 | MW
iv) Mymensingh area |  |  | 1070 |  | MW | iv) Rangpur area |  |  |  | 917 | MW
v) Sylhet area |  |  | 500 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 13138.13 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 24 | 18:30 | 67 | Ishurdi | 87 | 15:00 | 133 | Patuakhali | 86 | 00:00
2 | AKSML | 107 | 13:00 | 68 | Jaldhaka | 75 | 21:00 | 134 | Payra | 34 | 00:00
3 | Aftabnagar | 36 | 09:00 | 69 | Jamalpur | 112 | 21:00 | 135 | Postogola | 55 | 11:00
4 | Agargaon | 129 | 10:00 | 70 | Jashore | 146 | 13:00 | 136 | Purbachal | 19 | 00:00
5 | Agrabad | 94 | 18:00 | 71 | Jhenaidah | 128 | 00:00 | 137 | Purbasadipur | 144 | 00:00
6 | Amnura | 37 | 00:00 | 72 | Joydebpur | 149 | 21:00 | 138 | Rahanpur | 32 | 00:00
7 | Ashuganj | 90 | 03:00 | 73 | Joypurhat | 64 | 01:00 | 139 | Rahim | 43 | 00:00
8 | BSRM | 192 | 06:00 | 74 | Juldah | 13 | 00:00 | 140 | Rajbari | 81 | 19:30
9 | Bagerhat | 89 | 19:00 | 75 | KSRM | 23 | 05:00 | 141 | Rajendrapur | 143 | 09:00
10 | Bajitpur | 46 | 22:00 | 76 | Kabirpur | 262 | 16:00 | 142 | Rajshahi | 107 | 19:30
11 | Bakulia | 87 | 00:00 | 77 | Kachua | 91 | 00:00 | 143 | Rajshahi-230 | 99 | 15:00
12 | Banani | 36 | 10:00 | 78 | Kallyanpur | 108 | 19:00 | 144 | Ramganj | 116 | 00:00
13 | Bangabhaban | 19 | 10:00 | 79 | Kalurghat | 40 | 16:00 | 145 | Rampur | 36 | 23:00
14 | Barapukuria | 68 | 00:00 | 80 | Kamrangirchar | 64.1 | 13:00 | 146 | Rangamati | 15 | 17:00
15 | Barguna | 24 | 23:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 145 | 13:00
16 | Barishal | 116 | 00:00 | 82 | Kasba | 33 | 21:00 | 148 | Ruppur | 9.2 | 15:00
17 | Barishal-230 | 102 | 22:00 | 83 | Kazla | 97 | 12:00 | 149 | SSM | 15 | 07:00
18 | Baroaulia | 45 | 00:00 | 84 | Keranigonj | 75 | 00:00 | 150 | Saidpur | 122 | 14:00
19 | Baroirhat | 60 | 19:30 | 85 | Khagrachori | 24 | 19:00 | 151 | Satkhira | 148 | 00:00
20 | Bashundhara | 181 | 11:00 | 86 | Khulna | 72 | 14:00 | 152 | Satmasjid | 100 | 11:00
21 | BashundharaCement | 8 | 19:00 | 87 | Khulshi | 169 | 19:30 | 153 | Savar | 222 | 11:00
22 | Beanibazar | 72 | 21:00 | 88 | Kishoreganj | 132 | 22:00 | 154 | SevenRings | 14.52 | 00:00
23 | Benapole | 66 | 00:00 | 89 | Kodda | 302 | 18:00 | 155 | ShahCement | 22 | 21:00
24 | Bhaluka | 149 | 19:00 | 90 | Kulaura | 40 | 23:00 | 156 | Shahjadpur | 78 | 12:00
25 | Bhandaria | 58 | 00:00 | 91 | Kurigram | 60 | 19:30 | 157 | Shahjibazar | 115 | 22:00
26 | Bhangura | 36 | 01:00 | 92 | Kushtia | 164 | 00:00 | 158 | Shahmirpur | 46 | 23:00
27 | Bheramara(GK) | 70 | 22:00 | 93 | Lalbag | 58 | 13:00 | 159 | Shariatpur | 89 | 00:00
28 | Bhulta | 267 | 08:00 | 94 | Lalmonirhat | 48 | 19:00 | 160 | Sherpur | 132 | 19:00
29 | Bog-Sherpur | 68 | 00:00 | 95 | MI_Cement | 17.5 | 08:00 | 161 | Shikalbaha | 28 | 00:00
30 | Bogura | 168 | 01:00 | 96 | Madanganj | 48 | 00:00 | 162 | Shitalakhya | 89.9 | 11:00
31 | Borhanuddin | 87 | 23:00 | 97 | Madaripur | 113 | 00:00 | 163 | Sholosohor | 43 | 13:00
32 | Brahmanbaria | 123 | 22:00 | 98 | Madartek | 85.81 | 00:00 | 164 | Shyampur | 182 | 10:00
33 | Cantonment | 143 | 10:00 | 99 | Madunaghat | 58 | 00:00 | 165 | Siddhirganj | 115 | 09:00
34 | Chandina | 22.37 | 00:00 | 100 | Magura | 60 | 00:00 | 166 | Sirajganj | 104 | 10:00
35 | Chandpur | 82 | 23:00 | 101 | Mahasthangarh | 84 | 00:00 | 167 | Sonargaon | 107 | 00:00
36 | Chandraghona | 31 | 00:00 | 102 | Manikganj | 127 | 22:00 | 168 | Sreemongol | 61 | 23:00
37 | Chapai | 74 | 00:00 | 103 | Maniknagar | 80 | 10:00 | 169 | Sreepur | 97 | 08:00
38 | Charsaidpur | 45 | 12:00 | 104 | Matarbari | 46 | 00:00 | 170 | Srinagar | 43.69 | 01:00
39 | Chauddagram | 66 | 01:00 | 105 | Matuail | 65 | 09:00 | 171 | Sunamganj | 50 | 22:00
40 | Chhatak | 31 | 22:00 | 106 | Millgate | 95 | 10:00 | 172 | Sylhet | 40 | 22:00
41 | Chowmuhani | 219 | 19:00 | 107 | Mirpur | 114 | 11:00 | 173 | Sylhet-132 | 100 | 21:00
42 | Chuadanga | 119 | 00:00 | 108 | Mirsorai | 9 | 18:30 | 174 | TK | 32 | 00:00
43 | Coxsbazar | 124 | 00:00 | 109 | Mirzapur | 42 | 09:00 | 175 | Tangail | 160 | 21:00
44 | Cumilla(N) | 151 | 01:00 | 110 | Mithapukur | 74 | 00:00 | 176 | Thakurgaon | 111 | 20:00
45 | Cumilla(S) | 156 | 03:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 127 | 15:00
46 | Daudkandi | 148 | 21:00 | 112 | Mogbazar | 149.6 | 11:00 | 178 | Ullahpara | 37 | 13:00
47 | Dhaka | 64 | 11:00 | 113 | Mongla | 42 | 19:00 | 179 | Ullon | 36 | 00:00
48 | Dhamrai | 134 | 09:00 | 114 | Motijheel | 39 | 11:00 | 180 | Uttara | 75 | 11:00
49 | Dhanmondi | 146.4 | 11:00 | 115 | Muktagacha | 32 | 22:00 | 181 | UttaraNew | 54 | 00:00
50 | Dohazari | 85 | 02:00 | 116 | Munshiganj | 114 | 00:00 | 182 | Zigatola | 69 | 11:00
51 | Faridpur | 158 | 00:00 | 117 | Muradnagar | 30 | 21:00
52 | Fatullah | 100 | 11:00 | 118 | Mymensingh | 183 | 22:00
53 | Fenchuganj | 30 | 20:00 | 119 | Naogaon | 143 | 00:00
54 | Feni | 118 | 00:00 | 120 | Narail | 57 | 03:00
55 | GPH | 89 | 02:00 | 121 | Narinda | 76 | 12:00
56 | Ghatail | 70 | 18:30 | 122 | Narshingdi | 160 | 03:00
57 | Ghorashal | 14 | 19:00 | 123 | Natore | 159 | 00:00
58 | Ghorashal-230 | 93 | 01:00 | 124 | Nawabganj | 53.8 | 22:00
59 | Goalpara | 42 | 00:00 | 125 | Netrakona | 106 | 21:00
60 | Gollamari | 100 | 00:00 | 126 | New | 91 | 10:00
61 | Gopalganj | 107 | 00:00 | 127 | Niamatpur | 74 | 00:00
62 | Gulshan | 122 | 10:00 | 128 | Noapara | 49 | 00:00
63 | Halishahar | 99 | 01:00 | 129 | PHP | 2 | 00:00
64 | HaripurSBU | 170 | 10:00 | 130 | Pabna | 124 | 19:30
65 | Hasnabad | 75 | 00:00 | 131 | Palashbari | 102 | 00:00
66 | Hathazari | 79 | 20:00 | 132 | Panchagarh | 62 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 01-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 14473.2 | 74 |  | 14550.2
1:00 | 13644.7 | 88 |  | 13736.66
2:00 | 13068.2 | 79 |  | 13151.2
3:00 | 12697.2 | 52 |  | 12751.2
4:00 | 12360.7 | 57 |  | 12420.7
5:00 | 12196.7 | 52 |  | 12250.7
6:00 | 11687.91 | 32 |  | 11720.91
7:00 | 11788.45 | 0 |  | 11788.45
8:00 | 11803.64 | 0 |  | 11803.64
9:00 | 12244.69 | 0 |  | 12244.69
10:00 | 12435.7 | 0 |  | 12435.7
11:00 | 12637.21 | 0 |  | 12637.21
12:00 | 12880.09 | 0 |  | 12880.09
13:00 | 13047.24 | 0 |  | 13047.24
14:00 | 13060.79 | 0 |  | 13060.79
15:00 | 13116.53 | 0 |  | 13116.53
16:00 | 12766.77 | 0 |  | 12766.77
17:00 | 12355.26 | 0 |  | 12355.26
18:00 | 12360.12 | 0 |  | 12360.12
19:00 | 13104.42 | 0 |  | 13104.42
19:30 | 13503.5 | 0 |  | 13503.5
20:00 | 13332.13 | 0 |  | 13332.13
21:00 | 13631.03 | 0 |  | 13631.03
22:00 | 13749.11 | 0 |  | 13749.11
23:00 | 13769.27 | 0 |  | 13769.27
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 01-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7812 | 6661.2 | 14473.2 | DAILY GENERATION CURVE
00:30 | 7576.75 | 6482.2 | 14058.95
01:00 | 7341.5 | 6303.2 | 13644.7 | 01-06-2025
01:30 | 7203.25 | 6153.2 | 13356.45
02:00 | 7065 | 6003.2 | 13068.2
02:30 | 6935.5 | 5947.2 | 12882.7
03:00 | 6806 | 5891.2 | 12697.2
03:30 | 6671.75 | 5857.2 | 12528.95
04:00 | 6537.5 | 5823.2 | 12360.7
04:30 | 6465.5 | 5813.2 | 12278.7
05:00 | 6393.5 | 5803.2 | 12196.7
05:30 | 6229.25 | 5713.055 | 11942.305
06:00 | 6065 | 5622.91 | 11687.91
06:30 | 6071.5 | 5666.68 | 11738.18
07:00 | 6078 | 5710.45 | 11788.45
07:30 | 6092.54 | 5703.505 | 11796.045
08:00 | 6107.08 | 5696.56 | 11803.64
08:30 | 6285.345 | 5738.82 | 12024.165
09:00 | 6463.61 | 5781.08 | 12244.69
09:30 | 6451 | 5889.195 | 12340.195
10:00 | 6438.39 | 5997.31 | 12435.7
10:30 | 6550.955 | 5985.5 | 12536.455
11:00 | 6663.52 | 5973.69 | 12637.21
11:30 | 6713.405 | 6045.245 | 12758.65
12:00 | 6763.29 | 6116.8 | 12880.09
12:30 | 6745.585 | 6218.08 | 12963.665
13:00 | 6727.88 | 6319.36 | 13047.24
13:30 | 6797.555 | 6256.46 | 13054.015
14:00 | 6867.23 | 6193.56 | 13060.79
14:30 | 6898.565 | 6190.095 | 13088.66
15:00 | 6929.9 | 6186.63 | 13116.53
15:30 | 6863.44 | 6078.21 | 12941.65
16:00 | 6796.98 | 5969.79 | 12766.77
16:30 | 6716.42 | 5844.595 | 12561.015
17:00 | 6635.86 | 5719.4 | 12355.26
17:30 | 6604.485 | 5753.205 | 12357.69
18:00 | 6573.11 | 5787.01 | 12360.12
18:30 | 6926.555 | 5805.715 | 12732.27
19:00 | 7280 | 5824.42 | 13104.42
19:30 | 7507.2 | 5996.3 | 13503.5
20:00 | 7327 | 6005.13 | 13332.13
20:30 | 7319 | 6162.58 | 13481.58 |  | Executive Engineer
21:00 | 7311 | 6320.03 | 13631.03 |  | Network Operation Division
21:30 | 7309 | 6381.07 | 13690.07
22:00 | 7307 | 6442.11 | 13749.11
22:30 | 7314.5 | 6444.69 | 13759.19
23:00 | 7322 | 6447.27 | 13769.27

## En-Curve
QF-LDC-12
Date | 01-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3174 | 1518 | 917 | 0 | 42 | 1159 | 83 | 4564.2 | 0 | 532 | 2461 | 0 | 0 | 23 | 74 | DAILY ENERGY CURVE
00:30 | 3130 | 1528.75 | 917 | 0 | 39 | 1140.5 | 83 | 4531.2 | 18 | 459.5 | 2191 | 0 | 0 | 21 | 81 | 01-06-2025
01:00 | 3086 | 1539.5 | 917 | 0 | 36 | 1122 | 83 | 4498.2 | 36 | 387 | 1921 | 0 | 0 | 19 | 88
01:30 | 3100.5 | 1542.5 | 917 | 0 | 37 | 1068 | 83 | 4497.7 | 18 | 333.75 | 1736.5 | 0 | 0 | 22.5 | 83.5 | Energy Generated | 311.8177 |  | MKWHr
02:00 | 3115 | 1545.5 | 917 | 0 | 38 | 1014 | 83 | 4497.2 | 0 | 280.5 | 1552 | 0 | 0 | 26 | 79 | Energy not Served | 0.434 |  | MKWHr
02:30 | 3125 | 1540 | 917 | 0 | 38 | 1014.5 | 83 | 4499.2 | 0 | 245.5 | 1397.5 | 0 | 0 | 23 | 65.5 | Total Energy Requirement | 312.2517 |  | MKWHr
03:00 | 3135 | 1534.5 | 917 | 0 | 38 | 1015 | 83 | 4501.2 | 0 | 210.5 | 1243 | 0 | 0 | 20 | 52
03:30 | 3132.5 | 1532 | 917 | 0 | 38 | 1013.5 | 83 | 4500.2 | 0 | 191.25 | 1100 | 0 | 0 | 21.5 | 54.5
04:00 | 3130 | 1529.5 | 917 | 0 | 38 | 1012 | 83 | 4499.2 | 0 | 172 | 957 | 0 | 0 | 23 | 57
04:30 | 3153.5 | 1534.5 | 916.5 | 0 | 37 | 1014 | 82 | 4497.7 | 0 | 163 | 849.5 | 0 | 0 | 31 | 54.5
05:00 | 3177 | 1539.5 | 916 | 0 | 36 | 1016 | 81 | 4496.2 | 0 | 154 | 742 | 0 | 0 | 39 | 52
05:30 | 3187 | 1543.75 | 916.5 | 0 | 35 | 1014.5 | 80 | 4384.6 | 8.955 | 129.5 | 602 | 0 | 0 | 40.5 | 42
06:00 | 3197 | 1548 | 917 | 0 | 34 | 1013 | 79 | 4273 | 17.91 | 105 | 462 | 0 | 0 | 42 | 32
06:30 | 3221 | 1545.5 | 916.5 | 0 | 34 | 1014.5 | 78.5 | 4277 | 44.18 | 105 | 464 | 0 | 0 | 38 | 16
07:00 | 3245 | 1543 | 916 | 0 | 34 | 1016 | 78 | 4281 | 70.45 | 105 | 466 | 0 | 0 | 34 | 0
07:30 | 3266.5 | 1537.5 | 894.5 | 0 | 33 | 1015 | 78.5 | 4276 | 97.045 | 105 | 463.5 | 0 | 0 | 29.5 | 0
08:00 | 3288 | 1532 | 873 | 0 | 32 | 1014 | 79 | 4271 | 123.64 | 105 | 461 | 0 | 0 | 25 | 0
08:30 | 3278 | 1533.5 | 873 | 0 | 31 | 1015.5 | 81 | 4338.5 | 147.665 | 131 | 554 | 0 | 0 | 41 | 0
09:00 | 3268 | 1535 | 873 | 0 | 30 | 1017 | 83 | 4406 | 171.69 | 157 | 647 | 0 | 0 | 57 | 0
09:30 | 3188.5 | 1532.75 | 897 | 0 | 31 | 1009 | 83 | 4398 | 263.445 | 156.5 | 738.5 | 0 | 0 | 42.5 | 0
10:00 | 3109 | 1530.5 | 921 | 0 | 32 | 1001 | 83 | 4390 | 355.2 | 156 | 830 | 0 | 0 | 28 | 0
10:30 | 3192.5 | 1544 | 921 | 0 | 31 | 982.5 | 100.5 | 4308.5 | 386.455 | 156 | 888 | 0 | 0 | 26 | 0
11:00 | 3276 | 1557.5 | 921 | 0 | 30 | 964 | 118 | 4227 | 417.71 | 156 | 946 | 0 | 0 | 24 | 0
11:30 | 3346 | 1564.75 | 921 | 0 | 31 | 964 | 118 | 4249 | 418.9 | 184 | 946 | 0 | 0 | 16 | 0
12:00 | 3416 | 1572 | 921 | 0 | 32 | 964 | 118 | 4271 | 420.09 | 212 | 946 | 0 | 0 | 8 | 0
12:30 | 3307.5 | 1570.25 | 921 | 0 | 29 | 990 | 118 | 4395.6 | 392.315 | 227 | 995.5 | 0 | 0 | 17.5 | 0
13:00 | 3199 | 1568.5 | 921 | 0 | 26 | 1016 | 118 | 4520.2 | 364.54 | 242 | 1045 | 0 | 0 | 27 | 0
13:30 | 3276.5 | 1579 | 920.5 | 0 | 29 | 1015.03 | 134 | 4407.1 | 331.885 | 268.5 | 1069.5 | 0 | 0 | 23 | 0
14:00 | 3354 | 1589.5 | 920 | 0 | 32 | 1014.06 | 150 | 4294 | 299.23 | 295 | 1094 | 0 | 0 | 19 | 0
14:30 | 3350.5 | 1622.25 | 920 | 0 | 30 | 1012.62 | 150 | 4304.5 | 270.79 | 321.5 | 1091 | 0 | 0 | 15.5 | 0
15:00 | 3347 | 1655 | 920 | 0 | 28 | 1011.18 | 150 | 4315 | 242.35 | 348 | 1088 | 0 | 0 | 12 | 0
15:30 | 3360.5 | 1656 | 920.5 | 0 | 29 | 1010.62 | 132.5 | 4280 | 188.03 | 367 | 991.5 | 0 | 0 | 6 | 0
16:00 | 3374 | 1657 | 921 | 0 | 30 | 1010.06 | 115 | 4245 | 133.71 | 386 | 895 | 0 | 0 | 0 | 0
16:30 | 3401.5 | 1643 | 920.5 | 0 | 31 | 968.135 | 115 | 4116.5 | 92.88 | 387 | 882 | 0 | 0 | 3.5 | 0
17:00 | 3429 | 1629 | 920 | 0 | 32 | 926.21 | 115 | 3988 | 52.05 | 388 | 869 | 0 | 0 | 7 | 0
17:30 | 3380.5 | 1597.5 | 920 | 0 | 29 | 968.99 | 114 | 3996 | 38.7 | 418.5 | 883 | 0 | 0 | 11.5 | 0
18:00 | 3332 | 1566 | 920 | 0 | 26 | 1011.77 | 113 | 4004 | 25.35 | 449 | 897 | 0 | 0 | 16 | 0
18:30 | 3362 | 1577.5 | 896.5 | 0 | 29 | 1067.595 | 130.5 | 3953.5 | 12.675 | 557 | 1133 | 0 | 0 | 13 | 0
19:00 | 3392 | 1589 | 873 | 0 | 32 | 1123.42 | 148 | 3903 | 0 | 665 | 1369 | 0 | 0 | 10 | 0
19:30 | 3466 | 1722 | 873 | 0 | 32 | 1234.3 | 115 | 4085 | 0 | 570 | 1379.2 | 0 | 0 | 27 | 0
20:00 | 3497 | 1758 | 873 | 0 | 30 | 1262.13 | 115 | 4241 | 0 | 377 | 1124 | 0 | 0 | 55 | 0
20:30 | 3593 | 1828.5 | 897.5 | 0 | 34 | 1289.58 | 115 | 4309 | 0 | 356.5 | 1024 | 0 | 0 | 34.5 | 0
21:00 | 3689 | 1899 | 922 | 0 | 38 | 1317.03 | 115 | 4377 | 0 | 336 | 924 | 0 | 0 | 14 | 0
21:30 | 3693 | 1900 | 922 | 0 | 38 | 1341.07 | 135 | 4408.5 | 0 | 336 | 909.5 | 0 | 0 | 7 | 0
22:00 | 3697 | 1901 | 922 | 0 | 38 | 1365.11 | 155 | 4440 | 0 | 336 | 895 | 0 | 0 | 0 | 0
22:30 | 3700.5 | 1900 | 921.5 | 0 | 38 | 1369.69 | 155 | 4440.5 | 0 | 331.5 | 899.5 | 0 | 0 | 3 | 0
23:00 | 3704 | 1899 | 921 | 0 | 38 | 1374.27 | 155 | 4441 | 0 | 327 | 904 | 0 | 0 | 6 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 01-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 382 | 19:00 | 372 | 10:00 | Payra | 413 | 18:30 | 406 | 22:00
Ashuganj | 399 | 5:00 | 378 | 14:00 | Rahanpur | 409 | 18:30 | 393 | 00:00
Bhulta | 394 | 05:00 | 378 | 14:00 | Rampal | 401 | 18:30 | 388 | 00:00
Bibiana | 392 | 18:30 | 382 | 12:00
BIPTC | 401 | 08:00 | 387 | 23:00
Bogura | 400 | 18:30 | 383 | 21:00
Gopalganj | 395 | 18:30 | 383 | 22:00
Kaliakoir | 374 | 18:30 | 363 | 12:00
Madunaghat | 393 | 01:00 | 389 | 10:00
Meghnaghat | 385 | 18:30 | 375 | 10:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 223 | 19:00 | 216 | 10:00 | Keranigonj | 221 | 19:00 | 215 | 09:00
AKSML | 230 | 18:30 | 225 | 07:00 | Khulna(S) | 231 | 18:30 | 216 | 23:00
Aminbazar | 224 | 19:00 | 217 | 15:00 | Madunaghat | 233 | 00:00 | 229 | 23:00
Ashuganj | 229 | 18:30 | 222 | 22:00 | Madunaghat-400 | 233 | 00:00 | 230 | 04:00
Ashuganj-400 | 229 | 18:30 | 222 | 22:00 | Maniknagar | 219 | 19:00 | 213 | 09:00
Baghabari | 233 | 16:00 | 223 | 22:00 | Meghnaghat | 228 | 19:00 | 221 | 10:00
Barapukuria | 225 | 18:30 | 215 | 21:00 | Meghnaghat-400 | 223 | 18:30 | 217 | 10:00
Barapukuria-230 | 225 | 18:30 | 215 | 21:00 | Mirsorai | 227 | 19:00 | 220 | 07:00
Barishal | 235 | 18:30 | 226 | 00:00 | Rajshahi | 236 | 18:30 | 222 | 21:00
Bheramara | 234 | 09:00 | 221 | 23:00 | Rampal | 230 | 18:30 | 218 | 00:00
Bhulta | 230 | 05:00 | 214 | 09:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 229 | 06:00 | 225 | 21:00 | Rampura | 228 | 04:00 | 216 | 10:00
BIPTC | 235 | 08:00 | 222 | 21:00 | Shikalbaha | 232 | 00:00 | 225 | 23:00
Bogura | 232 | 18:30 | 220 | 23:00 | Shyampur | 221 | 19:00 | 214 | 10:00
Bogura-400 | 231 | 18:30 | 221 | 21:00 | Siddhirganj | 234 | 19:00 | 217 | 09:00
Borhanuddin | 242 | 07:00 | 231 | 00:00 | Sirajgonj | 236 | 09:00 | 230 | 00:00
BSRM | 227 | 18:00 | 222 | 02:00 | Sreepur | 226 | 18:30 | 219 | 21:00
Cumilla(N) | 223 | 19:00 | 217 | 23:00 | Tongi | 228 | 04:00 | 216 | 12:00
Faridpur | 232 | 18:00 | 222 | 00:00
Fenchuganj | 231 | 05:00 | 226 | 00:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 227 | 04:00 | 217 | 21:00
Gopalganj | 234 | 18:30 | 225 | 00:00
GPH | 230 | 00:00 | 222 | 02:00
Haripur | 221 | 19:00 | 215 | 10:00
Hasnabad | 221 | 19:00 | 214 | 09:00
Hathazari | 233 | 00:00 | 227 | 05:00
Ishurdi | 236 | 18:30 | 223 | 23:00
Jhenaidah | 231 | 18:30 | 215 | 23:00
Kaliakoir | 230 | 18:00 | 222 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 132 | 05:00 | 123 | 15:00 | Madartek | 131 | 04:00 | 123 | 10:00
Agargaon | 134 | 03:00 | 128 | 10:00 | Madunaghat | 133 | 13:00 | 129 | 22:00
Agrabad | 133 | 19:00 | 129 | 00:00 | Magura | 135 | 18:00 | 121 | 23:00
AKS | 131 | 18:00 | 128 | 10:00 | Mahasthangarh | 135 | 18:30 | 127 | 22:00
Aminbazar | 133 | 19:00 | 127 | 09:00 | Manikganj | 132 | 04:00 | 123 | 17:00
Amnura | 140 | 18:30 | 123 | 00:00 | Maniknagar | 132 | 02:00 | 127 | 10:00
Ashuganj | 137 | 10:00 | 134 | 21:00 | Matarbari | 130 | 09:00 | 116 | 03:00
Bagerhat | 132 | 18:30 | 118 | 23:00 | Matuail | 128.8 | 19:00 | 125 | 09:00
Bajitpur | 134 | 08:00 | 125 | 22:00 | Millgate | 135 | 00:00 | 128 | 15:00
Bakulia | 134 | 17:00 | 130 | 12:00 | Mirpur | 131 | 19:00 | 125 | 00:00
Banani | 133 | 05:00 | 124 | 12:00 | Mirzapur | 134 | 17:00 | 128 | 02:00
Bangabhaban | 132 | 03:00 | 128 | 10:00 | Mithapukur | 135 | 03:00 | 123 | 21:00
Barapukuria | 137 | 18:30 | 125 | 21:00 | MI_Cement | 129 | 19:00 | 124 | 09:00
Barguna | 138 | 00:00 | 127 | 23:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 130 | 18:00 | 122 | 00:00 | Mogbazar | 132 | 01:00 | 124 | 13:00
Barishal-230 | 131 | 18:30 | 123 | 00:00 | Mongla | 133 | 18:30 | 119 | 23:00
Baroaulia | 135 | 08:00 | 129 | 23:00 | Motijheel | 132 | 03:00 | 128 | 10:00
Baroirhat | 128 | 14:00 | 120 | 00:00 | Muktagacha | 134 | 17:00 | 125 | 02:00
Bashundhara | 136 | 06:00 | 124 | 10:00 | Munshiganj | 130 | 19:00 | 124 | 08:00
BashundharaCement | 128 | 03:00 | 124 | 17:00 | Muradnagar | 128 | 13:00 | 121 | 09:00
Beanibazar | 135 | 05:00 | 126 | 23:00 | Mymensingh | 135 | 07:00 | 116 | 22:00
Benapole | 137 | 19:30 | 117 | 23:00 | Naogaon | 135 | 18:30 | 124 | 23:00
Bhaluka | 131 | 09:00 | 123 | 21:00 | Narail | 137 | 18:00 | 120 | 23:00
Bhandaria | 125 | 17:00 | 112 | 00:00 | Narinda | 132 | 02:00 | 127 | 10:00
Bhangura | 133 | 17:00 | 127 | 21:00 | Narshingdi | 136 | 19:00 | 116 | 23:00
Bheramara | 138 | 18:30 | 131 | 00:00 | Natore | 135 | 18:00 | 128 | 00:00
Bheramara(GK) | 137 | 10:00 | 131 | 00:00 | Nawabganj | 131 | 05:00 | 127 | 09:00
Bhulta | 122 | 18:30 | 118 | 09:00 | Netrakona | 130 | 08:00 | 116 | 22:00
Bog-Sherpur | 136 | 18:30 | 128 | 23:00 | New | 136 | 03:00 | 129 | 15:00
Bogura | 138 | 18:30 | 130 | 23:00 | Niamatpur | 135 | 18:30 | 128 | 00:00
Bogura-230 | 138 | 18:30 | 130 | 22:00 | Noapara | 136 | 18:30 | 122 | 23:00
Brahmanbaria | 131 | 10:00 | 122 | 20:00 | Pabna | 135 | 18:30 | 128 | 00:00
Cantonment | 134 | 05:00 | 128 | 09:00 | Palashbari | 133 | 03:00 | 122 | 21:00
Chandina | 129 | 13:00 | 124 | 00:00 | Panchagarh | 138 | 00:00 | 119 | 07:00
Chandpur | 133 | 13:00 | 115 | 06:00 | Patuakhali | 138 | 00:00 | 130 | 21:00
Chandraghona | 133 | 00:00 | 131 | 05:00 | Payra | 136 | 01:00 | 132 | 23:00
Chapai | 132 | 18:30 | 124 | 00:00 | PHP | 128 | 14:00 | 118 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 129 | 19:00 | 125 | 09:00 | Postogola | 130 | 00:00 | 126 | 10:00
Chauddagram | 126 | 13:00 | 119 | 00:00 | Purbachal | 132 | 01:00 | 124 | 10:00
Chhatak | 132 | 04:00 | 125 | 19:30 | Purbasadipur | 135 | 18:30 | 118 | 08:00
Chowmuhani | 125 | 13:00 | 109 | 02:00 | Rahanpur | 136 | 18:00 | 130 | 00:00
Chuadanga | 134 | 18:30 | 119 | 23:00 | Rahanpur-400 | 136 | 18:00 | 130 | 00:00
Coxsbazar | 129 | 09:00 | 117 | 03:00 | Rahim | 129 | 06:00 | 125 | 09:00
Cumilla(N) | 129 | 13:00 | 123 | 23:00 | Rajbari | 136 | 18:30 | 126 | 00:00
Cumilla(S) | 134 | 06:00 | 122 | 07:00 | Rajendrapur | 132 | 01:00 | 122 | 00:00
Daudkandi | 127 | 13:00 | 118 | 09:00 | Rajshahi | 135 | 10:00 | 128 | 22:00
Dhaka | 133 | 04:00 | 124 | 12:00 | Rajshahi-230 | 136 | 18:30 | 116 | 00:00
Dhamrai | 130 | 18:30 | 125 | 12:00 | Ramganj | 128 | 13:00 | 112 | 00:00
Dhanmondi | 133 | 04:00 | 124 | 15:00 | Rampur | 133 | 19:00 | 129 | 11:00
Dohazari | 133 | 09:00 | 126 | 04:00 | Rampura | 132 | 04:00 | 123 | 10:00
Faridpur | 135 | 17:00 | 129 | 00:00 | Rangamati | 133 | 19:30 | 129 | 23:00
Fatullah | 130 | 18:30 | 124 | 10:00 | Rangpur | 134 | 12:00 | 117 | 01:00
Fenchuganj | 137 | 04:00 | 134 | 21:00 | Ruppur | 137 | 08:00 | 130 | 23:00
Feni | 126 | 14:00 | 116 | 01:00 | Saidpur | 134 | 00:00 | 122 | 08:00
Ghatail | 133 | 17:00 | 122 | 21:00 | Satkhira | 137 | 18:30 | 119 | 00:00
Ghorashal | 135 | 04:00 | 130 | 14:00 | Satmasjid | 134 | 04:00 | 128 | 10:00
Goalpara | 137 | 18:30 | 25 | 23:00 | Savar | 132 | 19:00 | 124 | 08:00
Gollamari | 138 | 18:30 | 127 | 22:00 | SevenRings | 135 | 01:00 | 129 | 21:00
Gopalganj | 136 | 18:30 | 126 | 22:00 | ShahCement | 129 | 19:00 | 125 | 09:00
Gopalganj-400 | 136 | 18:30 | 130 | 00:00 | Shahjadpur | 136 | 16:00 | 132 | 00:00
Gulshan | 132 | 04:00 | 124 | 15:00 | Shahjibazar | 134 | 10:00 | 126 | 20:00
Halishahar | 135 | 19:30 | 128 | 23:00 | Shahmirpur | 134 | 00:00 | 129 | 22:00
Haripur | 129 | 03:00 | 125 | 09:00 | Shariatpur | 132 | 18:00 | 125 | 00:00
HaripurSBU | 129 | 19:00 | 125 | 09:00 | Sherpur | 139 | 07:00 | 124 | 02:00
Hasnabad | 131 | 03:00 | 126 | 11:00 | Shikalbaha | 124 | 00:00 | 119 | 22:00
Hathazari | 136 | 17:00 | 131 | 04:00 | Shikalbaha-230 | 135 | 00:00 | 129 | 03:00
Ishurdi | 138 | 09:00 | 131 | 23:00 | Shitalakhya | 129 | 19:00 | 124 | 09:00
Jaldhaka | 133 | 00:00 | 119 | 20:00 | Sholosohor | 134 | 18:00 | 128 | 06:00
Jamalpur | 138 | 07:00 | 127 | 20:00 | Shyampur | 130 | 18:30 | 124 | 10:00
Jashore | 135 | 19:30 | 118 | 23:00 | Shyampur-230 | 130 | 19:00 | 124 | 10:00
Jhenaidah | 136 | 18:00 | 120 | 00:00 | Siddhirganj | 129 | 18:30 | 125 | 09:00
Jhenaidah-230 | 137 | 18:30 | 124 | 23:00 | Sirajganj | 134 | 15:00 | 127 | 21:00
Joydebpur | 134 | 19:00 | 123 | 13:00 | Sonargaon | 129 | 19:00 | 123 | 09:00
Joypurhat | 135 | 18:30 | 123 | 23:00 | Sreemongol | 134 | 10:00 | 127 | 20:00
Juldah | 135 | 00:00 | 129 | 23:00 | Sreepur | 132 | 18:30 | 126 | 22:00
Kabirpur | 137 | 19:00 | 127 | 14:00 | Srinagar | 132 | 05:00 | 127 | 09:00
Kachua | 129 | 13:00 | 116 | 07:00 | SSM | 138 | 00:00 | 132 | 09:00
Kaliakoir | 139 | 18:30 | 128 | 09:00 | Sunamganj | 131 | 03:00 | 123 | 22:00
Kallyanpur | 133 | 19:00 | 127 | 08:00 | Sylhet | 134 | 05:00 | 128 | 23:00
Kalurghat | 132 | 00:00 | 129 | 05:00 | Sylhet-132 | 133 | 07:00 | 128 | 23:00
Kamrangirchar | 133 | 18:30 | 127 | 10:00 | Tangail | 132 | 17:00 | 123 | 21:00
Kaptai | 135 | 1:00 | 133 | 2:00 | Thakurgaon | 138 | 00:00 | 114 | 08:00
Kasba | 128 | 13:00 | 121 | 02:00 | TK | 131 | 00:00 | 129 | 13:00
Kazla | 132 | 04:00 | 127 | 10:00 | Tongi | 137 | 03:00 | 130 | 12:00
Keranigonj | 132 | 04:00 | 128 | 10:00 | Ullahpara | 135 | 16:00 | 129 | 00:00
Khagrachori | 132 | 16:00 | 128 | 23:00 | Ullon | 132 | 06:00 | 123 | 15:00
Khulna | 137 | 18:30 | 124 | 22:00 | Uttara | 131 | 00:00 | 124 | 21:00
Khulna(S) | 139 | 18:30 | 126 | 23:00 | UttaraNew | 132 | 19:30 | 125 | 09:00
Khulshi | 132 | 00:00 | 128 | 23:00 | Zigatola | 132 | 04:00 | 128 | 09:00
Kishoreganj | 132 | 09:00 | 123 | 22:00
Kodda | 135 | 19:00 | 123 | 21:00
KSRM | 134 | 19:00 | 130 | 02:00
Kulaura | 136 | 04:00 | 132 | 23:00
Kurigram | 130 | 06:00 | 120 | 20:00
Kushtia | 134 | 18:30 | 125 | 00:00
Lalbag | 131 | 04:00 | 127 | 10:00
Lalmonirhat | 134 | 01:00 | 122 | 19:00
Madanganj | 128 | 08:00 | 124 | 17:00
Madaripur | 132 | 18:30 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division