## Forecast
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Forecasted Generation & Demand of National Grid
| Date : | 03-06-2025
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-06-2025 | during | 03-06-2025 | during | 03-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 | Gas | PDB | 1*210 | 210 | 240 | 0 | 0 | 230 | 230 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 190 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 260 | 260 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
4 | Ghorashal 108 MW PP (Regent) | Gas | IPP | 34*3.35 | 108 | 97.7 | 0 | 0 | 97.7 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP | Gas | SBU,PDB | 32*2 | 32 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | -
6 | Haripur 412 MW CCPP | Gas | EGCB | 1*273+1*139 | 412 | 400.75 | 334 | 328 | 400.75 | 400.75 | 362 | 362 | -
| Haripur 360 MW CCPP (HPL) | Gas | IPP | 1*235+1*125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 420 | 450 | 450 | 400 | 400 | -
8 | Meghnaghat CCPP(Summit) | Gas | IPP | 2*110+1*110 | 335 | 335 | 153 | 165 | 335 | 335 | 335 | 335 | FGMO
9 | Madanganj-55 MW PP(Summit) | HFO | IPP | 3*17+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 55 | -
10 | Keraniganj 100 MW PP (Powerpac) | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) | Gas | SIPP,REB | 8*2.90 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 208.13 | 208.13 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP | Gas | EGCB | 1*217+118 | 335 | 335 | 294 | 266 | 335 | 335 | 305 | 305 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 8 | 102 | 8 | 102 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) | HFO | IPP | 3*18 | 54 | 53.97 | 0 | 54 | 53.97 | 53.97 | 53.97 | 53.97 | -
18 | Kodda 150 MW PP B-R | HFO | PDB-RPCL | 9*17.06 | 149 | 149.36 | 32 | 145 | 149.36 | 149.36 | 149.36 | 149.36 | -
18 | Manikganj 55 MW PP (Northern) | HFO | IPP | 19.3*3 | 55 | 55 | 25 | 35 | 55 | 55 | 35 | 35 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) | HFO | IPP | 19.3*3 | 55 | 55 | 0 | 35 | 55 | 55 | 35 | 35 | -
22 | Summit Power Ashulia | Gas | IPP |  | 80 | 33.75 | 24 | 24 | 33 | 33 | 24 | 24 | Low gas pressure
22 | Summit Power Madhabdi | Gas | IPP | 3*3.67+4*8.73 | 80 | 23 | 22 | 22 | 22 | 22 | 22 | 22 | -
24 | Rupganj 33 MW PP(Summit) | Gas | IPP | 4*8.73 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | -
25 | Gazipur 52 MW PP | HFO | RPCL | 6*8.9 | 52 | 52.194 | 24 | 33 | 52.19 | 52.19 | 24 | 24 | Fuel shortage
26 | Tongi 80 MW GTPP | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) | HFO | IPP | 18*17.06 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | -
28 | Kodda 149 MW PP Unit-1 (Summit) | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 67 | 149 | 149 | 149 | 149 | 149 | Machine Problem
29 | Gazipur 100 MW PP | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 105 | 105 | 90 | 90 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) | HFO | IPP | 6*18.5 | 104 | 104 | 0 | 16 | 104 | 104 | 85 | 85 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) | HFO | IPP | 9*18 | 162 | 162 | 17 | 130 | 162 | 162 | 162 | 162 | -
32 | Spectra Solar Plant Ltd. | Solar | IPP |  | 35 | 35 | 22 | 0 | 35 | 0 | 35 | 0 | -
33 | Kanchan Purbachal Power Generation Ltd. | HFO | IPP | 18.4*3 | 55 | 55 | 35 | 54 | 55 | 55 | 55 | 55 | -
34 | Unique Meghnaghat Power Limited (UMPL) | Gas | IPP |  | 584 | 584 | 0 | 0 | 584 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 | Gas/HSD | IPP |  | 583 | 583 | 520 | 536 | 583 | 583 | 480 | 480 | -
| JERA Meghnaghat Power Limited | Gas | IPP | 250*2+268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
| Sreepur 150 MW PP | HFO | PDB-RPCL | 9*18 | 0 | 160 | 17 | 160 | 160 | 160 | 160 | 160 | -
Dhaka Area Total |  |  |  |  | 6156 | 5972.724 | 2038 | 2660 | 5227.1 | 5286.1 | 3324.33 | 3383.33
36 | Chattogram TPP | Gas | PDB | 1*210+1*210 | 420 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP | HFO | IPP | 3*8.9 | 25 | 25.5 | 0 | 8 | 25.5 | 25.5 | 25.5 | 25.5 | -
38 | Teknaf 20MW PP (Solartech) | Solar | IPP |  | 20 | 20 | 0 | 0 | 15 | 0 | 15 | 0 | -
39 | Patenga 50MW PP (Baraka) | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50 | 50 | 50 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Hydro | PDB | 2*40+3*50 | 230 | 230 | 155 | 155 | 155 | 155 | 155 | 155 | -
41 | Sikalbaha 225MW CCPP | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 223 | 219 | 221 | 221 | 221 | 221 | -
42 | Sikalbaha Peaking GT | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) | HFO | IPP | 6*17.5 | 105 | 105 | 0 | 30 | 105 | 105 | 105 | 105 | -
44 | Hathazari 100 MW peaking PP | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 39 | 82 | 82 | 60 | 60 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 68 | 68 | 51 | 51 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) | HFO | IPP | 8*13.5 | 100 | 100 | 51 | 100 | 100 | 100 | 100 | 100 | -
| Malancha, Ctg. EPZ (United) | Gas | IPP | 5*8.73+3*9.34 | 0 | 42 | 4 | 5 | 5 | 12 | 5 | 12 | -
47 | Chattogram 108 MW PP (ECPV) | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 108 | 108 | 108 | 108 | -
48 | Kaptai 7 MW Solar PP | Solar | PDB |  | 7 | 6 | 1 | 0 | 1.04 | 0 | 1.04 | 0 | -
49 | Anwara 300 MW PP (United) | HFO | IPP | 17*17+24 | 300 | 300 | 0 | 15 | 300 | 300 | 300 | 300 | -
50 | Jodiac Power | HFO | IPP | 3*18.55+1*3.6 | 54 | 54.36 | 0 | 0 | 54.36 | 54.36 | 54.36 | 54.36 | -
51 | Karnaphuli Power Ltd. | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 0 | 20 | 110 | 110 | 110 | 110 | -
52 | Juldah unit-2 (Acorn) | HFO | IPP | 8*13.6 | 100 | 100 | 24 | 24 | 100 | 100 | 100 | 100 | -
53 | Anlima Energy Ltd. | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116 | 116 | 116 | -
54 | Mirsharai 150 MW | HFO/Gas | IPP | 18.5*9 | 163 | 159.86 | 0 | 0 | 159.86 | 159.86 | 159.86 | 159.86 | -
55 | SS Power | Coal | IPP | 2*660 | 1224 | 1224 | 1005 | 1195 | 1224 | 1224 | 1224 | 1224 | -
56 | Cox's Bazar Wind | Wind | PDB | 22*3 | 60 | 60 | 21 | 30 | 16 | 26 | 16 | 26 | -
57 | Matarbari 2*600 MW (CPGCBL) | Coal | CPGCL | 2*600 | 1150 | 1150 | 360 | 568 | 360 | 360 | 360 | 360 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4917 | 4895.72 | 1844 | 2476 | 3375.76 | 3376.72 | 3336.76 | 3337.72
58 | Ashuganj CCPP 225 MW | Gas | APSCL | 1X142+1X75 | 221 | 221.43 | 205 | 183 | 221 | 221 | 205 | 205 | FGMO
59 | Ashuganj 450 MW CCPP(North) | Gas | APSCL | 1*360 | 360 | 353.35 | 355 | 356 | 353.35 | 353.35 | 353.35 | 353.35 | -
60 | Ashuganj 450 MW CCPP(South) | Gas | APSCL | 1*360 | 360 | 356.56 | 340 | 340 | 345 | 345 | 340 | 340 | -
61 | Ashuganj 420 MW CCPP(East) | Gas | APSCL | 284*1+116*1 | 400 | 393 | 0 | 0 | 0 | 0 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP | Gas | APSCL | 14*3.96 | 53 | 46.701 | 32 | 33 | 46.7 | 46.7 | 33 | 33 | machine problem
63 | Ashuganj 55 MW PP (Precision) | Gas | QRPP | 15*4 | 55 | 55 | 48 | 49 | 55 | 55 | 51 | 51 | -
64 | Ashuganj 195 MW PP (APSCL-United) | Gas | IPP | 20X9.73+1X16 | 195 | 195 | 63 | 63 | 195 | 195 | 63 | 63 | -
65 | Ashuganj 51 MW PP (Midland) | Gas | IPP | 6X9.34 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | -
66 | Ashuganj 150MW PP (Midland) | HFO | IPP | 23X7.015 | 150 | 150 | 0 | 120 | 150 | 150 | 138 | 138 | -
67 | Titas 50 MW Peaking PP | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 40 | 47 | 47 | 47 | 47 | machine problem
68 | Chandpur 150 MW CCPP | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 163 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) | HFO | IPP | 12*18.4 | 200 | 200 | 66 | 149 | 200 | 200 | 200 | 200 | -
70 | Feni 11 MW PP (Doreen) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) | Import | Import |  | 160 | 160 | 28 | 38 | 160 | 160 | 160 | 160 | -
71 | Jangalia 52 MW PP (Lakdanavi) | HFO | IPP | 6*8.92 | 52.2 | 52.2 | 0 | 43 | 52.2 | 52.2 | 52.2 | 52.2 | -
72 | Cumilla 25 MW PP (Summit) | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 0 | 15 | 17.75 | 17.75 | 14 | 14 | Machine Under Maintenance
73 | Feni Lanka Power | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 66 | 114 | 114 | 114 | 114 | 114 | -
74 | Chowmuhani 113 MW | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 28 | 113 | 113 | 113 | 113 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 69 | 34 | 115 | 115 | 115 | 115 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant | Solar | EGCB |  | 75 | 75 | 8 | 0 | 35 | 0 | 35 | 0 | -
Cumilla Area Total |  |  |  |  | 2925.2 | 2891.241 | 1332 | 1648 | 2434 | 2399 | 2084.55 | 2049.55
Sl. | Name of the Power Station | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation on |  | Forecasted Available Gen. on |  | Effective Available Gen. on |  | Remarks
[7 empty] | 02-06-2025 | during | 03-06-2025 | during | 03-06-2025 | during
[7 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Day Peak | Ev. Peak
|  |  |  | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
77 | RPCL 210MW CCPP | Gas | RPCL | 4*35+1*70 | 210 | 210 | 29 | 33 | 157.5 | 157.5 | 35 | 35 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant | Solar | IPP |  | 3 | 2.71 | 2 | 0 | 2.1 | 0 | 2.1 | 0 | -
80 | Mymensingh 200 MW PP (United) | HFO | IPP | 9.78*21 | 200 | 200 | 96 | 110 | 200 | 200 | 150 | 150 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) | HFO | IPP | 9.78*12 | 115 | 115 | 55 | 63 | 115 | 115 | 83 | 83 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP | Solar | IPP |  | 50 | 50 | 46.15 | 0 | 46 | 0 | 46 | 0 | -
83 | Tangail Palli Power Gen 22 MW | HFO | IPP | 4*6.7 | 22 | 22 | 11 | 12 | 22 | 22 | 12 | 12 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW | HFO | IPP | 3*18.2 | 54 | 54.5 | 0 | 17 | 54.5 | 54.5 | 54.5 | 54.5 | -
Mymensingh Area Total |  |  |  |  | 654 | 654.21 | 239.15 | 235 | 597.1 | 549 | 382.6 | 334.5
85 | Fenchugonj CCPP Phase-1 | Gas | PDB | 2*32+1*33 | 97 | 90 | 33 | 34 | 32 | 32 | 31 | 31 | FGMO
86 | Fenchugonj CCPP Phase-2 | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 | 30 | 30 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) | Gas | IPP | 1*109+1*54 | 163 | 163 | 153 | 148 | 163 | 163 | 147 | 147 | FGMO
88 | Shajibazar 330 MW CCPP | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) | Gas | NENP | 12*3.3+5*2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
90 | Hobiganj 11MW PP Cofidence-E | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
91 | Shahjibazar GTPP Unit- 8 & 9 | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 | 30 | 30 | -
92 | Shahjibazar 86MW PP (Shahjibazar) | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 86 | 86 | 84 | 84 | -
93 | Shahjibazar 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP | Gas | PDB | 1*142+1*89 | 231 | 231 | 162 | 164 | 160 | 160 | 160 | 160 | -
95 | Sylhet 20 MW GTPP | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | -
96 | Shahjahanulla 25 MW PP | Gas | SIPP,REB | 3*9.34 | 25 | 25 | 0 | 7 | 25 | 25 | 6 | 6 | -
97 | Bibiana-II 341 MW CCPP (Summit) | Gas | IPP | 1*222+1*119 | 341 | 341 | 260 | 260 | 341 | 341 | 341 | 341 | Gas shortage
98 | Bibiyana-III 400 MW CCPP | Gas | PDB | 285*1+134*1 | 400 | 400 | 383 | 368 | 380 | 380 | 352 | 352 | FGMO Activated
99 | Bibiyana South 400 MW | Gas | PDB | 1*400 | 383 | 383 | 320 | 320 | 320 | 320 | 320 | 320 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2411 | 2325 | 1470 | 1463 | 1585 | 1585 | 1519 | 1519
100 | Bheramara GTPP Unit-3 | HSD | PDB | 1X20 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) | Import | Import | 2X500 | 1000 | 1000 | 930 | 883 | 1000 | 1000 | 1000 | 1000 | -
101 | Faridpur 50 MW Peaking PP | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 42 | 42 | 42 | 42 | -
102 | Khulna 225 MW CCPP | HSD/Gas | NWPGCL | 1X150+1X75 | 230 | 230 | 0 | 0 | 230 | 230 | 230 | 230 | -
103 | Gopalganj 100 MW Peaking PP | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 50 | 50 | 50 | 50 | -
104 | Bheramara 410 MW CCPP | Gas | NWPGCL | 1X278+1X132 | 410 | 410 | 310 | 308 | 410 | 410 | 310 | 310 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 13 | 105 | 105 | 105 | 105 | Liquid fuel shortage
106 | Madhumati 100 MW PP | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 105 | 105 | 105 | 105 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 90 | 0 | 90 | 0 | -
108 | Khulna 330 MW CCPP | HSD/Gas | PDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 336 | GT Available
109 | Rampal 1320 MW (BIFPCL) | Coal | PDB | 660*2 | 1234 | 1234.2 | 919 | 1173 | 1234.2 | 1234.2 | 1234.2 | 1234.2 | -
** | HVDC(Nepal) | Import | Import | 1*40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3703 | 3699.2 | 2227 | 2377 | 3602.2 | 3512.2 | 3502.2 | 3412.2
| Patuakhali 1320 MW (RNPL) | Coal | RNPL | 660*2 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) | HFO | IPP | 7X17.076 | 110 | 110 | 0 | 0 | 110 | 110 | 110 | 110 | -
111 | Bhola 33 MW PP (Venture) | Gas | NENP | 1X34.50 | 40 | 10 | 4 | 8 | 10 | 10 | 10 | 10 | -
112 | Bhola 225 MW CCPP | Gas | PDB | 2X63+1X68 | 194 | 194 | 60 | 120 | 130 | 130 | 65 | 65 | Partial Shutdown of STG
113 | Payra 1320 MW | Coal | BCPCL | 2*622 | 1244 | 1244 | 930 | 1200 | 1244 | 1244 | 1204 | 1204 | FGMO
114 | Bhola Nutan Biddut BD LTD | Gas/HSD | IPP | 2*110 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150 | 150 | 150 | -
116 | Barisal 307 MW | Coal | BCPCL | 307X1 | 307 | 307 | 200 | 200 | 307 | 307 | 307 | 307 | -
117 | Barisal 1 MW Solar Plant | Solar | IPP |  | 1 | 1 | 0.4 | 0 | 1 | 0 | 1 | 0 | -
Barishal Area Total |  |  |  |  | 3586 | 2236 | 1414.4 | 1765 | 2172 | 2171 | 2067 | 2066
118 | Baghabari 71 MW GTPP | Gas | PDB | 1X71 | 71 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 20 | 47 | 47 | 47 | 47 | -
120 | Bera 70 MW Peaking PP | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 32 | 32 | 32 | 32 | -
121 | Amnura 50 MW PP(Sinha) | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 19 | 40 | 40 | 40 | 40 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 214 | 195 | 180 | 214 | 214 | 195 | 195 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 3 | 220 | 220 | 0 | 0 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 220 | 220 | 220 | 220 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 | Gas/HSD | NWPGCL | 1*282+1*132 | 414 | 413.79 | 414 | 323 | 413.79 | 413.79 | 372 | 372 | FGMO
127 | Santahar 50 MW Peaking PP | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 30 | 30 | 30 | 30 | Engine Problem
128 | Ullapara 11 MW PP (Summit) | Gas | SIPP,REB | 4*2.90 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
129 | Natore 52 MW PP (Rajlanka) | HFO | IPP | 6*8.92 | 52 | 52.2 | 0 | 0 | 52.2 | 52.2 | 52.2 | 52.2 | -
130 | Chapainawabganj 100 MW Peaking PP | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 96 | 95 | 95 | 95 | 95 | -
131 | Bagura 113 MW PP (Confidence)-2 | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 80 | 113 | 113 | 113 | 113 | -
132 | Confidence Power Bogura Unit-1 113 MW | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113 | 113 | 113 | -
133 | Sirajgonj 6.55 MW Solar | Solar | NWPGCL |  | 6 | 6.09 | 4.96 | 0 | 5.5 | 0 | 5.5 | 0 | -
** | Adani Power Jharkhanda Ltd | Import | Import | 2*673 | 1496 | 1435.88 | 957.76 | 1213 | 1435.88 | 1435.88 | 1435.88 | 1435.88 | -
134 | Sirajganj 68 MW Solar Park | Solar | IPP |  | 68 | 68 | 60.2 | 0 | 61 | 0 | 61 | 0 | -
| Pabna Solar 100 MW | Solar | IPP |  | 0 | 100 | 93 | 0 | 100 | 0 | 100 | 0 | -
Rajshahi Area Total |  |  |  |  | 3471 | 3452.96 | 1724.92 | 1959 | 3192.37 | 3025.87 | 2911.58 | 2745.08
135 | Barapukuria TPP Unit-1 & 2 | Coal | PDB | 1*125+1*125 | 250 | 170 | 51 | 50 | 50 | 50 | 50 | 50 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 | Coal | PDB | 1*275 | 274 | 274 | 200 | 200 | 200 | 200 | 200 | 200 | -
137 | Rangpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | -
138 | Saidpur 20 MW GTPP | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 14 | 14 | 14 | 14 | -
139 | Rangpur 113 MW PP (Confidence) | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 108 | 113 | 113 | 113 | 113 | -
140 | Sympa Solar Power 8 MW | Solar | IPP |  | 8 | 8 | 7.9 | 0 | 5.6 | 0 | 5.6 | 0 | -
141 | Energypac Power Venture Thakurgaon Ltd. | HFO | IPP |  | 115 | 115 | 35 | 110 | 115 | 115 | 115 | 115 | -
142 | Intraco Solar 30 MW | Solar | IPP | 1*30 | 30 | 30 | 30 | 0 | 24.5 | 0 | 24.5 | 0 | -
143 | Teesta Solar Limited | Solar | BCPCL |  | 200 | 200 | 188 | 0 | 177.52 | 0 | 177.52 | 0 | -
Rangpur Area Total |  |  |  |  | 1030 | 950 | 511.9 | 468 | 719.62 | 512 | 719.62 | 512
System Total |  |  |  |  | 28853.2 | 27077.055 | 12801.37 | 15051 | 22905.15 | 22416.89 | 19847.64 | 19359.38
Forecast Scenario (03-06-2025)
|  |  |  | Hour | Generation |  | Load-Shed |  | Demand
|  |  |  | 0:00 | 14020 |  | 0 |  | 14020
|  |  |  | 1:00 | 13470 |  | 0 |  | 13470
|  |  |  | 2:00 | 13060 |  | 0 |  | 13060
|  |  |  | 3:00 | 12680 |  | 0 |  | 12680
|  |  |  | 4:00 | 12260 |  | 0 |  | 12260
|  |  |  | 5:00 | 11500 |  | 0 |  | 11500
|  |  |  | 6:00 | 11000 |  | 0 |  | 11000
|  |  |  | 7:00 | 10890 |  | 0 |  | 10890
|  |  |  | 8:00 | 10680 |  | 0 |  | 10680
|  |  |  | 9:00 | 11280 |  | 0 |  | 11280
|  |  |  | 10:00 | 11810 |  | 0 |  | 11810
|  |  |  | 11:00 | 12420 |  | 0 |  | 12420
|  |  |  | 12:00 | 13100 |  | 0 |  | 13100
|  |  |  | 13:00 | 13550 |  | 0 |  | 13550
|  |  |  | 14:00 | 13630 |  | 0 |  | 13630
|  |  |  | 15:00 | 13810 |  | 0 |  | 13810
|  |  |  | 16:00 | 13690 |  | 0 |  | 13690
|  |  |  | 17:00 | 13380 |  | 0 |  | 13380
|  |  |  | 18:00 | 13010 |  | 0 |  | 13010
|  |  |  | 18:30 | 13500 |  | 0 |  | 13500
|  |  |  | 19:00 | 14250 |  | 0 |  | 14250
|  |  |  | 19:30 | 15400 |  | 0 |  | 15400
|  |  |  | 20:00 | 15300 |  | 0 |  | 15300
|  |  |  | 21:00 | 15330 |  | 0 |  | 15330
|  |  |  | 22:00 | 15000 |  | 0 |  | 15000
|  |  |  | 23:00 | 14800 |  | 0 |  | 14800
Probable Maximum Temperature: |  |  | 34.00°C
Probable Maximum Demand at Day Peak: |  |  | 13100.00 MW |  | Total Load Shed forecast (in MW) at evening peak hr. (Sub-station End): | [5 empty] | 0
Probable Maximum Demand at Evening Peak: |  |  | 15400.00 MW |  | Area Wise Load Shed forecast (in MW) at evening peak hr. (Sub-station End):
Probable Maximum Generation at Evening Peak: |  |  | 14231.00 MW |  | Dhaka | Chittagong | Cumilla | Mymensingh | Sylhet | Khulna | Barishal | Rajshahi | Rangpur | Total
Probable Total Energy Generation: |  |  | 340.8056 MKWHr. |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*** This report is generated digitally from Operation Information System (OIS) at 09:11 hrs on 03-06-2025
|  | Sub-Divisional Engineer | [6 empty] | Executive Engineer
|  | Network Operation Division | [6 empty] | Network Operation Division

## GenLog
[7 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC | [20 empty] | QF-LDC-01 | [8 empty] | Power Grid Bangladesh PLC |  |  |  | QF-LDC-01
[7 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 1 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 2 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 3 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 4 of 6 | [8 empty] | National Load Dispatch Center (NLDC) | [20 empty] | Page 5 of 6 | [8 empty] | National Load Dispatch Center (NLDC) |  |  |  | Page 6 of 6
[7 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt) | [29 empty] | Daily Generation Log (Mega Watt)
|  | Shift |  | Signature
|  | 06:00-14:00 | [22 empty] | Date: | 02-06-2025 | [28 empty] | Date: | 02-06-2025 | [28 empty] | Date: | 02-06-2025 | [28 empty] | Date: | 02-06-2025 | [28 empty] | Date: | 02-06-2025 | [12 empty] | Date: | 02-06-2025
|  | 14:00-22:00 | [22 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [28 empty] | Day: | Monday | [12 empty] | Day: | Monday
22:00-06:00
Hour | Gagnagar 102 MW PP (Digital Power) | Gazipur 100 MW PP | Gazipur 52 MW PP | Ghorasal 365 MW CCPP Unit-7 | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorashal 108 MW PP (Regent) | Haripur 412 MW CCPP | Haripur GTPP | JERA Meghnaghat Power Limited | Kamalaghat 54 MW PP(Banco Energy) | Kanchan Purbachal Power Generation Ltd. | Kodda 149 MW PP Unit-1 (Summit) | Kodda 150 MW PP B-R | Kodda 300 MW PP Unit-2 (Summit) | Madanganj-55 MW PP(Summit) | Manikganj 55 MW PP (Northern) | Manikgonj 162MW PP(MPGL) | Meghnaghat 104 MW PP (OPCL) | Meghnaghat 450 MW CCPP (MPL) | Meghnaghat CCPP(Summit) | Meghnaghat CCPP(Summit)-2 (Gas) | Meghnaghat CCPP(Summit)-2 (HSD) | Nababganj 55 MW PP (Southern power ) | Siddhirganj 335 MW CCPP | Siddhirgonj 2*120 MW GTPP | Siddhirgonj 210 MW TPP | Spectra Solar Plant Ltd. | Sreepur 150 MW PP | Summit Power Ashulia | Summit Power Madhabdi | Tongi 80 MW GTPP | Unique Meghnaghat Power Limited (UMPL) | Anlima Energy Ltd. | Anwara 300 MW PP (United) | Chattogram 108 MW PP (ECPV) | Chattogram TPP | Cox's Bazar Wind | Dohazari -Kalaish 100 MW Peaking | Hathazari 100 MW peaking PP | Jodiac Power | Juldah 100 MW PP Unit-3 (Acorn) | Juldah unit-2 (Acorn) | Kaptai 7 MW Solar PP | Karnaphuli Hydro PP Unit-1,2,3,4, 5 | Karnaphuli Power Ltd. | Malancha, Ctg. EPZ (United) | Matarbari 2*600 MW (CPGCBL) | Mirsharai 150 MW (HFO) | Mirsharai 150 MW (Gas) | Patenga 50MW PP (Baraka) | Raozan 25 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP (HSD) | Sikalbaha Peaking GT (Gas) | Sikalbaha Peaking GT (HSD) | SS Power | Teknaf 20MW PP (Solartech) | Ashuganj 51 MW PP (Midland) | Ashuganj 150MW PP (Midland) | Ashuganj 195 MW PP (APSCL-United) | Ashuganj 420 MW CCPP(East) | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 55 MW PP (Precision) | Ashuganj CCPP 225 MW | Ashuganj TSK 50 MW PP | Chandpur 115(Doreen) | Chandpur 150 MW CCPP | Chandpur 200MW (Desh energy) | Chowmuhani 113 MW | Cumilla 25 MW PP (Summit) | Feni Lanka Power | Import (Tripura) | Jangalia 52 MW PP (Lakdanavi) | Sonagazi 75 MW (AC) Solar Power Plant | Titas 50 MW Peaking PP | Bibiana-II 341 MW CCPP (Summit) | Bibiyana South 400 MW | Bibiyana-III 400 MW CCPP | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Kushiara 163 MW CCPP (KP) | Shahjahanulla 25 MW PP | Shahjibazar 100 MW GTPP | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar GTPP Unit- 8 & 9 | Shajibazar 330 MW CCPP | Sylhet 20 MW GTPP | Sylhet 225 MW CCPP | Bhairob 54.5 MW | Jamalpur 115 MW PP (United) | Mymensingh 200 MW PP (United) | RPCL 210MW CCPP | Sarishabari 3 MW Solar Plant | Sutiakhali 50 MW Solar PP | Tangail Palli Power Gen 22 MW | Eastern Total | Bheramara (HVDC ) | Bheramara 410 MW CCPP | Bheramara GTPP Unit-3 | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | HVDC(Nepal) | Khulna 225 MW CCPP (HSD) | Khulna 225 MW CCPP (Gas) | Khulna 330 MW CCPP (HSD) | Khulna 330 MW CCPP (Gas) | Madhumati 100 MW PP | Mongla Orion 100 MW Solar PP | Rampal 1320 MW (BIFPCL) | Rupsha 105 MW PP (Orion rupsha) | Adani Power Jharkhanda Ltd | Baghabari 100 MW GTPP | Baghabari 50 MW Peaking PP | Baghabari 71 MW GTPP | Bagura 113 MW PP (Confidence)-2 | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Confidence Power Bogura Unit-1 113 MW | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Pabna Solar 100 MW | Santahar 50 MW Peaking PP | Sirajganj 68 MW Solar Park | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1 (HSD) | Sirajgonj 225MW CCPP Unit-2 (Gas) | Sirajgonj 225MW CCPP Unit-2 (HSD) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (HSD) | Sirajgonj 400 MW CCPP Unit-4 (Gas) | Sirajgonj 400 MW CCPP Unit-4 (HSD) | Sirajgonj 6.55 MW Solar | Barapukuria 275 MW TPP Unit-3 | Barapukuria TPP Unit-1 & 2 | Energypac Power Venture Thakurgaon Ltd. | Intraco Solar 30 MW | Rangpur 113 MW PP (Confidence) | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sympa Solar Power 8 MW | Teesta Solar Limited | Barisal 1 MW Solar Plant | Barisal 110 MW PP (Summit ) | Barisal 307 MW | Bhola 33 MW PP (Venture) | Bhola 225 MW CCPP | Bhola Nutan Biddut BD LTD (Gas) | Bhola Nutan Biddut BD LTD (HSD) | Patuakhali 1320 MW (RNPL) | Payra 1320 MW | United Payra Power Ltd. | Western Total | National Grid Total | Water Level
| 102.000 MW | 105.000 MW | 52.194 MW | 365.000 MW | 260.000 MW | 240.000 MW | 190.000 MW | 97.700 MW | 400.750 MW | 20.000 MW | 0.000 MW | 53.970 MW | 55.000 MW | 149.000 MW | 149.360 MW | 300.000 MW | 55.000 MW | 55.000 MW | 162.000 MW | 104.000 MW | 450.000 MW | 335.000 MW | 583.000 MW | 583.000 MW | 55.000 MW | 335.000 MW | 210.000 MW | 115.000 MW | 35.000 MW | 160.000 MW | 33.750 MW | 23.000 MW | 105.000 MW | 584.000 MW | 116.000 MW | 300.000 MW | 108.000 MW | 360.000 MW | 60.000 MW | 102.000 MW | 98.000 MW | 54.360 MW | 100.000 MW | 100.000 MW | 6.000 MW | 230.000 MW | 110.000 MW | 42.000 MW | 1150.000 MW | 159.860 MW | 159.860 MW | 50.000 MW | 25.500 MW | 105.000 MW | 225.000 MW | 225.000 MW | 150.000 MW | 150.000 MW | 1224.000 MW | 20.000 MW | 51.000 MW | 150.000 MW | 195.000 MW | 393.000 MW | 353.350 MW | 356.560 MW | 55.000 MW | 221.430 MW | 46.701 MW | 115.000 MW | 163.000 MW | 200.000 MW | 113.000 MW | 25.000 MW | 114.000 MW | 160.000 MW | 52.200 MW | 75.000 MW | 52.000 MW | 341.000 MW | 383.000 MW | 400.000 MW | 90.000 MW | 90.000 MW | 163.000 MW | 25.000 MW | 100.000 MW | 86.000 MW | 66.000 MW | 330.000 MW | 20.000 MW | 231.000 MW | 54.500 MW | 115.000 MW | 200.000 MW | 210.000 MW | 2.710 MW | 50.000 MW | 22.000 MW | - | 1000.000 MW | 410.000 MW | 16.000 MW | 54.000 MW | 109.000 MW | 0.000 MW | 230.000 MW | 230.000 MW | 336.000 MW | 336.000 MW | 105.000 MW | 100.000 MW | 1234.200 MW | 105.000 MW | 1435.880 MW | 100.000 MW | 52.000 MW | 70.000 MW | 113.000 MW | 71.000 MW | 104.000 MW | 113.000 MW | 50.000 MW | 52.200 MW | 100.000 MW | 50.000 MW | 68.000 MW | 214.000 MW | 214.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 220.000 MW | 413.790 MW | 413.790 MW | 6.090 MW | 274.000 MW | 170.000 MW | 115.000 MW | 30.000 MW | 113.000 MW | 20.000 MW | 20.000 MW | 8.000 MW | 200.000 MW | 1.000 MW | 110.000 MW | 307.000 MW | 10.000 MW | 194.000 MW | 220.000 MW | 220.000 MW | 0.000 MW | 1244.000 MW | 150.000 MW | - | - | -
00:00 | 0 | 88 | 16 | 0 | 0 | 0 | 0 | 0 | 373 | 0 | 0 | 17 | 54 | 62 | 145 | 0 | 0 | 0 | 0 | 0 | 400 | 147 | 430 | 0 | 0 | 280 | 0 | 0 | 0 | 70 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 35 | 360 | 0 | 0 | 0 | 8 | 0 | 223 | 0 | 0 | 0 | 1224 | 0 | 51 | 0 | 36 | 0 | 356 | 340 | 51 | 192 | 28 | 115 | 0 | 167 | 13 | 14 | 96 | 38 | 7 | 0 | 0 | 260 | 320 | 361 | 34 | 30 | 156 | 6 | 0 | 83 | 28 | 0 | 18 | 162 | 0 | 73 | 110 | 22 | 0 | 0 | 12 | 7326 | 921 | 271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1150 | 0 | 1362.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 50 | 35 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 10 | 60 | 220 | 0 | 0 | 1244 | 0 | 6402.8 | 13728.8 | 85.95
01:00 | 0 | 52 | 8 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 17 | 54 | 34 | 145 | 0 | 0 | 0 | 0 | 0 | 400 | 144 | 430 | 0 | 0 | 270 | 0 | 0 | 0 | 70 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 35 | 360 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1104 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 51 | 191 | 31 | 94 | 0 | 153 | 9 | 14 | 95 | 36 | 8 | 0 | 0 | 260 | 320 | 353 | 32 | 30 | 136 | 6 | 0 | 83 | 28 | 0 | 18 | 162 | 0 | 45 | 94 | 22 | 0 | 0 | 12 | 6965 | 922 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1129 | 0 | 1317.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 | 200 | 50 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 9 | 60 | 220 | 0 | 0 | 1150 | 0 | 6204.73 | 13169.73 | 86.03
02:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 17 | 54 | 34 | 145 | 0 | 0 | 0 | 0 | 0 | 400 | 143 | 430 | 0 | 0 | 278 | 0 | 0 | 0 | 70 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 35 | 360 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1100 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 50 | 189 | 31 | 90 | 0 | 157 | 9 | 14 | 99 | 34 | 8 | 0 | 0 | 260 | 320 | 332 | 32 | 30 | 134 | 6 | 0 | 83 | 28 | 0 | 18 | 162 | 0 | 37 | 103 | 22 | 0 | 0 | 12 | 6898 | 927 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1022 | 0 | 1214.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 395 | 0 | 0 | 200 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 60 | 220 | 0 | 0 | 1100 | 0 | 5862.2 | 12760.2 | 86.11
03:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 54 | 34 | 145 | 0 | 0 | 0 | 0 | 0 | 400 | 146 | 430 | 0 | 0 | 285 | 0 | 0 | 0 | 70 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 35 | 360 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1020 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 50 | 197 | 31 | 86 | 0 | 153 | 9 | 14 | 100 | 34 | 8 | 0 | 0 | 260 | 320 | 309 | 32 | 30 | 130 | 0 | 0 | 83 | 28 | 0 | 18 | 162 | 0 | 37 | 104 | 22 | 0 | 0 | 12 | 6762 | 926 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1011 | 0 | 1006.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 200 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 60 | 220 | 0 | 0 | 1050 | 0 | 5617.77 | 12379.77 | 86.19
04:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 314 | 0 | 0 | 0 | 35 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 400 | 141 | 430 | 0 | 0 | 265 | 0 | 0 | 0 | 52 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 26 | 360 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1010 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 50 | 183 | 31 | 89 | 0 | 148 | 9 | 11 | 95 | 34 | 0 | 0 | 0 | 265 | 320 | 290 | 32 | 30 | 129 | 6 | 0 | 83 | 28 | 0 | 18 | 162 | 0 | 37 | 104 | 34 | 0 | 0 | 12 | 6627 | 927 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 939 | 0 | 922.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 200 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 60 | 220 | 0 | 0 | 950 | 0 | 5342.26 | 11969.26 | 86.27
05:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 323 | 0 | 0 | 0 | 17 | 17 | 110 | 0 | 0 | 0 | 0 | 0 | 330 | 138 | 430 | 0 | 0 | 282 | 0 | 0 | 0 | 52 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 36 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 879 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 47 | 191 | 31 | 90 | 0 | 68 | 9 | 11 | 75 | 34 | 0 | 0 | 0 | 270 | 320 | 301 | 32 | 30 | 132 | 6 | 0 | 83 | 28 | 0 | 18 | 162 | 0 | 37 | 104 | 34 | 0 | 0 | 12 | 6335 | 926 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 830 | 0 | 833.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 200 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 60 | 220 | 0 | 0 | 816 | 0 | 4872.37 | 11207.37 | 86.35
06:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 17 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 330 | 135 | 460 | 0 | 0 | 283 | 0 | 0 | 3 | 52 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 36 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 36 | 0 | 355 | 340 | 47 | 197 | 33 | 68 | 0 | 34 | 9 | 13 | 62 | 34 | 0 | 0 | 0 | 265 | 320 | 361 | 32 | 30 | 141 | 6 | 0 | 83 | 30 | 0 | 18 | 162 | 0 | 8 | 8 | 34 | 0 | 0 | 12 | 6105 | 927 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.58 | 760 | 0 | 820.58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 185 | 50 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.02 | 0 | 150 | 9 | 60 | 180 | 0 | 0 | 707 | 0 | 4598.48 | 10703.48 | 86.43
07:00 | 0 | 17 | 8 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 23 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 136 | 480 | 0 | 0 | 265 | 0 | 0 | 2 | 0 | 19 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 30 | 360 | 0 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 | 800 | 0 | 51 | 0 | 55 | 0 | 355 | 340 | 47 | 181 | 33 | 68 | 0 | 32 | 9 | 14 | 28 | 32 | 0 | 1 | 0 | 265 | 320 | 348 | 32 | 30 | 151 | 6 | 0 | 83 | 30 | 0 | 18 | 162 | 0 | 0 | 0 | 35 | 0 | 0.47 | 0 | 5955.47 | 927 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.36 | 763 | 0 | 820.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 4.76 | 140 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 0.47 | 185 | 50 | 0 | 3 | 0 | 0 | 0 | 0.7 | 3 | 0.04 | 0 | 150 | 8 | 60 | 220 | 0 | 0 | 650 | 0 | 4640.63 | 10596.1 | 86.51
08:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 151 | 350 | 0 | 0 | 290 | 0 | 0 | 9 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 5 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 759 | 0 | 51 | 0 | 63 | 0 | 300 | 300 | 44 | 209 | 33 | 70 | 0 | 30 | 9 | 14 | 34 | 32 | 0 | 5 | 0 | 265 | 320 | 392 | 32 | 30 | 152 | 6 | 0 | 83 | 30 | 0 | 18 | 162 | 0 | 0 | 0 | 34 | 1 | 2.07 | 0 | 5734.07 | 883 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.96 | 760 | 0 | 820.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 13.55 | 140 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 1.35 | 185 | 50 | 0 | 9 | 0 | 0 | 0 | 1.7 | 38 | 0.07 | 0 | 150 | 8 | 60 | 220 | 0 | 0 | 580 | 0 | 4653.68 | 10387.75 | 86.59
09:00 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 0 | 0 | 37 | 16 | 0 | 0 | 4 | 0 | 0 | 370 | 152 | 400 | 0 | 0 | 277 | 0 | 0 | 7 | 0 | 13 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 155 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 803 | 0 | 51 | 0 | 63 | 0 | 353 | 340 | 46 | 221 | 33 | 70 | 0 | 35 | 9 | 14 | 59 | 30 | 0 | 3 | 0 | 265 | 320 | 355 | 32 | 30 | 153 | 0 | 0 | 81 | 30 | 0 | 18 | 162 | 0 | 35 | 30 | 30 | 1 | 20.4 | 2 | 6107.4 | 883 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 758 | 0 | 817.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 16.12 | 157 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 1.22 | 196 | 50 | 0 | 23 | 0 | 0 | 0 | 4 | 160 | 0.11 | 0 | 150 | 7 | 60 | 220 | 0 | 0 | 615 | 0 | 4881.19 | 10988.59 | 86.67
10:00 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 19 | 65 | 32 | 0 | 0 | 17 | 0 | 0 | 370 | 148 | 450 | 0 | 0 | 280 | 0 | 0 | 28 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 34 | 0 | 0 | 155 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 850 | 0 | 43 | 0 | 63 | 0 | 357 | 340 | 48 | 193 | 30 | 70 | 0 | 66 | 9 | 0 | 58 | 18 | 0 | 7 | 0 | 265 | 320 | 367 | 32 | 30 | 156 | 0 | 0 | 81 | 30 | 0 | 18 | 162 | 0 | 37 | 64 | 30 | 1 | 40.11 | 10 | 6413.11 | 930 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 761 | 0 | 825.53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 34.18 | 191 | 0 | 0 | 0 | 0 | 0 | 405 | 0 | 2.71 | 200 | 50 | 0 | 29 | 0 | 0 | 0 | 3.7 | 161 | 0.15 | 0 | 195 | 7 | 60 | 220 | 0 | 0 | 650 | 0 | 5105.27 | 11518.38 | 86.75
11:00 | 0 | 35 | 24 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 35 | 68 | 32 | 0 | 0 | 17 | 0 | 0 | 400 | 152 | 520 | 0 | 0 | 305 | 0 | 0 | 28 | 17 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 51 | 0 | 1 | 155 | 0 | 2 | 360 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 865 | 0 | 43 | 0 | 63 | 0 | 356 | 340 | 48 | 206 | 30 | 69 | 0 | 65 | 9 | 0 | 68 | 28 | 0 | 33 | 0 | 265 | 320 | 400 | 34 | 30 | 155 | 0 | 0 | 81 | 30 | 0 | 18 | 161 | 0 | 46 | 70 | 29 | 2 | 32.09 | 12 | 6705.09 | 930 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 820 | 0 | 821.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 54.08 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.95 | 200 | 51 | 0 | 32 | 0 | 0 | 0 | 6.8 | 193 | 0.41 | 0 | 200 | 6 | 60 | 220 | 0 | 0 | 770 | 0 | 5415.06 | 12120.15 | 86.83
12:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 35 | 67 | 32 | 0 | 0 | 25 | 17 | 0 | 400 | 153 | 520 | 0 | 0 | 294 | 0 | 0 | 22 | 17 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 51 | 24 | 1 | 155 | 0 | 4 | 360 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 0 | 0 | 1005 | 0 | 43 | 0 | 63 | 0 | 355 | 340 | 48 | 205 | 32 | 69 | 0 | 66 | 9 | 0 | 66 | 28 | 0 | 8 | 0 | 260 | 320 | 383 | 33 | 30 | 153 | 0 | 0 | 81 | 30 | 0 | 18 | 162 | 0 | 55 | 96 | 29 | 2 | 46.15 | 11 | 6923.15 | 930 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 919 | 0 | 957.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 60.2 | 195 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 4.96 | 200 | 51 | 35 | 30 | 0 | 0 | 0 | 7.9 | 188 | 0.4 | 0 | 200 | 4 | 60 | 220 | 0 | 0 | 930 | 0 | 5878.22 | 12801.37 | 86.91
13:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 344 | 0 | 0 | 0 | 35 | 67 | 48 | 0 | 0 | 35 | 17 | 0 | 420 | 138 | 583 | 0 | 0 | 282 | 0 | 0 | 24 | 30 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 63 | 24 | 1 | 155 | 0 | 4 | 361 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1050 | 0 | 43 | 0 | 63 | 0 | 355 | 340 | 49 | 198 | 33 | 69 | 0 | 68 | 9 | 0 | 60 | 30 | 0 | 36 | 0 | 265 | 320 | 362 | 34 | 30 | 156 | 0 | 0 | 83 | 30 | 0 | 18 | 162 | 0 | 55 | 103 | 28 | 1 | 46.25 | 11 | 7114.25 | 930 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 992 | 0 | 1076.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 0 | 58.06 | 195 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 5.02 | 200 | 49 | 35 | 32 | 0 | 0 | 0 | 8 | 195 | 0.23 | 0 | 200 | 7 | 60 | 220 | 0 | 0 | 1020 | 0 | 6144.54 | 13258.79 | 87.01
14:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 35 | 56 | 48 | 0 | 0 | 35 | 17 | 0 | 420 | 143 | 540 | 0 | 0 | 276 | 0 | 0 | 21 | 35 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 51 | 24 | 0 | 155 | 0 | 4 | 360 | 0 | 0 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 1100 | 0 | 43 | 0 | 63 | 0 | 354 | 340 | 48 | 190 | 33 | 69 | 0 | 65 | 16 | 6 | 67 | 32 | 0 | 19 | 0 | 260 | 320 | 376 | 33 | 30 | 153 | 0 | 0 | 82 | 30 | 0 | 18 | 162 | 0 | 55 | 101 | 28 | 2 | 42.42 | 11 | 7073.42 | 930 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 1006 | 0 | 1219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 50.55 | 195 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 4.36 | 200 | 50 | 35 | 29 | 0 | 0 | 0 | 7 | 164 | 0.31 | 0 | 200 | 6 | 60 | 220 | 0 | 0 | 1060 | 0 | 6259.22 | 13332.64 | 87.11
15:00 | 0 | 52 | 24 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 35 | 50 | 48 | 0 | 0 | 35 | 17 | 0 | 420 | 165 | 583 | 0 | 0 | 285 | 0 | 0 | 22 | 35 | 23 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 51 | 24 | 1 | 156 | 0 | 3 | 362 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1188 | 4 | 43 | 0 | 63 | 0 | 350 | 340 | 47 | 202 | 33 | 68 | 0 | 65 | 9 | 6 | 60 | 34 | 0 | 32 | 0 | 265 | 320 | 365 | 34 | 30 | 156 | 6 | 0 | 81 | 30 | 0 | 18 | 163 | 0 | 55 | 90 | 23 | 2 | 33.95 | 7 | 7227.95 | 930 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 1079 | 0 | 1214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 38.37 | 193 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 3.5 | 200 | 50 | 35 | 16 | 0 | 0 | 0 | 4.8 | 135 | 0.02 | 0 | 200 | 5 | 60 | 220 | 0 | 0 | 1100 | 0 | 6287.69 | 13515.64 | 87.21
16:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 35 | 50 | 80 | 0 | 0 | 35 | 17 | 0 | 370 | 181 | 583 | 0 | 0 | 266 | 0 | 0 | 13 | 52 | 19.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 51 | 24 | 1 | 155 | 0 | 5 | 510 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1154 | 3 | 43 | 0 | 63 | 0 | 346 | 340 | 45 | 182 | 33 | 69 | 0 | 60 | 9 | 6 | 58 | 36 | 0 | 12 | 0 | 260 | 320 | 348 | 33 | 30 | 140 | 6 | 0 | 84 | 30 | 0 | 18 | 163 | 0 | 63 | 85 | 23 | 1 | 29.62 | 6 | 7220.12 | 930 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 1082 | 0 | 1209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 23.41 | 192 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 2.28 | 200 | 50 | 35 | 11 | 0 | 0 | 0 | 2.6 | 88 | 0.08 | 0 | 200 | 3 | 60 | 220 | 0 | 0 | 1140 | 0 | 6170.37 | 13390.49 | 87.33
17:00 | 0 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 346 | 0 | 0 | 0 | 35 | 50 | 78 | 0 | 0 | 35 | 17 | 0 | 370 | 280 | 500 | 0 | 0 | 266 | 0 | 0 | 9 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 70 | 24 | 0 | 155 | 0 | 8 | 575 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1206 | 1 | 43 | 0 | 63 | 0 | 300 | 340 | 47 | 183 | 33 | 44 | 0 | 65 | 9 | 10 | 63 | 34 | 0 | 4 | 0 | 265 | 320 | 348 | 34 | 30 | 132 | 6 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 63 | 87 | 11 | 0 | 12.83 | 6 | 7264.83 | 930 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1048 | 0 | 1119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 11.59 | 192 | 0 | 0 | 0 | 0 | 0 | 324 | 0 | 1.08 | 200 | 50 | 0 | 7 | 0 | 0 | 0 | 1.8 | 37 | 0.03 | 0 | 200 | 6 | 60 | 180 | 0 | 0 | 1092 | 0 | 5815.5 | 13080.33 | 87.45
18:00 | 0 | 88 | 27 | 0 | 0 | 0 | 0 | 0 | 357 | 0 | 0 | 0 | 35 | 50 | 78 | 0 | 0 | 35 | 17 | 0 | 420 | 90 | 350 | 0 | 0 | 302 | 0 | 0 | 3 | 52 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 70 | 24 | 0 | 155 | 0 | 5 | 567 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 | 1165 | 0 | 43 | 0 | 63 | 0 | 348 | 320 | 42 | 208 | 33 | 35 | 0 | 100 | 20 | 12 | 65 | 34 | 0 | 1 | 0 | 265 | 320 | 345 | 34 | 30 | 144 | 6 | 0 | 83 | 30 | 0 | 18 | 164 | 0 | 64 | 97 | 16 | 0 | 4.46 | 8 | 7112.46 | 930 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.68 | 912 | 0 | 1123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 2.75 | 150 | 0 | 8 | 0 | 0 | 0 | 397 | 0 | 0.22 | 200 | 50 | 35 | 1 | 34 | 0 | 0 | 0.4 | 11 | 0.01 | 0 | 200 | 6 | 60 | 220 | 0 | 0 | 942 | 0 | 5605.06 | 12717.52 | 87.57
19:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 365 | 0 | 0 | 35 | 44 | 95 | 145 | 0 | 0 | 35 | 51 | 3 | 420 | 135 | 480 | 0 | 30 | 295 | 0 | 0 | 0 | 155 | 24 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 50 | 38 | 0 | 90 | 24 | 0 | 155 | 5 | 8 | 568 | 0 | 0 | 4 | 1 | 12 | 219 | 0 | 0 | 0 | 1195 | 0 | 43 | 61 | 63 | 0 | 332 | 315 | 49 | 207 | 33 | 34 | 0 | 105 | 28 | 12 | 72 | 38 | 16 | 0 | 39 | 265 | 320 | 383 | 34 | 30 | 151 | 7 | 0 | 84 | 30 | 0 | 18 | 164 | 8 | 63 | 109 | 11 | 0 | 0 | 12 | 7990 | 883 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 991 | 0 | 1121 | 0 | 4 | 0 | 35 | 0 | 96 | 0 | 12 | 0 | 0 | 22 | 0 | 154 | 0 | 3 | 0 | 0 | 0 | 368 | 0 | 0 | 200 | 50 | 79 | 0 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 120 | 220 | 0 | 0 | 980 | 9 | 5967 | 13957 | 87.69
19:30 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 328 | 0 | 0 | 54 | 54 | 149 | 145 | 0 | 0 | 35 | 130 | 16 | 420 | 165 | 536 | 0 | 35 | 266 | 0 | 0 | 0 | 160 | 24 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 30 | 50 | 39 | 0 | 100 | 24 | 0 | 155 | 20 | 5 | 568 | 0 | 0 | 18 | 8 | 30 | 219 | 0 | 0 | 0 | 1195 | 0 | 43 | 120 | 63 | 0 | 356 | 340 | 49 | 183 | 33 | 34 | 0 | 149 | 28 | 15 | 114 | 38 | 43 | 0 | 40 | 260 | 320 | 368 | 34 | 30 | 148 | 7 | 0 | 84 | 30 | 0 | 18 | 164 | 17 | 63 | 110 | 33 | 0 | 0 | 12 | 8482 | 883 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1173 | 13 | 1213 | 0 | 20 | 0 | 80 | 0 | 96 | 0 | 19 | 0 | 0 | 25 | 0 | 180 | 0 | 3 | 0 | 0 | 0 | 323 | 0 | 0 | 200 | 50 | 110 | 0 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 120 | 220 | 0 | 0 | 1200 | 17 | 6569 | 15051
20:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 54 | 54 | 140 | 143 | 0 | 0 | 17 | 128 | 16 | 420 | 175 | 520 | 0 | 35 | 265 | 0 | 0 | 0 | 160 | 24 | 22 | 0 | 0 | 0 | 15 | 0 | 0 | 38 | 50 | 52 | 0 | 70 | 0 | 0 | 155 | 28 | 10 | 567 | 0 | 0 | 18 | 8 | 44 | 219 | 0 | 0 | 0 | 1224 | 0 | 43 | 118 | 8 | 0 | 357 | 340 | 49 | 183 | 33 | 34 | 0 | 145 | 28 | 15 | 114 | 38 | 43 | 0 | 40 | 260 | 320 | 300 | 35 | 30 | 135 | 7 | 0 | 84 | 30 | 0 | 18 | 164 | 17 | 64 | 110 | 33 | 0 | 0 | 12 | 8332 | 883 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1218 | 0 | 47 | 0 | 50 | 0 | 96 | 0 | 37 | 0 | 0 | 30 | 0 | 183 | 0 | 3 | 0 | 0 | 0 | 324 | 0 | 0 | 200 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 8 | 110 | 180 | 0 | 0 | 1200 | 17 | 6619.2 | 14951.2 | 87.81
21:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 54 | 54 | 78 | 143 | 0 | 0 | 0 | 112 | 16 | 420 | 273 | 520 | 0 | 17 | 276 | 0 | 0 | 0 | 160 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 49 | 63 | 0 | 70 | 0 | 0 | 155 | 17 | 17 | 567 | 0 | 0 | 0 | 8 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 80 | 8 | 0 | 356 | 340 | 50 | 190 | 33 | 29 | 0 | 155 | 29 | 15 | 114 | 38 | 43 | 0 | 40 | 265 | 320 | 309 | 35 | 30 | 140 | 7 | 0 | 84 | 30 | 0 | 18 | 164 | 0 | 63 | 110 | 32 | 0 | 0 | 12 | 8255 | 931 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.2 | 17 | 1211.34 | 0 | 28 | 0 | 50 | 0 | 96 | 0 | 0 | 0 | 0 | 30 | 0 | 186 | 0 | 20 | 0 | 0 | 0 | 331 | 0 | 0 | 200 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 10 | 110 | 220 | 0 | 0 | 1244 | 17 | 6717.54 | 14972.54 | 87.93
22:00 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 0 | 334 | 0 | 0 | 35 | 54 | 78 | 144 | 0 | 0 | 0 | 35 | 16 | 370 | 289 | 480 | 0 | 0 | 264 | 0 | 0 | 0 | 142 | 24 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 63 | 0 | 70 | 0 | 0 | 155 | 0 | 19 | 568 | 0 | 0 | 0 | 8 | 17 | 219 | 0 | 0 | 0 | 1224 | 0 | 51 | 30 | 8 | 0 | 356 | 340 | 50 | 183 | 33 | 34 | 0 | 152 | 29 | 15 | 114 | 38 | 43 | 0 | 40 | 270 | 320 | 301 | 35 | 30 | 149 | 7 | 0 | 84 | 28 | 0 | 18 | 165 | 0 | 81 | 128 | 47 | 0 | 0 | 12 | 7991 | 931 | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1179 | 17 | 1218.22 | 0 | 0 | 0 | 35 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 83 | 0 | 0 | 0 | 325 | 0 | 0 | 200 | 50 | 115 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 11 | 110 | 220 | 0 | 0 | 1140 | 0 | 6477.22 | 14468.22 | 88.05
23:00 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 333 | 0 | 0 | 17 | 35 | 60 | 144 | 0 | 0 | 0 | 17 | 0 | 370 | 293 | 400 | 0 | 0 | 282 | 0 | 0 | 0 | 125 | 24.5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 48 | 0 | 0 | 155 | 0 | 20 | 565 | 0 | 0 | 0 | 8 | 0 | 223 | 0 | 0 | 0 | 1130 | 0 | 25 | 0 | 8 | 0 | 300 | 340 | 49 | 196 | 33 | 34 | 0 | 188 | 29 | 15 | 114 | 34 | 43 | 0 | 40 | 265 | 320 | 325 | 35 | 30 | 149 | 7 | 0 | 84 | 28 | 0 | 18 | 164 | 0 | 81 | 145 | 44 | 0 | 0 | 12 | 7564.5 | 931 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1031 | 0 | 1078.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 129 | 0 | 0 | 0 | 345 | 0 | 0 | 200 | 49 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 10 | 120 | 220 | 0 | 0 | 1100 | 0 | 5915.91 | 13480.41 | 88.17
Total KWH | 0 | 1179840 | 463013 | 0 | 0 | 0 | 0 | 0 | 8139600 | 0 | 0 | 250920 | 914760 | 1321632 | 2020320 | 0 | 0 | 375749 | 519840 | 67200 | 9242000 | 4180480 | 11200000 | 0 | 78077 | 6887039 | 0 | 0 | 190126 | 1476000 | 468000 | 484560 | 0 | 0 | 0 | 45164 | 0 | 0 | 442080 | 165326 | 211248 | 0 | 914880 | 198720 | 5402 | 3732060 | 80290 | 410400 | 10370909.09 | 0 | 0 | 28800 | 44859.6 | 108727 | 5305298 | 0 | 0 | 0 | 24856361 | 9450 | 1074024 | 347927 | 1120727 | 0 | 8610400 | 8164000 | 1148640 | 4785000 | 781200 | 1521600 | 0 | 2471520 | 344400 | 227290 | 1895820 | 792960 | 268997 | 145109 | 210224 | 6376500 | 7642900 | 8728000 | 785000 | 709456 | 3490773 | 82752 | 0 | 1991040 | 705408 | 0 | 432000 | 3437540 | 29160 | 1146000 | 2083200 | 648000 | 14600 | 307690 | 230640 | 169139627.69 | 22266909 | 7271424 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 493200 | 23185450 | 51840 | 25181073 | 0 | 65773 | 0 | 233376 | 0 | 296848 | 0 | 50840 | 0 | 657840 | 74048 | 373496 | 4317727 | 0 | 454091 | 0 | 0 | 0 | 8832000 | 0 | 32460 | 4804000 | 1144145 | 638039 | 220744 | 590688 | 0 | 0 | 45622.68 | 1328400 | 2005 | 0 | 4560000 | 186563 | 1768000 | 5319400 | 0 | 0 | 24258909.09 | 46800 | 138751710.77 | 307891338.46

## P1
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
System Summary Report
|  | Date : | 02-06-2025
Power Supply Scenario
| Day Peak Generation |  |  | 12801.37 | MW | 12:00 Hr. | Energy Generated |  |  | 307.8913 |  | MKWHr.
| Day Peak Demand |  |  | 12801.37 | MW | 12:00 Hr. | Energy Unserverd |  |  | 0.138 |  | MKWHr.
| Evening Peak Generation |  |  | 15051 | MW | 19:30 Hr. | Energy Demand |  |  | 308.0293 |  | MKWHr.
| Evening Peak Demand |  |  | 15100 | MW | 19:30 Hr. | Maximum Temperature |  |  | 31.2 |  | °C
| Minimum Generation of the Day |  |  | 10387.75 | MW | 08:00 Hr. | Total Gas Supplied |  |  | 939.01 |  | MMCFD
| Maximum Generation of the Day |  |  | 15051 | MW | 19:30 Hr. | Production Cost per KWHr |  |  | 6.0702 |  | Tk.
Zone-wise Generation Summary (MKWHr.)
|  |  |  | Gas | Coal | HFO | HSD | Hydro | Solar | Import | Wind | Total
| Dhaka Zone |  |  | 40.6017 | 0 | 8.6674 | 0 | 0 | 0.19013 | 0 | 0 | 49.4592 | Gas | 135.4072 | Gas | 480894632.88
| Chattogram Zone |  |  | 5.7157 | 35.2273 | 1.798 | 0 | 3.7321 | 0.014852 | 0 | 0.44208 | 46.93 | Coal | 93.1798 | Coal | 646161153.5603
| Cumilla Zone |  |  | 25.9113 | 0 | 7.0605 | 0 | 0 | 0.14511 | 0.79296 | 0 | 33.9098 | HFO | 23.0631 | HFO | 430083163.652
| Mymensingh Zone |  |  | 0.648 | 0 | 3.489 | 0 | 0 | 0.32229 | 0 | 0 | 4.4593 | HSD | 0 | HSD | 0
| Sylhet Zone |  |  | 34.3814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.3814 | Hydro | 3.7321 | Hydro | 373206
| Khulna Zone |  |  | 7.2714 | 23.1854 | 0.05184 | 0 | 0 | 0.4932 | 22.2669 | 0 | 53.2688 | Solar | 3.8261 | Solar | 64158041.9548
| Barishal Zone |  |  | 7.274 | 28.8189 | 0.0468 | 0 | 0 | 0.002005 | 0 | 0 | 36.1417 | Import | 48.2409 | Import | 240817001.16
| Rajshahi Zone |  |  | 13.6038 | 0 | 0.72088 | 0 | 0 | 1.0638 | 25.1811 | 0 | 40.5696 | Wind | 0.44208 | Wind | 6472051.2
| Rangpur Zone |  |  | 0 | 5.9481 | 1.2287 | 0 | 0 | 1.5948 | 0 | 0 | 8.7716
| Total |  |  | 135.4072 | 93.1798 | 23.0631 | 0 | 3.7321 | 3.8261 | 48.2409 | 0.44208 | 307.8913
Production Cost (Tk.)
|  |  |  | Fuel | Tk. |  | Fuel | Tk.
|  |  |  | Gas | 480894632.88 |  | Hydro | 373206
|  |  |  | Coal | 646161153.5603 |  | Solar | 64158041.9548
|  |  |  | HFO | 430083163.652 |  | Import | 240817001.16
|  |  |  | HSD | 0 |  | Wind | 6472051.2
[5 empty] | Total: | 186,89,59,250 |  | Tk.
E-W Interconnector & Import Scenario
Energy Flow from East to West: |  |  | KWHr: | 0 |  | Import through HVDC C/B Interconnector: |  |  | MKWHr: | 22.2669 | Peak Hr Flow | 883.00 MW at 19:30 hrs.
Energy Flow from West to East: |  |  | KWHr: | 35876636.45 |  | Import through Adani C/B Interconnector: |  |  | MKWHr: | 25.1811 | Peak Hr Flow | 1213.00 MW at 19:30 hrs.
Power Flow during Peak Demand: |  |  | MW: | 422 |  | Import through Cumilla C/B Interconnector: |  |  | MKWHr: | 0.79296 | Peak Hr Flow | 38.00 MW at 19:30 hrs.
Maximum Power Flow: |  |  | MW: | 1052 |  | Total Import through C/B Interconnector: |  |  | MKWHr: | 48.2409 | Peak Hr Flow | 2134.00 MW at 19:30 hrs.
Zone-wise Load-shed and Demand Summary (MW) at evening peak Hour (19:30 Hr.)
|  |  |  | Zone |  | Load-Shed |  | Demand
|  |  |  | Dhaka |  | 0 |  | 5201
|  |  |  | Chattogram |  | 0 |  | 1357
|  |  |  | Cumilla |  | 0 |  | 1345
|  |  |  | Mymensingh |  | 47 |  | 1154
|  |  |  | Sylhet |  | 0 |  | 515
|  |  |  | Khulna |  | 0 |  | 1865
|  |  |  | Barishal |  | 0 |  | 435
|  |  |  | Rajshahi |  | 0 |  | 1583
|  |  |  | Rangpur |  | 0 |  | 1031
|  |  |  | Total |  | 47 |  | 14486
Status of unavailable Power Plant
|  | Planned S/D |  |  |  |  | Forced S/D
|  | Sl | Plant Name |  |  | Capacity | Sl | Plant Name |  |  | Capacity
|  | 1 | Baghabari 100 MW GTPP |  |  | 100 | 1 | Amnura 50 MW PP(Sinha) |  |  | 0
|  | 2 | Barapukuria TPP Unit-2 |  |  | 85 | 2 | Ashuganj 420 MW CCPP(East) GT |  |  | 284
|  | 3 | Siddhirgonj 210 MW TPP |  |  | 115 | 3 | Ashuganj 420 MW CCPP(East) ST |  |  | 116
[5 empty] | Total | 300 |  |  |  | Total | 400
|  |  |  | Total Unavailable Capacity |  |  |  | 700
Event Summary
| Outage Time | Restoration Time | Description of Event | [7 empty] | Description of Event
|  | 08:03 | Haripur-Madanganj 132kV Ckt-1 is restored.
| 08:21 | 09:43 | Bhaluka 132/33kV S/S Transformer- 01 LT Scheduled S/D Due to High temperature minimize | [7 empty] | 20.0MW load
interrup.
| 08:22 | 09:42 | Bhaluka 132/33kV S/S Transformer- 01 HT Scheduled S/D Due to High temperature minimize.
| 08:25 | 10:16 | Mymensingh 132/33kV S/S Transformer-3 (424T) LT Scheduled S/D Due to Due to High | [7 empty] | 20.0MW load
|  |  | temperature maintenance work in 33kV Capacitor bank-3 bus DS Y ph clamp of Tr-3 | [7 empty] | interrup.
Transformer.
|  | 08:49 | Madaripur 132/33kV S/S T3-426T HT is restored.
|  | 08:49 | Madaripur 132/33kV S/S T3-426T LT is restored.
|  | 09:18 | Rangpur-Saidpur 132kV Ckt-1 is restored.
|  | 09:19 | Rangpur-Saidpur 132kV Ckt-2 is restored.
|  | 09:28 | Magura 132/33kV S/S T-2 (415T) HT is restored.
|  | 09:34 | Faridpur 132/33kV S/S Transformer-1 HT is restored.
|  | 09:34 | Faridpur 132/33kV S/S Transformer-1 LT is restored.
| 09:34 | 17:33 | Bogura 400/230kV S/S ATR-03 HT Project Work S/D Due to DS operating Box Chance
| 09:34 | 17:34 | Bogura 400/230kV S/S ATR-03 LT Project Work S/D Due to DS operating Box Chance
|  | 09:35 | Faridpur 132/33kV S/S Transformer-3 HT is restored.
|  | 09:38 | Faridpur 132/33kV S/S Transformer-3 LT is restored.
|  | 10:16 | Mymensingh 132/33kV S/S Transformer-3 (424T) HT is restored.
| 10:24 | 12:51 | Bhaluka-Mymensingh 132 kV Ckt-1 Scheduled S/D from Mymensingh 132/33kV end Due to Due to
High temperature maintenance work in Gas Circuit Breaker Y-Ph upper clamp and Line DS Y -
Ph Breaker side . and from Bhaluka 132/33kV end Due to Work at Mymensingh end(High
temperature minimize).
| 11:10 | 13:58 | Aminbazar-Kallyanpur 132kV Ckt-1 Scheduled S/D from Kallyanpur 132/33kV end Due to CT Ten
delta Test
| 11:13 | 12:21 | Bhaluka 132/33kV S/S Bus A Scheduled S/D Due to Temperature minimize at Mymensingh
circuit1 (Bus DS)
| 11:35 | 13:24 | Barishal 230/132kV S/S T-4 HT Scheduled S/D Due to Korapur 33 kV Feeder maintenance | [7 empty] | 10.0MW load
interrup.
| 11:35 | 13:27 | Barishal 230/132kV S/S T-4 LT Scheduled S/D Due to Korapur 33 kV Feeder maintenance | [7 empty] | 10.0MW load
interrup.
| 13:04 | 14:47 | Mymensingh 132/33kV S/S Transformer-2 (414T) LT Scheduled S/D Due to Due to High
temperature maintenance work in HV bush B-ph and 132KV GCB Y ph clamp of Tr-2
Transformer.
| 13:04 | 14:47 | Mymensingh 132/33kV S/S Transformer-2 (414T) HT Scheduled S/D
| 13:04 |  | Bogura 400/230kV S/S 400 KV Reactor (125 MVAR) Forced S/D Due to ALDC Bogura Instruction.
| 13:07 |  | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Manikganj 132/33kV end Due to
Circuit -1 B-phase top "T" connector Redhot removal
|  | 14:02 | Khagrachori 132/33kV S/S TR-1 HT is restored.
|  | 14:07 | Khagrachori 132/33kV S/S TR-1 LT is restored.
| 14:11 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1
| 15:32 |  | Rooppur-Gopalgonj 400 kv ckt charge from Gopalgonj(N) S/S.
|  | 15:41 | Rangpur-Rangpur Confidence(100MW) 132kV Ckt-1 is restored.
|  | 16:25 | Netrakona 132/33kV S/S Transformer-1 (415T) HT is restored.
| 16:57 |  | Moghbazar-Rampura 132kV Ckt-2 Forced S/D from Rampura 230/132kV end.
| 17:00 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 17:01 |  | Sirajgonj 225MW CCPP Unit-2 GT Synchronized with remarks:- None
| 17:01 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- GT
| 17:10 | 17:24 | Bashundhara-Rampura 132 kV Ckt-1 Tripped from Rampura 230/132kV end showing Distance
protection 21/1, C.N. relays Due to Unknown
|  | 18:36 | Madanganj 132/33kV S/S GT-2 HT is restored.
|  | 18:46 | Madanganj 132/33kV S/S GT-2 LT is restored.
| 19:24 |  | Meghnaghat CCPP(Summit) Synchronized with remarks:- GT1
| 19:30 |  | Evening peak Generation is 15051 MW
| 20:24 |  | Sirajgonj 225MW CCPP Unit-2 ST Synchronized with remarks:- None
| 20:24 |  | Sirajgonj 225MW CCPP Unit-2 Synchronized with remarks:- ST
| 21:41 | 07:52 | Rangpur-Saidpur 132kV Ckt-2 Scheduled S/D from Saidpur 132/33kV end Due to QF- GMD-39
and as the instruction of NLDC (299727) 132 KV Saidpur - Rangpur ckt.-2 (Y phase) Red
hot)
| 21:46 |  | Meghnaghat CCPP(Summit), FGMO is ON with remarks:-
| 22:48 |  | Gopalganj-Ruppur CKT is tripped from Gopalganj end by Showing Distance B-Phase,199.99 km.
| 23:07 | 00:29 | Bhaluka 132/33kV S/S Bus Section- 01 Forced S/D Due to 33 kV feeder red hot minimize & | [7 empty] | 60.0MW load
|  |  | maintenance (Feeder no 12 & 09) | [7 empty] | interrup.
| 23:25 | 00:42 | Bogura 230/132kV S/S Confidance UN-1 Tripped showing Gen. Trip, Zone-1, R-Phase relays
Due to Rain & Storming
| 23:25 |  | Bogura 400/230kV S/S Bogura - Kaliakoir 400 kV Ckt-2 Tripped showing Lockout Relay KT86.1
Operated Lockout Relay KT86.2 Operated Drirectional Earth Fault DMT (87N)
Trip Distance =M1 28.0 km /M2 87.4 km Current = (R-Phase = 14.67 A, Y-Phase = 82.57 A,
B-Phase = 15.31 A) relays Due to Lockout Relay KT86.1 Operated Lockout Relay KT86.2
Operated Drirectional Earth Fault DMT (87N) Trip Distance =M1 28.0 km /M2 87.4
km Current = (R-Phase = 14.67 A, Y-Phase = 82.57 A, B-Phase = 15.31 A)
| 23:45 | 00:18 | Lalmonirhat-Rangpur 132 kV Ckt-2 Tripped from Rangpur 132/33kV end showing A-phase
,Distance Relay relays Due to A-phase ,Distance Relay
| 23:49 | 00:07 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Tripped showing SIPROTECH 7UT 86 | [7 empty] | 80.0MW load
|  |  | relays Due to Thunderstorm | [7 empty] | interrup.
| 23:49 | 00:07 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Tripped showing SIPROTECH 7UT86 | [7 empty] | 44.0MW load
|  |  | relays Due to Thunderstorm | [7 empty] | interrup.
| 23:52 | 00:47 | Sirajganj 132/33kV S/S T3-(435) LT Tripped showing Over Current Earth Fault relays Due
to 33 kV Economic Zone Feeder fault
| 23:52 | 00:48 | Sirajganj 132/33kV S/S T4-(445) LT Tripped showing Overcurrent Relay relays Due to 33kV
Economic Zone Feeder faulty
| 23:55 | 00:50 | Bogura 230/132kV S/S Confidance UN-2 Tripped showing Over Voltage relays Due to Rain &
Stroming
| 00:00 | 00:14 | Niamatpur 132/33kV S/S Transformer-1(407T) LT Tripped showing O/C & E/F Relay relays Due | [7 empty] | 3.0MW load
|  |  | to Shapahar feeder fault | [7 empty] | interrup.
| 01:10 | 01:13 | Saidpur 132/33kV S/S TR-2 (404T) LT Tripped showing MCGG relays Due to Fault for 33kv EPZ | [7 empty] | 16.0MW load
|  |  | Feeder. | [7 empty] | interrup.
| 02:07 | 02:38 | Kabirpur -Tongi 132kV Ckt-1 Tripped from Tongi 230/132/33kV end showing R-phase Z1
relays Due to Heavy rain and thunderstorm
| 02:20 | 02:47 | Noapara 132/33kV S/S T-1 LT Tripped showing SIEMENS 7SJ81 relays Due to REB-1 33kV FEEDER | [7 empty] | 0.5MW load
|  |  | FAULT | [7 empty] | interrup.
| 02:20 | 02:47 | Noapara 132/33kV S/S T-2 LT Tripped showing SIEMENS 7SJ81 relays Due to REB-1 33kV FEEDER | [7 empty] | 0.5MW load
|  |  | FAULT | [7 empty] | interrup.
| 02:51 |  | Gopalganj 400/132kV S/S 400kV Rampal Ckt-1 Forced S/D
| 02:53 | 02:57 | Nawabganj 132/33kV S/S TR-2 LT Tripped showing Overcurrent relays. | [7 empty] | 6.5MW load
interrup.
| 02:57 | 02:57 | Nawabganj 132/33kV S/S TR-1 LT Tripped showing Overcurrent relays. | [7 empty] | 6.5MW load
interrup.
| 03:12 | 06:38 | Brahmanbaria 132/33kV S/S 403T LT Tripped showing OCEF relays Due to Over Current Earth | [7 empty] | 16.0MW load
|  |  | fault | [7 empty] | interrup.
| 03:44 | 05:38 | Naogaon 132/33kV S/S T-2 LT Tripped showing MCGG ( E/F) relays Due to 33KV T-1 (Y-phase)
bus PT burst
| 03:44 |  | Naogaon 132/33kV S/S T-1 LT Tripped showing MCGG (O/C, Y-phase & E/F) relays Due to 33KV
T-1 (Y-phase) bus PT burst
| 05:00 |  | Minimum generation 8827 MW
| 06:10 | 06:40 | Halishahar-Julda 132kV Ckt-1 Tripped from Juldah 132/33kV end showing Relay Trip relays.
| 06:10 | 06:43 | Khulshi 132/33kV S/S Khulshi-Halishahar CKT-3 Tripped showing Distance Relay REL670
relays Due to Thunderstorm and heavy rainfall
| 06:23 |  | Madunaghat 132/33kV S/S TR-2(517T) LT Tripped showing RET-650 relays Due to OLTC PRD Trip | [7 empty] | 14.0MW load
interrup.
| 06:23 |  | Madunaghat 132/33kV S/S TR-1(507T) HT Tripped showing RET-650 relays Due to OLTC PRD Trip | [7 empty] | 14.0MW load
interrup.
| 06:43 |  | Dohazari-Sikalbaha 132 kV Ckt-2 Tripped from Shikalbaha 230/132kV end showing rel670
relays.
| 07:01 |  | Bogura 400/230kV S/S Bogura - Rooppur 400 KV Line-1 Project Work S/D Due to Project Work
For Rooppur Side.
| 07:20 |  | Bogura 132/33kV S/S Transformer-3 HT Scheduled S/D Due to maintenance work
| 07:20 |  | Bogura 132/33kV S/S Transformer-3 LT Scheduled S/D Due to maintenance work | [7 empty] | 15.0MW load
interrup.
| 07:39 |  | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to Maintenance | [7 empty] | 21.0MW load
interrup.
| 07:39 |  | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to Maintenance | [7 empty] | 21.0MW load
interrup.
| 07:51 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) LT Scheduled S/D Due to Maintenance Work | [7 empty] | 15.0MW load
interrup.
| 07:52 |  | Rajshahi 132/33kV S/S Transformer T-3 (425T) HT Scheduled S/D Due to Maintenance Work | [7 empty] | 15.0MW load
interrup.
|  | Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
|  | Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division

## P2
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 02-06-2025
Sl. | Name of the Power Stations |  | Producer | Installed Capacity | Present Capacity | Peak Hour Generation | Energy Generated | Remarks
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*260 | 260 | 0 | 0 | GT is under maintenance
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 240 | 0 | 0 | Allocation limit by Titas, instructed by DS(Gen)
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 97.7 | 0 | 0 | Gas restriction by titas
5 | Haripur GTPP |  | SBU,PDB | 32*2 | 20 | 0 | 0 | -
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 400.75 | 328 | 8139600 | -
| Haripur 360 MW CCPP (HPL) |  | IPP | 1*235+1*125 | 0 | 0 | 0 | Contract Expired
7 | Meghnaghat 450 MW CCPP (MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9242000 | -
8 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 165 | 4180480 | FGMO
9 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17+1*11.3 | 55 | 0 | 0 | -
10 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
11 | Narshingdi 22 MW PP (Doreen) |  | SIPP,REB | 8*2.90 | 0 | 0 | 0 | Contract Expired
12 | Siddhirgonj 210 MW TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under Major Overhauling
13 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage+ internal problem at TITAS RMS
14 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 266 | 6887039 | Gas shortage
15 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Liquid fuel shortage
17 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 53.97 | 54 | 250920 | -
18 | Kodda 150 MW PP B-R |  | PDB-RPCL | 9*17.06 | 149.36 | 145 | 2020320 | -
18 | Manikganj 55 MW PP (Northern) |  | IPP | 19.3*3 | 55 | 35 | 375749 | Liquid fuel shortage
20 | Nababganj 55 MW PP (Southern power ) |  | IPP | 19.3*3 | 55 | 35 | 78077 | -
22 | Summit Power Ashulia |  | IPP | 0 | 33.75 | 24 | 468000 | Low gas pressure
22 | Summit Power Madhabdi |  | IPP | 3*3.67+4*8.73 | 23 | 22 | 484560 | -
25 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52.194 | 33 | 463013 | Fuel shortage
26 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under Maintenance of Exciter
27 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.06 | 300 | 0 | 0 | -
28 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 1321632 | Machine Problem
29 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1179840 | Fuel Oil (HFO) Shortage
30 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 6*18.5 | 104 | 16 | 67200 | Liquid fuel shortage
31 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 130 | 519840 | -
32 | Spectra Solar Plant Ltd. |  | IPP | 0 | 35 | 0 | 190126 | -
33 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 54 | 914760 | -
34 | Unique Meghnaghat Power Limited (UMPL) |  | IPP | 0 | 584 | 0 | 0 | Gas shortage
35 | Meghnaghat CCPP(Summit)-2 |  | IPP | 0 | 583 | 536 | 11200000 | -
| JERA Meghnaghat Power Limited |  | IPP | 250*2+268 | 0 | 0 | 0 | -
| Sreepur 150 MW PP |  | PDB-RPCL | 9*18 | 160 | 160 | 1476000 | -
Dhaka Area Total |  |  |  |  | 5939.724 | 2660 | 49459156
36 | Chattogram TPP |  | PDB | 1*210+1*210 | 360 | 0 | 0 | Gas shortage
37 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25.5 | 8 | 44859.6 | -
38 | Teknaf 20MW PP (Solartech) |  | IPP | 0 | 20 | 0 | 9450 | -
39 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 28800 | -
40 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 155 | 3732060 | -
41 | Sikalbaha 225MW CCPP |  | PDB | 1*150+1*75 | 225 | 219 | 5305298 | -
42 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | -
43 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 30 | 108727 | Bill delay
44 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 39 | 211248 | machine problem
45 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 165326 | -
46 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 914880 | -
| Malancha, Ctg. EPZ (United) |  | IPP | 5*8.73+3*9.34 | 42 | 5 | 410400 | -
47 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | -
48 | Kaptai 7 MW Solar PP |  | PDB | 0 | 6 | 0 | 5402 | -
49 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 15 | 45164 | -
50 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54.36 | 0 | 0 | -
51 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 20 | 80290 | -
52 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 24 | 198720 | -
53 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | -
54 | Mirsharai 150 MW |  | IPP | 18.5*9 | 159.86 | 0 | 0 | -
55 | SS Power |  | IPP | 2*660 | 1224 | 1195 | 24856361 | -
56 | Cox's Bazar Wind |  | PDB | 22*3 | 60 | 30 | 442080 | -
57 | Matarbari 2*600 MW (CPGCBL) |  | CPGCL | 2*600 | 1150 | 568 | 10370909.09 | U1 S/D 25/Mar/25
Chattogram Area Total |  |  |  |  | 4895.72 | 2476 | 46929974.69
58 | Ashuganj CCPP 225 MW |  | APSCL | 1X142+1X75 | 221.43 | 183 | 4785000 | FGMO
59 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 353.35 | 356 | 8610400 | -
60 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 356.56 | 340 | 8164000 | -
61 | Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 393 | 0 | 0 | -
62 | Ashuganj TSK 50 MW PP |  | APSCL | 14*3.96 | 46.701 | 33 | 781200 | machine problem
63 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 49 | 1148640 | -
64 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20X9.73+1X16 | 195 | 63 | 1120727 | -
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6X9.34 | 51 | 43 | 1074024 | -
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23X7.015 | 150 | 120 | 347927 | -
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 40 | 210224 | machine problem
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | -
69 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 149 | 2471520 | -
70 | Feni 11 MW PP (Doreen) |  | SIPP,REB | 4*2.90 | 0 | 0 | 0 | Contract Expired
| Import (Tripura) |  | Import | 0 | 160 | 38 | 792960 | -
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52.2 | 43 | 268997 | -
72 | Cumilla 25 MW PP (Summit) |  | SIPP,REB | 3*3.67+2*6.97 | 25 | 15 | 227290 | Machine Under Maintenance
73 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1895820 | -
74 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 28 | 344400 | Liquid fuel Shortage
75 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 34 | 1521600 | -
76 | Sonagazi 75 MW (AC) Solar Power Plant |  | EGCB | 0 | 75 | 0 | 145109 | -
Cumilla Area Total |  |  |  |  | 2891.241 | 1648 | 33909838
77 | RPCL 210MW CCPP |  | RPCL | 4*35+1*70 | 210 | 33 | 648000 | Low gas pressure
79 | Sarishabari 3 MW Solar Plant |  | IPP | 0 | 2.71 | 0 | 14600 | -
80 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 110 | 2083200 | Liquid fuel shortage
81 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 63 | 1146000 | Fuel shortage
82 | Sutiakhali 50 MW Solar PP |  | IPP | 0 | 50 | 0 | 307690 | -
83 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 230640 | From 00:00 to 24:00 hr. will be dispatching 12 MW
84 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54.5 | 17 | 29160 | -
Mymensingh Area Total |  |  |  |  | 654.21 | 235 | 4459290
85 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 90 | 34 | 785000 | FGMO
86 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 709456 | Gas shortage
87 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 148 | 3490773 | FGMO
88 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under Maintenance
89 | Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
91 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 30 | 705408 | -
92 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1991040 | -
93 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | machine problem
94 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 164 | 3437540 | -
95 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 432000 | -
96 | Shahjahanulla 25 MW PP |  | SIPP,REB | 3*9.34 | 25 | 7 | 82752 | -
97 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 6376500 | FGMO
98 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 368 | 8728000 | FGMO Activated
99 | Bibiyana South 400 MW |  | PDB | 1*400 | 383 | 320 | 7642900 | AUTHORITY INSTRUCTION
Sylhet Area Total |  |  |  |  | 2325 | 1463 | 34381369
100 | Bheramara GTPP Unit-3 |  | PDB | 1X20 | 16 | 0 | 0 | Contract Expired
** | Bheramara (HVDC ) |  | Import | 2X500 | 1000 | 883 | 22266909 | -
101 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | -
102 | Khulna 225 MW CCPP |  | NWPGCL | 1X150+1X75 | 230 | 0 | 0 | -
103 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | -
104 | Bheramara 410 MW CCPP |  | NWPGCL | 1X278+1X132 | 410 | 308 | 7271424 | Gas shortage
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 13 | 51840 | Liquid fuel shortage
106 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Liquid fuel shortage
107 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 493200 | -
108 | Khulna 330 MW CCPP |  | PDB | 1*220+1*110 | 336 | 0 | 0 | GT Available
109 | Rampal 1320 MW (BIFPCL) |  | PDB | 660*2 | 1234.2 | 1173 | 23185450 | -
** | HVDC(Nepal) |  | Import | 1*40 | 0 | 0 | 0 | -
Khulna Area Total |  |  |  |  | 3699.2 | 2377 | 53268823
| Patuakhali 1320 MW (RNPL) |  | RNPL | 660*2 | 0 | 0 | 0 | -
110 | Barisal 110 MW PP (Summit ) |  | IPP | 7X17.076 | 110 | 0 | 0 | -
111 | Bhola 33 MW PP (Venture) |  | NENP | 1X34.50 | 10 | 8 | 186563 | -
112 | Bhola 225 MW CCPP |  | PDB | 2X63+1X68 | 194 | 120 | 1768000 | Partial Shutdown of STG
113 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1200 | 24258909.09 | FGMO
114 | Bhola Nutan Biddut BD LTD |  | IPP | 2*110 | 220 | 220 | 5319400 | MVAR Subjected to Grid Voltage
115 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 46800 | -
116 | Barisal 307 MW |  | BCPCL | 307X1 | 307 | 200 | 4560000 | -
117 | Barisal 1 MW Solar Plant |  | IPP | 0 | 1 | 0 | 2005 | -
Barishal Area Total |  |  |  |  | 2236 | 1765 | 36141677.09
118 | Baghabari 71 MW GTPP |  | PDB | 1X71 | 70 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Machine Under Maintenance
119 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 20 | 65773 | -
120 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | -
121 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 19 | 50840 | One Engine is under maintenance
123 | Sirajgonj 225MW CCPP Unit-1 |  | NWPGCL | 1*150+1*75 | 214 | 180 | 4317727 | Gas shortage
124 | Sirajgonj 225MW CCPP Unit-2 |  | NWPGCL | 1*150+1*75 | 220 | 3 | 454091 | Standby @NLDC's instruction due to gas shortage
125 | Sirajgonj 225MW CCPP Unit-3 |  | NWPGCL | 1*141 | 220 | 0 | 0 | Standby as per instruction of NLDC
126 | Sirajgonj 400 MW CCPP Unit-4 |  | NWPGCL | 1*282+1*132 | 413.79 | 323 | 8832000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 74048 | Engine Problem
129 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52.2 | 0 | 0 | -
130 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 296848 | -
131 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 80 | 233376 | -
132 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 0 | -
133 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 0 | 6.09 | 0 | 32460 | -
** | Adani Power Jharkhanda Ltd |  | Import | 2*673 | 1435.88 | 1213 | 25181073 | -
134 | Sirajganj 68 MW Solar Park |  | IPP | 0 | 68 | 0 | 373496 | -
| Pabna Solar 100 MW |  | IPP | 0 | 100 | 0 | 657840 | -
Rajshahi Area Total |  |  |  |  | 3452.96 | 1959 | 40569572
135 | Barapukuria TPP Unit-1 & 2 |  | PDB | 1*125+1*125 | 170 | 50 | 1144145 | Machine Problem
136 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 200 | 4804000 | -
137 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
138 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | -
139 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 108 | 590688 | -
140 | Sympa Solar Power 8 MW |  | IPP | 0 | 8 | 0 | 45622.68 | -
141 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 0 | 115 | 110 | 638039 | -
142 | Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 220744 | -
143 | Teesta Solar Limited |  | BCPCL | 0 | 200 | 0 | 1328400 | -
Rangpur Area Total |  |  |  |  | 950 | 468 | 8771638.68
Eastern Grid Total |  |  |  |  | 16705.895 | 8482 | 169139627.69
Western Grid Total |  |  |  |  | 10338.16 | 6569 | 138751710.77
National Grid Total |  |  |  |  | 27044.055 | 15051 | 307891338.46
*Data collected from respective power station via Operation Information System(OIS) software.
Executive Engineer
Network Operation Division

## P3
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date : | 02-06-2025
Zone Total Scenario at Evening Peak Hour (19:30 Hr.)
(a) ENTIRE EASTERN GRID: |  |  | 9525.79 |  | MW | (b) ENTIRE WESTERN GRID: |  |  |  | 4913.8 | MW
i) Dhaka area |  |  | 5201.45 |  | MW | i) Khulna area |  |  |  | 1865 | MW
ii) Chattogram area |  |  | 1357 |  | MW | ii) Barishal area |  |  |  | 435 | MW
iii) Cumilla area |  |  | 1345.34 |  | MW | iii) Rajshahi area |  |  |  | 1582.8 | MW
iv) Mymensingh area |  |  | 1107 |  | MW | iv) Rangpur area |  |  |  | 1031 | MW
v) Sylhet area |  |  | 515 |  | MW
System Total Demand at Evening Peak Hour (a + b) = | [5 empty] | 14439.59 | MW
Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time | Sl No. | Sub-station | Load (MW) | Time
1 | AKS | 22 | 20:00 | 67 | Ishurdi | 89 | 19:30 | 133 | Patuakhali | 82.5 | 23:00
2 | AKSML | 93 | 03:00 | 68 | Jaldhaka | 88 | 20:00 | 134 | Payra | 36 | 23:00
3 | Aftabnagar | 36 | 18:30 | 69 | Jamalpur | 119 | 23:00 | 135 | Postogola | 53 | 19:00
4 | Agargaon | 114 | 19:00 | 70 | Jashore | 154 | 22:00 | 136 | Purbachal | 18 | 21:00
5 | Agrabad | 80 | 17:00 | 71 | Jhenaidah | 142 | 19:30 | 137 | Purbasadipur | 127 | 21:00
6 | Amnura | 37 | 20:00 | 72 | Joydebpur | 146 | 15:00 | 138 | Rahanpur | 29 | 00:00
7 | Ashuganj | 88 | 00:00 | 73 | Joypurhat | 66 | 22:00 | 139 | Rahim | 24 | 02:00
8 | BSRM | 196 | 19:00 | 74 | Juldah | 16.5 | 12:00 | 140 | Rajbari | 88 | 19:30
9 | Bagerhat | 80 | 00:00 | 75 | KSRM | 27 | 21:00 | 141 | Rajendrapur | 127 | 16:00
10 | Bajitpur | 51 | 21:00 | 76 | Kabirpur | 240 | 15:00 | 142 | Rajshahi | 116 | 21:00
11 | Bakulia | 85 | 19:00 | 77 | Kachua | 81 | 22:00 | 143 | Rajshahi-230 | 100 | 21:00
12 | Banani | 34.4 | 14:00 | 78 | Kallyanpur | 105 | 00:00 | 144 | Ramganj | 116 | 22:00
13 | Bangabhaban | 16 | 16:00 | 79 | Kalurghat | 37 | 10:00 | 145 | Rampur | 35 | 00:00
14 | Barapukuria | 70 | 21:00 | 80 | Kamrangirchar | 62 | 19:00 | 146 | Rangamati | 13 | 08:00
15 | Barguna | 22 | 00:00 | 81 | Kaptai | N/A | N/A | 147 | Rangpur | 160 | 20:00
16 | Barishal | 126 | 13:00 | 82 | Kasba | 32 | 21:00 | 148 | Ruppur | 8.2 | 16:00
17 | Barishal-230 | 94 | 00:00 | 83 | Kazla | 93 | 12:00 | 149 | SSM | 0 | 00:00
18 | Baroaulia | 51 | 10:00 | 84 | Keranigonj | 74 | 19:00 | 150 | Saidpur | 119 | 19:30
19 | Baroirhat | 59 | 19:00 | 85 | Khagrachori | 28 | 19:30 | 151 | Satkhira | 139 | 23:00
20 | Bashundhara | 175 | 15:00 | 86 | Khulna | 71 | 12:00 | 152 | Satmasjid | 100 | 14:00
21 | BashundharaCement | 9 | 13:00 | 87 | Khulshi | 172 | 19:30 | 153 | Savar | 222 | 15:00
22 | Beanibazar | 68 | 00:00 | 88 | Kishoreganj | 137 | 23:00 | 154 | SevenRings | 6.48 | 16:00
23 | Benapole | 74 | 22:00 | 89 | Kodda | 303 | 18:30 | 155 | ShahCement | 22 | 11:00
24 | Bhaluka | 162 | 19:00 | 90 | Kulaura | 41 | 19:30 | 156 | Shahjadpur | 94 | 19:30
25 | Bhandaria | 57 | 23:00 | 91 | Kurigram | 64 | 19:00 | 157 | Shahjibazar | 113 | 21:00
26 | Bhangura | 40 | 19:00 | 92 | Kushtia | 178 | 20:00 | 158 | Shahmirpur | 54 | 00:00
27 | Bheramara(GK) | 75 | 22:00 | 93 | Lalbag | 58 | 18:00 | 159 | Shariatpur | 80 | 22:00
28 | Bhulta | 250 | 19:30 | 94 | Lalmonirhat | 66 | 19:30 | 160 | Sherpur | 140 | 23:00
29 | Bog-Sherpur | 68 | 20:00 | 95 | MI_Cement | 15.5 | 03:00 | 161 | Shikalbaha | 20 | 19:00
30 | Bogura | 181 | 22:00 | 96 | Madanganj | 20 | 19:00 | 162 | Shitalakhya | 83.2 | 12:00
31 | Borhanuddin | 92 | 00:00 | 97 | Madaripur | 107 | 22:00 | 163 | Sholosohor | 41 | 15:00
32 | Brahmanbaria | 127 | 22:00 | 98 | Madartek | 79.73 | 22:00 | 164 | Shyampur | 150 | 00:00
33 | Cantonment | 140 | 14:00 | 99 | Madunaghat | 45 | 19:30 | 165 | Siddhirganj | 118 | 12:00
34 | Chandina | 19.41 | 20:00 | 100 | Magura | 72 | 19:30 | 166 | Sirajganj | 122 | 21:00
35 | Chandpur | 77 | 19:00 | 101 | Mahasthangarh | 86 | 19:30 | 167 | Sonargaon | 110 | 22:00
36 | Chandraghona | 32 | 20:00 | 102 | Manikganj | 139 | 20:00 | 168 | Sreemongol | 68 | 22:00
37 | Chapai | 73 | 20:00 | 103 | Maniknagar | 76 | 14:00 | 169 | Sreepur | 109 | 19:30
38 | Charsaidpur | 47 | 19:30 | 104 | Matarbari | 46 | 19:30 | 170 | Srinagar | 44.71 | 22:00
39 | Chauddagram | 65 | 23:00 | 105 | Matuail | 66 | 12:00 | 171 | Sunamganj | 56 | 21:00
40 | Chhatak | 33 | 19:30 | 106 | Millgate | 87 | 09:00 | 172 | Sylhet | 41 | 21:00
41 | Chowmuhani | 213 | 22:00 | 107 | Mirpur | 115.5 | 19:00 | 173 | Sylhet-132 | 101 | 22:00
42 | Chuadanga | 126 | 22:00 | 108 | Mirsorai | 16 | 14:00 | 174 | TK | 30.5 | 19:00
43 | Coxsbazar | 110 | 20:00 | 109 | Mirzapur | 43 | 19:00 | 175 | Tangail | 181 | 22:00
44 | Cumilla(N) | 145 | 21:00 | 110 | Mithapukur | 70 | 19:30 | 176 | Thakurgaon | 119 | 20:00
45 | Cumilla(S) | 163 | 19:00 | 111 | Modern | N/A | N/A | 177 | Tongi | 123 | 19:30
46 | Daudkandi | 152 | 21:00 | 112 | Mogbazar | 142.8 | 16:00 | 178 | Ullahpara | 44 | 19:30
47 | Dhaka | 62 | 13:00 | 113 | Mongla | 41 | 12:00 | 179 | Ullon | 36 | 22:00
48 | Dhamrai | 138 | 14:00 | 114 | Motijheel | 39 | 13:00 | 180 | Uttara | 76 | 15:00
49 | Dhanmondi | 145 | 13:00 | 115 | Muktagacha | 38 | 23:00 | 181 | UttaraNew | 54 | 19:00
50 | Dohazari | 93 | 21:00 | 116 | Munshiganj | 116 | 21:00 | 182 | Zigatola | 66 | 13:00
51 | Faridpur | 167 | 19:30 | 117 | Muradnagar | 28 | 19:30
52 | Fatullah | 94 | 12:00 | 118 | Mymensingh | 202 | 20:00
53 | Fenchuganj | 36 | 20:00 | 119 | Naogaon | 143 | 19:30
54 | Feni | 113 | 20:00 | 120 | Narail | 63 | 23:00
55 | GPH | 87 | 09:00 | 121 | Narinda | 78 | 13:00
56 | Ghatail | 76 | 19:00 | 122 | Narshingdi | 174 | 22:00
57 | Ghorashal | 15 | 19:00 | 123 | Natore | 165 | 21:00
58 | Ghorashal-230 | 91 | 20:00 | 124 | Nawabganj | 81.4 | 00:00
59 | Goalpara | 42 | 23:00 | 125 | Netrakona | 119 | 23:00
60 | Gollamari | 108 | 23:00 | 126 | New | 81.5 | 12:00
61 | Gopalganj | 108 | 22:00 | 127 | Niamatpur | 79 | 21:00
62 | Gulshan | 114 | 15:00 | 128 | Noapara | 52 | 20:00
63 | Halishahar | 68 | 15:00 | 129 | PHP | 2 | 00:00
64 | HaripurSBU | 186 | 16:00 | 130 | Pabna | 128 | 23:00
65 | Hasnabad | 77 | 19:00 | 131 | Palashbari | 118 | 19:30
66 | Hathazari | 75 | 18:30 | 132 | Panchagarh | 64 | 20:00
| Sub-Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Network Operation Division
(1) Honbl. Advisor |  | (4) Chairman,BERC |  |  | (9) Member,Generation,PDB. | (14) G.M. Commercial Operation |  |  | (20) Director,Public Relation,PDB. | (26) Executive Eng. EMD.
Ministry of Power,Energy & Mineral |  | (5) Chairman, BPDB. |  |  | (10) Member,Distribution,PDB. | (15) C.E. Generation,PDB. |  |  | (21) Director Program, PDB. | (27) NLDC
Resources, GOB. |  | (6) Managing Director, PGCB. |  |  | (11) Member,Transmission & | (16) C.E, (P & D),PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(2) Secy (Power Divn.)Ministry of |  | (7) Member(Power & Industry) |  |  | System Operation,PDB. | (17) C.E. System Operation,PGCB |  |  | (23) Director,Project Planning,PDB.
Power,Energy & Mineral Resources. |  | Planning Commission. |  |  | (12) Member,P&D,PDB. | (18) C.E. Transmission (1&2) PGCB. |  |  | (24) Director,System Planning,PDB.
(3) Director General,Power cell |  | (8) Executive Director (O & M) PGCB. |  |  | (13) C.E (P & D), PGCB. | (19) S.E. System Protection,PGCB. |  |  | (25) Executive Eng.IMD.

## P4
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Hourly Demand, Generation & Load-Shed Report
Date : | 02-06-2025
Hour | Generation | Load-Shed |  | Demand
0:00 | 13728.8 | 0 |  | 13728.8
1:00 | 13169.73 | 0 |  | 13169.73
2:00 | 12760.2 | 0 |  | 12760.2
3:00 | 12379.77 | 0 |  | 12379.77
4:00 | 11969.26 | 0 |  | 11969.26
5:00 | 11207.37 | 0 |  | 11207.37
6:00 | 10703.48 | 0 |  | 10703.48
7:00 | 10596.1 | 0 |  | 10596.1
8:00 | 10387.75 | 0 |  | 10387.75
9:00 | 10988.59 | 0 |  | 10988.59
10:00 | 11518.38 | 0 |  | 11518.38
11:00 | 12120.15 | 0 |  | 12120.15
12:00 | 12801.37 | 0 |  | 12801.37
13:00 | 13258.79 | 0 |  | 13258.79
14:00 | 13332.64 | 0 |  | 13332.64
15:00 | 13515.64 | 0 |  | 13515.64
16:00 | 13390.49 | 0 |  | 13390.49
17:00 | 13080.33 | 0 |  | 13080.33
18:00 | 12717.52 | 0 |  | 12717.52
19:00 | 13957 | 0 |  | 13957
19:30 | 15051 | 47 |  | 15100
20:00 | 14951.2 | 52 |  | 15005.2
21:00 | 14972.54 | 55 |  | 15029.54
22:00 | 14468.22 | 31 |  | 14500.22
23:00 | 13480.41 | 0 |  | 13480.41
Sub-Divisional Engineer |  |  | Executive Engineer
Network Operation Division |  |  | Network Operation Division

## L-Curve
QF-LDC-11
Date | 02-06-2025 |  |  | Power Grid Bangladesh PLC
TIME | EAST GRID | WEST GRID | TOTAL | National Load Dispatch Center (NLDC)
00:00 | 7326 | 6402.8 | 13728.8 | DAILY GENERATION CURVE
00:30 | 7145.5 | 6303.765 | 13449.265
01:00 | 6965 | 6204.73 | 13169.73 | 02-06-2025
01:30 | 6931.5 | 6033.465 | 12964.965
02:00 | 6898 | 5862.2 | 12760.2
02:30 | 6830 | 5739.985 | 12569.985
03:00 | 6762 | 5617.77 | 12379.77
03:30 | 6694.5 | 5480.015 | 12174.515
04:00 | 6627 | 5342.26 | 11969.26
04:30 | 6481 | 5107.315 | 11588.315
05:00 | 6335 | 4872.37 | 11207.37
05:30 | 6220 | 4735.425 | 10955.425
06:00 | 6105 | 4598.48 | 10703.48
06:30 | 6030.235 | 4619.555 | 10649.79
07:00 | 5955.47 | 4640.63 | 10596.1
07:30 | 5844.77 | 4647.155 | 10491.925
08:00 | 5734.07 | 4653.68 | 10387.75
08:30 | 5920.735 | 4767.435 | 10688.17
09:00 | 6107.4 | 4881.19 | 10988.59
09:30 | 6260.255 | 4993.23 | 11253.485
10:00 | 6413.11 | 5105.27 | 11518.38
10:30 | 6559.1 | 5260.165 | 11819.265
11:00 | 6705.09 | 5415.06 | 12120.15
11:30 | 6814.12 | 5646.64 | 12460.76
12:00 | 6923.15 | 5878.22 | 12801.37
12:30 | 7018.7 | 6011.38 | 13030.08
13:00 | 7114.25 | 6144.54 | 13258.79
13:30 | 7093.835 | 6201.88 | 13295.715
14:00 | 7073.42 | 6259.22 | 13332.64
14:30 | 7150.685 | 6273.455 | 13424.14
15:00 | 7227.95 | 6287.69 | 13515.64
15:30 | 7224.035 | 6229.03 | 13453.065
16:00 | 7220.12 | 6170.37 | 13390.49
16:30 | 7242.475 | 5992.935 | 13235.41
17:00 | 7264.83 | 5815.5 | 13080.33
17:30 | 7188.645 | 5710.28 | 12898.925
18:00 | 7112.46 | 5605.06 | 12717.52
18:30 | 7551.23 | 5786.03 | 13337.26
19:00 | 7990 | 5967 | 13957
19:30 | 8482 | 6569 | 15051
20:00 | 8332 | 6619.2 | 14951.2
20:30 | 8293.5 | 6668.37 | 14961.87 |  | Executive Engineer
21:00 | 8255 | 6717.54 | 14972.54 |  | Network Operation Division
21:30 | 8123 | 6597.38 | 14720.38
22:00 | 7991 | 6477.22 | 14468.22
22:30 | 7777.75 | 6196.565 | 13974.315
23:00 | 7564.5 | 5915.91 | 13480.41

## En-Curve
QF-LDC-12
Date | 02-06-2025 | [14 empty] | Power Grid Bangladesh PLC
TIME | Gas-Public | Gas-Pvt | HVDC | Nepal | Tripura | Adani | Hydro | Coal | Solar | HFO-Public | HFO-Pvt | HSD-Public | HSD-Pvt | Wind | Shortage | National Load Dispatch Center (NLDC)
00:00 | 3693 | 1940 | 921 | 0 | 38 | 1362.8 | 155 | 4478 | 0 | 319 | 803 | 0 | 0 | 19 | 0 | DAILY ENERGY CURVE
00:30 | 3662.5 | 1928 | 921.5 | 0 | 37 | 1340.265 | 155 | 4360.5 | 0 | 297 | 726 | 0 | 0 | 21.5 | 0 | 02-06-2025
01:00 | 3632 | 1916 | 922 | 0 | 36 | 1317.73 | 155 | 4243 | 0 | 275 | 649 | 0 | 0 | 24 | 0
01:30 | 3620 | 1914.5 | 924.5 | 0 | 35 | 1265.965 | 155 | 4137.5 | 0 | 257.5 | 634.5 | 0 | 0 | 20.5 | 0 | Energy Generated | 307.8913 |  | MKWHr
02:00 | 3608 | 1913 | 927 | 0 | 34 | 1214.2 | 155 | 4032 | 0 | 240 | 620 | 0 | 0 | 17 | 0 | Energy not Served | 0.138 |  | MKWHr
02:30 | 3611 | 1909.5 | 926.5 | 0 | 34 | 1110.485 | 155 | 3961.5 | 0 | 240 | 608.5 | 0 | 0 | 13.5 | 0 | Total Energy Requirement | 308.0293 |  | MKWHr
03:00 | 3614 | 1906 | 926 | 0 | 34 | 1006.77 | 155 | 3891 | 0 | 240 | 597 | 0 | 0 | 10 | 0
03:30 | 3581 | 1903 | 926.5 | 0 | 34 | 964.515 | 155 | 3800 | 0 | 213.5 | 578 | 0 | 0 | 19 | 0
04:00 | 3548 | 1900 | 927 | 0 | 34 | 922.26 | 155 | 3709 | 0 | 187 | 559 | 0 | 0 | 28 | 0
04:30 | 3527 | 1870.5 | 926.5 | 0 | 34 | 877.815 | 155 | 3497 | 0 | 187 | 494 | 0 | 0 | 19.5 | 0
05:00 | 3506 | 1841 | 926 | 0 | 34 | 833.37 | 155 | 3285 | 0 | 187 | 429 | 0 | 0 | 11 | 0
05:30 | 3532.5 | 1837 | 926.5 | 0 | 34 | 826.975 | 155 | 3148.5 | 5.45 | 148 | 332 | 0 | 0 | 9.5 | 0
06:00 | 3559 | 1833 | 927 | 0 | 34 | 820.58 | 155 | 3012 | 10.9 | 109 | 235 | 0 | 0 | 8 | 0
06:30 | 3541 | 1875 | 927 | 0 | 33 | 820.44 | 155 | 2985 | 28.35 | 67 | 212 | 0 | 0 | 6 | 0
07:00 | 3523 | 1917 | 927 | 0 | 32 | 820.3 | 155 | 2958 | 45.8 | 25 | 189 | 0 | 0 | 4 | 0
07:30 | 3544.5 | 1840.5 | 905 | 0 | 32 | 820.175 | 155 | 2901 | 95.25 | 12.5 | 182.5 | 0 | 0 | 3.5 | 0
08:00 | 3566 | 1764 | 883 | 0 | 32 | 820.05 | 155 | 2844 | 144.7 | 0 | 176 | 0 | 0 | 3 | 0
08:30 | 3617.5 | 1811.5 | 883 | 0 | 31 | 818.895 | 155 | 2888 | 227.775 | 16.5 | 237.5 | 0 | 0 | 1.5 | 0
09:00 | 3669 | 1859 | 883 | 0 | 30 | 817.74 | 155 | 2932 | 310.85 | 33 | 299 | 0 | 0 | 0 | 0
09:30 | 3686.5 | 1868 | 906.5 | 0 | 24 | 821.635 | 155 | 2999 | 352.85 | 62 | 374 | 0 | 0 | 4 | 0
10:00 | 3704 | 1877 | 930 | 0 | 18 | 825.53 | 155 | 3066 | 394.85 | 91 | 449 | 0 | 0 | 8 | 0
10:30 | 3742.5 | 1928 | 930 | 0 | 23 | 823.675 | 155 | 3166 | 464.09 | 99.5 | 479.5 | 0 | 0 | 8 | 0
11:00 | 3781 | 1979 | 930 | 0 | 28 | 821.82 | 155 | 3266 | 533.33 | 108 | 510 | 0 | 0 | 8 | 0
11:30 | 3774 | 1987 | 930 | 0 | 28 | 889.79 | 155 | 3465.5 | 532.47 | 116.5 | 568 | 0 | 0 | 14.5 | 0
12:00 | 3767 | 1995 | 930 | 0 | 28 | 957.76 | 155 | 3665 | 531.61 | 125 | 626 | 0 | 0 | 21 | 0
12:30 | 3745 | 2036 | 930 | 0 | 29 | 1016.995 | 155 | 3768.5 | 545.085 | 139.5 | 638.5 | 0 | 0 | 26.5 | 0
13:00 | 3723 | 2077 | 930 | 0 | 30 | 1076.23 | 155 | 3872 | 558.56 | 154 | 651 | 0 | 0 | 32 | 0
13:30 | 3708.5 | 2055.5 | 930 | 0 | 31 | 1147.615 | 155 | 3924 | 514.1 | 156.5 | 644 | 0 | 0 | 29.5 | 0
14:00 | 3694 | 2034 | 930 | 0 | 32 | 1219 | 155 | 3976 | 469.64 | 159 | 637 | 0 | 0 | 27 | 0
14:30 | 3711 | 2071 | 930 | 0 | 33 | 1216.5 | 155.5 | 4077.5 | 429.64 | 159 | 619 | 0 | 0 | 22 | 0
15:00 | 3728 | 2108 | 930 | 0 | 34 | 1214 | 156 | 4179 | 389.64 | 159 | 601 | 0 | 0 | 17 | 0
15:30 | 3646 | 2079.25 | 930 | 0 | 35 | 1211.5 | 155.5 | 4257.5 | 331.815 | 192.5 | 599 | 0 | 0 | 15 | 0
16:00 | 3564 | 2050.5 | 930 | 0 | 36 | 1209 | 155 | 4336 | 273.99 | 226 | 597 | 0 | 0 | 13 | 0
16:30 | 3546 | 2032.75 | 930 | 0 | 35 | 1164 | 155 | 4353.5 | 202.66 | 225 | 582.5 | 0 | 0 | 9 | 0
17:00 | 3528 | 2015 | 930 | 0 | 34 | 1119 | 155 | 4371 | 131.33 | 224 | 568 | 0 | 0 | 5 | 0
17:30 | 3597.5 | 1905 | 930 | 0 | 34 | 1121 | 155 | 4203.5 | 84.925 | 236 | 628.5 | 0 | 0 | 3.5 | 0
18:00 | 3667 | 1795 | 930 | 0 | 34 | 1123 | 155 | 4036 | 38.52 | 248 | 689 | 0 | 0 | 2 | 0
18:30 | 3687.5 | 1893 | 906.5 | 0 | 36 | 1122 | 155 | 4110 | 19.26 | 465 | 934.5 | 0 | 0 | 8.5 | 0
19:00 | 3708 | 1991 | 883 | 0 | 38 | 1121 | 155 | 4184 | 0 | 682 | 1180 | 0 | 0 | 15 | 0
19:30 | 3656 | 2069 | 883 | 0 | 38 | 1213 | 155 | 4586 | 0 | 715 | 1706 | 0 | 0 | 30 | 47
20:00 | 3584 | 1960 | 883 | 0 | 38 | 1218 | 155 | 4675.2 | 0 | 776 | 1624 | 0 | 0 | 38 | 52
20:30 | 3610.5 | 2043 | 907 | 0 | 38 | 1214.67 | 155 | 4697.2 | 0 | 753 | 1507 | 0 | 0 | 36.5 | 53.5
21:00 | 3637 | 2126 | 931 | 0 | 38 | 1211.34 | 155 | 4719.2 | 0 | 730 | 1390 | 0 | 0 | 35 | 55
21:30 | 3659 | 2097.5 | 931 | 0 | 38 | 1214.78 | 155 | 4640.1 | 0 | 648 | 1303 | 0 | 0 | 34 | 43
22:00 | 3681 | 2069 | 931 | 0 | 38 | 1218.22 | 155 | 4561 | 0 | 566 | 1216 | 0 | 0 | 33 | 31
22:30 | 3714 | 2015.25 | 931 | 0 | 36 | 1148.565 | 155 | 4393 | 0 | 494 | 1058.5 | 0 | 0 | 29 | 15.5
23:00 | 3747 | 1961.5 | 931 | 0 | 34 | 1078.91 | 155 | 4225 | 0 | 422 | 901 | 0 | 0 | 25 | 0
Executive Engineer
Network Operation Division

## Voltage
Power Grid Bangladesh PLC
National Load Dispatch Center (NLDC)
Maximum & Minimum Voltages of Grid Sub-Stations
Date: | 02-06-2025
Substation | Maximum Voltage | Time | Minimum Voltage | Time | Substation | Maximum Voltage | Time | Minimum Voltage | Time
400 kV | KV |  | KV |  | 400 kV | KV |  | KV
Aminbazar | 389 | 07:00 | 372 | 14:00 | Payra | 415 | 07:00 | 404 | 00:00
Ashuganj | 413 | 3:00 | 377 | 14:00 | Rahanpur | 406 | 05:00 | 382 | 13:00
Bhulta | 403 | 07:00 | 376 | 15:00 | Rampal | 402 | 08:00 | 388 | 00:00
Bibiana | 391 | 06:00 | 384 | 00:00
BIPTC | 399 | 08:00 | 387 | 00:00
Bogura | 405 | 05:00 | 374 | 13:00
Gopalganj | 398 | 08:00 | 382 | 00:00
Kaliakoir | 379 | 07:00 | 362 | 15:00
Madunaghat | 398 | 08:00 | 389 | 00:00
Meghnaghat | 392 | 07:00 | 377 | 00:00
230 kV | KV |  | KV |  | 230 kV | KV |  | KV
Agargaon | 227 | 07:00 | 215 | 15:00 | Keranigonj | 225 | 07:00 | 212 | 15:00
AKSML | 232 | 18:30 | 225 | 16:00 | Khulna(S) | 228 | 05:00 | 215 | 19:30
Aminbazar | 229 | 07:00 | 217 | 13:00 | Madunaghat | 233 | 08:00 | 228 | 00:00
Ashuganj | 234 | 08:00 | 221 | 15:00 | Madunaghat-400 | 235 | 07:00 | 229 | 00:00
Ashuganj-400 | 234 | 08:00 | 221 | 15:00 | Maniknagar | 221 | 02:00 | 212 | 15:00
Baghabari | 235 | 06:00 | 223 | 12:00 | Meghnaghat | 230 | 08:00 | 221 | 13:00
Barapukuria | 227 | 23:00 | 214 | 19:30 | Meghnaghat-400 | 225 | 07:00 | 217 | 15:00
Barapukuria-230 | 227 | 23:00 | 214 | 19:30 | Mirsorai | 230 | 10:00 | 220 | 23:00
Barishal | 237 | 18:00 | 226 | 00:00 | Rajshahi | 236 | 05:00 | 220 | 21:00
Bheramara | 234 | 04:00 | 221 | 12:00 | Rampal | 229 | 06:00 | 216 | 21:00
Bhulta | 235 | 07:00 | 213 | 15:00 | Rampur | N/A | N/A | N/A | N/A
Bibiana | 232 | 07:00 | 224 | 00:00 | Rampura | 233 | 07:00 | 211 | 12:00
BIPTC | 236 | 05:00 | 221 | 12:00 | Shikalbaha | 232 | 07:00 | 225 | 00:00
Bogura | 234 | 05:00 | 218 | 13:00 | Shyampur | 224 | 07:00 | 214 | 15:00
Bogura-400 | 235 | 05:00 | 217 | 13:00 | Siddhirganj | 224 | 05:00 | 218 | 18:00
Borhanuddin | 240 | 08:00 | 232 | 00:00 | Sirajgonj | 240 | 10:00 | 230 | 00:00
BSRM | 229 | 06:00 | 221 | 17:00 | Sreepur | 233 | 07:00 | 218 | 15:00
Cumilla(N) | 225 | 10:00 | 215 | 15:00 | Tongi | 227 | 04:00 | 216 | 15:00
Faridpur | 233 | 08:00 | 222 | 00:00
Fenchuganj | 232 | 18:30 | 225 | 11:00
Ghorashal | 230 | 00:00 | 230 | 00:00
Ghorashal-230 | 233 | 07:00 | 214 | 15:00
Gopalganj | 235 | 07:00 | 225 | 00:00
GPH | 231 | 10:00 | 224 | 00:00
Haripur | 223 | 08:00 | 214 | 15:00
Hasnabad | 225 | 07:00 | 214 | 15:00
Hathazari | 234 | 06:00 | 228 | 00:00
Ishurdi | 236 | 05:00 | 224 | 12:00
Jhenaidah | 228 | 18:30 | 213 | 21:00
Kaliakoir | 235 | 06:00 | 221 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Aftabnagar | 135 | 07:00 | 123 | 14:00 | Madartek | 136 | 07:00 | 123 | 14:00
Agargaon | 137 | 07:00 | 128 | 15:00 | Madunaghat | 134 | 18:30 | 130 | 00:00
Agrabad | 134 | 07:00 | 128 | 23:00 | Magura | 132 | 09:00 | 119 | 19:30
AKS | 131 | 06:00 | 127 | 00:00 | Mahasthangarh | 139 | 05:00 | 125 | 19:30
Aminbazar | 134 | 07:00 | 126 | 15:00 | Manikganj | 134 | 05:00 | 122 | 14:00
Amnura | 137 | 18:30 | 120 | 20:00 | Maniknagar | 134 | 07:00 | 127 | 13:00
Ashuganj | 140 | 09:00 | 133 | 23:00 | Matarbari | 128 | 06:00 | 115 | 23:00
Bagerhat | 130 | 05:00 | 117 | 00:00 | Matuail | 129.3 | 07:00 | 124 | 15:00
Bajitpur | 135 | 08:00 | 125 | 23:00 | Millgate | 138 | 04:00 | 126 | 14:00
Bakulia | 134 | 10:00 | 129 | 23:00 | Mirpur | 133 | 07:00 | 123 | 15:00
Banani | 136 | 07:00 | 124 | 15:00 | Mirzapur | 136 | 07:00 | 127 | 19:00
Bangabhaban | 134 | 08:00 | 127 | 13:00 | Mithapukur | 137 | 05:00 | 120 | 10:00
Barapukuria | 140 | 23:00 | 124 | 19:30 | MI_Cement | 130 | 05:00 | 124 | 15:00
Barguna | 135 | 08:00 | 128 | 00:00 | Modern | N/A | N/A | N/A | N/A
Barishal | 131 | 18:00 | 123 | 00:00 | Mogbazar | 137 | 07:00 | 125 | 12:00
Barishal-230 | 132 | 18:00 | 123 | 00:00 | Mongla | 130 | 09:00 | 118 | 00:00
Baroaulia | 133 | 07:00 | 122 | 0:00 | Motijheel | 134 | 08:00 | 127 | 13:00
Baroirhat | 130 | 10:00 | 119 | 00:00 | Muktagacha | 136 | 05:00 | 125 | 01:00
Bashundhara | 138 | 06:00 | 123 | 14:00 | Munshiganj | 130 | 08:00 | 123 | 15:00
BashundharaCement | 129 | 07:00 | 124 | 03:00 | Muradnagar | 130 | 10:00 | 119 | 00:00
Beanibazar | 133 | 09:00 | 126 | 00:00 | Mymensingh | 139 | 06:00 | 116 | 23:00
Benapole | 130 | 18:30 | 118 | 00:00 | Naogaon | 140 | 05:00 | 124 | 00:00
Bhaluka | 135 | 07:00 | 121 | 15:00 | Narail | 132 | 18:30 | 118 | 19:30
Bhandaria | 126 | 17:00 | 114 | 00:00 | Narinda | 134 | 07:00 | 127 | 13:00
Bhangura | 135 | 05:00 | 126 | 12:00 | Narshingdi | 134 | 09:00 | 117 | 19:30
Bheramara | 138 | 04:00 | 131 | 19:30 | Natore | 136 | 05:00 | 126 | 21:00
Bheramara(GK) | 136 | 4:00 | 130 | 21:00 | Nawabganj | 133 | 05:00 | 127 | 00:00
Bhulta | 122 | 08:00 | 117 | 15:00 | Netrakona | 133 | 07:00 | 115 | 21:00
Bog-Sherpur | 139 | 05:00 | 126 | 20:00 | New | 139 | 07:00 | 128 | 14:00
Bogura | 141 | 05:00 | 129 | 19:30 | Niamatpur | 135 | 05:00 | 126 | 13:00
Bogura-230 | 141 | 05:00 | 129 | 13:00 | Noapara | 133 | 07:00 | 122 | 00:00
Brahmanbaria | 135 | 09:00 | 122 | 00:00 | Pabna | 136 | 05:00 | 127 | 19:30
Cantonment | 137 | 07:00 | 128 | 14:00 | Palashbari | 137 | 05:00 | 118 | 19:30
Chandina | 132 | 10:00 | 122 | 15:00 | Panchagarh | 140 | 22:00 | 119 | 17:00
Chandpur | 133 | 10:00 | 117 | 15:00 | Patuakhali | 135 | 18:30 | 130 | 00:00
Chandraghona | 134 | 07:00 | 130 | 00:00 | Payra | 136 | 07:00 | 132 | 00:00
Chapai | 131 | 04:00 | 123 | 01:00 | PHP | 129 | 10:00 | 118 | 00:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Charsaidpur | 130 | 07:00 | 124 | 15:00 | Postogola | 133 | 08:00 | 126 | 15:00
Chauddagram | 129 | 10:00 | 117 | 23:00 | Purbachal | 135 | 07:00 | 122 | 15:00
Chhatak | 132 | 07:00 | 124 | 23:00 | Purbasadipur | 136 | 23:00 | 117 | 10:00
Chowmuhani | 126 | 10:00 | 110 | 19:30 | Rahanpur | 135 | 04:00 | 127 | 19:30
Chuadanga | 131 | 06:00 | 116 | 19:30 | Rahanpur-400 | 136 | 05:00 | 126 | 13:00
Coxsbazar | 123 | 07:00 | 115 | 22:00 | Rahim | 130 | 09:00 | 125 | 13:00
Cumilla(N) | 132 | 10:00 | 122 | 00:00 | Rajbari | 135 | 08:00 | 127 | 00:00
Cumilla(S) | 133 | 10:00 | 120 | 00:00 | Rajendrapur | 136 | 08:00 | 121 | 15:00
Daudkandi | 128 | 09:00 | 117 | 00:00 | Rajshahi | 136 | 05:00 | 127 | 21:00
Dhaka | 136 | 06:00 | 124 | 15:00 | Rajshahi-230 | 137 | 05:00 | 112 | 13:00
Dhamrai | 133 | 04:00 | 123 | 14:00 | Ramganj | 129 | 10:00 | 111 | 15:00
Dhanmondi | 136.7 | 07:00 | 125 | 14:00 | Rampur | 133 | 07:00 | 128 | 00:00
Dohazari | 131 | 06:00 | 124 | 23:00 | Rampura | 136 | 07:00 | 123 | 15:00
Faridpur | 136 | 08:00 | 128 | 23:00 | Rangamati | 133 | 07:00 | 129 | 00:00
Fatullah | 131 | 06:00 | 124 | 15:00 | Rangpur | 133 | 03:00 | 117 | 19:30
Fenchuganj | 138 | 09:00 | 133 | 00:00 | Ruppur | 138 | 05:00 | 130 | 21:00
Feni | 128 | 10:00 | 117 | 00:00 | Saidpur | 138 | 23:00 | 118 | 17:00
Ghatail | 138 | 06:00 | 122 | 19:00 | Satkhira | 130 | 18:30 | 117 | 23:00
Ghorashal | 139 | 14:00 | 130 | 01:00 | Satmasjid | 137 | 07:00 | 128 | 15:00
Goalpara | 135 | 09:00 | 125 | 00:00 | Savar | 132 | 07:00 | 122 | 15:00
Gollamari | 135 | 06:00 | 126 | 00:00 | SevenRings | 139 | 08:00 | 130 | 15:00
Gopalganj | 134 | 07:00 | 125 | 23:00 | ShahCement | 130 | 07:00 | 124 | 15:00
Gopalganj-400 | 136 | 07:00 | 130 | 00:00 | Shahjadpur | 137 | 02:00 | 131 | 21:00
Gulshan | 135 | 07:00 | 124 | 15:00 | Shahjibazar | 138 | 09:00 | 124 | 23:00
Halishahar | 134 | 05:00 | 128 | 00:00 | Shahmirpur | 134 | 06:00 | 122 | 0:00
Haripur | 129 | 04:00 | 125 | 13:00 | Shariatpur | 133 | 07:00 | 125 | 00:00
HaripurSBU | 129 | 04:00 | 125 | 13:00 | Sherpur | 141 | 06:00 | 118 | 19:00
Hasnabad | 132 | 04:00 | 126 | 15:00 | Shikalbaha | 123 | 05:00 | 118 | 00:00
Hathazari | 136 | 06:00 | 131 | 00:00 | Shikalbaha-230 | 135 | 06:00 | 130 | 00:00
Ishurdi | 139 | 05:00 | 131 | 19:30 | Shitalakhya | 130 | 05:00 | 124 | 15:00
Jaldhaka | 138 | 23:00 | 115 | 19:30 | Sholosohor | 133 | 05:00 | 127 | 23:00
Jamalpur | 141 | 06:00 | 123 | 08:00 | Shyampur | 130 | 05:00 | 125 | 00:00
Jashore | 128 | 03:00 | 115 | 19:30 | Shyampur-230 | 131 | 07:00 | 124 | 15:00
Jhenaidah | 133 | 07:00 | 119 | 19:30 | Siddhirganj | 130 | 08:00 | 125 | 12:00
Jhenaidah-230 | 133 | 06:00 | 121 | 21:00 | Sirajganj | 135 | 07:00 | 124 | 19:30
Joydebpur | 135 | 19:00 | 123 | 14:00 | Sonargaon | 129 | 08:00 | 122 | 15:00
Joypurhat | 136 | 04:00 | 121 | 19:30 | Sreemongol | 137 | 09:00 | 127 | 00:00
Juldah | 134 | 13:00 | 129 | 00:00 | Sreepur | 137 | 07:00 | 126 | 12:00
Kabirpur | 137 | 07:00 | 123 | 15:00 | Srinagar | 135 | 07:00 | 127 | 14:00
Kachua | 132 | 10:00 | 117 | 23:00 | SSM | 136 | 03:00 | 132 | 08:00
Kaliakoir | 140 | 07:00 | 128 | 14:00 | Sunamganj | 131 | 08:00 | 123 | 21:00
Kallyanpur | 134 | 03:00 | 125 | 15:00 | Sylhet | 133 | 08:00 | 128 | 00:00
Kalurghat | 132 | 06:00 | 129 | 00:00 | Sylhet-132 | 132 | 06:00 | 129 | 00:00
Kamrangirchar | 136 | 07:00 | 126 | 14:00 | Tangail | 133 | 06:00 | 122 | 19:00
Kaptai | 135 | 9:00 | 133 | 1:00 | Thakurgaon | 138 | 22:00 | 115 | 17:00
Kasba | 129 | 09:00 | 119 | 15:00 | TK | 132 | 04:00 | 129 | 22:00
Kazla | 133 | 06:00 | 127 | 13:00 | Tongi | 139 | 04:00 | 131 | 15:00
Keranigonj | 136 | 08:00 | 127 | 15:00 | Ullahpara | 137 | 05:00 | 126 | 19:30
Khagrachori | 132 | 06:00 | 128 | 00:00 | Ullon | 135 | 07:00 | 124 | 15:00
Khulna | 134 | 05:00 | 125 | 00:00 | Uttara | 133 | 07:00 | 123 | 15:00
Khulna(S) | 135 | 05:00 | 126 | 19:30 | UttaraNew | 133 | 07:00 | 123 | 15:00
Khulshi | 132 | 06:00 | 127 | 00:00 | Zigatola | 135 | 07:00 | 127 | 13:00
Kishoreganj | 135 | 07:00 | 122 | 23:00
Kodda | 134 | 04:00 | 124 | 00:00
KSRM | 134 | 09:00 | 129 | 00:00
Kulaura | 137 | 06:00 | 128 | 22:00
Kurigram | 134 | 05:00 | 115 | 19:30
Kushtia | 133 | 04:00 | 124 | 21:00
Lalbag | 135 | 07:00 | 127 | 13:00
Lalmonirhat | 135 | 05:00 | 116 | 19:30
Madanganj | 129 | 07:00 | 124 | 00:00
Madaripur | 134 | 07:00 | 127 | 00:00
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division